1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.66 | hwiACMETERChannel1L2PhaseNegativeReactiveEnergy | Channel 1 L2 phase negative reactive energy | 通道1L2相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 L2 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.67 | hwiACMETERChannel1L3PhaseNegativeReactiveEnergy | Channel 1 L3 phase negative reactive energy | 通道1L3相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 L3 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.68 | hwiACMETERChannel1TotalApparentEnergy | Channel 1 total apparent energy | 通道1总视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 total apparent energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.69 | hwiACMETERChannel1PhaseApparentEnergyL1 | Channel 1 phase apparent energy L1 | 通道1L1相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 phase apparent energy L1 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.70 | hwiACMETERChannel1PhaseApparentEnergyL2 | Channel 1 phase apparent energy L2 | 通道1L2相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 phase apparent energy L2 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.71 | hwiACMETERChannel1PhaseApparentEnergyL3 | Channel 1 phase apparent energy L3 | 通道1L3相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 phase apparent energy L3 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.72 | hwiACMETERChannel1L1PhaseCurrentPhaseAngle | Channel 1 L1 phase current phase angle | 通道1L1相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 1 L1 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.73 | hwiACMETERChannel1L2PhaseCurrentPhaseAngle | Channel 1 L2 phase current phase angle | 通道1L2相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 1 L2 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.74 | hwiACMETERChannel1L3PhaseCurrentPhaseAngle | Channel 1 L3 phase current phase angle | 通道1L3相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 1 L3 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.75 | hwiACMETERChannel1L1PhaseCurrentThd | Channel 1 L1 phase current THD | 通道1L1相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 1 L1 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.76 | hwiACMETERChannel1L2PhaseCurrentThd | Channel 1 L2 phase current THD | 通道1L2相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 1 L2 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.77 | hwiACMETERChannel1L3PhaseCurrentThd | Channel 1 L3 phase current THD | 通道1L3相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 1 L3 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.78 | hwiACMETERChannel2L1PhaseCurrent | Channel 2 L1 phase current | 通道2L1相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 2 L1 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.79 | hwiACMETERChannel2L2PhaseCurrent | Channel 2 L2 phase current | 通道2L2相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 2 L2 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.80 | hwiACMETERChannel2L3PhaseCurrent | Channel 2 L3 phase current | 通道2L3相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 2 L3 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.81 | hwiACMETERChannel2ThreePhaseAverageCurrent | Channel 2 three-phase average current | 通道2三相平均电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Channel 2 three-phase average current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.82 | hwiACMETERChannel2TotalActivePower | Channel 2 total active power | 通道2总有功功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 2 total active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.83 | hwiACMETERChannel2TotalReactivePower | Channel 2 total reactive power | 通道2总无功功率 | 0-Read_Only | 只读 | -480000..480000 | -480000..480000 | Channel 2 total reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.84 | hwiACMETERChannel2TotalApparentPower | Channel 2 total apparent power | 通道2总视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 2 total apparent power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.85 | hwiACMETERChannel2L1PhaseActivePower | Channel 2 L1 phase active power | 通道2L1相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 2 L1 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.86 | hwiACMETERChannel2L2PhaseActivePower | Channel 2 L2 phase active power | 通道2L2相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 2 L2 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.87 | hwiACMETERChannel2L3PhaseActivePower | Channel 2 L3 phase active power | 通道2L3相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 2 L3 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.88 | hwiACMETERChannel2L1PhaseReactivePower | Channel 2 L1 phase reactive power | 通道2L1相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 2 L1 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.89 | hwiACMETERChannel2L2PhaseReactivePower | Channel 2 L2 phase reactive power | 通道2L2相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 2 L2 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.90 | hwiACMETERChannel2L3PhaseReactivePower | Channel 2 L3 phase reactive power | 通道2L3相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 2 L3 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.91 | hwiACMETERChannel2ApparentPowerOfL1Phase | Channel 2 apparent power of L1 phase | 通道2L1相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 2 apparent power of L1 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.92 | hwiACMETERChannel2ApparentPowerOfL2Phase | Channel 2 apparent power of L2 phase | 通道2L2相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 2 apparent power of L2 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.93 | hwiACMETERChannel2ApparentPowerOfL3Phase | Channel 2 apparent power of L3 phase | 通道2L3相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 2 apparent power of L3 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.94 | hwiACMETERChannel2TotalPowerFactor | Channel 2 total power factor | 通道2总功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 2 total power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.95 | hwiACMETERChannel2L1PhasePowerFactor | Channel 2 L1 phase power factor | 通道2L1相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 2 L1 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.96 | hwiACMETERChannel2L2PhasePowerFactor | Channel 2 L2 phase power factor | 通道2L2相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 2 L2 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.97 | hwiACMETERChannel2L3PhasePowerFactor | Channel 2 L3 phase power factor | 通道2L3相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 2 L3 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.98 | hwiACMETERChannel2TotalPositiveActiveEnergy | Channel 2 total positive active energy | 通道2总正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 2 total positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.99 | hwiACMETERChannel2L1PhasePositiveActiveEnergy | Channel 2 L1 phase positive active energy | 通道2L1相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 2 L1 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.100 | hwiACMETERChannel2L2PhasePositiveActiveEnergy | Channel 2 L2 phase positive active energy | 通道2L2相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 2 L2 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.101 | hwiACMETERChannel2L3PhasePositiveActiveEnergy | Channel 2 L3 phase positive active energy | 通道2L3相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 2 L3 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.102 | hwiACMETERChannel2TotalNegativeActiveEnergy | Channel 2 total negative active energy | 通道2总负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 2 total negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.103 | hwiACMETERChannel2L1PhaseNegativeActiveEnergy | Channel 2 L1 phase negative active energy | 通道2L1相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 2 L1 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.104 | hwiACMETERChannel2L2PhaseNegativeActiveEnergy | Channel 2 L2 phase negative active energy | 通道2L2相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 2 L2 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.105 | hwiACMETERChannel2L3PhaseNegativeActiveEnergy | Channel 2 L3 phase negative active energy | 通道2L3相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 2 L3 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.106 | hwiACMETERChannel2TotalPositiveReactiveEnergy | Channel 2 total positive reactive energy | 通道2总正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 total positive reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.107 | hwiACMETERChannel2L1PhaseForwardReactiveEnergy | Channel 2 L1 phase forward reactive energy | 通道2L1相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 L1 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.108 | hwiACMETERChannel2L2PhaseForwardReactiveEnergy | Channel 2 L2 phase forward reactive energy | 通道2L2相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 L2 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.109 | hwiACMETERChannel2L3PhaseForwardReactiveEnergy | Channel 2 L3 phase forward reactive energy | 通道2L3相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 L3 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.110 | hwiACMETERChannel2TotalNegativeReactiveEnergy | Channel 2 total negative reactive energy | 通道2总负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 total negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.111 | hwiACMETERChannel2L1PhaseNegativeReactiveEnergy | Channel 2 L1 phase negative reactive energy | 通道2L1相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 L1 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.112 | hwiACMETERChannel2L2PhaseNegativeReactiveEnergy | Channel 2 L2 phase negative reactive energy | 通道2L2相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 L2 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.113 | hwiACMETERChannel2L3PhaseNegativeReactiveEnergy | Channel 2 L3 phase negative reactive energy | 通道2L3相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 L3 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.114 | hwiACMETERChannel2TotalApparentEnergy | Channel 2 total apparent energy | 通道2总视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 total apparent energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.115 | hwiACMETERChannel2PhaseApparentEnergyL1 | Channel 2 phase apparent energy L1 | 通道2L1相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 phase apparent energy L1 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.116 | hwiACMETERChannel2PhaseApparentEnergyL2 | Channel 2 phase apparent energy L2 | 通道2L2相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 phase apparent energy L2 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.117 | hwiACMETERChannel2PhaseApparentEnergyL3 | Channel 2 phase apparent energy L3 | 通道2L3相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 2 phase apparent energy L3 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.118 | hwiACMETERChannel2L1PhaseCurrentPhaseAngle | Channel 2 L1 phase current phase angle | 通道2L1相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 2 L1 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.119 | hwiACMETERChannel2L2PhaseCurrentPhaseAngle | Channel 2 L2 phase current phase angle | 通道2L2相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 2 L2 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.120 | hwiACMETERChannel2L3PhaseCurrentPhaseAngle | Channel 2 L3 phase current phase angle | 通道2L3相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 2 L3 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.121 | hwiACMETERChannel2L1PhaseCurrentThd | Channel 2 L1 phase current THD | 通道2L1相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 2 L1 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.122 | hwiACMETERChannel2L2PhaseCurrentThd | Channel 2 L2 phase current THD | 通道2L2相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 2 L2 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.123 | hwiACMETERChannel2L3PhaseCurrentThd | Channel 2 L3 phase current THD | 通道2L3相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 2 L3 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.124 | hwiACMETERChannel3L1PhaseCurrent | Channel 3 L1 phase current | 通道3L1相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 3 L1 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.125 | hwiACMETERChannel3L2PhaseCurrent | Channel 3 L2 phase current | 通道3L2相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 3 L2 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.126 | hwiACMETERChannel3L3PhaseCurrent | Channel 3 L3 phase current | 通道3L3相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 3 L3 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.127 | hwiACMETERChannel3ThreePhaseAverageCurrent | Channel 3 three-phase average current | 通道3三相平均电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Channel 3 three-phase average current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.128 | hwiACMETERChannel3TotalActivePower | Channel 3 total active power | 通道3总有功功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 3 total active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.129 | hwiACMETERChannel3TotalReactivePower | Channel 3 total reactive power | 通道3总无功功率 | 0-Read_Only | 只读 | -480000..480000 | -480000..480000 | Channel 3 total reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.130 | hwiACMETERChannel3TotalApparentPower | Channel 3 total apparent power | 通道3总视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 3 total apparent power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.131 | hwiACMETERChannel3L1PhaseActivePower | Channel 3 L1 phase active power | 通道3L1相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 3 L1 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.132 | hwiACMETERChannel3L2PhaseActivePower | Channel 3 L2 phase active power | 通道3L2相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 3 L2 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.133 | hwiACMETERChannel3L3PhaseActivePower | Channel 3 L3 phase active power | 通道3L3相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 3 L3 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.134 | hwiACMETERChannel3L1PhaseReactivePower | Channel 3 L1 phase reactive power | 通道3L1相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 3 L1 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.135 | hwiACMETERChannel3L2PhaseReactivePower | Channel 3 L2 phase reactive power | 通道3L2相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 3 L2 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.136 | hwiACMETERChannel3L3PhaseReactivePower | Channel 3 L3 phase reactive power | 通道3L3相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 3 L3 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.137 | hwiACMETERChannel3ApparentPowerOfL1Phase | Channel 3 apparent power of L1 phase | 通道3L1相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 3 apparent power of L1 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.138 | hwiACMETERChannel3ApparentPowerOfL2Phase | Channel 3 apparent power of L2 phase | 通道3L2相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 3 apparent power of L2 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.139 | hwiACMETERChannel3ApparentPowerOfL3Phase | Channel 3 apparent power of L3 phase | 通道3L3相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 3 apparent power of L3 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.140 | hwiACMETERChannel3TotalPowerFactor | Channel 3 total power factor | 通道3总功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 3 total power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.141 | hwiACMETERChannel3L1PhasePowerFactor | Channel 3 L1 phase power factor | 通道3L1相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 3 L1 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.142 | hwiACMETERChannel3L2PhasePowerFactor | Channel 3 L2 phase power factor | 通道3L2相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 3 L2 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.143 | hwiACMETERChannel3L3PhasePowerFactor | Channel 3 L3 phase power factor | 通道3L3相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 3 L3 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.144 | hwiACMETERChannel3TotalPositiveActiveEnergy | Channel 3 total positive active energy | 通道3总正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 3 total positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.145 | hwiACMETERChannel3L1PhasePositiveActiveEnergy | Channel 3 L1 phase positive active energy | 通道3L1相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 3 L1 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.146 | hwiACMETERChannel3L2PhasePositiveActiveEnergy | Channel 3 L2 phase positive active energy | 通道3L2相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 3 L2 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.147 | hwiACMETERChannel3L3PhasePositiveActiveEnergy | Channel 3 L3 phase positive active energy | 通道3L3相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 3 L3 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.148 | hwiACMETERChannel3TotalNegativeActiveEnergy | Channel 3 total negative active energy | 通道3总负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 3 total negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.149 | hwiACMETERChannel3L1PhaseNegativeActiveEnergy | Channel 3 L1 phase negative active energy | 通道3L1相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 3 L1 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.150 | hwiACMETERChannel3L2PhaseNegativeActiveEnergy | Channel 3 L2 phase negative active energy | 通道3L2相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 3 L2 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.151 | hwiACMETERChannel3L3PhaseNegativeActiveEnergy | Channel 3 L3 phase negative active energy | 通道3L3相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 3 L3 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.152 | hwiACMETERChannel3TotalPositiveReactiveEnergy | Channel 3 total positive reactive energy | 通道3总正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 total positive reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.153 | hwiACMETERChannel3L1PhaseForwardReactiveEnergy | Channel 3 L1 phase forward reactive energy | 通道3L1相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 L1 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.154 | hwiACMETERChannel3L2PhaseForwardReactiveEnergy | Channel 3 L2 phase forward reactive energy | 通道3L2相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 L2 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.155 | hwiACMETERChannel3L3PhaseForwardReactiveEnergy | Channel 3 L3 phase forward reactive energy | 通道3L3相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 L3 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.156 | hwiACMETERChannel3TotalNegativeReactiveEnergy | Channel 3 total negative reactive energy | 通道3总负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 total negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.157 | hwiACMETERChannel3L1PhaseNegativeReactiveEnergy | Channel 3 L1 phase negative reactive energy | 通道3L1相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 L1 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.158 | hwiACMETERChannel3L2PhaseNegativeReactiveEnergy | Channel 3 L2 phase negative reactive energy | 通道3L2相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 L2 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.159 | hwiACMETERChannel3L3PhaseNegativeReactiveEnergy | Channel 3 L3 phase negative reactive energy | 通道3L3相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 L3 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.160 | hwiACMETERChannel3TotalApparentEnergy | Channel 3 total apparent energy | 通道3总视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 total apparent energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.161 | hwiACMETERChannel3PhaseApparentEnergyL1 | Channel 3 phase apparent energy L1 | 通道3L1相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 phase apparent energy L1 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.162 | hwiACMETERChannel3PhaseApparentEnergyL2 | Channel 3 phase apparent energy L2 | 通道3L2相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 phase apparent energy L2 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.163 | hwiACMETERChannel3PhaseApparentEnergyL3 | Channel 3 phase apparent energy L3 | 通道3L3相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 3 phase apparent energy L3 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.164 | hwiACMETERChannel3L1PhaseCurrentPhaseAngle | Channel 3 L1 phase current phase angle | 通道3L1相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 3 L1 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.165 | hwiACMETERChannel3L2PhaseCurrentPhaseAngle | Channel 3 L2 phase current phase angle | 通道3L2相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 3 L2 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.166 | hwiACMETERChannel3L3PhaseCurrentPhaseAngle | Channel 3 L3 phase current phase angle | 通道3L3相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 3 L3 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.167 | hwiACMETERChannel3L1PhaseCurrentThd | Channel 3 L1 phase current THD | 通道3L1相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 3 L1 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.168 | hwiACMETERChannel3L2PhaseCurrentThd | Channel 3 L2 phase current THD | 通道3L2相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 3 L2 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.169 | hwiACMETERChannel3L3PhaseCurrentThd | Channel 3 L3 phase current THD | 通道3L3相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 3 L3 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.170 | hwiACMETERChannel4L1PhaseCurrent | Channel 4 L1 phase current | 通道4L1相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 4 L1 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.171 | hwiACMETERChannel4L2PhaseCurrent | Channel 4 L2 phase current | 通道4L2相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 4 L2 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.172 | hwiACMETERChannel4L3PhaseCurrent | Channel 4 L3 phase current | 通道4L3相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 4 L3 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.173 | hwiACMETERChannel4ThreePhaseAverageCurrent | Channel 4 three-phase average current | 通道4三相平均电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Channel 4 three-phase average current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.174 | hwiACMETERChannel4TotalActivePower | Channel 4 total active power | 通道4总有功功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 4 total active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.175 | hwiACMETERChannel4TotalReactivePower | Channel 4 total reactive power | 通道4总无功功率 | 0-Read_Only | 只读 | -480000..480000 | -480000..480000 | Channel 4 total reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.176 | hwiACMETERChannel4TotalApparentPower | Channel 4 total apparent power | 通道4总视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 4 total apparent power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.177 | hwiACMETERChannel4L1PhaseActivePower | Channel 4 L1 phase active power | 通道4L1相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 4 L1 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.178 | hwiACMETERChannel4L2PhaseActivePower | Channel 4 L2 phase active power | 通道4L2相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 4 L2 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.179 | hwiACMETERChannel4L3PhaseActivePower | Channel 4 L3 phase active power | 通道4L3相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 4 L3 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.180 | hwiACMETERChannel4L1PhaseReactivePower | Channel 4 L1 phase reactive power | 通道4L1相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 4 L1 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.181 | hwiACMETERChannel4L2PhaseReactivePower | Channel 4 L2 phase reactive power | 通道4L2相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 4 L2 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.182 | hwiACMETERChannel4L3PhaseReactivePower | Channel 4 L3 phase reactive power | 通道4L3相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 4 L3 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.183 | hwiACMETERChannel4ApparentPowerOfL1Phase | Channel 4 apparent power of L1 phase | 通道4L1相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 4 apparent power of L1 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.184 | hwiACMETERChannel4ApparentPowerOfL2Phase | Channel 4 apparent power of L2 phase | 通道4L2相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 4 apparent power of L2 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.185 | hwiACMETERChannel4ApparentPowerOfL3Phase | Channel 4 apparent power of L3 phase | 通道4L3相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 4 apparent power of L3 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.186 | hwiACMETERChannel4TotalPowerFactor | Channel 4 total power factor | 通道4总功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 4 total power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.187 | hwiACMETERChannel4L1PhasePowerFactor | Channel 4 L1 phase power factor | 通道4L1相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 4 L1 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.188 | hwiACMETERChannel4L2PhasePowerFactor | Channel 4 L2 phase power factor | 通道4L2相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 4 L2 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.189 | hwiACMETERChannel4L3PhasePowerFactor | Channel 4 L3 phase power factor | 通道4L3相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 4 L3 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.190 | hwiACMETERChannel4TotalPositiveActiveEnergy | Channel 4 total positive active energy | 通道4总正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 4 total positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.191 | hwiACMETERChannel4L1PhasePositiveActiveEnergy | Channel 4 L1 phase positive active energy | 通道4L1相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 4 L1 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.192 | hwiACMETERChannel4L2PhasePositiveActiveEnergy | Channel 4 L2 phase positive active energy | 通道4L2相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 4 L2 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.193 | hwiACMETERChannel4L3PhasePositiveActiveEnergy | Channel 4 L3 phase positive active energy | 通道4L3相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 4 L3 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.194 | hwiACMETERChannel4TotalNegativeActiveEnergy | Channel 4 total negative active energy | 通道4总负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 4 total negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.195 | hwiACMETERChannel4L1PhaseNegativeActiveEnergy | Channel 4 L1 phase negative active energy | 通道4L1相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 4 L1 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.196 | hwiACMETERChannel4L2PhaseNegativeActiveEnergy | Channel 4 L2 phase negative active energy | 通道4L2相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 4 L2 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.197 | hwiACMETERChannel4L3PhaseNegativeActiveEnergy | Channel 4 L3 phase negative active energy | 通道4L3相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 4 L3 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.198 | hwiACMETERChannel4TotalPositiveReactiveEnergy | Channel 4 total positive reactive energy | 通道4总正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 total positive reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.199 | hwiACMETERChannel4L1PhaseForwardReactiveEnergy | Channel 4 L1 phase forward reactive energy | 通道4L1相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 L1 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.200 | hwiACMETERChannel4L2PhaseForwardReactiveEnergy | Channel 4 L2 phase forward reactive energy | 通道4L2相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 L2 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.201 | hwiACMETERChannel4L3PhaseForwardReactiveEnergy | Channel 4 L3 phase forward reactive energy | 通道4L3相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 L3 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.202 | hwiACMETERChannel4TotalNegativeReactiveEnergy | Channel 4 total negative reactive energy | 通道4总负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 total negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.203 | hwiACMETERChannel4L1PhaseNegativeReactiveEnergy | Channel 4 L1 phase negative reactive energy | 通道4L1相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 L1 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.204 | hwiACMETERChannel4L2PhaseNegativeReactiveEnergy | Channel 4 L2 phase negative reactive energy | 通道4L2相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 L2 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.205 | hwiACMETERChannel4L3PhaseNegativeReactiveEnergy | Channel 4 L3 phase negative reactive energy | 通道4L3相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 L3 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.206 | hwiACMETERChannel4TotalApparentEnergy | Channel 4 total apparent energy | 通道4总视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 total apparent energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.207 | hwiACMETERChannel4PhaseApparentEnergyL1 | Channel 4 phase apparent energy L1 | 通道4L1相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 phase apparent energy L1 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.208 | hwiACMETERChannel4PhaseApparentEnergyL2 | Channel 4 phase apparent energy L2 | 通道4L2相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 phase apparent energy L2 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.209 | hwiACMETERChannel4PhaseApparentEnergyL3 | Channel 4 phase apparent energy L3 | 通道4L3相视在电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 4 phase apparent energy L3 of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.210 | hwiACMETERChannel4L1PhaseCurrentPhaseAngle | Channel 4 L1 phase current phase angle | 通道4L1相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 4 L1 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.211 | hwiACMETERChannel4L2PhaseCurrentPhaseAngle | Channel 4 L2 phase current phase angle | 通道4L2相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 4 L2 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.212 | hwiACMETERChannel4L3PhaseCurrentPhaseAngle | Channel 4 L3 phase current phase angle | 通道4L3相电流相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 4 L3 phase current phase angle of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.213 | hwiACMETERChannel4L1PhaseCurrentThd | Channel 4 L1 phase current THD | 通道4L1相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 4 L1 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.214 | hwiACMETERChannel4L2PhaseCurrentThd | Channel 4 L2 phase current THD | 通道4L2相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 4 L2 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.215 | hwiACMETERChannel4L3PhaseCurrentThd | Channel 4 L3 phase current THD | 通道4L3相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Channel 4 L3 phase current THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.216 | hwiACMETERDryContact1Status | Dry contact 1 status | 干接点1状态 | 0-Read_Only | 只读 | closed(1), disconnecting(2), unknown(255) | [闭合=1]/[断开=2] | Dry contact 1 status of the device config table for the iACMETER. Value 1 indicate closed Value 2 indicate disconnecting
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.217 | hwiACMETERDryContact2Status | Dry contact 2 status | 干接点2状态 | 0-Read_Only | 只读 | closed(1), disconnecting(2), unknown(255) | [闭合=1]/[断开=2] | Dry contact 2 status of the device config table for the iACMETER. Value 1 indicate closed Value 2 indicate disconnecting
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.218 | hwiACMETERDryContact3Status | Dry contact 3 status | 干接点3状态 | 0-Read_Only | 只读 | closed(1), disconnecting(2), unknown(255) | [闭合=1]/[断开=2] | Dry contact 3 status of the device config table for the iACMETER. Value 1 indicate closed Value 2 indicate disconnecting
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.219 | hwiACMETERCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the iACMETER. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.220 | hwiACMETEREsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.221 | hwiACMETERNumberOfMeterResets | Number of meter resets | 电表复位次数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Number of meter resets of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.222 | hwiACMETERSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.223 | hwiACMETERHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.224 | hwiACMETERIacmeterELable | iACMETER E-lable | iACMETER电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | iACMETER E-lable of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.225 | hwiACMETERNodeANetworkingStatus | Node A networking status | 节点A组网状态 | 0-Read_Only | 只读 | notConnected(1), connected(2), unknown(255) | [未组网=1]/[组网成功=2] | Node A networking status of the device config table for the iACMETER. Value 1 indicate not connected Value 2 indicate connected
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.226 | hwiACMETERNodeANetworkPanId | Node A network PAN ID | 节点A网络PANID | 0-Read_Only | 只读 | 0..7 | 0..7 | Node A network PAN ID of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.227 | hwiACMETERNodeANetworkShortAddress | Node A network short address | 节点A网络短地址 | 0-Read_Only | 只读 | 0..7 | 0..7 | Node A network short address of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.228 | hwiACMETERNodeAMacAddress | Node A MAC address | 节点A MAC地址 | 0-Read_Only | 只读 | 0..24 | 0..24 | Node A MAC address of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.229 | hwiACMETERNodeARssi | Node A RSSI | 节点A RSSI | 0-Read_Only | 只读 | -150..20 | -150..20 | Node A RSSI of the device config table for the iACMETER.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.230 | hwiACMETERVendorType | Vendor type | 厂家类型 | 0-Read_Only | 只读 | yada(1), zdl(2), chint(3), unknown(255) | [雅达=1]/[中电力=2]/[正泰=3] | Vendor type of the device config table for the iACMETER. Value 1 indicate Yada Value 2 indicate ZDL Value 3 indicate CHINT
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.231 | hwiACMETERHardwareVersionOfTheWirelessSubboard | Hardware version of the wireless subboard | 无线扣板硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the wireless subboard of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.232 | hwiACMETERNodeASoftwareVersion | Node A software version | 节点A软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Node A software version of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.233 | hwiACMETERWirelessNodeNetworkAccessAllowedSwitchStatus | Wireless node network access allowed switch status | 允许无线节点入网开关状态 | 0-Read_Only | 只读 | networkAccessForbidden(1), networkAccessAllowed(2), unknown(255) | [禁止入网=1]/[允许入网=2] | Wireless node network access allowed switch status of the device config table for the iACMETER. Value 1 indicate network access forbidden Value 2 indicate network access allowed
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.234 | hwiACMETERBoardFeatureId | Board feature ID | 单板特征标识 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Board feature ID of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.235 | hwiACMETERDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.236 | hwiACMETERAcRatedFrequency | AC rated frequency | 交流额定频率 | 1-Read_Write | 读写 | fifty(1), sixty(2), unknown(255) | [50=1]/[60=2] | AC rated frequency of the device config table for the iACMETER. Value 1 indicate fifty Value 2 indicate sixty.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.237 | hwiACMETERWorkingModeSetting | Working mode setting | 工作模式设置 | 1-Read_Write | 读写 | towWayIndependentMeter(1), oneWayIndependentMeter(2), unknown(255) | [2路独立电表工作模式=1]/[1路独立电表工作模式=2] | Working mode setting of the device config table for the iACMETER. Value 1 indicate tow way independent meter Value 2 indicate one way independent meter
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.238 | hwiACMETERWiringMode | Wiring mode | 接线方式 | 1-Read_Write | 读写 | threePhaseAndFourWire(1), threePhaseAndThreeWire(2), singlePhaseLN(3), singlePhaseLL(4), singlePhaseAndThreeWire(5), unknown(255) | [三相四线=1]/[三相三线=2]/[单相LN=3]/[单相LL=4]/[单相三线=5] | Wiring mode of the device config table for the iACMETER. Value 1 indicate three-phase,four-wire Value 2 indicate three-phase,three-wire Value 3 indicate single-phase LN Value 4 indicate single-phase LL Value 5 indicate single-phase,three-wire
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.239 | hwiACMETERLoadType | Load type | 负载类型 | 1-Read_Write | 读写 | electricEquipment(1), generationEquipment(2), unknown(255) | [用电设备=1]/[发电设备=2] | Load type of the device config table for the iACMETER. Value 1 indicate electric equipment Value 2 indicate generation equipment
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.240 | hwiACMETERCurrentPhaseAutomaticCorrectionEnable | / | / | 1-Read_Write | 读写 | disabling(1), enable(2), unknown(255) | / | Current phase automatic correction enable of the device config table for the iACMETER. Value 1 indicate disabling Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.241 | hwiACMETERCurPhaseAutoCorrectionPowerFactorThreshold | / | / | 1-Read_Write | 读写 | 50..100 | / | Current phase automatic correction power factor threshold of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.242 | hwiACMETERMaximumTransmitPowerAllowedByNodeA | Maximum transmit power allowed by node A | 节点A允许最大发射功率 | 1-Read_Write | 读写 | 0..15 | 0..15 | Maximum transmit power allowed by node A of the device config table for the iACMETER.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.243 | hwiACMETERNodeAChannel | Node A channel | 节点A信道 | 1-Read_Write | 读写 | 11..26 | 11..26 | Node A channel of the device config table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.244 | hwiACMETERBlinkingDuration | Blinking duration | 眨眼时长 | 1-Read_Write | 读写 | 5..120 | 5..120 | Blinking duration of the device config table for the iACMETER.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.245 | hwiACMETERBoardReset | Board reset | 单板复位 | 1-Read_Write | 读写 | reset(1) | [复位=1] | Board reset of the device config table for the iACMETER. Value 1 indicate reset
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.246 | hwiACMETERSensorBlinking | Sensor blinking | 传感器眨眼 | 1-Read_Write | 读写 | startBlinking(1) | [开始眨眼=1] | Sensor blinking of the device config table for the iACMETER. Value 1 indicate start blinking
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.247 | hwiACMETEREnergyParameterErasing | Energy parameter erasing | 电能参数擦除 | 1-Read_Write | 读写 | erase(1) | [擦除=1] | Energy parameter erasing of the device config table for the iACMETER. Value 1 indicate erase
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.300 | hwiACMETERConfigAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iACMETER.

## iACSENSE
iACSENSE
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.126 | iACSENSE | iACSENSE | iACSENSE | / | / | / | / | iACSENSE Equipment.
1.3.6.1.4.1.2011.6.178.1.1.126.1 | hwiACSENSERunning1Table | / | / |  |  | / | / | The running table of iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.1 | hwiACSENSERunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.2 | hwiACSENSECommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the iACSENSE. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.3 | hwiACSENSEPhaseL1State | Phase L1 state | L1相状态 | 0-Read_Only | 只读 | normal(1), failure(2), unknown(255) | [正常=1]/[停电=2] | Phase L1 state of the device config table for the iACSENSE. Value 1 indicate normal Value 2 indicate failure
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.4 | hwiACSENSEPhaseL2State | Phase L2 state | L2相状态 | 0-Read_Only | 只读 | normal(1), failure(2), unknown(255) | [正常=1]/[停电=2] | Phase L2 state of the device config table for the iACSENSE. Value 1 indicate normal Value 2 indicate failure
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.5 | hwiACSENSEPhaseL3State | Phase L3 state | L3相状态 | 0-Read_Only | 只读 | normal(1), failure(2), unknown(255) | [正常=1]/[停电=2] | Phase L3 state of the device config table for the iACSENSE. Value 1 indicate normal Value 2 indicate failure
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.6 | hwiACSENSEBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | Battery voltage of the device config table for the iACSENSE.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.7 | hwiACSENSEBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Battery temperature of the device config table for the iACSENSE.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.8 | hwiACSENSEBatteryCapacityState | Battery capacity state | 电池容量状态 | 0-Read_Only | 只读 | full(1), aroundhalf(2), needtoreplace(3), unknown(255) | [满电=1]/[半电=2]/[需更换=3] | Battery capacity state of the device config table for the iACSENSE. Value 1 indicate full Value 2 indicate around half Value 3 indicate need to replace
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.9 | hwiACSENSEWorkState | Work state | 工作状态 | 0-Read_Only | 只读 | sleeping(1), wakePeriodically(2), wakeManually(3), off(4), unknown(255) | [休眠=1]/[定时唤醒=2]/[手动唤醒=3]/[关机=4] | Work state of the device config table for the iACSENSE. Value 1 indicate sleeping Value 2 indicate wake periodically Value 3 indicate wake manually Value 4 indicate off
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.10 | hwiACSENSEWirelessSubboardHwVersion | Wireless subboard HW version | 无线扣板硬件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Wireless subboard HW version of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.11 | hwiACSENSESoftwarePackageVersion | Software package version | 软件包版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Software package version of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.12 | hwiACSENSENodeASoftwareVersion | Node A software version | 节点A软件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Node A software version of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.13 | hwiACSENSENodeANetState | Node A net state | 节点A组网状态 | 0-Read_Only | 只读 | notconnected(1), connected(2), unknown(255) | [未组网=1]/[组网成功=2] | Node A net state of the device config table for the iACSENSE. Value 1 indicate notconnected Value 2 indicate connected
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.14 | hwiACSENSENodeANetPanid | Node A net PANID | 节点A网络PANID | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net PANID of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.15 | hwiACSENSENodeANetShortAddress | Node A net short address | 节点A网络短地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net short address of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.16 | hwiACSENSENodeAMacAddress | Node A MAC address | 节点A MAC地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A MAC address of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.17 | hwiACSENSEIacsenseELable | iACSENSE E-lable | iACSENSE电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | iACSENSE E-lable of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.18 | hwiACSENSENodeARssi | Node A RSSI | 节点A RSSI | 0-Read_Only | 只读 | -150..20 | -150..20 | Node A RSSI of the device config table for the iACSENSE.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.19 | hwiACSENSEIacsenseESN | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | iACSENSE ESN of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.1.1.300 | hwiACSENSERunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.2 | hwiACSENSEConfig2Table | / | / |  |  | / | / | The config table of iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.2.1.1 | hwiACSENSEConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.2.1.2 | hwiACSENSEResetBoard | Reset board | 单板复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Reset board of the device config table for the iACSENSE. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.126.2.1.3 | hwiACSENSEReportingPeriod | Reporting period | 上报周期 | 1-Read_Write | 读写 | 30..300 | 30..300 | Reporting period of the device config table for the iACSENSE.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.126.2.1.4 | hwiACSENSELedBlink | LED blink | LED眨眼 | 1-Read_Write | 读写 | start(1) | [开始眨眼=1] | LED blink of the device config table for the iACSENSE. Value 1 indicate start
1.3.6.1.4.1.2011.6.178.1.1.126.2.1.5 | hwiACSENSEDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iACSENSE.
1.3.6.1.4.1.2011.6.178.1.1.126.2.1.6 | hwiACSENSEHeartbeatPeriod | Heartbeat period | 心跳周期 | 1-Read_Write | 读写 | 10..30 | 10..30 | Heartbeat period of the device config table for the iACSENSE.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.126.2.1.300 | hwiACSENSEConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iACSENSE.

## iDOOR
iDOOR
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.131.3 | iDOOR | iDOOR | iDOOR | / | / | / | / | iDOOR Equipment.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1 | hwiDOORRunningandConfig1Table | / | / |  |  | / | / | The running table of iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.1 | hwiDOORRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.2 | hwiDOORCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | commFailed(1), commSuccess(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the iDOOR. Value 1 indicate comm failed Value 2 indicate comm success
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.3 | hwiDOORBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | Battery voltage of the device config table for the iDOOR.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.4 | hwiDOORBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Battery temperature of the device config table for the iDOOR.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.5 | hwiDOORBatteryCapacityState | Battery capacity state | 电池容量状态 | 0-Read_Only | 只读 | full(1), aroundHalf(2), needToReplace(3), unknown(255) | [满电=1]/[半电=2]/[需更换=3] | Battery capacity state of the device config table for the iDOOR. Value 1 indicate full Value 2 indicate around half Value 3 indicate need to replace
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.6 | hwiDOORWorkState | Work state | 工作状态 | 0-Read_Only | 只读 | sleeping(1), wakePeriodically(2), wakeManually(3), off(4), unknown(255) | [休眠=1]/[定时唤醒=2]/[手动唤醒=3]/[关机=4] | Work state of the device config table for the iDOOR. Value 1 indicate sleeping Value 2 indicate wake periodically Value 3 indicate wake manually Value 4 indicate off
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.7 | hwiDOORDoorStatus | Door status | 门磁状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关=1]/[开=2] | Door status of the device config table for the iDOOR. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.8 | hwiDOORSoftwarePackageVersion | Software package version | 软件包版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Software package version of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.9 | hwiDOORWirelessSubboardHwVersion | Wireless subboard HW version | 无线扣板硬件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Wireless subboard HW version of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.10 | hwiDOORNodeASoftwareVersion | Node A software version | 节点A软件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Node A software version of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.11 | hwiDOORNodeANetState | Node A net state | 节点A组网状态 | 0-Read_Only | 只读 | notConnected(1), connected(2), unknown(255) | [未组网=1]/[组网成功=2] | Node A net state of the device config table for the iDOOR. Value 1 indicate not connected Value 2 indicate connected
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.12 | hwiDOORNodeANetPanid | Node A net PANID | 节点A网络PANID | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net PANID of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.13 | hwiDOORNodeANetShortAddress | Node A net short address | 节点A网络短地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net short address of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.14 | hwiDOORNodeAMacAddress | Node A MAC address | 节点A MAC地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A MAC address of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.15 | hwiDOORBatteryCapacityLow | / | / | 0-Read_Only | 只读 | normal(1), low(2), unknown(255) | / | Battery capacity low of the device config table for the iDOOR. Value 1 indicate normal Value 2 indicate low
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.16 | hwiDOORDeviceDetails | Device details | 设备详细信息 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Device details of the device config table for the iDOOR. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.17 | hwiDOORReportingPeriod | Reporting period | 心跳周期 | 1-Read_Write | 读写 | 20..30 | 20..30 | Reporting period of the device config table for the iDOOR.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.18 | hwiDOORNodeAMaxTransmitPower | Node A max transmit power | 节点A允许最大发射功率 | 1-Read_Write | 读写 | 0..15 | 0..15 | Node A max transmit power of the device config table for the iDOOR.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.19 | hwiDOORNodeBMaxTransmitPower | / | / | 1-Read_Write | 读写 | 0..15 | / | Node B max transmit power of the device config table for the iDOOR.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.20 | hwiDOORSlotIdOnTheNms | Slot ID on the NMS | 网管用槽位号 | 1-Read_Write | 读写 | 0..10 | 0..10 | Slot ID on the NMS of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.21 | hwiDOORDeleteCommFailDevice | / | / | 1-Read_Write | 读写 | yes(1) | / | Delete Comm fail device of the device config table for the iDOOR. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.22 | hwiDOORResetBoard | Reset board | 单板复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Reset board of the device config table for the iDOOR. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.23 | hwiDOORLedBlink | LED blink | LED眨眼 | 1-Read_Write | 读写 | start(1) | [开始眨眼=1] | LED blink of the device config table for the iDOOR. Value 1 indicate start
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.24 | hwiDOORDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.25 | hwiDOOREsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the iDOOR.
1.3.6.1.4.1.2011.6.178.1.1.131.3.1.1.300 | hwiDOORRunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iDOOR.

## iMOTION
iMOTION
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.131.5 | iMOTION | iMOTION | iMOTION | / | / | / | / | iMOTION Equipment.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1 | hwiMOTIONRunningandConfig1Table | / | / |  |  | / | / | The running table of iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.1 | hwiMOTIONRunningandConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.2 | hwiMOTIONCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | commFailed(1), commSuccess(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the iMOTION. Value 1 indicate comm failed Value 2 indicate comm success
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.3 | hwiMOTIONBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | Battery voltage of the device config table for the iMOTION.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.4 | hwiMOTIONBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Battery temperature of the device config table for the iMOTION.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.5 | hwiMOTIONBatteryCapacityState | Battery capacity state | 电池容量状态 | 0-Read_Only | 只读 | full(1), aroundHalf(2), needToReplace(3), unknown(255) | [满电=1]/[半电=2]/[需更换=3] | Battery capacity state of the device config table for the iMOTION. Value 1 indicate full Value 2 indicate around half Value 3 indicate need to replace
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.6 | hwiMOTIONWorkState | Work state | 工作状态 | 0-Read_Only | 只读 | sleeping(1), wakePeriodically(2), wakeManually(3), off(4), unknown(255) | [休眠=1]/[定时唤醒=2]/[手动唤醒=3]/[关机=4] | Work state of the device config table for the iMOTION. Value 1 indicate sleeping Value 2 indicate wake periodically Value 3 indicate wake manually Value 4 indicate off
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.7 | hwiMOTIONSoftwarePackageVersion | Software package version | 软件包版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Software package version of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.8 | hwiMOTIONWirelessSubboardHwVersion | Wireless subboard HW version | 无线扣板硬件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Wireless subboard HW version of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.9 | hwiMOTIONNodeASoftwareVersion | Node A software version | 节点A软件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Node A software version of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.10 | hwiMOTIONMainBoardSoftwareVersion | Main board software version | 主板软件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Main board software version of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.11 | hwiMOTIONMainBoardHardwareVersion | Main board hardware version | 主板硬件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Main board hardware version of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.12 | hwiMOTIONSensorType | Sensor type | 传感器类型 | 0-Read_Only | 只读 | singleInfrared(1), infraredAndMicrowave(2), doubleInfrared(3), unknown(255) | [单红外=1]/[红外+微波=2]/[双红外=3] | Sensor type of the device config table for the iMOTION. Value 1 indicate single infrared Value 2 indicate infrared and microwave Value 3 indicate double infrared
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.13 | hwiMOTIONNodeANetState | Node A net state | 节点A组网状态 | 0-Read_Only | 只读 | notConnected(1), connected(2), unknown(255) | [未组网=1]/[组网成功=2] | Node A net state of the device config table for the iMOTION. Value 1 indicate not connected Value 2 indicate connected
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.14 | hwiMOTIONNodeANetPanid | Node A net PANID | 节点A网络PANID | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net PANID of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.15 | hwiMOTIONNodeANetShortAddress | Node A net short address | 节点A网络短地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net short address of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.16 | hwiMOTIONNodeAMacAddress | Node A MAC address | 节点A MAC地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A MAC address of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.17 | hwiMOTIONBatteryCapacityLow | / | / | 0-Read_Only | 只读 | normal(1), low(2), unknown(255) | / | Battery capacity low of the device config table for the iMOTION. Value 1 indicate normal Value 2 indicate low
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.18 | hwiMOTIONAlarmState | Alarm state | 告警状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Alarm state of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.19 | hwiMOTIONMotionState | Motion state | 移动状态 | 0-Read_Only | 只读 | nobody(1), motion(2), unknown(255) | [无人=1]/[有人=2] | Motion state of the device config table for the iMOTION. Value 1 indicate nobody Value 2 indicate motion
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.20 | hwiMOTIONDeviceDetails | Device details | 设备详细信息 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Device details of the device config table for the iMOTION. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.21 | hwiMOTIONReportingPeriod | Reporting period | 上报周期 | 1-Read_Write | 读写 | 25..30 | 25..30 | Reporting period of the device config table for the iMOTION.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.22 | hwiMOTIONAlarmSensitivity | Alarm sensitivity | 告警灵敏度 | 1-Read_Write | 读写 | low(1), middle(2), high(3), unknown(255) | [低=1]/[中=2]/[高=3] | Alarm sensitivity of the device config table for the iMOTION. Value 1 indicate low Value 2 indicate middle Value 3 indicate high
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.23 | hwiMOTIONResetBoard | Reset board | 单板复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Reset board of the device config table for the iMOTION. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.24 | hwiMOTIONNodeAMaxTransmitPower | Node A max transmit power | 节点A允许最大发射功率 | 1-Read_Write | 读写 | 0..15 | 0..15 | Node A max transmit power of the device config table for the iMOTION.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.25 | hwiMOTIONLedBlink | LED blink | LED眨眼 | 1-Read_Write | 读写 | start(1) | [开始眨眼=1] | LED blink of the device config table for the iMOTION. Value 1 indicate start
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.26 | hwiMOTIONSlotNumber | Slot number | 网管用槽位号 | 1-Read_Write | 读写 | 0..10 | 0..10 | Slot number of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.27 | hwiMOTIONDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.28 | hwiMOTIONEsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the iMOTION.
1.3.6.1.4.1.2011.6.178.1.1.131.5.1.1.300 | hwiMOTIONRunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iMOTION.

## iSMOKE
iSMOKE
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.131.4 | iSMOKE | iSMOKE | iSMOKE | / | / | / | / | iSMOKE Equipment.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1 | hwiSMOKERunningandConfig1Table | / | / |  |  | / | / | The running table of iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.1 | hwiSMOKERunningandConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.2 | hwiSMOKECommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | commFailed(1), commSuccess(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the iSMOKE. Value 1 indicate comm failed Value 2 indicate comm success
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.3 | hwiSMOKEBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | Battery voltage of the device config table for the iSMOKE.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.4 | hwiSMOKEBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Battery temperature of the device config table for the iSMOKE.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.5 | hwiSMOKEBatteryCapacityState | Battery capacity state | 电池容量状态 | 0-Read_Only | 只读 | full(1), aroundHalf(2), needToReplace(3), unknown(255) | [满电=1]/[半电=2]/[需更换=3] | Battery capacity state of the device config table for the iSMOKE. Value 1 indicate full Value 2 indicate around half Value 3 indicate need to replace
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.6 | hwiSMOKEWorkState | Work state | 工作状态 | 0-Read_Only | 只读 | sleeping(1), wakePeriodically(2), wakeManually(3), off(4), unknown(255) | [休眠=1]/[定时唤醒=2]/[手动唤醒=3]/[关机=4] | Work state of the device config table for the iSMOKE. Value 1 indicate sleeping Value 2 indicate wake periodically Value 3 indicate wake manually Value 4 indicate off
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.7 | hwiSMOKESmokingState | Smoking state | 烟雾状态 | 0-Read_Only | 只读 | normal(1), smoking(2), unknown(255) | [正常=1]/[有烟雾=2] | Smoking state of the device config table for the iSMOKE. Value 1 indicate normal Value 2 indicate smoking
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.8 | hwiSMOKESoftwarePackageVersion | Software package version | 软件包版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Software package version of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.9 | hwiSMOKEWirelessSubboardHwVersion | Wireless subboard HW version | 无线扣板硬件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Wireless subboard HW version of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.10 | hwiSMOKENodeASoftwareVersion | Node A software version | 节点A软件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Node A software version of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.11 | hwiSMOKEMainBoardSoftwareVersion | Main board software version | 主板软件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Main board software version of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.12 | hwiSMOKEMainBoardHardwareVersion | Main board hardware version | 主板硬件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Main board hardware version of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.13 | hwiSMOKENodeANetState | Node A net state | 节点A组网状态 | 0-Read_Only | 只读 | notConnected(1), connected(2), unknown(255) | [未组网=1]/[组网成功=2] | Node A net state of the device config table for the iSMOKE. Value 1 indicate not connected Value 2 indicate connected
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.14 | hwiSMOKENodeANetPanid | Node A net PANID | 节点A网络PANID | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net PANID of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.15 | hwiSMOKENodeANetShortAddress | Node A net short address | 节点A网络短地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net short address of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.16 | hwiSMOKENodeAMacAddress | Node A MAC address | 节点A MAC地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A MAC address of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.17 | hwiSMOKEBatteryCapacityLow | / | / | 0-Read_Only | 只读 | normal(1), low(2), unknown(255) | / | Battery capacity low of the device config table for the iSMOKE. Value 1 indicate normal Value 2 indicate low
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.18 | hwiSMOKEAlarmState | Alarm state | 告警状态 | 0-Read_Only | 只读 | 0..1 | 0..1 | Alarm state of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.19 | hwiSMOKEDeviceDetails | Device details | 设备详细信息 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Device details of the device config table for the iSMOKE. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.20 | hwiSMOKEReportingPeriod | Reporting period | 上报周期 | 1-Read_Write | 读写 | 20..30 | 20..30 | Reporting period of the device config table for the iSMOKE.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.21 | hwiSMOKEAlarmSensitivity | Alarm sensitivity | 告警灵敏度 | 1-Read_Write | 读写 | low(1), high(2), unknown(255) | [低=1]/[高=2] | Alarm sensitivity of the device config table for the iSMOKE. Value 1 indicate low Value 2 indicate high
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.22 | hwiSMOKEResetBoard | Reset board | 单板复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Reset board of the device config table for the iSMOKE. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.23 | hwiSMOKENodeAMaxTransmitPower | Node A max transmit power | 节点A允许最大发射功率 | 1-Read_Write | 读写 | 0..15 | 0..15 | Node A max transmit power of the device config table for the iSMOKE.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.24 | hwiSMOKELedBlink | LED blink | LED眨眼 | 1-Read_Write | 读写 | start(1) | [开始眨眼=1] | LED blink of the device config table for the iSMOKE. Value 1 indicate start
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.25 | hwiSMOKESlotNumber | Slot number | 网管用槽位号 | 1-Read_Write | 读写 | 0..10 | 0..10 | Slot number of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.26 | hwiSMOKEAlarmReset | Alarm reset | 告警复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Alarm reset of the device config table for the iSMOKE. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.27 | hwiSMOKESmokeSensorAlarmStatus | Smoke sensor alarm status | 烟感告警状态 | 1-Read_Write | 读写 | 0..1 | 0..1 | Smoke sensor alarm status of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.28 | hwiSMOKESmokeDetectionUnitAlarmStatus | Smoke detection unit alarm status | 烟雾检测单元告警状态 | 1-Read_Write | 读写 | 0..1 | 0..1 | Smoke detection unit alarm status of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.29 | hwiSMOKESmokingAlarmHoldEnabled | Smoking alarm hold enabled | 烟雾告警锁存使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Smoking alarm hold enabled of the device config table for the iSMOKE. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.30 | hwiSMOKEDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.31 | hwiSMOKEEsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the iSMOKE.
1.3.6.1.4.1.2011.6.178.1.1.131.4.1.1.300 | hwiSMOKERunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iSMOKE.

## iTeaQ Cool Row
iTeaQ Cool Row
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.13 | iTeaQCoolRow | iTeaQ Cool Row | iTeaQ Cool Row | / | / | / | / | iTeaQ Cool Row Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1 | hwiTeaQCoolRowRunningAndConfig1Table | / | / |  |  | / | / | The running table of iTeaQ Cool Row.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.1 | hwiTeaQCoolRowRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iTeaQ Cool Row.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.2 | hwiTeaQCoolRowMeasuredReturnAirTemperature | Measured return air temperature | 回风温度测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Measured return air temperature of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.3 | hwiTeaQCoolRowMeasuredReturnAirHumidity | Measured return air humidity | 回风湿度测量值 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Measured return air humidity of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.4 | hwiTeaQCoolRowMeasuredSupplyAirTemperature1 | Measured supply air temperature 1 | 送风温度1测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Measured supply air temperature 1 of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.5 | hwiTeaQCoolRowMeasuredSupplyAirTemperature2 | Measured supply air temperature 2 | 送风温度2测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Measured supply air temperature 2 of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.6 | hwiTeaQCoolRowDischargePressure | Discharge pressure | 排气压力 | 0-Read_Only | 只读 | 0..460 | 0..460 | Discharge pressure of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Bar.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.7 | hwiTeaQCoolRowSuctionPressure | Suction pressure | 吸气压力 | 0-Read_Only | 只读 | 0..200 | 0..200 | Suction pressure of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Bar.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.8 | hwiTeaQCoolRowDischargeTemperature | Discharge temperature | 排气温度 | 0-Read_Only | 只读 | -400..1550 | -400..1550 | Discharge temperature of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.9 | hwiTeaQCoolRowSuctionTemperature | Suction temperature | 吸气温度 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Suction temperature of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.10 | hwiTeaQCoolRowUnitRunningStatus | Unit running status | 机组运行状态 | 0-Read_Only | 只读 | localshutdown(1), airconditionerrunning(2), standby(3), displayshutdown(4), remoteshutdown(5), monitoringshutdown(6), unknown(255) | [本地关机=1]/[机组运行=2]/[待机=3]/[显示关机=4]/[远程关机=5]/[监控关机=6] | Unit running status of the device config table for the iTeaQ Cool Row. Value 1 indicate local shutdown Value 2 indicate air conditioner running Value 3 indicate standby Value 4 indicate display shutdown Value 5 indicate remote shutdown Value 6 indicate monitoring shutdown
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.11 | hwiTeaQCoolRowRemoteTemperature1MeasuredValue | Remote temperature 1 measured value | 远程温度1测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 1 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.12 | hwiTeaQCoolRowRemoteTemperature2MeasuredValue | Remote temperature 2 measured value | 远程温度2测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 2 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.13 | hwiTeaQCoolRowRemoteTemperature3MeasuredValue | Remote temperature 3 measured value | 远程温度3测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 3 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.14 | hwiTeaQCoolRowRemoteTemperature4MeasuredValue | Remote temperature 4 measured value | 远程温度4测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 4 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.15 | hwiTeaQCoolRowRemoteTemperature5MeasuredValue | Remote temperature 5 measured value | 远程温度5测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 5 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.16 | hwiTeaQCoolRowRemoteTemperature6MeasuredValue | Remote temperature 6 measured value | 远程温度6测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 6 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.17 | hwiTeaQCoolRowRemoteTemperature7MeasuredValue | Remote temperature 7 measured value | 远程温度7测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 7 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.18 | hwiTeaQCoolRowRemoteTemperature8MeasuredValue | Remote temperature 8 measured value | 远程温度8测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 8 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.19 | hwiTeaQCoolRowRemoteTemperature9MeasuredValue | Remote temperature 9 measured value | 远程温度9测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 9 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.20 | hwiTeaQCoolRowRemoteTemperature10MeasuredValue | Remote temperature 10 measured value | 远程温度10测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 10 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.21 | hwiTeaQCoolRowRemoteTemperature11MeasuredValue | Remote temperature 11 measured value | 远程温度11测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 11 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.22 | hwiTeaQCoolRowRemoteTemperature12MeasuredValue | Remote temperature 12 measured value | 远程温度12测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 12 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.23 | hwiTeaQCoolRowRemoteTemperature13MeasuredValue | Remote temperature 13 measured value | 远程温度13测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 13 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.24 | hwiTeaQCoolRowRemoteTemperature14MeasuredValue | Remote temperature 14 measured value | 远程温度14测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 14 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.25 | hwiTeaQCoolRowRemoteTemperature15MeasuredValue | Remote temperature 15 measured value | 远程温度15测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 15 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.26 | hwiTeaQCoolRowRemoteTemperature16MeasuredValue | Remote temperature 16 measured value | 远程温度16测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Remote temperature 16 measured value of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.27 | hwiTeaQCoolRowSuctionSuperheatDegree | Suction superheat degree | 吸气过热度 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Suction superheat degree of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.28 | hwiTeaQCoolRowDischargeSuperheatDegree | Discharge superheat degree | 排气过热度 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Discharge superheat degree of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.29 | hwiTeaQCoolRowCompressorSpeed | Compressor speed | 压机转速 | 0-Read_Only | 只读 | 0..90 | 0..90 | Compressor speed of the device config table for the iTeaQ Cool Row.SigUnitInfo:rps.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.30 | hwiTeaQCoolRowEevOpening | EEV opening | EEV开度 | 0-Read_Only | 只读 | 0..100 | 0..100 | EEV opening of the device config table for the iTeaQ Cool Row.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.31 | hwiTeaQCoolRowFanSpeed | Fan speed | 风机转速 | 0-Read_Only | 只读 | 0..100 | 0..100 | Fan speed of the device config table for the iTeaQ Cool Row.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.32 | hwiTeaQCoolRowHumidificationCurrent | Humidification current | 加湿电流 | 0-Read_Only | 只读 | 0..300 | 0..300 | Humidification current of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.33 | hwiTeaQCoolRowCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the iTeaQ Cool Row. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.34 | hwiTeaQCoolRowPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the iTeaQ Cool Row.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.35 | hwiTeaQCoolRowModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the iTeaQ Cool Row.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.36 | hwiTeaQCoolRowCooling | Cooling | 制冷 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | Cooling of the device config table for the iTeaQ Cool Row. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.37 | hwiTeaQCoolRowHeating | Heating | 加热 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | Heating of the device config table for the iTeaQ Cool Row. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.38 | hwiTeaQCoolRowHumidification | Humidification | 加湿 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | Humidification of the device config table for the iTeaQ Cool Row. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.39 | hwiTeaQCoolRowDehumidification | Dehumidification | 除湿 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | Dehumidification of the device config table for the iTeaQ Cool Row. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.40 | hwiTeaQCoolRowDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iTeaQ Cool Row.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.41 | hwiTeaQCoolRowSupplyAirorRemoteTemperatureSetpoint | Supply air/Remote temperature setpoint | 送风/远程温度设定点 | 1-Read_Write | 读写 | 150..320 | 150..320 | Supply air/Remote temperature setpoint of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.42 | hwiTeaQCoolRowReturnAirTemperatureSetPoint | Return air temperature set point | 回风温度设定点 | 1-Read_Write | 读写 | 180..400 | 180..400 | Return air temperature set point of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.43 | hwiTeaQCoolRowSupplyAirHumiditySetpoint | Supply air humidity setpoint | 送风湿度设定点 | 1-Read_Write | 读写 | 200..800 | 200..800 | Supply air humidity setpoint of the device config table for the iTeaQ Cool Row.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.44 | hwiTeaQCoolRowMonitoringStartuporShutdown | Monitoring startup/shutdown | 监控开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Monitoring startup/shutdown of the device config table for the iTeaQ Cool Row. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.13.1.1.300 | hwiTeaQCoolRowRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iTeaQ Cool Row.

## iTeaQ Cool Row-CF
iTeaQ Cool Row-CF
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.12 | iTeaQCoolRowCF | iTeaQ Cool Row-CF | iTeaQ Cool Row-CF | / | / | / | / | iTeaQ Cool Row-CF Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1 | hwiTeaQCoolRowCFRunningAndConfigTable | / | / |  |  | / | / | The running table of iTeaQ Cool Row-CF.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.1 | hwiTeaQCoolRowCFRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iTeaQ Cool Row-CF.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.2 | hwiTeaQCoolRowCFMeasuredReturnAirTemperature | Measured return air temperature | 回风温度测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Measured return air temperature of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.3 | hwiTeaQCoolRowCFMeasuredReturnAirHumidity | Measured return air humidity | 回风湿度测量值 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Measured return air humidity of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.4 | hwiTeaQCoolRowCFMeasuredSupplyAirTemperature1 | Measured supply air temperature 1 | 送风温度1测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Measured supply air temperature 1 of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.5 | hwiTeaQCoolRowCFMeasuredSupplyAirTemperature2 | Measured supply air temperature 2 | 送风温度2测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Measured supply air temperature 2 of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.6 | hwiTeaQCoolRowCFMeasuredPumpAmbientTemperature | Measured pump ambient temperature | 泵环境温度测量值 | 0-Read_Only | 只读 | -400..1000 | -400..1000 | Measured pump ambient temperature of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.7 | hwiTeaQCoolRowCFCondensingPressure | Condensing pressure | 冷凝压力 | 0-Read_Only | 只读 | 0..460 | 0..460 | Condensing pressure of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Bar.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.8 | hwiTeaQCoolRowCFDischargeTemperature | Discharge temperature | 排气温度 | 0-Read_Only | 只读 | -400..1550 | -400..1550 | Discharge temperature of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.9 | hwiTeaQCoolRowCFFanSpeed | Fan speed | 风机转速 | 0-Read_Only | 只读 | 0..100 | 0..100 | Fan speed of the device config table for the iTeaQ Cool Row-CF.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.10 | hwiTeaQCoolRowCFUnitRunningStatus | Unit running status | 机组运行状态 | 0-Read_Only | 只读 | off(1), running(2), standby(3), localShutdown(4), remoteShutdown(5), monitoringShutdown(6), unknown(255) | [关机=1]/[运行=2]/[待机=3]/[本地关机=4]/[远程关机=5]/[监控关机=6] | Unit running status of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate off Value 2 indicate running Value 3 indicate standby Value 4 indicate local shutdown Value 5 indicate remote shutdown Value 6 indicate monitoring shutdown
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.11 | hwiTeaQCoolRowCFSystemCoolingMode | System cooling mode | 系统制冷模式 | 0-Read_Only | 只读 | idleMode(1), compressorMode(2), hybridMode(3), pumpMode(4), vacuumizing(5), unknown(255) | [空闲模式=1]/[压缩机模式=2]/[混合模式=3]/[泵模式=4]/[抽真空=5] | System cooling mode of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate idle mode Value 2 indicate compressor mode Value 3 indicate hybrid mode Value 4 indicate pump mode Value 5 indicate vacuumizing
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.12 | hwiTeaQCoolRowCFLowPressure | Low pressure | 低压压力 | 0-Read_Only | 只读 | 0..200 | 0..200 | Low pressure of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Bar.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.13 | hwiTeaQCoolRowCFFan | Fan | 风机 | 0-Read_Only | 只读 | shutdown(1), turnOn(2), unknown(255) | [关闭=1]/[开启=2] | Fan of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate shutdown Value 2 indicate turn on
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.14 | hwiTeaQCoolRowCFCompressor | Compressor | 压缩机 | 0-Read_Only | 只读 | shutdown(1), turnOn(2), unknown(255) | [关闭=1]/[开启=2] | Compressor of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate shutdown Value 2 indicate turn on
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.15 | hwiTeaQCoolRowCFCoolingPump | Cooling pump | 制冷泵 | 0-Read_Only | 只读 | shutdown(1), turnOn(2), unknown(255) | [关闭=1]/[开启=2] | Cooling pump of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate shutdown Value 2 indicate turn on
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.16 | hwiTeaQCoolRowCFHeating | Heating | 加热 | 0-Read_Only | 只读 | shutdown(1), turnOn(2), unknown(255) | [关闭=1]/[开启=2] | Heating of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate shutdown Value 2 indicate turn on
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.17 | hwiTeaQCoolRowCFHumidification | Humidification | 加湿 | 0-Read_Only | 只读 | shutdown(1), turnOn(2), unknown(255) | [关闭=1]/[开启=2] | Humidification of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate shutdown Value 2 indicate turn on
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.18 | hwiTeaQCoolRowCFCondensatePump | Condensate pump | 冷凝水泵 | 0-Read_Only | 只读 | shutdown(1), turnOn(2), unknown(255) | [关闭=1]/[开启=2] | Condensate pump of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate shutdown Value 2 indicate turn on
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.19 | hwiTeaQCoolRowCFCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.20 | hwiTeaQCoolRowCFPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the iTeaQ Cool Row-CF.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.21 | hwiTeaQCoolRowCFModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the iTeaQ Cool Row-CF.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.22 | hwiTeaQCoolRow-CFConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the iTeaQ Cool Row-CF.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.23 | hwiTeaQCoolRowCFDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iTeaQ Cool Row-CF.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.24 | hwiTeaQCoolRowCFMonitoringStartuporOrShutdown | Monitoring startup/shutdown | 监控开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Monitoring startup/shutdown of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.25 | hwiTeaQCoolRowCFReturnAirTemperatureSetPoint | Return air temperature set point | 回风温度设定点 | 1-Read_Write | 读写 | 180..400 | 180..400 | Return air temperature set point of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.26 | hwiTeaQCoolRowCFTemperaturePrecisionSetting | Temperature precision setting | 温度精度设定 | 1-Read_Write | 读写 | 10..100 | 10..100 | Temperature precision setting of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:Degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.27 | hwiTeaQCoolRowCFReturnAirHumiditySetPoint | Return air humidity set point | 湿度设定点 | 1-Read_Write | 读写 | 200..800 | 200..800 | Return air humidity set point of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.28 | hwiTeaQCoolRowCFHumidityPrecisionSetting | Humidity precision setting | 湿度精度设定 | 1-Read_Write | 读写 | 10..100 | 10..100 | Humidity precision setting of the device config table for the iTeaQ Cool Row-CF.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.29 | hwiTeaQCoolRowCFDetailModel | Detail model | 详细机型 | 1-Read_Write | 读写 | cr025ef(1), cr035ef(2), cr035eaDx(3), unknown(255) | [CR025EF=1]/[CR035EF=2]/[CR035EA-DX=3] | Detail model of the device config table for the iTeaQ Cool Row-CF. Value 1 indicate cr025ef Value 2 indicate cr035ef Value 3 indicate cr035ea-dx
1.3.6.1.4.1.2011.6.178.1.1.10.12.1.1.300 | hwiTeaQCoolRowCFRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iTeaQ Cool Row-CF.

## Envicool-IFX Terminal
Envicool-IFX Terminal
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.14 | EnvicoolIFXTerminal | Envicool-IFX Terminal | 英维克IFX末端 | / | / | / | / | Envicool-IFX Terminal Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1 | hwEnvicool-IFXTerminalRunningAndConfig1Table | / | / | / | / | / | / | The running table of Envicool-IFX Terminal.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.1 | hwEnvicool-IFXTerminalRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Envicool-IFX Terminal.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.2 | hwEnvicoolIFXTerminal1ReturnAirTemperature | 1# Return air temperature | 1#回风温度 | 0-Read_Only | 只读 | -200..1400 | -200..1400 | Number 1 return air temperature of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.3 | hwEnvicoolIFXTerminal2ReturnAirTemperature | 2# Return air temperature | 2#回风温度 | 0-Read_Only | 只读 | -200..1400 | -200..1400 | Number 2 return air temperature of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.4 | hwEnvicoolIFXTerminal3ReturnAirTemperature | 3# Return air temperature | 3#回风温度 | 0-Read_Only | 只读 | -200..1400 | -200..1400 | Number 3 return air temperature of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.5 | hwEnvicoolIFXTerminal1SupplyAirTemperature | 1# Supply air temperature | 1#出风温度 | 0-Read_Only | 只读 | -200..1400 | -200..1400 | Number 1 supply air temperature of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.6 | hwEnvicoolIFXTerminal2SupplyAirTemperature | 2# Supply air temperature | 2#出风温度 | 0-Read_Only | 只读 | -200..1400 | -200..1400 | Number 2 supply air temperature of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.7 | hwEnvicoolIFXTerminal3SupplyAirTemperature | 3# Supply air temperature | 3#出风温度 | 0-Read_Only | 只读 | -200..1400 | -200..1400 | Number 3 supply air temperature of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.8 | hwEnvicoolIFXTerminal1InletTemperature | 1# Inlet temperature | 1#进口温度 | 0-Read_Only | 只读 | -200..1400 | -200..1400 | Number 1 Inlet temperature of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.9 | hwEnvicoolIFXTerminal1OutletTemperature | 1# Outlet temperature | 1#出口温度 | 0-Read_Only | 只读 | -200..1400 | -200..1400 | Number 1 outlet temperature of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.10 | hwEnvicoolIFXTerminal1ReturnAirHumidity | 1# Return air humidity | 1#回风湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Number 1 return air humidity of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.11 | hwEnvicoolIFXTerminal1SupplyAirHumidity | 1# Supply air humidity | 1#出风湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Number 1 supply air humidity of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.12 | hwEnvicoolIFXTerminal1InletPressure | 1# Inlet pressure | 1#进口压力 | 0-Read_Only | 只读 | 0..4600 | 0..4600 | Number 1 inlet pressure of the device config table for the Envicool-IFX Terminal.Multiple:100.SigUnitInfo:Bar.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.13 | hwEnvicoolIFXTerminal1OutletPressure | 1# Outlet pressure | 1#出口压力 | 0-Read_Only | 只读 | 0..4600 | 0..4600 | Number 1 outlet pressure of the device config table for the Envicool-IFX Terminal.Multiple:100.SigUnitInfo:Bar.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.14 | hwEnvicoolIFXTerminalVoltage | Voltage | 电网电压 | 0-Read_Only | 只读 | 0..500 | 0..500 | Voltage of the device config table for the Envicool-IFX Terminal.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.15 | hwEnvicoolIFXTerminalInternalFanStatus | Internal fan status | 内风机 | 0-Read_Only | 只读 | 0..100 | 0..100 | Internal fan status of the device config table for the Envicool-IFX Terminal.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.16 | hwEnvicoolIFXTerminal1SolenoidValveStatus | 1# Solenoid valve status | 1#电磁阀 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | 1# Solenoid valve status of the device config table for the Envicool-IFX Terminal.Multiple:10. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.17 | hwEnvicoolIFXTerminalSystemOnorOff | System ON/OFF | 系统开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | System ON/OFF of the device config table for the Envicool-IFX Terminal.Multiple:10. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.18 | hwEnvicoolIFXTerminal1System1PumpStatus | 1# System 1# pump status | 1#系统1#泵 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | 1# System 1# pump status of the device config table for the Envicool-IFX Terminal.Multiple:10. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.19 | hwEnvicoolIFXTerminal1System2PumpStatus | 1# System 2# pump status | 1#系统2#泵 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | 1# System 2# pump status of the device config table for the Envicool-IFX Terminal.Multiple:10. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.20 | hwEnvicoolIFXTerminalCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Envicool-IFX Terminal. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.21 | hwEnvicoolIFXTerminalPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Envicool-IFX Terminal.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.22 | hwEnvicoolIFXTerminalModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Envicool-IFX Terminal.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.23 | hwEnvicoolIFXTerminalSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the Envicool-IFX Terminal.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.24 | hwEnvicoolIFXTerminalDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Envicool-IFX Terminal.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.25 | hwEnvicoolIFXTerminalRemoteOnorOff | Remote ON/OFF | 监控开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Remote ON/OFF of the device config table for the Envicool-IFX Terminal. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.26 | hwEnvicoolIFXTerminalInternalFanTemperatureControlSetPoint | Internal fan temperature control set point | 风机温度设定 | 1-Read_Write | 读写 | 70..450 | 70..450 | Internal fan temperature control set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.27 | hwEnvicoolIFXTerminalSolenoidValveTemperatureControlSetPoint | Solenoid valve temperature control set point | 电磁阀温度设定 | 1-Read_Write | 读写 | 70..450 | 70..450 | Solenoid valve temperature control set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.28 | hwEnvicoolIFXTerminalHumiditySetPoint | Humidity set point | 湿度设定点 | 1-Read_Write | 读写 | 100..900 | 100..900 | Humidity set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.29 | hwEnvicoolIFXTerminalHighTemperatureSetPoint | High temperature set point | 回风高温告警点 | 1-Read_Write | 读写 | 200..700 | 200..700 | High temperature set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.30 | hwEnvicoolIFXTerminalLowTemperatureSetPoint | Low temperature set point | 回风低温告警点 | 1-Read_Write | 读写 | -200..200 | -200..200 | Low temperature set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.31 | hwEnvicoolIFXTerminalHighHumiditySetPoint | High humidity set point | 回风高湿告警点 | 1-Read_Write | 读写 | 600..900 | 600..900 | High humidity set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.32 | hwEnvicoolIFXTerminalLowHumiditySetPoint | Low humidity set point | 回风低湿告警点 | 1-Read_Write | 读写 | 100..600 | 100..600 | Low humidity set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.33 | hwEnvicoolIFXTerminalSupplyAirHighTemperatureSetPoint | Supply air high temperature set point | 出风高温告警点 | 1-Read_Write | 读写 | 180..450 | 180..450 | Supply air high temperature set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.34 | hwEnvicoolIFXTerminalSupplyAirLowTemperatureSetPoint | Supply air low temperature set point | 出风低温告警点 | 1-Read_Write | 读写 | -200..200 | -200..200 | Supply air low temperature set point of the device config table for the Envicool-IFX Terminal.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.14.1.1.300 | hwEnvicool-IFXTerminalRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Envicool-IFX Terminal.

## MTS9604B-MTS9606B Power Supply
MTS9604B_MTS9606B供电设备
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.32 | MTS9604BMTS9606BPowerSupply | MTS9604B_MTS9606B Power Supply | MTS9604B_MTS9606B供电设备 | / | / | / | / | MTS9604B_MTS9606B Power Supply Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1 | hwMTS9604B_MTS9606BPowerSupplyRunning1Table | / | / |  |  | / | / | The running table of MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.1 | hwMTS9604B_MTS9606BPowerSupplyRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.2 | hwMTS9604BMTS9606BPowerSupplyCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.3 | hwMTS9604BMTS9606BPowerSupplyPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.4 | hwMTS9604BMTS9606BPowerSupplyModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.5 | hwMTS9604BMTS9606BPowerSupplyManufacturerCode | Manufacturer code | 生产厂家编码 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Manufacturer code of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.6 | hwMTS9604BMTS9606BPowerSupplyEquipmentType | Equipment type | 设备型号 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Equipment type of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.7 | hwMTS9604BMTS9606BPowerSupplyProtocolVersion | Protocol version | 协议版本 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Protocol version of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.8 | hwMTS9604BMTS9606BPowerSupplySoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.9 | hwMTS9604BMTS9606BPowerSupplyHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.10 | hwMTS9604BMTS9606BPowerSupplySystemType | System type | 系统类型 | 0-Read_Only | 只读 | 0..28 | 0..28 | System type of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.11 | hwMTS9604BMTS9606BPowerSupplySystemDcVoltage | System DC voltage | 系统电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | System DC voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.12 | hwMTS9604BMTS9606BPowerSupplyTotalDcLoadCurrent | Total DC load current | 总负载电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total DC load current of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.13 | hwMTS9604BMTS9606BPowerSupplyLoadShunt1Current | Load shunt 1 current | 负载支路1电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Load shunt 1 current of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.14 | hwMTS9604BMTS9606BPowerSupplyAcVoltage | AC voltage | 交流电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | AC voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.15 | hwMTS9604BMTS9606BPowerSupplyAcCurrent | AC current | 交流电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AC current of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.16 | hwMTS9604BMTS9606BPowerSupplyPhaseL1Voltage | Phase L1 voltage | L1相电压 | 0-Read_Only | 只读 | 0..4000 | 0..4000 | Phase L1 voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.17 | hwMTS9604BMTS9606BPowerSupplyPhaseL2Voltage | Phase L2 voltage | L2相电压 | 0-Read_Only | 只读 | 0..4000 | 0..4000 | Phase L2 voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.18 | hwMTS9604BMTS9606BPowerSupplyPhaseL3Voltage | Phase L3 voltage | L3相电压 | 0-Read_Only | 只读 | 0..4000 | 0..4000 | Phase L3 voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.19 | hwMTS9604BMTS9606BPowerSupplyPhaseL1Current | Phase L1 current | L1相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase L1 current of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.20 | hwMTS9604BMTS9606BPowerSupplyPhaseL2Current | Phase L2 current | L2相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase L2 current of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.21 | hwMTS9604BMTS9606BPowerSupplyPhaseL3Current | Phase L3 current | L3相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase L3 current of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.22 | hwMTS9604BMTS9606BPowerSupplyAcFrequency | AC frequency | 交流频率 | 0-Read_Only | 只读 | 0..100 | 0..100 | AC frequency of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.23 | hwMTS9604BMTS9606BPowerSupplyEquipmentAreaTemperature | Equipment area temperature | 设备区温度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Equipment area temperature of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.24 | hwMTS9604BMTS9606BPowerSupplyAmbientHumidity | Ambient humidity | 环境湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Ambient humidity of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.25 | hwMTS9604BMTS9606BPowerSupplyRectifierTotalOutputCurrent | Rectifier total output current | 模块总输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rectifier total output current of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.26 | hwMTS9604BMTS9606BPowerSupplyRectifierAmount | Rectifier amount | 整流模块个数 | 0-Read_Only | 只读 | 0..8 | 0..8 | Rectifier amount of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.27 | hwMTS9604BMTS9606BPowerSupplyRectifierTotalDcPower | Rectifier total DC power | 直流总功率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Rectifier total DC power of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.28 | hwMTS9604BMTS9606BPowerSupplyAmbientTemperature | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -20..80 | -20..80 | Ambient temperature of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.29 | hwMTS9604BMTS9606BPowerSupplySoftwareEntireVersion | Software entire version | 软件完整版本号 | 0-Read_Only | 只读 | 0..28 | 0..28 | Software entire version of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.30 | hwMTS9604BMTS9606BPowerSupplyBatteryStatus | Battery status | 电池状态 | 0-Read_Only | 只读 | floatcharging(1), equalizedcharging(2), discharge(3), hibernated(4), unknown(255) | [浮充=1]/[均充=2]/[放电=3]/[休眠=4] | Battery status of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate floatcharging Value 2 indicate equalizedcharging Value 3 indicate discharge Value 4 indicate hibernated
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.31 | hwMTS9604BMTS9606BPowerSupplyTotalBatteryCurrent | Total battery current | 电池总电流 | 0-Read_Only | 只读 |  |  | Total battery current of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:A.
| hwMTS9604BMTS9606BPowerSupplyTotalBatteryRemainingCapacityPercent | Total battery remaining capacity percent | 电池总剩余容量百分比 | 0-Read_Only | 只读 |  |  | Total battery remaining capacity percent of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.33 | hwMTS9604BMTS9606BPowerSupplyBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 |  |  | Battery temperature of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.34 | hwMTS9604BMTS9606BPowerSupplyBatteryAmount | Battery amount | 电池电量 | 0-Read_Only | 只读 |  |  | Battery amount of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.1.1.300 | hwMTS9604B_MTS9606BPowerSupplyRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2 | hwMTS9604B_MTS9606BPowerSupplyConfig2Table | / | / |  |  | / | / | The config table of MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.1 | hwMTS9604B_MTS9606BPowerSupplyConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.2 | hwMTS9604BMTS9606BPowerSupplyDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.3 | hwMTS9604BMTS9606BPowerSupplyYear | Year | 年 | 1-Read_Write | 只读 | 2000..2037 | 2000..2037 | Year of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.4 | hwMTS9604BMTS9606BPowerSupplyMonth | Month | 月 | 1-Read_Write | 只读 | 1..12 | 1..12 | Month of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.5 | hwMTS9604BMTS9606BPowerSupplyDay | Day | 日 | 1-Read_Write | 只读 | 1..31 | 1..31 | Day of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.6 | hwMTS9604BMTS9606BPowerSupplyHour | Hour | 时 | 1-Read_Write | 只读 | 0..23 | 0..23 | Hour of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.7 | hwMTS9604BMTS9606BPowerSupplyMinute | Minute | 分 | 1-Read_Write | 只读 | 0..59 | 0..59 | Minute of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.8 | hwMTS9604BMTS9606BPowerSupplySecond | Second | 秒 | 1-Read_Write | 只读 | 0..59 | 0..59 | Second of the device config table for the MTS9604B_MTS9606B Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.9 | hwMTS9604BMTS9606BPowerSupplyAcOvervoltageThreshold | AC overvoltage threshold | 交流过压告警点 | 1-Read_Write | 读写 | 60..300 | 60..300 | AC overvoltage threshold of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.10 | hwMTS9604BMTS9606BPowerSupplyAcUndervoltageThreshold | AC undervoltage threshold | 交流欠压告警点 | 1-Read_Write | 读写 | 60..300 | 60..300 | AC undervoltage threshold of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.11 | hwMTS9604BMTS9606BPowerSupplyDcOvervoltageThreshold | DC overvoltage threshold | 直流过压告警点 | 1-Read_Write | 读写 | 530..600 | 530..600 | DC overvoltage threshold of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.12 | hwMTS9604BMTS9606BPowerSupplyDcUndervoltageThreshold | DC undervoltage threshold | 直流欠压告警点 | 1-Read_Write | 读写 | 350..570 | 350..570 | DC undervoltage threshold of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.13 | hwMTS9604BMTS9606BPowerSupplyLlvd1Enable | LLVD1 enable | LLVD1使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | LLVD1 enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.14 | hwMTS9604BMTS9606BPowerSupplyLlvd1Voltage | LLVD1 voltage | LLVD1下电电压 | 1-Read_Write | 读写 | 360..560 | 360..560 | LLVD1 voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.15 | hwMTS9604BMTS9606BPowerSupplyLlvd1ConnectionVoltage | LLVD1 connection voltage | LLVD1上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | LLVD1 connection voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.16 | hwMTS9604BMTS9606BPowerSupplyLlvd1DisconnectMode | LLVD1 disconnect mode | LLVD1下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | LLVD1 disconnect mode of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate voltagemode Value 2 indicate timemode Value 3 indicate capacitymode
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.17 | hwMTS9604BMTS9606BPowerSupplyLlvd1DisconnectTime | LLVD1 disconnect time | LLVD1下电时间 | 1-Read_Write | 读写 | 0..50000 | 0..50000 | LLVD1 disconnect time of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.18 | hwMTS9604BMTS9606BPowerSupplyLlvd1DisconnectCapacity | LLVD1 disconnect capacity | LLVD1下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | LLVD1 disconnect capacity of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.19 | hwMTS9604BMTS9606BPowerSupplyLlvd1HighTempDisconnectEnable | LLVD1 high temp disconnect enable | LLVD1高温下电 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD1 high temp disconnect enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.20 | hwMTS9604BMTS9606BPowerSupplyLlvd1HighTempDisconnectTemperature | LLVD1 high temp disconnect temperature | LLVD1高温下电温度 | 1-Read_Write | 读写 | 250..800 | 250..800 | LLVD1 high temp disconnect temperature of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.21 | hwMTS9604BMTS9606BPowerSupplyLlvd2Enable | LLVD2 enable | LLVD2使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | LLVD2 enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.22 | hwMTS9604BMTS9606BPowerSupplyLlvd2Voltage | LLVD2 voltage | LLVD2下电电压 | 1-Read_Write | 读写 | 360..560 | 360..560 | LLVD2 voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.23 | hwMTS9604BMTS9606BPowerSupplyLlvd2ConnectionVoltage | LLVD2 connection voltage | LLVD2上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | LLVD2 connection voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.24 | hwMTS9604BMTS9606BPowerSupplyLlvd2DisconnectMode | LLVD2 disconnect mode | LLVD2下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | LLVD2 disconnect mode of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate voltagemode Value 2 indicate timemode Value 3 indicate capacitymode
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.25 | hwMTS9604BMTS9606BPowerSupplyLlvd2DisconnectTime | LLVD2 disconnect time | LLVD2下电时间 | 1-Read_Write | 读写 | 0..50000 | 0..50000 | LLVD2 disconnect time of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.26 | hwMTS9604BMTS9606BPowerSupplyLlvd2DisconnectCapacity | LLVD2 disconnect capacity | LLVD2下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | LLVD2 disconnect capacity of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.27 | hwMTS9604BMTS9606BPowerSupplyLlvd2HighTempDisconnectEnable | LLVD2 high temp disconnect enable | LLVD2高温下电 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD2 high temp disconnect enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.28 | hwMTS9604BMTS9606BPowerSupplyLlvd2HighTempDisconnectTemperature | LLVD2 high temp disconnect temperature | LLVD2高温下电温度 | 1-Read_Write | 读写 | 250..800 | 250..800 | LLVD2 high temp disconnect temperature of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.29 | hwMTS9604BMTS9606BPowerSupplyLlvd3Enable | LLVD3 enable | LLVD3使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | LLVD3 enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.30 | hwMTS9604BMTS9606BPowerSupplyLlvd3DisconnectVoltage | LLVD3 disconnect voltage | LLVD3下电电压 | 1-Read_Write | 读写 | 350..560 | 350..560 | LLVD3 disconnect voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.31 | hwMTS9604BMTS9606BPowerSupplyLlvd3ConnectionVoltage | LLVD3 connection voltage | LLVD3上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | LLVD3 connection voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.32 | hwMTS9604BMTS9606BPowerSupplyLlvd3DisconnectMode | LLVD3 disconnect mode | LLVD3下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | LLVD3 disconnect mode of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate voltagemode Value 2 indicate timemode Value 3 indicate capacitymode
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.33 | hwMTS9604BMTS9606BPowerSupplyLlvd3DisconnectTime | LLVD3 disconnect time | LLVD3下电时间 | 1-Read_Write | 读写 | 0..50000 | 0..50000 | LLVD3 disconnect time of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.34 | hwMTS9604BMTS9606BPowerSupplyLlvd3DisconnectCapacity | LLVD3 disconnect capacity | LLVD3下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | LLVD3 disconnect capacity of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.35 | hwMTS9604BMTS9606BPowerSupplyLlvd3HighTempDisconnectEnable | LLVD3 high temp disconnect enable | LLVD3高温下电 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD3 high temp disconnect enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.36 | hwMTS9604BMTS9606BPowerSupplyLlvd3HighTempDisconnectTemperature | LLVD3 high temp disconnect temperature | LLVD3高温下电温度 | 1-Read_Write | 读写 | 250..800 | 250..800 | LLVD3 high temp disconnect temperature of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.37 | hwMTS9604BMTS9606BPowerSupplyLlvd4Enable | LLVD4 enable | LLVD4使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | LLVD4 enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.38 | hwMTS9604BMTS9606BPowerSupplyLlvd4DisconnectVoltage | LLVD4 disconnect voltage | LLVD4下电电压 | 1-Read_Write | 读写 | 350..560 | 350..560 | LLVD4 disconnect voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.39 | hwMTS9604BMTS9606BPowerSupplyLlvd4ConnectionVoltage | LLVD4 connection voltage | LLVD4上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | LLVD4 connection voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.40 | hwMTS9604BMTS9606BPowerSupplyLlvd4DisconnectMode | LLVD4 disconnect mode | LLVD4下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | LLVD4 disconnect mode of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate voltagemode Value 2 indicate timemode Value 3 indicate capacitymode
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.41 | hwMTS9604BMTS9606BPowerSupplyLlvd4DisconnectTime | LLVD4 disconnect time | LLVD4下电时间 | 1-Read_Write | 读写 | 0..50000 | 0..50000 | LLVD4 disconnect time of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.42 | hwMTS9604BMTS9606BPowerSupplyLlvd4DisconnectCapacity | LLVD4 disconnect capacity | LLVD4下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | LLVD4 disconnect capacity of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.43 | hwMTS9604BMTS9606BPowerSupplyLlvd4HighTempDisconnectEnable | LLVD4 high temp disconnect enable | LLVD4高温下电 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD4 high temp disconnect enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.44 | hwMTS9604BMTS9606BPowerSupplyLlvd4HighTempDisconnectTemperature | LLVD4 high temp disconnect temperature | LLVD4高温下电温度 | 1-Read_Write | 读写 | 250..800 | 250..800 | LLVD4 high temp disconnect temperature of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.45 | hwMTS9604BMTS9606BPowerSupplyResetControl | Reset control | 监控复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Reset control of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.46 | hwMTS9604BMTS9606BPowerSupplyResetSmokeSensor | Reset smoke sensor | 烟感复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Reset smoke sensor of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.47 | hwMTS9604BMTS9606BPowerSupplyAcOverfrequencyAlarmthreshold | AC overfrequency alarm threshold | 交流过频告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | AC overfrequency alarmthreshold of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.48 | hwMTS9604BMTS9606BPowerSupplyAcUnderfrequencyAlarmThreshold | AC underfrequency alarm threshold | 交流欠频告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | AC underfrequency alarm threshold of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.49 | hwMTS9604BMTS9606BPowerSupplyBatteryRatedCapacity | Battery rated capacity | 电池额定容量 | 1-Read_Write | 读写 | 5..10000 | 5..10000 | Battery rated capacity of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.50 | hwMTS9604BMTS9606BPowerSupplyFloatChargingVoltage | Float charging voltage | 浮充电压 | 1-Read_Write | 读写 | 420..580 | 420..580 | Float charging voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.51 | hwMTS9604BMTS9606BPowerSupplyBoostChargingVoltage | Boost charging voltage | 均充电压 | 1-Read_Write | 读写 | 420..580 | 420..580 | Boost charging voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.52 | hwMTS9604BMTS9606BPowerSupplyBlvdEnable | BLVD enable | BLVD使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | BLVD enable of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.53 | hwMTS9604BMTS9606BPowerSupplyBlvdVoltage | BLVD voltage | BLVD电压 | 1-Read_Write | 读写 | 360..560 | 360..560 | BLVD voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.54 | hwMTS9604BMTS9606BPowerSupplyBlvdConnectionVoltage | BLVD connection voltage | BLVD连接电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | BLVD connection voltage of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.55 | hwMTS9604BMTS9606BPowerSupplyChargeCurrentLimitCoefficient | Charge current limit coefficient | 充电限流系数 | 1-Read_Write | 读写 | 5..25 | 5..25 | Charge current limit coefficient of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.56 | hwMTS9604BMTS9606BPowerSupplyBlvdDisconnectMode | BLVD disconnect mode | BLVD下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | BLVD disconnect mode of the device config table for the MTS9604B_MTS9606B Power Supply. Value 1 indicate voltagemode Value 2 indicate timemode Value 3 indicate capacitymode
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.57 | hwMTS9604BMTS9606BPowerSupplyBlvdDisconnectTime | BLVD disconnect time | BLVD下电时间 | 1-Read_Write | 读写 | 0..10000 | 0..10000 | BLVD disconnect time of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.58 | hwMTS9604BMTS9606BPowerSupplyBlvdDisconnectCapacity | BLVD disconnect capacity | BLVD下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | BLVD disconnect capacity of the device config table for the MTS9604B_MTS9606B Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.59 | hwMTS9604BMTS9606BPowerSupplyBatteryLowAlarmThreshold | Battery low alarm threshold | 电池电量低告警阈值 | 1-Read_Write | 读写 | 10..40 | 10..40 | Battery low alarm threshold of the device config table for the MTS9604B_MTS9606B Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.32.2.1.300 | hwMTS9604B_MTS9606BPowerSupplyConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of MTS9604B_MTS9606B Power Supply.

## iTEMP
iTEMP
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.131.2 | iTEMP | iTEMP | iTEMP | / | / | / | / | iTEMP Equipment.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1 | hwiTEMPRunningandConfig1Table | / | / |  |  | / | / | The running table of iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.1 | hwiTEMPRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.2 | hwiTEMPCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | commFailed(1), commSuccess(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the iTEMP. Value 1 indicate comm failed Value 2 indicate comm success
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.3 | hwiTEMPTemperature | Temperature | 温度 | 0-Read_Only | 只读 | -20..80 | -20..80 | Temperature of the device config table for the iTEMP.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.4 | hwiTEMPHumidity | Humidity | 湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity of the device config table for the iTEMP.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.5 | hwiTEMPBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery voltage of the device config table for the iTEMP.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.6 | hwiTEMPBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Battery temperature of the device config table for the iTEMP.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.7 | hwiTEMPRemainingSensorBatteryCapacity | Remaining sensor battery capacity | 传感器电池剩余容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Remaining sensor battery capacity of the device config table for the iTEMP.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.8 | hwiTEMPBatteryCapacityState | Battery capacity state | 电池容量状态 | 0-Read_Only | 只读 | full(1), aroundHalf(2), needToReplace(3), unknown(255) | [满电=1]/[半电=2]/[需更换=3] | Battery capacity state of the device config table for the iTEMP. Value 1 indicate full Value 2 indicate around half Value 3 indicate need to replace
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.9 | hwiTEMPWorkState | Work state | 工作状态 | 0-Read_Only | 只读 | sleeping(1), wakePeriodically(2), wakeManually(3), off(4), unknown(255) | [休眠=1]/[定时唤醒=2]/[手动唤醒=3]/[关机=4] | Work state of the device config table for the iTEMP. Value 1 indicate sleeping Value 2 indicate wake periodically Value 3 indicate wake manually Value 4 indicate off
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.10 | hwiTEMPAmbientTemperatureStatus | Ambient temperature status | 环境温度状态 | 0-Read_Only | 只读 | 1..255 | 1..255 | Ambient temperature status of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.11 | hwiTEMPAmbientHumidityStatus | Ambient humidity status | 环境湿度状态 | 0-Read_Only | 只读 | 1..255 | 1..255 | Ambient humidity status of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.12 | hwiTEMPSoftwarePackageVersion | Software package version | 软件包版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Software package version of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.13 | hwiTEMPWirelessSubboardHwVersion | Wireless subboard HW version | 无线扣板硬件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Wireless subboard HW version of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.14 | hwiTEMPNodeASoftwareVersion | Node A software version | 节点A软件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Node A software version of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.15 | hwiTEMPSensorBatteryCapacityLow | / | / | 0-Read_Only | 只读 | normal(1), low(2), unknown(255) | / | Sensor battery capacity low of the device config table for the iTEMP. Value 1 indicate normal Value 2 indicate low
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.16 | hwiTEMPNodeANetState | Node A net state | 节点A组网状态 | 0-Read_Only | 只读 | notConnected(1), connected(2), unknown(255) | [未组网=1]/[组网成功=2] | Node A net state of the device config table for the iTEMP. Value 1 indicate not connected Value 2 indicate connected
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.17 | hwiTEMPNodeANetPanid | Node A net PANID | 节点A网络PANID | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net PANID of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.18 | hwiTEMPNodeANetShortAddress | Node A net short address | 节点A网络短地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net short address of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.19 | hwiTEMPNodeAMacAddress | Node A MAC address | 节点A MAC地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A MAC address of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.20 | hwiTEMPDeviceDetails | Device details | 设备详细信息 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Device details of the device config table for the iTEMP. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.21 | hwiTEMPReportingPeriod | Reporting period | 上报周期 | 1-Read_Write | 读写 | 20..30 | 20..30 | Reporting period of the device config table for the iTEMP.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.22 | hwiTEMPSamplingPeriod | Sampling period | 采样周期 | 1-Read_Write | 读写 | 240..300 | 240..300 | Sampling period of the device config table for the iTEMP.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.23 | hwiTEMPAmbientHighTemperatureThreshold | Ambient high temperature threshold | 环境温度高告警点 | 1-Read_Write | 读写 | -15..75 | -15..75 | Ambient high temperature threshold of the device config table for the iTEMP.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.24 | hwiTEMPAmbientLowTemperatureThreshold | Ambient low temperature threshold | 环境温度低告警点 | 1-Read_Write | 读写 | -15..75 | -15..75 | Ambient low temperature threshold of the device config table for the iTEMP.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.25 | hwiTEMPAmbientUltraHighTemperatureThreshold | Ambient ultra high temperature threshold | 环境高温告警点 | 1-Read_Write | 读写 | 25..75 | 25..75 | Ambient ultra high temperature threshold of the device config table for the iTEMP.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.26 | hwiTEMPAmbientHighHumidityThreshold | Ambient high humidity threshold | 环境湿度高告警点 | 1-Read_Write | 读写 | 5..95 | 5..95 | Ambient high humidity threshold of the device config table for the iTEMP.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.27 | hwiTEMPAmbientLowHumidityThreshold | Ambient low humidity threshold | 环境湿度低告警点 | 1-Read_Write | 读写 | 5..95 | 5..95 | Ambient low humidity threshold of the device config table for the iTEMP.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.28 | hwiTEMPResetBoard | Reset board | 单板复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Reset board of the device config table for the iTEMP. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.29 | hwiTEMPLedBlink | LED blink | LED眨眼 | 1-Read_Write | 读写 | start(1) | [开始眨眼=1] | LED blink of the device config table for the iTEMP. Value 1 indicate start
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.30 | hwiTEMPTorHSensorIdOnNms | T/H sensor ID on NMS | 网管用温湿度编号 | 1-Read_Write | 读写 | 0..10 | 0..10 | T/H sensor ID on NMS of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.31 | hwiTEMPNodeAMaxTransmitPower | Node A max transmit power | 节点A允许最大发射功率 | 1-Read_Write | 读写 | 0..15 | 0..15 | Node A max transmit power of the device config table for the iTEMP.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.32 | hwiTEMPDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.33 | hwiTEMPEsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | Esn of the device config table for the iTEMP.
1.3.6.1.4.1.2011.6.178.1.1.131.2.1.1.300 | hwiTEMPRunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iTEMP.

## iWATER
iWATER
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.131.1 | iWATER | iWATER | iWATER | / | / | / | / | iWATER Equipment.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1 | hwiWATERRunningandConfig1Table | / | / |  |  | / | / | The running table of iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.1 | hwiWATERRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.2 | hwiWATERCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | commFailed(1), commSuccess(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the iWATER. Value 1 indicate comm failed Value 2 indicate comm success
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.3 | hwiWATERWateringState | Watering state | 水浸状态 | 0-Read_Only | 只读 | normal(1), iwater(2), unknown(255) | [正常=1]/[水浸=2] | Watering state of the device config table for the iWATER. Value 1 indicate normal Value 2 indicate iwater
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.4 | hwiWATERBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | Battery voltage of the device config table for the iWATER.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.5 | hwiWATERBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Battery temperature of the device config table for the iWATER.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.6 | hwiWATERBatteryCapacityState | Battery capacity state | 电池容量状态 | 0-Read_Only | 只读 | full(1), aroundHalf(2), needToReplace(3), unknown(255) | [满电=1]/[半电=2]/[需更换=3] | Battery capacity state of the device config table for the iWATER. Value 1 indicate full Value 2 indicate around half Value 3 indicate need to replace
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.7 | hwiWATERWorkState | Work state | 工作状态 | 0-Read_Only | 只读 | sleeping(1), wakePeriodically(2), wakeManually(3), off(4), unknown(255) | [休眠=1]/[定时唤醒=2]/[手动唤醒=3]/[关机=4] | Work state of the device config table for the iWATER. Value 1 indicate sleeping Value 2 indicate wake periodically Value 3 indicate wake manually Value 4 indicate off
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.8 | hwiWATERSensorBatteryCapacityLow | / | / | 0-Read_Only | 只读 | normal(1), low(2), unknown(255) | / | Sensor battery capacity low of the device config table for the iWATER. Value 1 indicate normal Value 2 indicate low
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.9 | hwiWATERWirelessSubboardHwVersion | Wireless subboard HW version | 无线扣板硬件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Wireless subboard HW version of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.10 | hwiWATERSoftwarePackageVersion | Software package version | 软件包版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Software package version of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.11 | hwiWATERNodeASoftwareVersion | Node A software version | 节点A软件版本 | 0-Read_Only | 只读 | 0..5 | 0..5 | Node A software version of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.12 | hwiWATERNodeANetState | Node A net state | 节点A组网状态 | 0-Read_Only | 只读 | notConnected(1), connected(2), unknown(255) | [未组网=1]/[组网成功=2] | Node A net state of the device config table for the iWATER. Value 1 indicate not connected Value 2 indicate connected
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.13 | hwiWATERNodeANetPanid | Node A net PANID | 节点A网络PANID | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net PANID of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.14 | hwiWATERNodeANetShortAddress | Node A net short address | 节点A网络短地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A net short address of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.15 | hwiWATERNodeAMacAddress | Node A MAC address | 节点A MAC地址 | 0-Read_Only | 只读 | 0..23 | 0..23 | Node A MAC address of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.16 | hwiWATERDeviceDetails | Device details | 设备详细信息 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Device details of the device config table for the iWATER. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.17 | hwiWATERWaterSensorIdOnNms | Water sensor ID on NMS | 网管用水浸编号 | 1-Read_Write | 读写 | 0..10 | 0..10 | Water sensor ID on NMS of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.18 | hwiWATERBlinkDuration | Blink duration | 眨眼时长 | 1-Read_Write | 读写 | 5..120 | 5..120 | Blink duration of the device config table for the iWATER.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.19 | hwiWATERResetBoard | Reset board | 单板复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | Reset board of the device config table for the iWATER. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.20 | hwiWATERReportingPeriod | Reporting period | 上报周期 | 1-Read_Write | 读写 | 20..30 | 20..30 | Reporting period of the device config table for the iWATER.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.21 | hwiWATERNodeAMaxTransmitPower | Node A max transmit power | 节点A允许最大发射功率 | 1-Read_Write | 读写 | 0..15 | 0..15 | Node A max transmit power of the device config table for the iWATER.SigUnitInfo:dBm.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.22 | hwiWATERLedBlink | LED blink | LED眨眼 | 1-Read_Write | 读写 | start(1) | [开始眨眼=1] | LED blink of the device config table for the iWATER. Value 1 indicate start
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.23 | hwiWATERDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.24 | hwiWATEREsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the iWATER.
1.3.6.1.4.1.2011.6.178.1.1.131.1.1.1.300 | hwiWATERRunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of iWATER.

## Lithium Battery Cabinet
锂电柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.100 | Lithiumbatterycabinet | Lithium Battery Cabinet | 锂电柜 | / | / | / | / | Lithium battery cabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.100.1 | hwLithiumbatterycabinetRunning1Table | / | / |  |  | / | / | The running table of Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.1 | hwLithiumbatterycabinetRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.2 | hwLithiumbatterycabinetRunningStatus | Running status | 运行状态 | 0-Read_Only | 只读 | standby(1), charging(2), discharging(3), fault(4), unknown(255) | [待机=1]/[充电=2]/[放电=3]/[故障=4] | Running status of the device config table for the Lithium battery cabinet. Value 1 indicate standby Value 2 indicate charging Value 3 indicate discharging Value 4 indicate fault
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.3 | hwLithiumbatterycabinetBatteryModule1MaxCellVoltage | Battery module 1 max cell voltage | 电池模块1电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 1 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.4 | hwLithiumbatterycabinetCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Lithium battery cabinet. Value 1 indicate normal Value 2 indicate abnormal
| hwLithiumbatterycabinetELabel | / | / | 0-Read_Only | 只读 | 0..2048 | / | E label of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.6 | hwLithiumbatterycabinetBatteryCabinetId | Battery cabinet id | 电池柜编号 | 0-Read_Only | 只读 | 0..15 | 0..15 | Battery cabinet id of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.7 | hwLithiumbatterycabinetRealtedBatterySystemId | Related battery system id | 关联电池系统编号 | 0-Read_Only | 只读 | 1..7 | 1..7 | Related battery system id of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.8 | hwLithiumbatterycabinetBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery voltage of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.9 | hwLithiumbatterycabinetBatteryCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -10000..10000 | -10000..10000 | Battery current of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.10 | hwLithiumbatterycabinetSoc | SOC | SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.11 | hwLithiumbatterycabinetSoh | SOH | SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.12 | hwLithiumbatterycabinetMaximumCellVoltage | Maximum cell voltage | 电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Maximum cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.13 | hwLithiumbatterycabinetMinimumCellVoltage | Minimum cell voltage | 电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Minimum cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.14 | hwLithiumbatterycabinetMaximumCellTemperature | Maximum cell temperature | 电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Maximum cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.15 | hwLithiumbatterycabinetMinimumCellTemperature | Minimum cell temperature | 电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Minimum cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.16 | hwLithiumbatterycabinetBatteryModuleQuantity | Battery module quantity | 电池模块数量 | 0-Read_Only | 只读 | 0..16 | 0..16 | Battery module quantity of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.17 | hwLithiumbatterycabinetTotalDischargeTimes | Total discharge times | 累计放电次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Total discharge times of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.18 | hwLithiumbatterycabinetTotalDischargeCapacity | Total discharge capacity | 累计放电容量 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Total discharge capacity of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.19 | hwLithiumbatterycabinetBatteryModule2MaxCellVoltage | Battery module 2 max cell voltage | 电池模块2电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 2 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.20 | hwLithiumbatterycabinetBatteryModule3MaxCellVoltage | Battery module 3 max cell voltage | 电池模块3电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 3 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.21 | hwLithiumbatterycabinetBatteryModule4MaxCellVoltage | Battery module 4 max cell voltage | 电池模块4电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 4 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.22 | hwLithiumbatterycabinetBatteryModule5MaxCellVoltage | Battery module 5 max cell voltage | 电池模块5电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 5 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.23 | hwLithiumbatterycabinetBatteryModule6MaxCellVoltage | Battery module 6 max cell voltage | 电池模块6电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 6 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.24 | hwLithiumbatterycabinetBatteryModule7MaxCellVoltage | Battery module 7 max cell voltage | 电池模块7电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 7 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.25 | hwLithiumbatterycabinetBatteryModule8MaxCellVoltage | Battery module 8 max cell voltage | 电池模块8电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 8 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.26 | hwLithiumbatterycabinetBatteryModule9MaxCellVoltage | Battery module 9 max cell voltage | 电池模块9电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 9 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.27 | hwLithiumbatterycabinetBatteryModule10MaxCellVoltage | Battery module 10 max cell voltage | 电池模块10电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 10 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.28 | hwLithiumbatterycabinetBatteryModule11MaxCellVoltage | Battery module 11 max cell voltage | 电池模块11电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 11 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.29 | hwLithiumbatterycabinetBatteryModule12MaxCellVoltage | Battery module 12 max cell voltage | 电池模块12电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 12 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.30 | hwLithiumbatterycabinetBatteryModule13MaxCellVoltage | Battery module 13 max cell voltage | 电池模块13电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 13 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.31 | hwLithiumbatterycabinetBatteryModule14MaxCellVoltage | Battery module 14 max cell voltage | 电池模块14电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 14 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.32 | hwLithiumbatterycabinetBatteryModule15MaxCellVoltage | Battery module 15 max cell voltage | 电池模块15电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 15 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.33 | hwLithiumbatterycabinetBatteryModule16MaxCellVoltage | Battery module 16 max cell voltage | 电池模块16电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 16 max cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.34 | hwLithiumbatterycabinetBatteryModule1MinCellVoltage | Battery module 1 min cell voltage | 电池模块1电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 1 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.35 | hwLithiumbatterycabinetBatteryModule2MinCellVoltage | Battery module 2 min cell voltage | 电池模块2电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 2 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.36 | hwLithiumbatterycabinetBatteryModule3MinCellVoltage | Battery module 3 min cell voltage | 电池模块3电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 3 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.37 | hwLithiumbatterycabinetBatteryModule4MinCellVoltage | Battery module 4 min cell voltage | 电池模块4电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 4 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.38 | hwLithiumbatterycabinetBatteryModule5MinCellVoltage | Battery module 5 min cell voltage | 电池模块5电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 5 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.39 | hwLithiumbatterycabinetBatteryModule6MinCellVoltage | Battery module 6 min cell voltage | 电池模块6电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 6 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.40 | hwLithiumbatterycabinetBatteryModule7MinCellVoltage | Battery module 7 min cell voltage | 电池模块7电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 7 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.41 | hwLithiumbatterycabinetBatteryModule8MinCellVoltage | Battery module 8 min cell voltage | 电池模块8电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 8 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.42 | hwLithiumbatterycabinetBatteryModule9MinCellVoltage | Battery module 9 min cell voltage | 电池模块9电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 9 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.43 | hwLithiumbatterycabinetBatteryModule10MinCellVoltage | Battery module 10 min cell voltage | 电池模块10电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 10 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.44 | hwLithiumbatterycabinetBatteryModule11MinCellVoltage | Battery module 11 min cell voltage | 电池模块11电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 11 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.45 | hwLithiumbatterycabinetBatteryModule12MinCellVoltage | Battery module 12 min cell voltage | 电池模块12电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 12 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.46 | hwLithiumbatterycabinetBatteryModule13MinCellVoltage | Battery module 13 min cell voltage | 电池模块13电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 13 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.47 | hwLithiumbatterycabinetBatteryModule14MinCellVoltage | Battery module 14 min cell voltage | 电池模块14电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 14 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.48 | hwLithiumbatterycabinetBatteryModule15MinCellVoltage | Battery module 15 min cell voltage | 电池模块15电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 15 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.49 | hwLithiumbatterycabinetBatteryModule16MinCellVoltage | Battery module 16 min cell voltage | 电池模块16电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery module 16 min cell voltage of the device config table for the Lithium battery cabinet.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.50 | hwLithiumbatterycabinetBatteryModule1MaxCellTemperature | Battery module 1 max cell temperature | 电池模块1电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 1 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.51 | hwLithiumbatterycabinetBatteryModule2MaxCellTemperature | Battery module 2 max cell temperature | 电池模块2电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 2 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.52 | hwLithiumbatterycabinetBatteryModule3MaxCellTemperature | Battery module 3 max cell temperature | 电池模块3电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 3 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.53 | hwLithiumbatterycabinetBatteryModule4MaxCellTemperature | Battery module 4 max cell temperature | 电池模块4电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 4 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.54 | hwLithiumbatterycabinetBatteryModule5MaxCellTemperature | Battery module 5 max cell temperature | 电池模块5电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 5 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.55 | hwLithiumbatterycabinetBatteryModule6MaxCellTemperature | Battery module 6 max cell temperature | 电池模块6电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 6 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.56 | hwLithiumbatterycabinetBatteryModule7MaxCellTemperature | Battery module 7 max cell temperature | 电池模块7电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 7 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.57 | hwLithiumbatterycabinetBatteryModule8MaxCellTemperature | Battery module 8 max cell temperature | 电池模块8电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 8 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.58 | hwLithiumbatterycabinetBatteryModule9MaxCellTemperature | Battery module 9 max cell temperature | 电池模块9电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 9 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.59 | hwLithiumbatterycabinetBatteryModule10MaxCellTemperature | Battery module 10 max cell temperature | 电池模块10电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 10 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.60 | hwLithiumbatterycabinetBatteryModule11MaxCellTemperature | Battery module 11 max cell temperature | 电池模块11电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 11 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.61 | hwLithiumbatterycabinetBatteryModule12MaxCellTemperature | Battery module 12 max cell temperature | 电池模块12电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 12 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.62 | hwLithiumbatterycabinetBatteryModule13MaxCellTemperature | Battery module 13 max cell temperature | 电池模块13电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 13 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.63 | hwLithiumbatterycabinetBatteryModule14MaxCellTemperature | Battery module 14 max cell temperature | 电池模块14电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 14 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.64 | hwLithiumbatterycabinetBatteryModule15MaxCellTemperature | Battery module 15 max cell temperature | 电池模块15电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 15 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.65 | hwLithiumbatterycabinetBatteryModule16MaxCellTemperature | Battery module 16 max cell temperature | 电池模块16电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 16 max cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.66 | hwLithiumbatterycabinetBatteryModule1MinCellTemperature | Battery module 1 min cell temperature | 电池模块1电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 1 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.67 | hwLithiumbatterycabinetBatteryModule2MinCellTemperature | Battery module 2 min cell temperature | 电池模块2电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 2 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.68 | hwLithiumbatterycabinetBatteryModule3MinCellTemperature | Battery module 3 min cell temperature | 电池模块3电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 3 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.69 | hwLithiumbatterycabinetBatteryModule4MinCellTemperature | Battery module 4 min cell temperature | 电池模块4电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 4 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.70 | hwLithiumbatterycabinetBatteryModule5MinCellTemperature | Battery module 5 min cell temperature | 电池模块5电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 5 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.71 | hwLithiumbatterycabinetBatteryModule6MinCellTemperature | Battery module 6 min cell temperature | 电池模块6电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 6 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.72 | hwLithiumbatterycabinetBatteryModule7MinCellTemperature | Battery module 7 min cell temperature | 电池模块7电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 7 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.73 | hwLithiumbatterycabinetBatteryModule8MinCellTemperature | Battery module 8 min cell temperature | 电池模块8电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 8 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.74 | hwLithiumbatterycabinetBatteryModule9MinCellTemperature | Battery module 9 min cell temperature | 电池模块9电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 9 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.75 | hwLithiumbatterycabinetBatteryModule10MinCellTemperature | Battery module 10 min cell temperature | 电池模块10电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 10 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.76 | hwLithiumbatterycabinetBatteryModule11MinCellTemperature | Battery module 11 min cell temperature | 电池模块11电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 11 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.77 | hwLithiumbatterycabinetBatteryModule12MinCellTemperature | Battery module 12 min cell temperature | 电池模块12电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 12 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.78 | hwLithiumbatterycabinetBatteryModule13MinCellTemperature | Battery module 13 min cell temperature | 电池模块13电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 13 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.79 | hwLithiumbatterycabinetBatteryModule14MinCellTemperature | Battery module 14 min cell temperature | 电池模块14电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 14 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.80 | hwLithiumbatterycabinetBatteryModule15MinCellTemperature | Battery module 15 min cell temperature | 电池模块15电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 15 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.81 | hwLithiumbatterycabinetBatteryModule16MinCellTemperature | Battery module 16 min cell temperature | 电池模块16电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Battery module 16 min cell temperature of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.82 | hwLithiumbatterycabinetBatteryModule1Voltage | Battery module 1 voltage | 电池模块1电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 1 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.83 | hwLithiumbatterycabinetBatteryModule2Voltage | Battery module 2 voltage | 电池模块2电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 2 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.84 | hwLithiumbatterycabinetBatteryModule3Voltage | Battery module 3 voltage | 电池模块3电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 3 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.85 | hwLithiumbatterycabinetBatteryModule4Voltage | Battery module 4 voltage | 电池模块4电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 4 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.86 | hwLithiumbatterycabinetBatteryModule5Voltage | Battery module 5 voltage | 电池模块5电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 5 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.87 | hwLithiumbatterycabinetBatteryModule6Voltage | Battery module 6 voltage | 电池模块6电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 6 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.88 | hwLithiumbatterycabinetBatteryModule7Voltage | Battery module 7 voltage | 电池模块7电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 7 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.89 | hwLithiumbatterycabinetBatteryModule8Voltage | Battery module 8 voltage | 电池模块8电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 8 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.90 | hwLithiumbatterycabinetBatteryModule9Voltage | Battery module 9 voltage | 电池模块9电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 9 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.91 | hwLithiumbatterycabinetBatteryModule10Voltage | Battery module 10 voltage | 电池模块10电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 10 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.92 | hwLithiumbatterycabinetBatteryModule11Voltage | Battery module 11 voltage | 电池模块11电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 11 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.93 | hwLithiumbatterycabinetBatteryModule12Voltage | Battery module 12 voltage | 电池模块12电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 12 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.94 | hwLithiumbatterycabinetBatteryModule13Voltage | Battery module 13 voltage | 电池模块13电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 13 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.95 | hwLithiumbatterycabinetBatteryModule14Voltage | Battery module 14 voltage | 电池模块14电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 14 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.96 | hwLithiumbatterycabinetBatteryModule15Voltage | Battery module 15 voltage | 电池模块15电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 15 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.97 | hwLithiumbatterycabinetBatteryModule16Voltage | Battery module 16 voltage | 电池模块16电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery module 16 voltage of the device config table for the Lithium battery cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.98 | hwLithiumbatterycabinetBatteryModule1Soc | Battery module 1 SOC | 电池模块1SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 1 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.99 | hwLithiumbatterycabinetBatteryModule2Soc | Battery module 2 SOC | 电池模块2SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 2 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.100 | hwLithiumbatterycabinetBatteryModule3Soc | Battery module 3 SOC | 电池模块3SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 3 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.101 | hwLithiumbatterycabinetBatteryModule4Soc | Battery module 4 SOC | 电池模块4SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 4 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.102 | hwLithiumbatterycabinetBatteryModule5Soc | Battery module 5 SOC | 电池模块5SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 5 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.103 | hwLithiumbatterycabinetBatteryModule6Soc | Battery module 6 SOC | 电池模块6SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 6 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.104 | hwLithiumbatterycabinetBatteryModule7Soc | Battery module 7 SOC | 电池模块7SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 7 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.105 | hwLithiumbatterycabinetBatteryModule8Soc | Battery module 8 SOC | 电池模块8SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 8 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.106 | hwLithiumbatterycabinetBatteryModule9Soc | Battery module 9 SOC | 电池模块9SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 9 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.107 | hwLithiumbatterycabinetBatteryModule10Soc | Battery module 10 SOC | 电池模块10SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 10 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.108 | hwLithiumbatterycabinetBatteryModule11Soc | Battery module 11 SOC | 电池模块11SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 11 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.109 | hwLithiumbatterycabinetBatteryModule12Soc | Battery module 12 SOC | 电池模块12SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 12 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.110 | hwLithiumbatterycabinetBatteryModule13Soc | Battery module 13 SOC | 电池模块13SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 13 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.111 | hwLithiumbatterycabinetBatteryModule14Soc | Battery module 14 SOC | 电池模块14SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 14 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.112 | hwLithiumbatterycabinetBatteryModule15Soc | Battery module 15 SOC | 电池模块15SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 15 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.113 | hwLithiumbatterycabinetBatteryModule16Soc | Battery module 16 SOC | 电池模块16SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 16 SOC of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.114 | hwLithiumbatterycabinetBatteryModule1Soh | Battery module 1 SOH | 电池模块1SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 1 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.115 | hwLithiumbatterycabinetBatteryModule2Soh | Battery module 2 SOH | 电池模块2SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 2 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.116 | hwLithiumbatterycabinetBatteryModule3Soh | Battery module 3 SOH | 电池模块3SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 3 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.117 | hwLithiumbatterycabinetBatteryModule4Soh | Battery module 4 SOH | 电池模块4SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 4 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.118 | hwLithiumbatterycabinetBatteryModule5Soh | Battery module 5 SOH | 电池模块5SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 5 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.119 | hwLithiumbatterycabinetBatteryModule6Soh | Battery module 6 SOH | 电池模块6SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 6 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.120 | hwLithiumbatterycabinetBatteryModule7Soh | Battery module 7 SOH | 电池模块7SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 7 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.121 | hwLithiumbatterycabinetBatteryModule8Soh | Battery module 8 SOH | 电池模块8SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 8 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.122 | hwLithiumbatterycabinetBatteryModule9Soh | Battery module 9 SOH | 电池模块9SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 9 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.123 | hwLithiumbatterycabinetBatteryModule10Soh | Battery module 10 SOH | 电池模块10SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 10 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.124 | hwLithiumbatterycabinetBatteryModule11Soh | Battery module 11 SOH | 电池模块11SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 11 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.125 | hwLithiumbatterycabinetBatteryModule12Soh | Battery module 12 SOH | 电池模块12SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 12 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.126 | hwLithiumbatterycabinetBatteryModule13Soh | Battery module 13 SOH | 电池模块13SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 13 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.127 | hwLithiumbatterycabinetBatteryModule14Soh | Battery module 14 SOH | 电池模块14SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 14 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.128 | hwLithiumbatterycabinetBatteryModule15Soh | Battery module 15 SOH | 电池模块15SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 15 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.129 | hwLithiumbatterycabinetBatteryModule16Soh | Battery module 16 SOH | 电池模块16SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery module 16 SOH of the device config table for the Lithium battery cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.130 | hwLithiumbatterycabinetESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.131 | hwLithiumbatterycabinetBatterycapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery capacity of the device config table for the Lithium battery cabinet.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.132 | hwLithiumbatterycabinetBatMd1TotalTimeMaxCellTemp60To125 | Battery module 1 total time for max cell temperature [60,125]°C | 电池模块1电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 1 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.133 | hwLithiumbatterycabinetBatMd2TotalTimeMaxCellTemp60To125 | Battery module 2 total time for max cell temperature [60,125]°C | 电池模块2电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 2 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.134 | hwLithiumbatterycabinetBatMd3TotalTimeMaxCellTemp60To125 | Battery module 3 total time for max cell temperature [60,125]°C | 电池模块3电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 3 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.135 | hwLithiumbatterycabinetBatMd4TotalTimeMaxCellTemp60To125 | Battery module 4 total time for max cell temperature [60,125]°C | 电池模块4电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 4 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.136 | hwLithiumbatterycabinetBatMd5TotalTimeMaxCellTemp60To125 | Battery module 5 total time for max cell temperature [60,125]°C | 电池模块5电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 5 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.137 | hwLithiumbatterycabinetBatMd6TotalTimeMaxCellTemp60To125 | Battery module 6 total time for max cell temperature [60,125]°C | 电池模块6电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 6 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.138 | hwLithiumbatterycabinetBatMd7TotalTimeMaxCellTemp60To125 | Battery module 7 total time for max cell temperature [60,125]°C | 电池模块7电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 7 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.139 | hwLithiumbatterycabinetBatMd8TotalTimeMaxCellTemp60To125 | Battery module 8 total time for max cell temperature [60,125]°C | 电池模块8电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 8 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.140 | hwLithiumbatterycabinetBatMd9TotalTimeMaxCellTemp60To125 | Battery module 9 total time for max cell temperature [60,125]°C | 电池模块9电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 9 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.141 | hwLithiumbatterycabinetBatMd10TotalTimeMaxCellTemp60To125 | Battery module 10 total time for max cell temperature [60,125]°C | 电池模块10电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 10 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.142 | hwLithiumbatterycabinetBatMd11TotalTimeMaxCellTemp60To125 | Battery module 11 total time for max cell temperature [60,125]°C | 电池模块11电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 11 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.143 | hwLithiumbatterycabinetBatMd12TotalTimeMaxCellTemp60To125 | Battery module 12 total time for max cell temperature [60,125]°C | 电池模块12电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 12 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.144 | hwLithiumbatterycabinetBatMd13TotalTimeMaxCellTemp60To125 | Battery module 13 total time for max cell temperature [60,125]°C | 电池模块13电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 13 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.145 | hwLithiumbatterycabinetBatMd14TotalTimeMaxCellTemp60To125 | Battery module 14 total time for max cell temperature [60,125]°C | 电池模块14电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 14 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.146 | hwLithiumbatterycabinetBatMd15TotalTimeMaxCellTemp60To125 | Battery module 15 total time for max cell temperature [60,125]°C | 电池模块15电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 15 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.147 | hwLithiumbatterycabinetBatMd16TotalTimeMaxCellTemp60To125 | Battery module 16 total time for max cell temperature [60,125]°C | 电池模块16电芯最高温度[60,125]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 16 total time for max cell temperature 60 to 125 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.148 | hwLithiumbatterycabinetBatMd1TotalTimeMaxCellTemp50To60 | Battery module 1 total time for max cell temperature [50,60]°C | 电池模块1电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 1 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.149 | hwLithiumbatterycabinetBatMd2TotalTimeMaxCellTemp50To60 | Battery module 2 total time for max cell temperature [50,60]°C | 电池模块2电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 2 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.150 | hwLithiumbatterycabinetBatMd3TotalTimeMaxCellTemp50To60 | Battery module 3 total time for max cell temperature [50,60]°C | 电池模块3电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 3 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.151 | hwLithiumbatterycabinetBatMd4TotalTimeMaxCellTemp50To60 | Battery module 4 total time for max cell temperature [50,60]°C | 电池模块4电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 4 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.152 | hwLithiumbatterycabinetBatMd5TotalTimeMaxCellTemp50To60 | Battery module 5 total time for max cell temperature [50,60]°C | 电池模块5电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 5 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.153 | hwLithiumbatterycabinetBatMd6TotalTimeMaxCellTemp50To60 | Battery module 6 total time for max cell temperature [50,60]°C | 电池模块6电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 6 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.154 | hwLithiumbatterycabinetBatMd7TotalTimeMaxCellTemp50To60 | Battery module 7 total time for max cell temperature [50,60]°C | 电池模块7电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 7 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.155 | hwLithiumbatterycabinetBatMd8TotalTimeMaxCellTemp50To60 | Battery module 8 total time for max cell temperature [50,60]°C | 电池模块8电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 8 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.156 | hwLithiumbatterycabinetBatMd9TotalTimeMaxCellTemp50To60 | Battery module 9 total time for max cell temperature [50,60]°C | 电池模块9电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 9 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.157 | hwLithiumbatterycabinetBatMd10TotalTimeMaxCellTemp50To60 | Battery module 10 total time for max cell temperature [50,60]°C | 电池模块10电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 10 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.158 | hwLithiumbatterycabinetBatMd11TotalTimeMaxCellTemp50To60 | Battery module 11 total time for max cell temperature [50,60]°C | 电池模块11电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 11 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.159 | hwLithiumbatterycabinetBatMd12TotalTimeMaxCellTemp50To60 | Battery module 12 total time for max cell temperature [50,60]°C | 电池模块12电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 12 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.160 | hwLithiumbatterycabinetBatMd13TotalTimeMaxCellTemp50To60 | Battery module 13 total time for max cell temperature [50,60]°C | 电池模块13电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 13 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.161 | hwLithiumbatterycabinetBatMd14TotalTimeMaxCellTemp50To60 | Battery module 14 total time for max cell temperature [50,60]°C | 电池模块14电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 14 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.162 | hwLithiumbatterycabinetBatMd15TotalTimeMaxCellTemp50To60 | Battery module 15 total time for max cell temperature [50,60]°C | 电池模块15电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 15 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.163 | hwLithiumbatterycabinetBatMd16TotalTimeMaxCellTemp50To60 | Battery module 16 total time for max cell temperature [50,60]°C | 电池模块16电芯最高温度[50,60]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 16 total time for max cell temperature 50 to 60 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.164 | hwLithiumbatterycabinetBatMd1TotalTimeMaxCellTemp40To50 | Battery module 1 total time for max cell temperature [40,50]°C | 电池模块1电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 1 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.165 | hwLithiumbatterycabinetBatMd2TotalTimeMaxCellTemp40To50 | Battery module 2 total time for max cell temperature [40,50]°C | 电池模块2电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 2 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.166 | hwLithiumbatterycabinetBatMd3TotalTimeMaxCellTemp40To50 | Battery module 3 total time for max cell temperature [40,50]°C | 电池模块3电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 3 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.167 | hwLithiumbatterycabinetBatMd4TotalTimeMaxCellTemp40To50 | Battery module 4 total time for max cell temperature [40,50]°C | 电池模块4电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 4 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.168 | hwLithiumbatterycabinetBatMd5TotalTimeMaxCellTemp40To50 | Battery module 5 total time for max cell temperature [40,50]°C | 电池模块5电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 5 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.169 | hwLithiumbatterycabinetBatMd6TotalTimeMaxCellTemp40To50 | Battery module 6 total time for max cell temperature [40,50]°C | 电池模块6电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 6 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.170 | hwLithiumbatterycabinetBatMd7TotalTimeMaxCellTemp40To50 | Battery module 7 total time for max cell temperature [40,50]°C | 电池模块7电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 7 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.171 | hwLithiumbatterycabinetBatMd8TotalTimeMaxCellTemp40To50 | Battery module 8 total time for max cell temperature [40,50]°C | 电池模块8电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 8 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.172 | hwLithiumbatterycabinetBatMd9TotalTimeMaxCellTemp40To50 | Battery module 9 total time for max cell temperature [40,50]°C | 电池模块9电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 9 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.173 | hwLithiumbatterycabinetBatMd10TotalTimeMaxCellTemp40To50 | Battery module 10 total time for max cell temperature [40,50]°C | 电池模块10电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 10 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.174 | hwLithiumbatterycabinetBatMd11TotalTimeMaxCellTemp40To50 | Battery module 11 total time for max cell temperature [40,50]°C | 电池模块11电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 11 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.175 | hwLithiumbatterycabinetBatMd12TotalTimeMaxCellTemp40To50 | Battery module 12 total time for max cell temperature [40,50]°C | 电池模块12电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 12 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.176 | hwLithiumbatterycabinetBatMd13TotalTimeMaxCellTemp40To50 | Battery module 13 total time for max cell temperature [40,50]°C | 电池模块13电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 13 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.177 | hwLithiumbatterycabinetBatMd14TotalTimeMaxCellTemp40To50 | Battery module 14 total time for max cell temperature [40,50]°C | 电池模块14电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 14 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.178 | hwLithiumbatterycabinetBatMd15TotalTimeMaxCellTemp40To50 | Battery module 15 total time for max cell temperature [40,50]°C | 电池模块15电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 15 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.179 | hwLithiumbatterycabinetBatMd16TotalTimeMaxCellTemp40To50 | Battery module 16 total time for max cell temperature [40,50]°C | 电池模块16电芯最高温度[40,50]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 16 total time for max cell temperature 40 to 50 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.180 | hwLithiumbatterycabinetBatMd1TotalTimeMaxCellTemp10To40 | Battery module 1 total time for max cell temperature [10,40]°C | 电池模块1电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 1 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.181 | hwLithiumbatterycabinetBatMd2TotalTimeMaxCellTemp10To40 | Battery module 2 total time for max cell temperature [10,40]°C | 电池模块2电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 2 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.182 | hwLithiumbatterycabinetBatMd3TotalTimeMaxCellTemp10To40 | Battery module 3 total time for max cell temperature [10,40]°C | 电池模块3电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 3 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.183 | hwLithiumbatterycabinetBatMd4TotalTimeMaxCellTemp10To40 | Battery module 4 total time for max cell temperature [10,40]°C | 电池模块4电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 4 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.184 | hwLithiumbatterycabinetBatMd5TotalTimeMaxCellTemp10To40 | Battery module 5 total time for max cell temperature [10,40]°C | 电池模块5电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 5 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.185 | hwLithiumbatterycabinetBatMd6TotalTimeMaxCellTemp10To40 | Battery module 6 total time for max cell temperature [10,40]°C | 电池模块6电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 6 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.186 | hwLithiumbatterycabinetBatMd7TotalTimeMaxCellTemp10To40 | Battery module 7 total time for max cell temperature [10,40]°C | 电池模块7电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 7 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.187 | hwLithiumbatterycabinetBatMd8TotalTimeMaxCellTemp10To40 | Battery module 8 total time for max cell temperature [10,40]°C | 电池模块8电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 8 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.188 | hwLithiumbatterycabinetBatMd9TotalTimeMaxCellTemp10To40 | Battery module 9 total time for max cell temperature [10,40]°C | 电池模块9电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 9 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.189 | hwLithiumbatterycabinetBatMd10TotalTimeMaxCellTemp10To40 | Battery module 10 total time for max cell temperature [10,40]°C | 电池模块10电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 10 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.190 | hwLithiumbatterycabinetBatMd11TotalTimeMaxCellTemp10To40 | Battery module 11 total time for max cell temperature [10,40]°C | 电池模块11电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 11 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.191 | hwLithiumbatterycabinetBatMd12TotalTimeMaxCellTemp10To40 | Battery module 12 total time for max cell temperature [10,40]°C | 电池模块12电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 12 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.192 | hwLithiumbatterycabinetBatMd13TotalTimeMaxCellTemp10To40 | Battery module 13 total time for max cell temperature [10,40]°C | 电池模块13电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 13 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.193 | hwLithiumbatterycabinetBatMd14TotalTimeMaxCellTemp10To40 | Battery module 14 total time for max cell temperature [10,40]°C | 电池模块14电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 14 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.194 | hwLithiumbatterycabinetBatMd15TotalTimeMaxCellTemp10To40 | Battery module 15 total time for max cell temperature [10,40]°C | 电池模块15电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 15 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.195 | hwLithiumbatterycabinetBatMd16TotalTimeMaxCellTemp10To40 | Battery module 16 total time for max cell temperature [10,40]°C | 电池模块16电芯最高温度[10,40]℃总时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Battery module 16 total time for max cell temperature 10 to 40 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.1.1.201 | hwLithiumbatterycabinetRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.2 | hwLithiumbatterycabinetConfigTable | / | / |  |  | / | / | The config table of Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.2.1.1 | hwLithiumbatterycabinetConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.2.1.2 | hwLithiumbatterycabinetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.2.1.3 | hwLithiumbatterycabinetDetailModel | Detail model | 详细机型 | 1-Read_Write | 读写 | auxiliaryCabinet(1), mainCabinet(2), unknown(255) | [辅柜=1]/[主柜=2] | Detail model of the device config table for the Lithium battery cabinet. Value 1 indicate auxiliary cabinet Value 2 indicate main cabinet
1.3.6.1.4.1.2011.6.178.1.1.100.2.1.101 | hwLithiumbatterycabinetConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3 | hwLithiumbatterycabinetRunning2Table | / | / |  |  | / | / | The running table of Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.1 | hwLithiumbatterycabinetRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.2 | hwLithiumbatterycabinetBatMd1TotalTimeMinCellTemp0To10 | Battery module 1 total time for min cell temperature [0,10]°C | 电池模块1电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 1 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.3 | hwLithiumbatterycabinetBatMd2TotalTimeMinCellTemp0To10 | Battery module 2 total time for min cell temperature [0,10]°C | 电池模块2电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 2 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.4 | hwLithiumbatterycabinetBatMd3TotalTimeMinCellTemp0To10 | Battery module 3 total time for min cell temperature [0,10]°C | 电池模块3电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 3 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.5 | hwLithiumbatterycabinetBatMd4TotalTimeMinCellTemp0To10 | Battery module 4 total time for min cell temperature [0,10]°C | 电池模块4电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 4 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.6 | hwLithiumbatterycabinetBatMd5TotalTimeMinCellTemp0To10 | Battery module 5 total time for min cell temperature [0,10]°C | 电池模块5电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 5 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.7 | hwLithiumbatterycabinetBatMd6TotalTimeMinCellTemp0To10 | Battery module 6 total time for min cell temperature [0,10]°C | 电池模块6电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 6 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.8 | hwLithiumbatterycabinetBatMd7TotalTimeMinCellTemp0To10 | Battery module 7 total time for min cell temperature [0,10]°C | 电池模块7电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 7 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.9 | hwLithiumbatterycabinetBatMd8TotalTimeMinCellTemp0To10 | Battery module 8 total time for min cell temperature [0,10]°C | 电池模块8电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 8 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.10 | hwLithiumbatterycabinetBatMd9TotalTimeMinCellTemp0To10 | Battery module 9 total time for min cell temperature [0,10]°C | 电池模块9电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 9 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.11 | hwLithiumbatterycabinetBatMd10TotalTimeMinCellTemp0To10 | Battery module 10 total time for min cell temperature [0,10]°C | 电池模块10电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 10 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.12 | hwLithiumbatterycabinetBatMd11TotalTimeMinCellTemp0To10 | Battery module 11 total time for min cell temperature [0,10]°C | 电池模块11电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 11 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.13 | hwLithiumbatterycabinetBatMd12TotalTimeMinCellTemp0To10 | Battery module 12 total time for min cell temperature [0,10]°C | 电池模块12电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 12 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.14 | hwLithiumbatterycabinetBatMd13TotalTimeMinCellTemp0To10 | Battery module 13 total time for min cell temperature [0,10]°C | 电池模块13电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 13 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.15 | hwLithiumbatterycabinetBatMd14TotalTimeMinCellTemp0To10 | Battery module 14 total time for min cell temperature [0,10]°C | 电池模块14电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 14 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.16 | hwLithiumbatterycabinetBatMd15TotalTimeMinCellTemp0To10 | Battery module 15 total time for min cell temperature [0,10]°C | 电池模块15电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 15 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.17 | hwLithiumbatterycabinetBatMd16TotalTimeMinCellTemp0To10 | Battery module 16 total time for min cell temperature [0,10]°C | 电池模块16电芯最低温度[0,10]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 16 total time for min cell temperature 0 to 10 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.18 | hwLithiumbatterycabinetBatMd1TotalTimeMinCellTempNeg40To0 | Battery module 1 total time for min cell temperature [-40,0]°C | 电池模块1电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 1 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.19 | hwLithiumbatterycabinetBatMd2TotalTimeMinCellTempNeg40To0 | Battery module 2 total time for min cell temperature [-40,0]°C | 电池模块2电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 2 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.20 | hwLithiumbatterycabinetBatMd3TotalTimeMinCellTempNeg40To0 | Battery module 3 total time for min cell temperature [-40,0]°C | 电池模块3电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 3 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.21 | hwLithiumbatterycabinetBatMd4TotalTimeMinCellTempNeg40To0 | Battery module 4 total time for min cell temperature [-40,0]°C | 电池模块4电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 4 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.22 | hwLithiumbatterycabinetBatMd5TotalTimeMinCellTempNeg40To0 | Battery module 5 total time for min cell temperature [-40,0]°C | 电池模块5电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 5 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.23 | hwLithiumbatterycabinetBatMd6TotalTimeMinCellTempNeg40To0 | Battery module 6 total time for min cell temperature [-40,0]°C | 电池模块6电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 6 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.24 | hwLithiumbatterycabinetBatMd7TotalTimeMinCellTempNeg40To0 | Battery module 7 total time for min cell temperature [-40,0]°C | 电池模块7电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 7 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.25 | hwLithiumbatterycabinetBatMd8TotalTimeMinCellTempNeg40To0 | Battery module 8 total time for min cell temperature [-40,0]°C | 电池模块8电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 8 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.26 | hwLithiumbatterycabinetBatMd9TotalTimeMinCellTempNeg40To0 | Battery module 9 total time for min cell temperature [-40,0]°C | 电池模块9电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 9 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.27 | hwLithiumbatterycabinetBatMd10TotalTimeMinCellTempNeg40To0 | Battery module 10 total time for min cell temperature [-40,0]°C | 电池模块10电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 10 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.28 | hwLithiumbatterycabinetBatMd11TotalTimeMinCellTempNeg40To0 | Battery module 11 total time for min cell temperature [-40,0]°C | 电池模块11电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 11 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.29 | hwLithiumbatterycabinetBatMd12TotalTimeMinCellTempNeg40To0 | Battery module 12 total time for min cell temperature [-40,0]°C | 电池模块12电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 12 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.30 | hwLithiumbatterycabinetBatMd13TotalTimeMinCellTempNeg40To0 | Battery module 13 total time for min cell temperature [-40,0]°C | 电池模块13电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 13 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.31 | hwLithiumbatterycabinetBatMd14TotalTimeMinCellTempNeg40To0 | Battery module 14 total time for min cell temperature [-40,0]°C | 电池模块14电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 14 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.32 | hwLithiumbatterycabinetBatMd15TotalTimeMinCellTempNeg40To0 | Battery module 15 total time for min cell temperature [-40,0]°C | 电池模块15电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 15 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.33 | hwLithiumbatterycabinetBatMd16TotalTimeMinCellTempNeg40To0 | Battery module 16 total time for min cell temperature [-40,0]°C | 电池模块16电芯最低温度[-40,0]℃总时间 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | Battery module 16 total time for min cell temperature -40 to 0 degrees celcius of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.34 | hwLithiumbatterycabinetBatMd1TotalCellOvervoltageAlarms | Battery module 1 Total cell overvoltage alarms | 电池模块1电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 1 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.35 | hwLithiumbatterycabinetBatMd2TotalCellOvervoltageAlarms | Battery module 2 Total cell overvoltage alarms | 电池模块2电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 2 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.36 | hwLithiumbatterycabinetBatMd3TotalCellOvervoltageAlarms | Battery module 3 Total cell overvoltage alarms | 电池模块3电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 3 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.37 | hwLithiumbatterycabinetBatMd4TotalCellOvervoltageAlarms | Battery module 4 Total cell overvoltage alarms | 电池模块4电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 4 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.38 | hwLithiumbatterycabinetBatMd5TotalCellOvervoltageAlarms | Battery module 5 Total cell overvoltage alarms | 电池模块5电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 5 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.39 | hwLithiumbatterycabinetBatMd6TotalCellOvervoltageAlarms | Battery module 6 Total cell overvoltage alarms | 电池模块6电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 6 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.40 | hwLithiumbatterycabinetBatMd7TotalCellOvervoltageAlarms | Battery module 7 Total cell overvoltage alarms | 电池模块7电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 7 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.41 | hwLithiumbatterycabinetBatMd8TotalCellOvervoltageAlarms | Battery module 8 Total cell overvoltage alarms | 电池模块8电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 8 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.42 | hwLithiumbatterycabinetBatMd9TotalCellOvervoltageAlarms | Battery module 9 Total cell overvoltage alarms | 电池模块9电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 9 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.43 | hwLithiumbatterycabinetBatMd10TotalCellOvervoltageAlarms | Battery module 10 Total cell overvoltage alarms | 电池模块10电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 10 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.44 | hwLithiumbatterycabinetBatMd11TotalCellOvervoltageAlarms | Battery module 11 Total cell overvoltage alarms | 电池模块11电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 11 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.45 | hwLithiumbatterycabinetBatMd12TotalCellOvervoltageAlarms | Battery module 12 Total cell overvoltage alarms | 电池模块12电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 12 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.46 | hwLithiumbatterycabinetBatMd13TotalCellOvervoltageAlarms | Battery module 13 Total cell overvoltage alarms | 电池模块13电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 13 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.47 | hwLithiumbatterycabinetBatMd14TotalCellOvervoltageAlarms | Battery module 14 Total cell overvoltage alarms | 电池模块14电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 14 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.48 | hwLithiumbatterycabinetBatMd15TotalCellOvervoltageAlarms | Battery module 15 Total cell overvoltage alarms | 电池模块15电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 15 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.49 | hwLithiumbatterycabinetBatMd16TotalCellOvervoltageAlarms | Battery module 16 Total cell overvoltage alarms | 电池模块16电芯过压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 16 total cell overvoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.50 | hwLithiumbatterycabinetBatMd1TotalCellUndervoltageAlarms | Battery module 1 Total cell undervoltage alarms | 电池模块1电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 1 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.51 | hwLithiumbatterycabinetBatMd2TotalCellUndervoltageAlarms | Battery module 2 Total cell undervoltage alarms | 电池模块2电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 2 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.52 | hwLithiumbatterycabinetBatMd3TotalCellUndervoltageAlarms | Battery module 3 Total cell undervoltage alarms | 电池模块3电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 3 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.53 | hwLithiumbatterycabinetBatMd4TotalCellUndervoltageAlarms | Battery module 4 Total cell undervoltage alarms | 电池模块4电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 4 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.54 | hwLithiumbatterycabinetBatMd5TotalCellUndervoltageAlarms | Battery module 5 Total cell undervoltage alarms | 电池模块5电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 5 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.55 | hwLithiumbatterycabinetBatMd6TotalCellUndervoltageAlarms | Battery module 6 Total cell undervoltage alarms | 电池模块6电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 6 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.56 | hwLithiumbatterycabinetBatMd7TotalCellUndervoltageAlarms | Battery module 7 Total cell undervoltage alarms | 电池模块7电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 7 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.57 | hwLithiumbatterycabinetBatMd8TotalCellUndervoltageAlarms | Battery module 8 Total cell undervoltage alarms | 电池模块8电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 8 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.58 | hwLithiumbatterycabinetBatMd9TotalCellUndervoltageAlarms | Battery module 9 Total cell undervoltage alarms | 电池模块9电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 9 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.59 | hwLithiumbatterycabinetBatMd10TotalCellUndervoltageAlarms | Battery module 10 Total cell undervoltage alarms | 电池模块10电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 10 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.60 | hwLithiumbatterycabinetBatMd11TotalCellUndervoltageAlarms | Battery module 11 Total cell undervoltage alarms | 电池模块11电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 11 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.61 | hwLithiumbatterycabinetBatMd12TotalCellUndervoltageAlarms | Battery module 12 Total cell undervoltage alarms | 电池模块12电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 12 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.62 | hwLithiumbatterycabinetBatMd13TotalCellUndervoltageAlarms | Battery module 13 Total cell undervoltage alarms | 电池模块13电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 13 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.63 | hwLithiumbatterycabinetBatMd14TotalCellUndervoltageAlarms | Battery module 14 Total cell undervoltage alarms | 电池模块14电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 14 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.64 | hwLithiumbatterycabinetBatMd15TotalCellUndervoltageAlarms | Battery module 15 Total cell undervoltage alarms | 电池模块15电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 15 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.65 | hwLithiumbatterycabinetBatMd16TotalCellUndervoltageAlarms | Battery module 16 Total cell undervoltage alarms | 电池模块16电芯欠压告警总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 16 total cell undervoltage alarms of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.66 | hwLithiumbatterycabinetBatMd1TotalHighTempAlarmsCharge | Battery module 1 total high temperature alarms (charge) | 电池模块1高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 1 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.67 | hwLithiumbatterycabinetBatMd2TotalHighTempAlarmsCharge | Battery module 2 total high temperature alarms (charge) | 电池模块2高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 2 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.68 | hwLithiumbatterycabinetBatMd3TotalHighTempAlarmsCharge | Battery module 3 total high temperature alarms (charge) | 电池模块3高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 3 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.69 | hwLithiumbatterycabinetBatMd4TotalHighTempAlarmsCharge | Battery module 4 total high temperature alarms (charge) | 电池模块4高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 4 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.70 | hwLithiumbatterycabinetBatMd5TotalHighTempAlarmsCharge | Battery module 5 total high temperature alarms (charge) | 电池模块5高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 5 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.71 | hwLithiumbatterycabinetBatMd6TotalHighTempAlarmsCharge | Battery module 6 total high temperature alarms (charge) | 电池模块6高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 6 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.72 | hwLithiumbatterycabinetBatMd7TotalHighTempAlarmsCharge | Battery module 7 total high temperature alarms (charge) | 电池模块7高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 7 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.73 | hwLithiumbatterycabinetBatMd8TotalHighTempAlarmsCharge | Battery module 8 total high temperature alarms (charge) | 电池模块8高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 8 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.74 | hwLithiumbatterycabinetBatMd9TotalHighTempAlarmsCharge | Battery module 9 total high temperature alarms (charge) | 电池模块9高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 9 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.75 | hwLithiumbatterycabinetBatMd10TotalHighTempAlarmsCharge | Battery module 10 total high temperature alarms (charge) | 电池模块10高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 10 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.76 | hwLithiumbatterycabinetBatMd11TotalHighTempAlarmsCharge | Battery module 11 total high temperature alarms (charge) | 电池模块11高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 11 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.77 | hwLithiumbatterycabinetBatMd12TotalHighTempAlarmsCharge | Battery module 12 total high temperature alarms (charge) | 电池模块12高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 12 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.78 | hwLithiumbatterycabinetBatMd13TotalHighTempAlarmsCharge | Battery module 13 total high temperature alarms (charge) | 电池模块13高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 13 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.79 | hwLithiumbatterycabinetBatMd14TotalHighTempAlarmsCharge | Battery module 14 total high temperature alarms (charge) | 电池模块14高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 14 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.80 | hwLithiumbatterycabinetBatMd15TotalHighTempAlarmsCharge | Battery module 15 total high temperature alarms (charge) | 电池模块15高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 15 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.81 | hwLithiumbatterycabinetBatMd16TotalHighTempAlarmsCharge | Battery module 16 total high temperature alarms (charge) | 电池模块16高温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 16 total high temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.82 | hwLithiumbatterycabinetBatMd1TotalHighTempAlarmsDischarge | Battery module 1 total high temperature alarms (discharge) | 电池模块1高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 1 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.83 | hwLithiumbatterycabinetBatMd2TotalHighTempAlarmsDischarge | Battery module 2 total high temperature alarms (discharge) | 电池模块2高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 2 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.84 | hwLithiumbatterycabinetBatMd3TotalHighTempAlarmsDischarge | Battery module 3 total high temperature alarms (discharge) | 电池模块3高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 3 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.85 | hwLithiumbatterycabinetBatMd4TotalHighTempAlarmsDischarge | Battery module 4 total high temperature alarms (discharge) | 电池模块4高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 4 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.86 | hwLithiumbatterycabinetBatMd5TotalHighTempAlarmsDischarge | Battery module 5 total high temperature alarms (discharge) | 电池模块5高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 5 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.87 | hwLithiumbatterycabinetBatMd6TotalHighTempAlarmsDischarge | Battery module 6 total high temperature alarms (discharge) | 电池模块6高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 6 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.88 | hwLithiumbatterycabinetBatMd7TotalHighTempAlarmsDischarge | Battery module 7 total high temperature alarms (discharge) | 电池模块7高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 7 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.89 | hwLithiumbatterycabinetBatMd8TotalHighTempAlarmsDischarge | Battery module 8 total high temperature alarms (discharge) | 电池模块8高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 8 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.90 | hwLithiumbatterycabinetBatMd9TotalHighTempAlarmsDischarge | Battery module 9 total high temperature alarms (discharge) | 电池模块9高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 9 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.91 | hwLithiumbatterycabinetBatMd10TotalHighTempAlarmsDischarge | Battery module 10 total high temperature alarms (discharge) | 电池模块10高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 10 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.92 | hwLithiumbatterycabinetBatMd11TotalHighTempAlarmsDischarge | Battery module 11 total high temperature alarms (discharge) | 电池模块11高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 11 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.93 | hwLithiumbatterycabinetBatMd12TotalHighTempAlarmsDischarge | Battery module 12 total high temperature alarms (discharge) | 电池模块12高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 12 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.94 | hwLithiumbatterycabinetBatMd13TotalHighTempAlarmsDischarge | Battery module 13 total high temperature alarms (discharge) | 电池模块13高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 13 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.95 | hwLithiumbatterycabinetBatMd14TotalHighTempAlarmsDischarge | Battery module 14 total high temperature alarms (discharge) | 电池模块14高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 14 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.96 | hwLithiumbatterycabinetBatMd15TotalHighTempAlarmsDischarge | Battery module 15 total high temperature alarms (discharge) | 电池模块15高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 15 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.97 | hwLithiumbatterycabinetBatMd16TotalHighTempAlarmsDischarge | Battery module 16 total high temperature alarms (discharge) | 电池模块16高温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 16 total high temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.98 | hwLithiumbatterycabinetBatMd1TotalLowTempAlarmsCharge | Battery module 1 total low temperature alarms (charge) | 电池模块1低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 1 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.99 | hwLithiumbatterycabinetBatMd2TotalLowTempAlarmsCharge | Battery module 2 total low temperature alarms (charge) | 电池模块2低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 2 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.100 | hwLithiumbatterycabinetBatMd3TotalLowTempAlarmsCharge | Battery module 3 total low temperature alarms (charge) | 电池模块3低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 3 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.101 | hwLithiumbatterycabinetBatMd4TotalLowTempAlarmsCharge | Battery module 4 total low temperature alarms (charge) | 电池模块4低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 4 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.102 | hwLithiumbatterycabinetBatMd5TotalLowTempAlarmsCharge | Battery module 5 total low temperature alarms (charge) | 电池模块5低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 5 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.103 | hwLithiumbatterycabinetBatMd6TotalLowTempAlarmsCharge | Battery module 6 total low temperature alarms (charge) | 电池模块6低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 6 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.104 | hwLithiumbatterycabinetBatMd7TotalLowTempAlarmsCharge | Battery module 7 total low temperature alarms (charge) | 电池模块7低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 7 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.105 | hwLithiumbatterycabinetBatMd8TotalLowTempAlarmsCharge | Battery module 8 total low temperature alarms (charge) | 电池模块8低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 8 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.106 | hwLithiumbatterycabinetBatMd9TotalLowTempAlarmsCharge | Battery module 9 total low temperature alarms (charge) | 电池模块9低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 9 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.107 | hwLithiumbatterycabinetBatMd10TotalLowTempAlarmsCharge | Battery module 10 total low temperature alarms (charge) | 电池模块10低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 10 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.108 | hwLithiumbatterycabinetBatMd11TotalLowTempAlarmsCharge | Battery module 11 total low temperature alarms (charge) | 电池模块11低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 11 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.109 | hwLithiumbatterycabinetBatMd12TotalLowTempAlarmsCharge | Battery module 12 total low temperature alarms (charge) | 电池模块12低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 12 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.110 | hwLithiumbatterycabinetBatMd13TotalLowTempAlarmsCharge | Battery module 13 total low temperature alarms (charge) | 电池模块13低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 13 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.111 | hwLithiumbatterycabinetBatMd14TotalLowTempAlarmsCharge | Battery module 14 total low temperature alarms (charge) | 电池模块14低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 14 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.112 | hwLithiumbatterycabinetBatMd15TotalLowTempAlarmsCharge | Battery module 15 total low temperature alarms (charge) | 电池模块15低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 15 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.113 | hwLithiumbatterycabinetBatMd16TotalLowTempAlarmsCharge | Battery module 16 total low temperature alarms (charge) | 电池模块16低温告警(充电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 16 total low temperature alarms charge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.114 | hwLithiumbatterycabinetBatMd1TotalLowTempAlarmsDischarge | Battery module 1 total low temperature alarms (discharge) | 电池模块1低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 1 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.115 | hwLithiumbatterycabinetBatMd2TotalLowTempAlarmsDischarge | Battery module 2 total low temperature alarms (discharge) | 电池模块2低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 2 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.116 | hwLithiumbatterycabinetBatMd3TotalLowTempAlarmsDischarge | Battery module 3 total low temperature alarms (discharge) | 电池模块3低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 3 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.117 | hwLithiumbatterycabinetBatMd4TotalLowTempAlarmsDischarge | Battery module 4 total low temperature alarms (discharge) | 电池模块4低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 4 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.118 | hwLithiumbatterycabinetBatMd5TotalLowTempAlarmsDischarge | Battery module 5 total low temperature alarms (discharge) | 电池模块5低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 5 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.119 | hwLithiumbatterycabinetBatMd6TotalLowTempAlarmsDischarge | Battery module 6 total low temperature alarms (discharge) | 电池模块6低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 6 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.120 | hwLithiumbatterycabinetBatMd7TotalLowTempAlarmsDischarge | Battery module 7 total low temperature alarms (discharge) | 电池模块7低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 7 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.121 | hwLithiumbatterycabinetBatMd8TotalLowTempAlarmsDischarge | Battery module 8 total low temperature alarms (discharge) | 电池模块8低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 8 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.122 | hwLithiumbatterycabinetBatMd9TotalLowTempAlarmsDischarge | Battery module 9 total low temperature alarms (discharge) | 电池模块9低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 9 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.123 | hwLithiumbatterycabinetBatMd10TotalLowTempAlarmsDischarge | Battery module 10 total low temperature alarms (discharge) | 电池模块10低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 10 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.124 | hwLithiumbatterycabinetBatMd11TotalLowTempAlarmsDischarge | Battery module 11 total low temperature alarms (discharge) | 电池模块11低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 11 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.125 | hwLithiumbatterycabinetBatMd12TotalLowTempAlarmsDischarge | Battery module 12 total low temperature alarms (discharge) | 电池模块12低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 12 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.126 | hwLithiumbatterycabinetBatMd13TotalLowTempAlarmsDischarge | Battery module 13 total low temperature alarms (discharge) | 电池模块13低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 13 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.127 | hwLithiumbatterycabinetBatMd14TotalLowTempAlarmsDischarge | Battery module 14 total low temperature alarms (discharge) | 电池模块14低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 14 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.128 | hwLithiumbatterycabinetBatMd15TotalLowTempAlarmsDischarge | Battery module 15 total low temperature alarms (discharge) | 电池模块15低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 15 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.129 | hwLithiumbatterycabinetBatMd16TotalLowTempAlarmsDischarge | Battery module 16 total low temperature alarms (discharge) | 电池模块16低温告警(放电)总次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery module 16 total low temperature alarms discharge of the device config table for the Lithium battery cabinet.
| [Nouse]hwLithiumbatterycabinetTotalChargeCapacity | / | / | 0-Read_Only | 只读 | 0..4294967294 | / | Total charge capacity of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.131 | hwLithiumbatterycabinetCOSensor1 | Gas concentration measured by CO sensor 1 | CO传感器1气体浓度 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Gas concentration measured by CO sensor 1 of the device config table for the Lithium battery cabinet.SigUnitInfo:ppm.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.132 | hwLithiumbatterycabinetCOSensor2 | Gas concentration measured by CO sensor 2 | CO传感器2气体浓度 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Gas concentration measured by CO sensor 2 of the device config table for the Lithium battery cabinet.SigUnitInfo:ppm.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.133 | hwLithiumbatterycabinetPortVoltage | Port voltage | 端口电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Port voltage of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.134 | hwLithiumbatterycabinetPortCurrent | Port current | 端口电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Port current of the device config table for the Lithium battery cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.100.3.1.200 | hwLithiumbatterycabinetRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Lithium battery cabinet.

## MA01D DC PDU
MA01D直流配电柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.123 | MA01DDCPDU | MA01D DC PDU | MA01D直流配电柜 | / | / | / | / | MA01D DC PDU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.123.1 | hwMA01DDCPDURunning1Table | / | / |  |  | / | / | The running table of MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.1 | hwMA01DDCPDURunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.2 | hwMA01DDCPDUSerialNumber | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Serial number of the device config table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.3 | hwMA01DDCPDUInputCableForRouteIInputVoltage | Input cable for route Ⅰ - input voltage | Ⅰ路进线-输入电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route I - input voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.4 | hwMA01DDCPDUInputCableForRouteIInputCurrent | Input cable for route Ⅰ - input current | Ⅰ路进线-输入电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route I - input current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.5 | hwMA01DDCPDUInputCableForRouteIActivePower | Input cable for route Ⅰ - active power | Ⅰ路进线-有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route I - active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.6 | hwMA01DDCPDUInputCableForRouteIActiveEnergy | Input cable for route Ⅰ - active energy | Ⅰ路进线-有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route I - active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.7 | hwMA01DDCPDUInputCableForRouteILoadRatio | Input cable for route Ⅰ - load ratio | Ⅰ路进线-负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route I - load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.8 | hwMA01DDCPDUInputCableForRouteIIInputVoltage | Input cable for route Ⅱ - input voltage | Ⅱ路进线-输入电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route II - input voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.9 | hwMA01DDCPDUInputCableForRouteIIInputCurrent | Input cable for route Ⅱ - input current | Ⅱ路进线-输入电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route II - input current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.10 | hwMA01DDCPDUInputCableForRouteIIActivePower | Input cable for route Ⅱ - active power | Ⅱ路进线-有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route II - active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.11 | hwMA01DDCPDUInputCableForRouteIIActiveEnergy | Input cable for route Ⅱ - active energy | Ⅱ路进线-有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route II - active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.12 | hwMA01DDCPDUInputCableForRouteIILoadRatio | Input cable for route Ⅱ - load ratio | Ⅱ路进线-负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route II - load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.13 | hwMA01DDCPDUI01Voltage | Ⅰ01 voltage | Ⅰ01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I01 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.14 | hwMA01DDCPDUI02Voltage | Ⅰ02 voltage | Ⅰ02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I02 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.15 | hwMA01DDCPDUI03Voltage | Ⅰ03 voltage | Ⅰ03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I03 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.16 | hwMA01DDCPDUI01Current | Ⅰ01 current | Ⅰ01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I01 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.17 | hwMA01DDCPDUI02Current | Ⅰ02 current | Ⅰ02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I02 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.18 | hwMA01DDCPDUI03Current | Ⅰ03 current | Ⅰ03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I03 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.19 | hwMA01DDCPDUI01ActivePower | Ⅰ01 active power | Ⅰ01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I01 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.20 | hwMA01DDCPDUI02ActivePower | Ⅰ02 active power | Ⅰ02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I02 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.21 | hwMA01DDCPDUI03ActivePower | Ⅰ03 active power | Ⅰ03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I03 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.22 | hwMA01DDCPDUI01ActiveEnergy | Ⅰ01 active energy | Ⅰ01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I01 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.23 | hwMA01DDCPDUI02ActiveEnergy | Ⅰ02 active energy | Ⅰ02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I02 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.24 | hwMA01DDCPDUI03ActiveEnergy | Ⅰ03 active energy | Ⅰ03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I03 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.25 | hwMA01DDCPDUI01CurrentLoadRatio | Ⅰ01 current load ratio | Ⅰ01电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I01 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.26 | hwMA01DDCPDUI02CurrentLoadRatio | Ⅰ02 current load ratio | Ⅰ02电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I02 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.27 | hwMA01DDCPDUI03CurrentLoadRatio | Ⅰ03 current load ratio | Ⅰ03电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I03 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.28 | hwMA01DDCPDUI04Voltage | Ⅰ04 voltage | Ⅰ04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I04 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.29 | hwMA01DDCPDUI05Voltage | Ⅰ05 voltage | Ⅰ05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I05 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.30 | hwMA01DDCPDUI06Voltage | Ⅰ06 voltage | Ⅰ06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I06 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.31 | hwMA01DDCPDUI04Current | Ⅰ04 current | Ⅰ04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I04 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.32 | hwMA01DDCPDUI05Current | Ⅰ05 current | Ⅰ05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I05 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.33 | hwMA01DDCPDUI06Current | Ⅰ06 current | Ⅰ06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I06 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.34 | hwMA01DDCPDUI04ActivePower | Ⅰ04 active power | Ⅰ04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I04 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.35 | hwMA01DDCPDUI05ActivePower | Ⅰ05 active power | Ⅰ05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I05 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.36 | hwMA01DDCPDUI06ActivePower | Ⅰ06 active power | Ⅰ06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I06 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.37 | hwMA01DDCPDUI04ActiveEnergy | Ⅰ04 active energy | Ⅰ04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I04 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.38 | hwMA01DDCPDUI05ActiveEnergy | Ⅰ05 active energy | Ⅰ05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I05 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.39 | hwMA01DDCPDUI06ActiveEnergy | Ⅰ06 active energy | Ⅰ06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I06 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.40 | hwMA01DDCPDUI04CurrentLoadRatio | Ⅰ04 current load ratio | Ⅰ04电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I04 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.41 | hwMA01DDCPDUI05CurrentLoadRatio | Ⅰ05 current load ratio | Ⅰ05电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I05 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.42 | hwMA01DDCPDUI06CurrentLoadRatio | Ⅰ06 current load ratio | Ⅰ06电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I06 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.43 | hwMA01DDCPDUI07Voltage | Ⅰ07 voltage | Ⅰ07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I07 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.44 | hwMA01DDCPDUI08Voltage | Ⅰ08 voltage | Ⅰ08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I08 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.45 | hwMA01DDCPDUI09Voltage | Ⅰ09 voltage | Ⅰ09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I09 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.46 | hwMA01DDCPDUI07Current | Ⅰ07 current | Ⅰ07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I07 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.47 | hwMA01DDCPDUI08Current | Ⅰ08 current | Ⅰ08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I08 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.48 | hwMA01DDCPDUI09Current | Ⅰ09 current | Ⅰ09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I09 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.49 | hwMA01DDCPDUI07ActivePower | Ⅰ07 active power | Ⅰ07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I07 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.50 | hwMA01DDCPDUI08ActivePower | Ⅰ08 active power | Ⅰ08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I08 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.51 | hwMA01DDCPDUI09ActivePower | Ⅰ09 active power | Ⅰ09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I09 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.52 | hwMA01DDCPDUI07ActiveEnergy | Ⅰ07 active energy | Ⅰ07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I07 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.53 | hwMA01DDCPDUI08ActiveEnergy | Ⅰ08 active energy | Ⅰ08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I08 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.54 | hwMA01DDCPDUI09ActiveEnergy | Ⅰ09 active energy | Ⅰ09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I09 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.55 | hwMA01DDCPDUI07CurrentLoadRatio | Ⅰ07 current load ratio | Ⅰ07电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I07 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.56 | hwMA01DDCPDUI08CurrentLoadRatio | Ⅰ08 current load ratio | Ⅰ08电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I08 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.57 | hwMA01DDCPDUI09CurrentLoadRatio | Ⅰ09 current load ratio | Ⅰ09电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I09 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.58 | hwMA01DDCPDUI10Voltage | Ⅰ10 voltage | Ⅰ10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I10 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.59 | hwMA01DDCPDUI11Voltage | Ⅰ11 voltage | Ⅰ11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I11 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.60 | hwMA01DDCPDUI12Voltage | Ⅰ12 voltage | Ⅰ12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I12 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.61 | hwMA01DDCPDUI10Current | Ⅰ10 current | Ⅰ10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I10 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.62 | hwMA01DDCPDUI11Current | Ⅰ11 current | Ⅰ11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I11 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.63 | hwMA01DDCPDUI12Current | Ⅰ12 current | Ⅰ12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I12 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.64 | hwMA01DDCPDUI10ActivePower | Ⅰ10 active power | Ⅰ10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I10 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.65 | hwMA01DDCPDUI11ActivePower | Ⅰ11 active power | Ⅰ11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I11 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.66 | hwMA01DDCPDUI12ActivePower | Ⅰ12 active power | Ⅰ12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I12 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.67 | hwMA01DDCPDUI10ActiveEnergy | Ⅰ10 active energy | Ⅰ10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I10 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.68 | hwMA01DDCPDUI11ActiveEnergy | Ⅰ11 active energy | Ⅰ11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I11 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.69 | hwMA01DDCPDUI12ActiveEnergy | Ⅰ12 active energy | Ⅰ12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I12 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.70 | hwMA01DDCPDUI10CurrentLoadRatio | Ⅰ10 current load ratio | Ⅰ10电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I10 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.71 | hwMA01DDCPDUI11CurrentLoadRatio | Ⅰ11 current load ratio | Ⅰ11电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I11 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.72 | hwMA01DDCPDUI12CurrentLoadRatio | Ⅰ12 current load ratio | Ⅰ12电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I12 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.73 | hwMA01DDCPDUII01Voltage | Ⅱ01 voltage | Ⅱ01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II01 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.74 | hwMA01DDCPDUII02Voltage | Ⅱ02 voltage | Ⅱ02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II02 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.75 | hwMA01DDCPDUII03Voltage | Ⅱ03 voltage | Ⅱ03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II03 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.76 | hwMA01DDCPDUII01Current | Ⅱ01 current | Ⅱ01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II01 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.77 | hwMA01DDCPDUII02Current | Ⅱ02 current | Ⅱ02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II02 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.78 | hwMA01DDCPDUII03Current | Ⅱ03 current | Ⅱ03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II03 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.79 | hwMA01DDCPDUII01ActivePower | Ⅱ01 active power | Ⅱ01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II01 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.80 | hwMA01DDCPDUII02ActivePower | Ⅱ02 active power | Ⅱ02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II02 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.81 | hwMA01DDCPDUII03ActivePower | Ⅱ03 active power | Ⅱ03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II03 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.82 | hwMA01DDCPDUII01ActiveEnergy | Ⅱ01 active energy | Ⅱ01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II01 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.83 | hwMA01DDCPDUII02ActiveEnergy | Ⅱ02 active energy | Ⅱ02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II02 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.84 | hwMA01DDCPDUII03ActiveEnergy | Ⅱ03 active energy | Ⅱ03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II03 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.85 | hwMA01DDCPDUII01CurrentLoadRatio | Ⅱ01 current load ratio | Ⅱ01电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II01 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.86 | hwMA01DDCPDUII02CurrentLoadRatio | Ⅱ02 current load ratio | Ⅱ02电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II02 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.87 | hwMA01DDCPDUII03CurrentLoadRatio | Ⅱ03 current load ratio | Ⅱ03电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II03 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.88 | hwMA01DDCPDUII04Voltage | Ⅱ04 voltage | Ⅱ04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II04 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.89 | hwMA01DDCPDUII05Voltage | Ⅱ05 voltage | Ⅱ05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II05 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.90 | hwMA01DDCPDUII06Voltage | Ⅱ06 voltage | Ⅱ06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II06 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.91 | hwMA01DDCPDUII04Current | Ⅱ04 current | Ⅱ04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II04 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.92 | hwMA01DDCPDUII05Current | Ⅱ05 current | Ⅱ05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II05 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.93 | hwMA01DDCPDUII06Current | Ⅱ06 current | Ⅱ06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II06 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.94 | hwMA01DDCPDUII04ActivePower | Ⅱ04 active power | Ⅱ04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II04 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.95 | hwMA01DDCPDUII05ActivePower | Ⅱ05 active power | Ⅱ05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II05 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.96 | hwMA01DDCPDUII06ActivePower | Ⅱ06 active power | Ⅱ06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II06 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.97 | hwMA01DDCPDUII04ActiveEnergy | Ⅱ04 active energy | Ⅱ04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II04 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.98 | hwMA01DDCPDUII05ActiveEnergy | Ⅱ05 active energy | Ⅱ05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II05 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.99 | hwMA01DDCPDUII06ActiveEnergy | Ⅱ06 active energy | Ⅱ06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II06 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.100 | hwMA01DDCPDUII04CurrentLoadRatio | Ⅱ04 current load ratio | Ⅱ04电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II04 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.101 | hwMA01DDCPDUII05CurrentLoadRatio | Ⅱ05 current load ratio | Ⅱ05电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II05 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.102 | hwMA01DDCPDUII06CurrentLoadRatio | Ⅱ06 current load ratio | Ⅱ06电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II06 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.103 | hwMA01DDCPDUII07Voltage | Ⅱ07 voltage | Ⅱ07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II07 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.104 | hwMA01DDCPDUII08Voltage | Ⅱ08 voltage | Ⅱ08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II08 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.105 | hwMA01DDCPDUII09Voltage | Ⅱ09 voltage | Ⅱ09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II09 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.106 | hwMA01DDCPDUII07Current | Ⅱ07 current | Ⅱ07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II07 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.107 | hwMA01DDCPDUII08Current | Ⅱ08 current | Ⅱ08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II08 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.108 | hwMA01DDCPDUII09Current | Ⅱ09 current | Ⅱ09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II09 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.109 | hwMA01DDCPDUII07ActivePower | Ⅱ07 active power | Ⅱ07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II07 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.110 | hwMA01DDCPDUII08ActivePower | Ⅱ08 active power | Ⅱ08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II08 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.111 | hwMA01DDCPDUII09ActivePower | Ⅱ09 active power | Ⅱ09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II09 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.112 | hwMA01DDCPDUII07ActiveEnergy | Ⅱ07 active energy | Ⅱ07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II07 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.113 | hwMA01DDCPDUII08ActiveEnergy | Ⅱ08 active energy | Ⅱ08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II08 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.114 | hwMA01DDCPDUII09ActiveEnergy | Ⅱ09 active energy | Ⅱ09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II09 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.115 | hwMA01DDCPDUII07CurrentLoadRatio | Ⅱ07 current load ratio | Ⅱ07电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II07 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.116 | hwMA01DDCPDUII08CurrentLoadRatio | Ⅱ08 current load ratio | Ⅱ08电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II08 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.117 | hwMA01DDCPDUII09CurrentLoadRatio | Ⅱ09 current load ratio | Ⅱ09电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II09 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.118 | hwMA01DDCPDUII10Voltage | Ⅱ10 voltage | Ⅱ10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II10 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.119 | hwMA01DDCPDUII11Voltage | Ⅱ11 voltage | Ⅱ11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II11 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.120 | hwMA01DDCPDUII12Voltage | Ⅱ12 voltage | Ⅱ12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II12 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.121 | hwMA01DDCPDUII10Current | Ⅱ10 current | Ⅱ10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II10 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.122 | hwMA01DDCPDUII11Current | Ⅱ11 current | Ⅱ11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II11 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.123 | hwMA01DDCPDUII12Current | Ⅱ12 current | Ⅱ12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II12 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.124 | hwMA01DDCPDUII10ActivePower | Ⅱ10 active power | Ⅱ10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II10 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.125 | hwMA01DDCPDUII11ActivePower | Ⅱ11 active power | Ⅱ11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II11 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.126 | hwMA01DDCPDUII12ActivePower | Ⅱ12 active power | Ⅱ12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II12 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.127 | hwMA01DDCPDUII10ActiveEnergy | Ⅱ10 active energy | Ⅱ10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II10 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.128 | hwMA01DDCPDUII11ActiveEnergy | Ⅱ11 active energy | Ⅱ11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II11 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.129 | hwMA01DDCPDUII12ActiveEnergy | Ⅱ12 active energy | Ⅱ12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II12 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.130 | hwMA01DDCPDUII10CurrentLoadRatio | Ⅱ10 current load ratio | Ⅱ10电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II10 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.131 | hwMA01DDCPDUII11CurrentLoadRatio | Ⅱ11 current load ratio | Ⅱ11电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II11 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.132 | hwMA01DDCPDUII12CurrentLoadRatio | Ⅱ12 current load ratio | Ⅱ12电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II12 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.133 | hwMA01DDCPDUI13Voltage | Ⅰ13 voltage | Ⅰ13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I13 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.134 | hwMA01DDCPDUI14Voltage | Ⅰ14 voltage | Ⅰ14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I14 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.135 | hwMA01DDCPDUI15Voltage | Ⅰ15 voltage | Ⅰ15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I15 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.136 | hwMA01DDCPDUI13Current | Ⅰ13 current | Ⅰ13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I13 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.137 | hwMA01DDCPDUI14Current | Ⅰ14 current | Ⅰ14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I14 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.138 | hwMA01DDCPDUI15Current | Ⅰ15 current | Ⅰ15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I15 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.139 | hwMA01DDCPDUI13ActivePower | Ⅰ13 active power | Ⅰ13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I13 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.140 | hwMA01DDCPDUI14ActivePower | Ⅰ14 active power | Ⅰ14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I14 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.141 | hwMA01DDCPDUI15ActivePower | Ⅰ15 active power | Ⅰ15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I15 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.142 | hwMA01DDCPDUI13ActiveEnergy | Ⅰ13 active energy | Ⅰ13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I13 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.143 | hwMA01DDCPDUI14ActiveEnergy | Ⅰ14 active energy | Ⅰ14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I14 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.144 | hwMA01DDCPDUI15ActiveEnergy | Ⅰ15 active energy | Ⅰ15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I15 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.145 | hwMA01DDCPDUI13CurrentLoadRatio | Ⅰ13 current load ratio | Ⅰ13电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I13 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.146 | hwMA01DDCPDUI14CurrentLoadRatio | Ⅰ14 current load ratio | Ⅰ14电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I14 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.147 | hwMA01DDCPDUI15CurrentLoadRatio | Ⅰ15 current load ratio | Ⅰ15电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I15 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.148 | hwMA01DDCPDUI16Voltage | Ⅰ16 voltage | Ⅰ16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I16 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.149 | hwMA01DDCPDUI17Voltage | Ⅰ17 voltage | Ⅰ17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I17 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.150 | hwMA01DDCPDUI18Voltage | Ⅰ18 voltage | Ⅰ18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I18 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.151 | hwMA01DDCPDUI16Current | Ⅰ16 current | Ⅰ16电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I16 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.152 | hwMA01DDCPDUI17Current | Ⅰ17 current | Ⅰ17电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I17 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.153 | hwMA01DDCPDUI18Current | Ⅰ18 current | Ⅰ18电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I18 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.154 | hwMA01DDCPDUI16ActivePower | Ⅰ16 active power | Ⅰ16有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I16 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.155 | hwMA01DDCPDUI17ActivePower | Ⅰ17 active power | Ⅰ17有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I17 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.156 | hwMA01DDCPDUI18ActivePower | Ⅰ18 active power | Ⅰ18有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I18 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.157 | hwMA01DDCPDUI16ActiveEnergy | Ⅰ16 active energy | Ⅰ16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I16 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.158 | hwMA01DDCPDUI17ActiveEnergy | Ⅰ17 active energy | Ⅰ17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I17 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.159 | hwMA01DDCPDUI18ActiveEnergy | Ⅰ18 active energy | Ⅰ18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I18 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.160 | hwMA01DDCPDUI16CurrentLoadRatio | Ⅰ16 current load ratio | Ⅰ16电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I16 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.161 | hwMA01DDCPDUI17CurrentLoadRatio | Ⅰ17 current load ratio | Ⅰ17电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I17 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.162 | hwMA01DDCPDUI18CurrentLoadRatio | Ⅰ18 current load ratio | Ⅰ18电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I18 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.163 | hwMA01DDCPDUI19Voltage | Ⅰ19 voltage | Ⅰ19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I19 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.164 | hwMA01DDCPDUI20Voltage | Ⅰ20 voltage | Ⅰ20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I20 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.165 | hwMA01DDCPDUI21Voltage | Ⅰ21 voltage | Ⅰ21电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I21 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.166 | hwMA01DDCPDUI19Current | Ⅰ19 current | Ⅰ19电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I19 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.167 | hwMA01DDCPDUI20Current | Ⅰ20 current | Ⅰ20电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I20 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.168 | hwMA01DDCPDUI21Current | Ⅰ21 current | Ⅰ21电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I21 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.169 | hwMA01DDCPDUI19ActivePower | Ⅰ19 active power | Ⅰ19有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I19 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.170 | hwMA01DDCPDUI20ActivePower | Ⅰ20 active power | Ⅰ20有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I20 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.171 | hwMA01DDCPDUI21ActivePower | Ⅰ21 active power | Ⅰ21有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I21 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.172 | hwMA01DDCPDUI19ActiveEnergy | Ⅰ19 active energy | Ⅰ19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I19 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.173 | hwMA01DDCPDUI20ActiveEnergy | Ⅰ20 active energy | Ⅰ20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I20 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.174 | hwMA01DDCPDUI21ActiveEnergy | Ⅰ21 active energy | Ⅰ21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I21 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.175 | hwMA01DDCPDUI19CurrentLoadRatio | Ⅰ19 current load ratio | Ⅰ19电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I19 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.176 | hwMA01DDCPDUI20CurrentLoadRatio | Ⅰ20 current load ratio | Ⅰ20电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I20 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.177 | hwMA01DDCPDUI21CurrentLoadRatio | Ⅰ21 current load ratio | Ⅰ21电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I21 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.178 | hwMA01DDCPDUI22Voltage | Ⅰ22 voltage | Ⅰ22电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I22 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.179 | hwMA01DDCPDUI23Voltage | Ⅰ23 voltage | Ⅰ23电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I23 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.180 | hwMA01DDCPDUI24Voltage | Ⅰ24 voltage | Ⅰ24电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I24 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.181 | hwMA01DDCPDUI22Current | Ⅰ22 current | Ⅰ22电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I22 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.182 | hwMA01DDCPDUI23Current | Ⅰ23 current | Ⅰ23电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I23 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.183 | hwMA01DDCPDUI24Current | Ⅰ24 current | Ⅰ24电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I24 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.184 | hwMA01DDCPDUI22ActivePower | Ⅰ22 active power | Ⅰ22有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I22 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.185 | hwMA01DDCPDUI23ActivePower | Ⅰ23 active power | Ⅰ23有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I23 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.186 | hwMA01DDCPDUI24ActivePower | Ⅰ24 active power | Ⅰ24有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I24 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.187 | hwMA01DDCPDUI22ActiveEnergy | Ⅰ22 active energy | Ⅰ22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I22 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.188 | hwMA01DDCPDUI23ActiveEnergy | Ⅰ23 active energy | Ⅰ23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I23 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.189 | hwMA01DDCPDUI24ActiveEnergy | Ⅰ24 active energy | Ⅰ24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I24 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.190 | hwMA01DDCPDUI22CurrentLoadRatio | Ⅰ22 current load ratio | Ⅰ22电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I22 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.191 | hwMA01DDCPDUI23CurrentLoadRatio | Ⅰ23 current load ratio | Ⅰ23电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I23 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.192 | hwMA01DDCPDUI24CurrentLoadRatio | Ⅰ24 current load ratio | Ⅰ24电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I24 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.193 | hwMA01DDCPDUII13Voltage | Ⅱ13 voltage | Ⅱ13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II13 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.194 | hwMA01DDCPDUII14Voltage | Ⅱ14 voltage | Ⅱ14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II14 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.195 | hwMA01DDCPDUII15Voltage | Ⅱ15 voltage | Ⅱ15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II15 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.196 | hwMA01DDCPDUII13Current | Ⅱ13 current | Ⅱ13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II13 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.197 | hwMA01DDCPDUII14Current | Ⅱ14 current | Ⅱ14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II14 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.198 | hwMA01DDCPDUII15Current | Ⅱ15 current | Ⅱ15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II15 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.199 | hwMA01DDCPDUII13ActivePower | Ⅱ13 active power | Ⅱ13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II13 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.200 | hwMA01DDCPDUII14ActivePower | Ⅱ14 active power | Ⅱ14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II14 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.201 | hwMA01DDCPDUII15ActivePower | Ⅱ15 active power | Ⅱ15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II15 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.202 | hwMA01DDCPDUII13ActiveEnergy | Ⅱ13 active energy | Ⅱ13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II13 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.203 | hwMA01DDCPDUII14ActiveEnergy | Ⅱ14 active energy | Ⅱ14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II14 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.204 | hwMA01DDCPDUII15ActiveEnergy | Ⅱ15 active energy | Ⅱ15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II15 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.205 | hwMA01DDCPDUII13CurrentLoadRatio | Ⅱ13 current load ratio | Ⅱ13电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II13 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.206 | hwMA01DDCPDUII14CurrentLoadRatio | Ⅱ14 current load ratio | Ⅱ14电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II14 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.207 | hwMA01DDCPDUII15CurrentLoadRatio | Ⅱ15 current load ratio | Ⅱ15电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II15 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.208 | hwMA01DDCPDUII16Voltage | Ⅱ16 voltage | Ⅱ16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II16 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.209 | hwMA01DDCPDUII17Voltage | Ⅱ17 voltage | Ⅱ17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II17 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.210 | hwMA01DDCPDUII18Voltage | Ⅱ18 voltage | Ⅱ18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II18 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.211 | hwMA01DDCPDUII16Current | Ⅱ16 current | Ⅱ16电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II16 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.212 | hwMA01DDCPDUII17Current | Ⅱ17 current | Ⅱ17电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II17 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.213 | hwMA01DDCPDUII18Current | Ⅱ18 current | Ⅱ18电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II18 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.214 | hwMA01DDCPDUII16ActivePower | Ⅱ16 active power | Ⅱ16有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II16 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.215 | hwMA01DDCPDUII17ActivePower | Ⅱ17 active power | Ⅱ17有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II17 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.216 | hwMA01DDCPDUII18ActivePower | Ⅱ18 active power | Ⅱ18有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II18 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.217 | hwMA01DDCPDUII16ActiveEnergy | Ⅱ16 active energy | Ⅱ16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II16 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.218 | hwMA01DDCPDUII17ActiveEnergy | Ⅱ17 active energy | Ⅱ17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II17 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.219 | hwMA01DDCPDUII18ActiveEnergy | Ⅱ18 active energy | Ⅱ18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II18 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.220 | hwMA01DDCPDUII16CurrentLoadRatio | Ⅱ16 current load ratio | Ⅱ16电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II16 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.221 | hwMA01DDCPDUII17CurrentLoadRatio | Ⅱ17 current load ratio | Ⅱ17电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II17 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.222 | hwMA01DDCPDUII18CurrentLoadRatio | Ⅱ18 current load ratio | Ⅱ18电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II18 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.223 | hwMA01DDCPDUII19Voltage | Ⅱ19 voltage | Ⅱ19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II19 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.224 | hwMA01DDCPDUII20Voltage | Ⅱ20 voltage | Ⅱ20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II20 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.225 | hwMA01DDCPDUII21Voltage | Ⅱ21 voltage | Ⅱ21电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II21 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.226 | hwMA01DDCPDUII19Current | Ⅱ19 current | Ⅱ19电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II19 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.227 | hwMA01DDCPDUII20Current | Ⅱ20 current | Ⅱ20电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II20 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.228 | hwMA01DDCPDUII21Current | Ⅱ21 current | Ⅱ21电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II21 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.229 | hwMA01DDCPDUII19ActivePower | Ⅱ19 active power | Ⅱ19有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II19 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.230 | hwMA01DDCPDUII20ActivePower | Ⅱ20 active power | Ⅱ20有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II20 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.231 | hwMA01DDCPDUII21ActivePower | Ⅱ21 active power | Ⅱ21有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II21 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.232 | hwMA01DDCPDUII19ActiveEnergy | Ⅱ19 active energy | Ⅱ19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II19 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.233 | hwMA01DDCPDUII20ActiveEnergy | Ⅱ20 active energy | Ⅱ20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II20 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.234 | hwMA01DDCPDUII21ActiveEnergy | Ⅱ21 active energy | Ⅱ21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II21 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.235 | hwMA01DDCPDUII19CurrentLoadRatio | Ⅱ19 current load ratio | Ⅱ19电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II19 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.236 | hwMA01DDCPDUII20CurrentLoadRatio | Ⅱ20 current load ratio | Ⅱ20电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II20 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.237 | hwMA01DDCPDUII21CurrentLoadRatio | Ⅱ21 current load ratio | Ⅱ21电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II21 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.238 | hwMA01DDCPDUII22Voltage | Ⅱ22 voltage | Ⅱ22电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II22 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.239 | hwMA01DDCPDUII23Voltage | Ⅱ23 voltage | Ⅱ23电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II23 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.240 | hwMA01DDCPDUII24Voltage | Ⅱ24 voltage | Ⅱ24电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II24 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.241 | hwMA01DDCPDUII22Current | Ⅱ22 current | Ⅱ22电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II22 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.242 | hwMA01DDCPDUII23Current | Ⅱ23 current | Ⅱ23电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II23 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.243 | hwMA01DDCPDUII24Current | Ⅱ24 current | Ⅱ24电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II24 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.244 | hwMA01DDCPDUII22ActivePower | Ⅱ22 active power | Ⅱ22有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II22 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.245 | hwMA01DDCPDUII23ActivePower | Ⅱ23 active power | Ⅱ23有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II23 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.246 | hwMA01DDCPDUII24ActivePower | Ⅱ24 active power | Ⅱ24有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II24 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.247 | hwMA01DDCPDUII22ActiveEnergy | Ⅱ22 active energy | Ⅱ22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II22 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.248 | hwMA01DDCPDUII23ActiveEnergy | Ⅱ23 active energy | Ⅱ23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II23 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.249 | hwMA01DDCPDUII24ActiveEnergy | Ⅱ24 active energy | Ⅱ24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II24 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.250 | hwMA01DDCPDUII22CurrentLoadRatio | Ⅱ22 current load ratio | Ⅱ22电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II22 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.251 | hwMA01DDCPDUII23CurrentLoadRatio | Ⅱ23 current load ratio | Ⅱ23电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II23 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.252 | hwMA01DDCPDUII24CurrentLoadRatio | Ⅱ24 current load ratio | Ⅱ24电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II24 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.253 | hwMA01DDCPDUI25Voltage | Ⅰ25 voltage | Ⅰ25电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I25 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.254 | hwMA01DDCPDUI26Voltage | Ⅰ26 voltage | Ⅰ26电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I26 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.255 | hwMA01DDCPDUI27Voltage | Ⅰ27 voltage | Ⅰ27电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I27 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.256 | hwMA01DDCPDUI25Current | Ⅰ25 current | Ⅰ25电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I25 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.257 | hwMA01DDCPDUI26Current | Ⅰ26 current | Ⅰ26电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I26 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.258 | hwMA01DDCPDUI27Current | Ⅰ27 current | Ⅰ27电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I27 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.259 | hwMA01DDCPDUI25ActivePower | Ⅰ25 active power | Ⅰ25有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I25 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.260 | hwMA01DDCPDUI26ActivePower | Ⅰ26 active power | Ⅰ26有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I26 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.261 | hwMA01DDCPDUI27ActivePower | Ⅰ27 active power | Ⅰ27有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I27 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.262 | hwMA01DDCPDUI25ActiveEnergy | Ⅰ25 active energy | Ⅰ25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I25 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.263 | hwMA01DDCPDUI26ActiveEnergy | Ⅰ26 active energy | Ⅰ26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I26 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.264 | hwMA01DDCPDUI27ActiveEnergy | Ⅰ27 active energy | Ⅰ27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I27 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.265 | hwMA01DDCPDUI25CurrentLoadRatio | Ⅰ25 current load ratio | Ⅰ25电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I25 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.266 | hwMA01DDCPDUI26CurrentLoadRatio | Ⅰ26 current load ratio | Ⅰ26电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I26 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.267 | hwMA01DDCPDUI27CurrentLoadRatio | Ⅰ27 current load ratio | Ⅰ27电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I27 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.268 | hwMA01DDCPDUI28Voltage | Ⅰ28 voltage | Ⅰ28电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I28 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.269 | hwMA01DDCPDUI29Voltage | Ⅰ29 voltage | Ⅰ29电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I29 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.270 | hwMA01DDCPDUI30Voltage | Ⅰ30 voltage | Ⅰ30电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I30 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.271 | hwMA01DDCPDUI28Current | Ⅰ28 current | Ⅰ28电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I28 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.272 | hwMA01DDCPDUI29Current | Ⅰ29 current | Ⅰ29电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I29 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.273 | hwMA01DDCPDUI30Current | Ⅰ30 current | Ⅰ30电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I30 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.274 | hwMA01DDCPDUI28ActivePower | Ⅰ28 active power | Ⅰ28有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I28 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.275 | hwMA01DDCPDUI29ActivePower | Ⅰ29 active power | Ⅰ29有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I29 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.276 | hwMA01DDCPDUI30ActivePower | Ⅰ30 active power | Ⅰ30有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I30 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.277 | hwMA01DDCPDUI28ActiveEnergy | Ⅰ28 active energy | Ⅰ28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I28 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.278 | hwMA01DDCPDUI29ActiveEnergy | Ⅰ29 active energy | Ⅰ29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I29 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.279 | hwMA01DDCPDUI30ActiveEnergy | Ⅰ30 active energy | Ⅰ30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I30 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.280 | hwMA01DDCPDUI28CurrentLoadRatio | Ⅰ28 current load ratio | Ⅰ28电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I28 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.281 | hwMA01DDCPDUI29CurrentLoadRatio | Ⅰ29 current load ratio | Ⅰ29电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I29 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.282 | hwMA01DDCPDUI30CurrentLoadRatio | Ⅰ30 current load ratio | Ⅰ30电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I30 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.283 | hwMA01DDCPDUI31Voltage | Ⅰ31 voltage | Ⅰ31电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I31 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.284 | hwMA01DDCPDUI32Voltage | Ⅰ32 voltage | Ⅰ32电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I32 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.285 | hwMA01DDCPDUI33Voltage | Ⅰ33 voltage | Ⅰ33电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I33 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.286 | hwMA01DDCPDUI31Current | Ⅰ31 current | Ⅰ31电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I31 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.287 | hwMA01DDCPDUI32Current | Ⅰ32 current | Ⅰ32电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I32 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.288 | hwMA01DDCPDUI33Current | Ⅰ33 current | Ⅰ33电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I33 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.289 | hwMA01DDCPDUI31ActivePower | Ⅰ31 active power | Ⅰ31有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I31 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.290 | hwMA01DDCPDUI32ActivePower | Ⅰ32 active power | Ⅰ32有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I32 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.291 | hwMA01DDCPDUI33ActivePower | Ⅰ33 active power | Ⅰ33有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I33 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.292 | hwMA01DDCPDUI31ActiveEnergy | Ⅰ31 active energy | Ⅰ31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I31 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.293 | hwMA01DDCPDUI32ActiveEnergy | Ⅰ32 active energy | Ⅰ32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I32 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.294 | hwMA01DDCPDUI33ActiveEnergy | Ⅰ33 active energy | Ⅰ33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I33 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.295 | hwMA01DDCPDUI31CurrentLoadRatio | Ⅰ31 current load ratio | Ⅰ31电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I31 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.296 | hwMA01DDCPDUI32CurrentLoadRatio | Ⅰ32 current load ratio | Ⅰ32电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I32 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.297 | hwMA01DDCPDUI33CurrentLoadRatio | Ⅰ33 current load ratio | Ⅰ33电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I33 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.298 | hwMA01DDCPDUI34Voltage | Ⅰ34 voltage | Ⅰ34电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I34 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.299 | hwMA01DDCPDUI35Voltage | Ⅰ35 voltage | Ⅰ35电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I35 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.1.1.300 | hwMA01DDCPDURunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.2 | hwMA01DDCPDURunning2Table | / | / |  |  | / | / | The running table of MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.1 | hwMA01DDCPDURunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.2 | hwMA01DDCPDUI36Voltage | Ⅰ36 voltage | Ⅰ36电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I36 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.3 | hwMA01DDCPDUI34Current | Ⅰ34 current | Ⅰ34电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I34 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.4 | hwMA01DDCPDUI35Current | Ⅰ35 current | Ⅰ35电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I35 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.5 | hwMA01DDCPDUI36Current | Ⅰ36 current | Ⅰ36电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I36 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.6 | hwMA01DDCPDUI34ActivePower | Ⅰ34 active power | Ⅰ34有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I34 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.7 | hwMA01DDCPDUI35ActivePower | Ⅰ35 active power | Ⅰ35有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I35 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.8 | hwMA01DDCPDUI36ActivePower | Ⅰ36 active power | Ⅰ36有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I36 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.9 | hwMA01DDCPDUI34ActiveEnergy | Ⅰ34 active energy | Ⅰ34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I34 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.10 | hwMA01DDCPDUI35ActiveEnergy | Ⅰ35 active energy | Ⅰ35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I35 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.11 | hwMA01DDCPDUI36ActiveEnergy | Ⅰ36 active energy | Ⅰ36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I36 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.12 | hwMA01DDCPDUI34CurrentLoadRatio | Ⅰ34 current load ratio | Ⅰ34电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I34 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.13 | hwMA01DDCPDUI35CurrentLoadRatio | Ⅰ35 current load ratio | Ⅰ35电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I35 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.14 | hwMA01DDCPDUI36CurrentLoadRatio | Ⅰ36 current load ratio | Ⅰ36电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I36 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.15 | hwMA01DDCPDUII25Voltage | Ⅱ25 voltage | Ⅱ25电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II25 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.16 | hwMA01DDCPDUII26Voltage | Ⅱ26 voltage | Ⅱ26电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II26 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.17 | hwMA01DDCPDUII27Voltage | Ⅱ27 voltage | Ⅱ27电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II27 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.18 | hwMA01DDCPDUII25Current | Ⅱ25 current | Ⅱ25电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II25 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.19 | hwMA01DDCPDUII26Current | Ⅱ26 current | Ⅱ26电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II26 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.20 | hwMA01DDCPDUII27Current | Ⅱ27 current | Ⅱ27电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II27 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.21 | hwMA01DDCPDUII25ActivePower | Ⅱ25 active power | Ⅱ25有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II25 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.22 | hwMA01DDCPDUII26ActivePower | Ⅱ26 active power | Ⅱ26有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II26 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.23 | hwMA01DDCPDUII27ActivePower | Ⅱ27 active power | Ⅱ27有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II27 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.24 | hwMA01DDCPDUII25ActiveEnergy | Ⅱ25 active energy | Ⅱ25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II25 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.25 | hwMA01DDCPDUII26ActiveEnergy | Ⅱ26 active energy | Ⅱ26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II26 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.26 | hwMA01DDCPDUII27ActiveEnergy | Ⅱ27 active energy | Ⅱ27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II27 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.27 | hwMA01DDCPDUII25CurrentLoadRatio | Ⅱ25 current load ratio | Ⅱ25电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II25 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.28 | hwMA01DDCPDUII26CurrentLoadRatio | Ⅱ26 current load ratio | Ⅱ26电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II26 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.29 | hwMA01DDCPDUII27CurrentLoadRatio | Ⅱ27 current load ratio | Ⅱ27电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II27 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.30 | hwMA01DDCPDUII28Voltage | Ⅱ28 voltage | Ⅱ28电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II28 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.31 | hwMA01DDCPDUII29Voltage | Ⅱ29 voltage | Ⅱ29电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II29 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.32 | hwMA01DDCPDUII30Voltage | Ⅱ30 voltage | Ⅱ30电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II30 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.33 | hwMA01DDCPDUII28Current | Ⅱ28 current | Ⅱ28电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II28 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.34 | hwMA01DDCPDUII29Current | Ⅱ29 current | Ⅱ29电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II29 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.35 | hwMA01DDCPDUII30Current | Ⅱ30 current | Ⅱ30电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II30 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.36 | hwMA01DDCPDUII28ActivePower | Ⅱ28 active power | Ⅱ28有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II28 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.37 | hwMA01DDCPDUII29ActivePower | Ⅱ29 active power | Ⅱ29有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II29 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.38 | hwMA01DDCPDUII30ActivePower | Ⅱ30 active power | Ⅱ30有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II30 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.39 | hwMA01DDCPDUII28ActiveEnergy | Ⅱ28 active energy | Ⅱ28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II28 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.40 | hwMA01DDCPDUII29ActiveEnergy | Ⅱ29 active energy | Ⅱ29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II29 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.41 | hwMA01DDCPDUII30ActiveEnergy | Ⅱ30 active energy | Ⅱ30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II30 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.42 | hwMA01DDCPDUII28CurrentLoadRatio | Ⅱ28 current load ratio | Ⅱ28电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II28 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.43 | hwMA01DDCPDUII29CurrentLoadRatio | Ⅱ29 current load ratio | Ⅱ29电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II29 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.44 | hwMA01DDCPDUII30CurrentLoadRatio | Ⅱ30 current load ratio | Ⅱ30电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II30 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.45 | hwMA01DDCPDUII31Voltage | Ⅱ31 voltage | Ⅱ31电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II31 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.46 | hwMA01DDCPDUII32Voltage | Ⅱ32 voltage | Ⅱ32电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II32 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.47 | hwMA01DDCPDUII33Voltage | Ⅱ33 voltage | Ⅱ33电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II33 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.48 | hwMA01DDCPDUII31Current | Ⅱ31 current | Ⅱ31电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II31 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.49 | hwMA01DDCPDUII32Current | Ⅱ32 current | Ⅱ32电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II32 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.50 | hwMA01DDCPDUII33Current | Ⅱ33 current | Ⅱ33电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II33 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.51 | hwMA01DDCPDUII31ActivePower | Ⅱ31 active power | Ⅱ31有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II31 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.52 | hwMA01DDCPDUII32ActivePower | Ⅱ32 active power | Ⅱ32有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II32 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.53 | hwMA01DDCPDUII33ActivePower | Ⅱ33 active power | Ⅱ33有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II33 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.54 | hwMA01DDCPDUII31ActiveEnergy | Ⅱ31 active energy | Ⅱ31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II31 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.55 | hwMA01DDCPDUII32ActiveEnergy | Ⅱ32 active energy | Ⅱ32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II32 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.56 | hwMA01DDCPDUII33ActiveEnergy | Ⅱ33 active energy | Ⅱ33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II33 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.57 | hwMA01DDCPDUII31CurrentLoadRatio | Ⅱ31 current load ratio | Ⅱ31电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II31 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.58 | hwMA01DDCPDUII32CurrentLoadRatio | Ⅱ32 current load ratio | Ⅱ32电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II32 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.59 | hwMA01DDCPDUII33CurrentLoadRatio | Ⅱ33 current load ratio | Ⅱ33电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II33 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.60 | hwMA01DDCPDUII34Voltage | Ⅱ34 voltage | Ⅱ34电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II34 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.61 | hwMA01DDCPDUII35Voltage | Ⅱ35 voltage | Ⅱ35电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II35 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.62 | hwMA01DDCPDUII36Voltage | Ⅱ36 voltage | Ⅱ36电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II36 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.63 | hwMA01DDCPDUII34Current | Ⅱ34 current | Ⅱ34电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II34 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.64 | hwMA01DDCPDUII35Current | Ⅱ35 current | Ⅱ35电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II35 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.65 | hwMA01DDCPDUII36Current | Ⅱ36 current | Ⅱ36电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II36 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.66 | hwMA01DDCPDUII34ActivePower | Ⅱ34 active power | Ⅱ34有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II34 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.67 | hwMA01DDCPDUII35ActivePower | Ⅱ35 active power | Ⅱ35有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II35 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.68 | hwMA01DDCPDUII36ActivePower | Ⅱ36 active power | Ⅱ36有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II36 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.69 | hwMA01DDCPDUII34ActiveEnergy | Ⅱ34 active energy | Ⅱ34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II34 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.70 | hwMA01DDCPDUII35ActiveEnergy | Ⅱ35 active energy | Ⅱ35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II35 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.71 | hwMA01DDCPDUII36ActiveEnergy | Ⅱ36 active energy | Ⅱ36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II36 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.72 | hwMA01DDCPDUII34CurrentLoadRatio | Ⅱ34 current load ratio | Ⅱ34电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II34 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.73 | hwMA01DDCPDUII35CurrentLoadRatio | Ⅱ35 current load ratio | Ⅱ35电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II35 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.74 | hwMA01DDCPDUII36CurrentLoadRatio | Ⅱ36 current load ratio | Ⅱ36电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II36 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.75 | hwMA01DDCPDUI37Voltage | Ⅰ37 voltage | Ⅰ37电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I37 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.76 | hwMA01DDCPDUI38Voltage | Ⅰ38 voltage | Ⅰ38电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I38 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.77 | hwMA01DDCPDUI39Voltage | Ⅰ39 voltage | Ⅰ39电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I39 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.78 | hwMA01DDCPDUI37Current | Ⅰ37 current | Ⅰ37电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I37 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.79 | hwMA01DDCPDUI38Current | Ⅰ38 current | Ⅰ38电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I38 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.80 | hwMA01DDCPDUI39Current | Ⅰ39 current | Ⅰ39电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I39 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.81 | hwMA01DDCPDUI37ActivePower | Ⅰ37 active power | Ⅰ37有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I37 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.82 | hwMA01DDCPDUI38ActivePower | Ⅰ38 active power | Ⅰ38有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I38 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.83 | hwMA01DDCPDUI39ActivePower | Ⅰ39 active power | Ⅰ39有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I39 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.84 | hwMA01DDCPDUI37ActiveEnergy | Ⅰ37 active energy | Ⅰ37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I37 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.85 | hwMA01DDCPDUI38ActiveEnergy | Ⅰ38 active energy | Ⅰ38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I38 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.86 | hwMA01DDCPDUI39ActiveEnergy | Ⅰ39 active energy | Ⅰ39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I39 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.87 | hwMA01DDCPDUI37CurrentLoadRatio | Ⅰ37 current load ratio | Ⅰ37电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I37 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.88 | hwMA01DDCPDUI38CurrentLoadRatio | Ⅰ38 current load ratio | Ⅰ38电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I38 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.89 | hwMA01DDCPDUI39CurrentLoadRatio | Ⅰ39 current load ratio | Ⅰ39电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I39 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.90 | hwMA01DDCPDUI40Voltage | Ⅰ40 voltage | Ⅰ40电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I40 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.91 | hwMA01DDCPDUI41Voltage | Ⅰ41 voltage | Ⅰ41电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I41 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.92 | hwMA01DDCPDUI42Voltage | Ⅰ42 voltage | Ⅰ42电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I42 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.93 | hwMA01DDCPDUI40Current | Ⅰ40 current | Ⅰ40电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I40 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.94 | hwMA01DDCPDUI41Current | Ⅰ41 current | Ⅰ41电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I41 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.95 | hwMA01DDCPDUI42Current | Ⅰ42 current | Ⅰ42电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I42 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.96 | hwMA01DDCPDUI40ActivePower | Ⅰ40 active power | Ⅰ40有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I40 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.97 | hwMA01DDCPDUI41ActivePower | Ⅰ41 active power | Ⅰ41有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I41 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.98 | hwMA01DDCPDUI42ActivePower | Ⅰ42 active power | Ⅰ42有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I42 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.99 | hwMA01DDCPDUI40ActiveEnergy | Ⅰ40 active energy | Ⅰ40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I40 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.100 | hwMA01DDCPDUI41ActiveEnergy | Ⅰ41 active energy | Ⅰ41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I41 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.101 | hwMA01DDCPDUI42ActiveEnergy | Ⅰ42 active energy | Ⅰ42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I42 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.102 | hwMA01DDCPDUI40CurrentLoadRatio | Ⅰ40 current load ratio | Ⅰ40电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I40 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.103 | hwMA01DDCPDUI41CurrentLoadRatio | Ⅰ41 current load ratio | Ⅰ41电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I41 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.104 | hwMA01DDCPDUI42CurrentLoadRatio | Ⅰ42 current load ratio | Ⅰ42电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I42 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.105 | hwMA01DDCPDUI43Voltage | Ⅰ43 voltage | Ⅰ43电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I43 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.106 | hwMA01DDCPDUI44Voltage | Ⅰ44 voltage | Ⅰ44电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I44 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.107 | hwMA01DDCPDUI45Voltage | Ⅰ45 voltage | Ⅰ45电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I45 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.108 | hwMA01DDCPDUI43Current | Ⅰ43 current | Ⅰ43电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I43 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.109 | hwMA01DDCPDUI44Current | Ⅰ44 current | Ⅰ44电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I44 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.110 | hwMA01DDCPDUI45Current | Ⅰ45 current | Ⅰ45电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I45 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.111 | hwMA01DDCPDUI43ActivePower | Ⅰ43 active power | Ⅰ43有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I43 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.112 | hwMA01DDCPDUI44ActivePower | Ⅰ44 active power | Ⅰ44有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I44 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.113 | hwMA01DDCPDUI45ActivePower | Ⅰ45 active power | Ⅰ45有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I45 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.114 | hwMA01DDCPDUI43ActiveEnergy | Ⅰ43 active energy | Ⅰ43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I43 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.115 | hwMA01DDCPDUI44ActiveEnergy | Ⅰ44 active energy | Ⅰ44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I44 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.116 | hwMA01DDCPDUI45ActiveEnergy | Ⅰ45 active energy | Ⅰ45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I45 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.117 | hwMA01DDCPDUI43CurrentLoadRatio | Ⅰ43 current load ratio | Ⅰ43电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I43 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.118 | hwMA01DDCPDUI44CurrentLoadRatio | Ⅰ44 current load ratio | Ⅰ44电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I44 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.119 | hwMA01DDCPDUI45CurrentLoadRatio | Ⅰ45 current load ratio | Ⅰ45电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I45 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.120 | hwMA01DDCPDUI46Voltage | Ⅰ46 voltage | Ⅰ46电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I46 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.121 | hwMA01DDCPDUI47Voltage | Ⅰ47 voltage | Ⅰ47电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I47 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.122 | hwMA01DDCPDUI48Voltage | Ⅰ48 voltage | Ⅰ48电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I48 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.123 | hwMA01DDCPDUI46Current | Ⅰ46 current | Ⅰ46电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I46 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.124 | hwMA01DDCPDUI47Current | Ⅰ47 current | Ⅰ47电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I47 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.125 | hwMA01DDCPDUI48Current | Ⅰ48 current | Ⅰ48电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I48 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.126 | hwMA01DDCPDUI46ActivePower | Ⅰ46 active power | Ⅰ46有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I46 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.127 | hwMA01DDCPDUI47ActivePower | Ⅰ47 active power | Ⅰ47有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I47 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.128 | hwMA01DDCPDUI48ActivePower | Ⅰ48 active power | Ⅰ48有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I48 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.129 | hwMA01DDCPDUI46ActiveEnergy | Ⅰ46 active energy | Ⅰ46有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I46 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.130 | hwMA01DDCPDUI47ActiveEnergy | Ⅰ47 active energy | Ⅰ47有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I47 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.131 | hwMA01DDCPDUI48ActiveEnergy | Ⅰ48 active energy | Ⅰ48有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I48 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.132 | hwMA01DDCPDUI46CurrentLoadRatio | Ⅰ46 current load ratio | Ⅰ46电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I46 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.133 | hwMA01DDCPDUI47CurrentLoadRatio | Ⅰ47 current load ratio | Ⅰ47电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I47 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.134 | hwMA01DDCPDUI48CurrentLoadRatio | Ⅰ48 current load ratio | Ⅰ48电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | I48 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.135 | hwMA01DDCPDUII37Voltage | Ⅱ37 voltage | Ⅱ37电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II37 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.136 | hwMA01DDCPDUII38Voltage | Ⅱ38 voltage | Ⅱ38电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II38 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.137 | hwMA01DDCPDUII39Voltage | Ⅱ39 voltage | Ⅱ39电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II39 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.138 | hwMA01DDCPDUII37Current | Ⅱ37 current | Ⅱ37电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II37 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.139 | hwMA01DDCPDUII38Current | Ⅱ38 current | Ⅱ38电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II38 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.140 | hwMA01DDCPDUII39Current | Ⅱ39 current | Ⅱ39电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II39 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.141 | hwMA01DDCPDUII37ActivePower | Ⅱ37 active power | Ⅱ37有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II37 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.142 | hwMA01DDCPDUII38ActivePower | Ⅱ38 active power | Ⅱ38有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II38 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.143 | hwMA01DDCPDUII39ActivePower | Ⅱ39 active power | Ⅱ39有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II39 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.144 | hwMA01DDCPDUII37ActiveEnergy | Ⅱ37 active energy | Ⅱ37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II37 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.145 | hwMA01DDCPDUII38ActiveEnergy | Ⅱ38 active energy | Ⅱ38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II38 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.146 | hwMA01DDCPDUII39ActiveEnergy | Ⅱ39 active energy | Ⅱ39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II39 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.147 | hwMA01DDCPDUII37CurrentLoadRatio | Ⅱ37 current load ratio | Ⅱ37电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II37 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.148 | hwMA01DDCPDUII38CurrentLoadRatio | Ⅱ38 current load ratio | Ⅱ38电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II38 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.149 | hwMA01DDCPDUII39CurrentLoadRatio | Ⅱ39 current load ratio | Ⅱ39电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II39 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.150 | hwMA01DDCPDUII40Voltage | Ⅱ40 voltage | Ⅱ40电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II40 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.151 | hwMA01DDCPDUII41Voltage | Ⅱ41 voltage | Ⅱ41电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II41 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.152 | hwMA01DDCPDUII42Voltage | Ⅱ42 voltage | Ⅱ42电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II42 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.153 | hwMA01DDCPDUII40Current | Ⅱ40 current | Ⅱ40电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II40 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.154 | hwMA01DDCPDUII41Current | Ⅱ41 current | Ⅱ41电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II41 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.155 | hwMA01DDCPDUII42Current | Ⅱ42 current | Ⅱ42电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II42 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.156 | hwMA01DDCPDUII40ActivePower | Ⅱ40 active power | Ⅱ40有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II40 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.157 | hwMA01DDCPDUII41ActivePower | Ⅱ41 active power | Ⅱ41有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II41 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.158 | hwMA01DDCPDUII42ActivePower | Ⅱ42 active power | Ⅱ42有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II42 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.159 | hwMA01DDCPDUII40ActiveEnergy | Ⅱ40 active energy | Ⅱ40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II40 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.160 | hwMA01DDCPDUII41ActiveEnergy | Ⅱ41 active energy | Ⅱ41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II41 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.161 | hwMA01DDCPDUII42ActiveEnergy | Ⅱ42 active energy | Ⅱ42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II42 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.162 | hwMA01DDCPDUII40CurrentLoadRatio | Ⅱ40 current load ratio | Ⅱ40电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II40 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.163 | hwMA01DDCPDUII41CurrentLoadRatio | Ⅱ41 current load ratio | Ⅱ41电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II41 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.164 | hwMA01DDCPDUII42CurrentLoadRatio | Ⅱ42 current load ratio | Ⅱ42电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II42 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.165 | hwMA01DDCPDUII43Voltage | Ⅱ43 voltage | Ⅱ43电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II43 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.166 | hwMA01DDCPDUII44Voltage | Ⅱ44 voltage | Ⅱ44电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II44 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.167 | hwMA01DDCPDUII45Voltage | Ⅱ45 voltage | Ⅱ45电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II45 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.168 | hwMA01DDCPDUII43Current | Ⅱ43 current | Ⅱ43电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II43 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.169 | hwMA01DDCPDUII44Current | Ⅱ44 current | Ⅱ44电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II44 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.170 | hwMA01DDCPDUII45Current | Ⅱ45 current | Ⅱ45电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II45 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.171 | hwMA01DDCPDUII43ActivePower | Ⅱ43 active power | Ⅱ43有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II43 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.172 | hwMA01DDCPDUII44ActivePower | Ⅱ44 active power | Ⅱ44有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II44 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.173 | hwMA01DDCPDUII45ActivePower | Ⅱ45 active power | Ⅱ45有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II45 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.174 | hwMA01DDCPDUII43ActiveEnergy | Ⅱ43 active energy | Ⅱ43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II43 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.175 | hwMA01DDCPDUII44ActiveEnergy | Ⅱ44 active energy | Ⅱ44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II44 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.176 | hwMA01DDCPDUII45ActiveEnergy | Ⅱ45 active energy | Ⅱ45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II45 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.177 | hwMA01DDCPDUII43CurrentLoadRatio | Ⅱ43 current load ratio | Ⅱ43电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II43 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.178 | hwMA01DDCPDUII44CurrentLoadRatio | Ⅱ44 current load ratio | Ⅱ44电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II44 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.179 | hwMA01DDCPDUII45CurrentLoadRatio | Ⅱ45 current load ratio | Ⅱ45电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II45 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.180 | hwMA01DDCPDUII46Voltage | Ⅱ46 voltage | Ⅱ46电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II46 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.181 | hwMA01DDCPDUII47Voltage | Ⅱ47 voltage | Ⅱ47电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II47 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.182 | hwMA01DDCPDUII48Voltage | Ⅱ48 voltage | Ⅱ48电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II48 voltage of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.183 | hwMA01DDCPDUII46Current | Ⅱ46 current | Ⅱ46电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II46 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.184 | hwMA01DDCPDUII47Current | Ⅱ47 current | Ⅱ47电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II47 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.185 | hwMA01DDCPDUII48Current | Ⅱ48 current | Ⅱ48电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II48 current of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.186 | hwMA01DDCPDUII46ActivePower | Ⅱ46 active power | Ⅱ46有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II46 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.187 | hwMA01DDCPDUII47ActivePower | Ⅱ47 active power | Ⅱ47有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II47 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.188 | hwMA01DDCPDUII48ActivePower | Ⅱ48 active power | Ⅱ48有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II48 active power of the device config table for the MA01D DC PDU.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.189 | hwMA01DDCPDUII46ActiveEnergy | Ⅱ46 active energy | Ⅱ46有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II46 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.190 | hwMA01DDCPDUII47ActiveEnergy | Ⅱ47 active energy | Ⅱ47有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II47 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.191 | hwMA01DDCPDUII48ActiveEnergy | Ⅱ48 active energy | Ⅱ48有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II48 active energy of the device config table for the MA01D DC PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.192 | hwMA01DDCPDUII46CurrentLoadRatio | Ⅱ46 current load ratio | Ⅱ46电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II46 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.193 | hwMA01DDCPDUII47CurrentLoadRatio | Ⅱ47 current load ratio | Ⅱ47电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II47 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.194 | hwMA01DDCPDUII48CurrentLoadRatio | Ⅱ48 current load ratio | Ⅱ48电流负载比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | II48 current load ratio of the device config table for the MA01D DC PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.195 | hwMA01DDCPDUCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the MA01D DC PDU. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.196 | hwMA01DDCPDUPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.197 | hwMA01DDCPDUModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.198 | hwMA01DDCPDUSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.199 | hwMA01DDCPDUHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.2.1.300 | hwMA01DDCPDURunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.3 | hwMA01DDCPDUConfig3Table | / | / |  |  | / | / | The config table of MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.3.1.1 | hwMA01DDCPDUConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.3.1.2 | hwMA01DDCPDUDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the MA01D DC PDU.
1.3.6.1.4.1.2011.6.178.1.1.123.3.1.300 | hwMA01DDCPDUConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of MA01D DC PDU.

## FusionCol-M
FusionCol-M
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.114 | FusionColM | FusionCol-M | FusionCol-M | / | / | / | / | FusionCol-M Equipment.
1.3.6.1.4.1.2011.6.178.1.1.114.1 | hwFusionColMRunning1Table | / | / |  |  | / | / | The running table of FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.1 | hwFusionColMRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.2 | hwFusionColMFirstStartLockingStatus | First start locking status | 初次上电锁定状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | First Start Locking Status of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.3 | hwFusionColMElectricHeat | Electric heat | 电加热 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Electric Heat of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.4 | hwFusionColMLiquidSolenoidValve | Liquid solenoid valve | 液路电磁阀 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Liquid Solenoid Valve of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.5 | hwFusionColMRemoteAlarmOnOff | Remote alarm on off | 远程报警输出 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Remote alarm on off of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.6 | hwFusionColMRemoteOff | Remote off | 远程关机 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Remote off of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.7 | hwFusionColMHumidifierWaterPump | Humidifier water pump | 加湿水泵 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Humidifier Water Pump of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.8 | hwFusionColMWaterInletSolenoidValve | Water inlet solenoid valve | 补水电磁阀 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Water Inlet Solenoid Valve of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.9 | hwFusionColMWaterRefillLevelSwitch | Water refill level switch | 补水液位开关 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Water refill level switch of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.10 | hwFusionColMForcedDrainLevelSwitch | Forced drain level switch | 强排液位开关 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Forced drain level switch of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.11 | hwFusionColMForcibleDrainagePump | Forcible drainage pump | 强排水泵 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Forcible drainage pump of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.12 | hwFusionColMWaterOverflowLevelSwitch | Water overflow level switch | 溢水液位开关 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Water overflow level switch of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.13 | hwFusionColMCustomAlarm1 | Custom alarm1 | 自定义告警1 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Custom Alarm 1 of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.14 | hwFusionColMCustomAlarm2 | Custom alarm2 | 自定义告警2 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Custom Alarm2 of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.15 | hwFusionColMOnOffStatus | On off status | 系统开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | On off status of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.16 | hwFusionColMLockAlarm | Lock alarm | 存在锁定告警 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Lock alarm of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.17 | hwFusionColMStopHumidifierAlarm | Stop humidifier alarm | 存在停加湿器告警 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Stop humidifier alarm of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.18 | hwFusionColMStopEheatAlarm | Stop eheat alarm | 存在停电加热告警 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Stop eheat alarm of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.19 | hwFusionColMStopCompAlarm | Stop comp alarm | 存在停压缩机告警 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Stop comp alarm of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.20 | hwFusionColMStopSystemAlarm | Stop system alarm | 存在停整机告警 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Stop system alarm of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.21 | hwFusionColMReturnTemp | Return temp | 回风温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Return temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.22 | hwFusionColMReturnHumid | Return humid | 回风湿度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Return humid of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.23 | hwFusionColMSupplyTemp | Supply temp | 送风温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Supply temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.24 | hwFusionColMInFanSpeed | In fan speed | 室内风机转速 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | In fan speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.25 | hwFusionColMInfanRuntime | In fan runtime | 室内风机运行时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | In fan runtime of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.26 | hwFusionColMCompRuntime | Comp runtime | 压缩机运行时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Comp runtime of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.27 | hwFusionColMHumidifierRuntime | Humidifier runtime | 加湿器运行时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Humidifier runtime of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.28 | hwFusionColMHeaterRuntime | Heater runtime | 加热器运行时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Heater runtime of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.29 | hwFusionColMAirFilterRuntime | Air filter runtime | 过滤网运行时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Air filter runtime of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.30 | hwFusionColMEev | EEV | 电子膨胀阀开度 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | EEV of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.31 | hwFusionColMUnitAddres | Unit addres | 群控地址 | 0-Read_Only | 只读 | 1..32 | 1..32 | Unit addres of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.32 | hwFusionColMSupercool | Supercool | 过冷度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Supercool of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.33 | hwFusionColMBoardType | Board type | 机型信息 | 0-Read_Only | 只读 | huaweiIDU13KW800mm(1), huaweiIDU13KW600mm(2), huaweiIDU7Point5KW(3), huaweiAIO3Point5KW(4), unknown(255) | [华为13KW内机800mm=1]/[华为13KW内机600mm=2]/[华为7.5KW内机=3]/[华为3.5KW一体机=4] | Board type of the device config table for the FusionCol-M. Value 1 indicate huaweiIDU13KW800mm Value 2 indicate huaweiIDU13KW600mm Value 3 indicate huaweiIDU7Point5KW Value 4 indicate huaweiAIO3Point5KW
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.34 | hwFusionColMIndoorFanPower | Indoor fan power | 室内风机功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Indoor fan power of the device config table for the FusionCol-M.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.35 | hwFusionColMAverageTemp | Average temp | 群控平均回风温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Average temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.36 | hwFusionColMAverageHumidity | Average humidity | 群控平均回风湿度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Average humidity of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.37 | hwFusionColMMaxTemp | Max temp | 群控最大回风温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Max temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.38 | hwFusionColMMinTemp | Min temp | 群控最小回风温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Min temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.39 | hwFusionColMCompPreheatingTime | Comp preheating time | 压缩机预热运行时间 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Comp preheating time of the device config table for the FusionCol-M.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.40 | hwFusionColMCool | Cool | 制冷模式 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Cool of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.41 | hwFusionColMBlowair | Blowair | 送风模式 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Blowair of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.42 | hwFusionColMDehumidity | Dehumidity | 除湿模式 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Dehumidity of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.43 | hwFusionColMDehumidityLowTempOffset | Dehumidity low temp offset | 除湿温度补偿 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Dehumidity low temp offset of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.44 | hwFusionColMCompOilReturn | Comp oil return | 压缩机回油 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Comp oil return of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.45 | hwFusionColMEvaporatorCoilTemperature | Evaporator coil temperature | 蒸发器盘管温度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Evaporator coil temperature of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.46 | hwFusionColMTempDemand | Temp demand | 温度需求 | 0-Read_Only | 只读 | -100..100 | -100..100 | Temp demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.47 | hwFusionColMHumidDemand | Humid demand | 湿度需求 | 0-Read_Only | 只读 | -100..100 | -100..100 | Humid demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.48 | hwFusionColMOutdoorFan1Runtime | Outdoor fan 1 runtime | 室外风机1运行时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Outdoor fan 1 runtime of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.49 | hwFusionColMOutdoorFan2Runtime | Outdoor fan 2 runtime | 室外风机2运行时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Outdoor fan 2 runtime of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.50 | hwFusionColMHumidWaterPumpRuntime | Humid water pump runtime | 加湿水泵运行时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Humid water pump runtime of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.51 | hwFusionColMOutdoorUnitLimit | Outdoor unit limit | 外机限频 | 0-Read_Only | 只读 | unlimitedfrequency(1), limitedfrequencyreduction(2), frequencyincrease(3), frequencyretain(4), limitedfrequencyincrease(5), frequencyreduction(6), shutdownduetofrequencylimit(7), unknown(255) | [无限频=1]/[限降频=2]/[升频=3]/[保持=4]/[限升频=5]/[降频=6]/[限频停机=7] | Outdoor unit limit of the device config table for the FusionCol-M. Value 1 indicate unlimitedFrequency Value 2 indicate limitedFrequencyReduction Value 3 indicate frequencyIncrease Value 4 indicate frequencyRetain Value 5 indicate limitedFrequencyIncrease Value 6 indicate frequencyReduction Value 7 indicate shutdownDueToFrequencyLimit
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.52 | hwFusionColMExhaustPressLimit | Exhaust press limit | 排气压力限频 | 0-Read_Only | 只读 | unlimitedfrequency(1), limitedfrequencyreduction(2), frequencyincrease(3), frequencyretain(4), limitedfrequencyincrease(5), frequencyreduction(6), shutdownduetofrequencylimit(7), unknown(255) | [无限频=1]/[限降频=2]/[升频=3]/[保持=4]/[限升频=5]/[降频=6]/[限频停机=7] | Exhaust press limit of the device config table for the FusionCol-M. Value 1 indicate unlimitedFrequency Value 2 indicate limitedFrequencyReduction Value 3 indicate frequencyIncrease Value 4 indicate frequencyRetain Value 5 indicate limitedFrequencyIncrease Value 6 indicate frequencyReduction Value 7 indicate shutdownDueToFrequencyLimit
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.53 | hwFusionColMSuctionPressLimit | Suction press limit | 吸气压力限频 | 0-Read_Only | 只读 | unlimitedfrequency(1), limitedfrequencyreduction(2), frequencyincrease(3), frequencyretain(4), limitedfrequencyincrease(5), frequencyreduction(6), shutdownduetofrequencylimit(7), unknown(255) | [无限频=1]/[限降频=2]/[升频=3]/[保持=4]/[限升频=5]/[降频=6]/[限频停机=7] | Suction press limit of the device config table for the FusionCol-M. Value 1 indicate unlimitedFrequency Value 2 indicate limitedFrequencyReduction Value 3 indicate frequencyIncrease Value 4 indicate frequencyRetain Value 5 indicate limitedFrequencyIncrease Value 6 indicate frequencyReduction Value 7 indicate shutdownDueToFrequencyLimit
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.54 | hwFusionColMExhaustTempLimit | Exhaust temp limit | 排气温度限频 | 0-Read_Only | 只读 | unlimitedfrequency(1), limitedfrequencyreduction(2), frequencyincrease(3), frequencyretain(4), limitedfrequencyincrease(5), frequencyreduction(6), shutdownduetofrequencylimit(7), unknown(255) | [无限频=1]/[限降频=2]/[升频=3]/[保持=4]/[限升频=5]/[降频=6]/[限频停机=7] | Exhaust temp limit of the device config table for the FusionCol-M. Value 1 indicate unlimitedFrequency Value 2 indicate limitedFrequencyReduction Value 3 indicate frequencyIncrease Value 4 indicate frequencyRetain Value 5 indicate limitedFrequencyIncrease Value 6 indicate frequencyReduction Value 7 indicate shutdownDueToFrequencyLimit
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.55 | hwFusionColMFrequencyLimitOfEvaporatorCoilTemperature | Frequency limit of evaporator coil temperature | 蒸发器盘管T2限频 | 0-Read_Only | 只读 | unlimitedfrequency(1), limitedfrequencyreduction(2), frequencyincrease(3), frequencyretain(4), limitedfrequencyincrease(5), frequencyreduction(6), shutdownduetofrequencylimit(7), unknown(255) | [无限频=1]/[限降频=2]/[升频=3]/[保持=4]/[限升频=5]/[降频=6]/[限频停机=7] | Frequency limit of evaporator coil temperature of the device config table for the FusionCol-M. Value 1 indicate unlimitedFrequency Value 2 indicate limitedFrequencyReduction Value 3 indicate frequencyIncrease Value 4 indicate frequencyRetain Value 5 indicate limitedFrequencyIncrease Value 6 indicate frequencyReduction Value 7 indicate shutdownDueToFrequencyLimit
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.56 | hwFusionColMTpSuperHeatLimit | Tp super heat limit | 排气过热度限频 | 0-Read_Only | 只读 | unlimitedfrequency(1), limitedfrequencyreduction(2), frequencyincrease(3), frequencyretain(4), limitedfrequencyincrease(5), frequencyreduction(6), shutdownduetofrequencylimit(7), unknown(255) | [无限频=1]/[限降频=2]/[升频=3]/[保持=4]/[限升频=5]/[降频=6]/[限频停机=7] | Tp super heat limit of the device config table for the FusionCol-M. Value 1 indicate unlimitedFrequency Value 2 indicate limitedFrequencyReduction Value 3 indicate frequencyIncrease Value 4 indicate frequencyRetain Value 5 indicate limitedFrequencyIncrease Value 6 indicate frequencyReduction Value 7 indicate shutdownDueToFrequencyLimit
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.57 | hwFusionColMPowerControlLimit | Power control limit | 功率控制限频 | 0-Read_Only | 只读 | unlimitedfrequency(1), limitedfrequencyreduction(2), frequencyincrease(3), frequencyretain(4), limitedfrequencyincrease(5), frequencyreduction(6), shutdownduetofrequencylimit(7), unknown(255) | [无限频=1]/[限降频=2]/[升频=3]/[保持=4]/[限升频=5]/[降频=6]/[限频停机=7] | Power control limit of the device config table for the FusionCol-M. Value 1 indicate unlimitedFrequency Value 2 indicate limitedFrequencyReduction Value 3 indicate frequencyIncrease Value 4 indicate frequencyRetain Value 5 indicate limitedFrequencyIncrease Value 6 indicate frequencyReduction Value 7 indicate shutdownDueToFrequencyLimit
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.58 | hwFusionColMInunitPowerVolt | InUnit power volt | 室内机电源电压 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | In unit power volt of the device config table for the FusionCol-M.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.59 | hwFusionColMInunitPowerFreq | InUnit power freq | 室内机电源频率 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | In unit power freq of the device config table for the FusionCol-M.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.60 | hwFusionColMOutunitPower | OutUnit power | 室外机功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Out unit power of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.61 | hwFusionColMOutunitFanSpeed | OutUnit fan speed | 风机运行转速 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | Out unit fan speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.62 | hwFusionColMFanRunningStatus | / | / | 0-Read_Only | 只读 | poweronselfCheck(1), stop(2), run(3), error(4), alarm(5), outdoorfandrivererror(6), outdoorfanlockalarm(7), unknown(255) | / | Fan operating status of the device config table for the FusionCol-M. Value 1 indicate powerOnSelf-Check Value 2 indicate stop Value 3 indicate run Value 4 indicate error Value 5 indicate alarm Value 6 indicate outdoorFanDriverError Value 7 indicate outdoorFanLockAlarm
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.63 | hwFusionColMOutdoorAmbientTemp | Outdoor ambient temp | 环境温度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Outdoor ambient temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.64 | hwFusionColMCondensationTemp | Condensation temp | 冷凝温度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Condensation temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.65 | hwFusionColMCompressorSpeed | Compressor speed | 压缩机转速 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Compressor speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.66 | hwFusionColMCompressorPhaseCur | Compressor phase cur | 压缩机相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Compressor phase cur of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.67 | hwFusionColMOutUnitPowerFreq | Out unit power freq | 电网频率 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Out unit power freq of the device config table for the FusionCol-M.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.68 | hwFusionColMOutUnitPowerVolt | Out unit power volt | 电网电压 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Out unit power volt of the device config table for the FusionCol-M.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.69 | hwFusionColMTp | Tp | 排气温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Tp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.70 | hwFusionColMTh | Th | 气管温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Th of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.71 | hwFusionColMDischargePreesure | Discharge pressure | 排气压力 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Discharge pressures of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.72 | hwFusionColMSuctionPressure | Suction pressure | 吸气压力 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Suction pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.73 | hwFusionColMHpSwitch | Hp switch | 高压开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Hp switch of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.74 | hwFusionColMLpSwitch | Lp switch | 低压开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Lp switch of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.75 | hwFusionColMTpSaturation | Tp saturation | 排气饱和温度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Tp saturation of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.76 | hwFusionColMEevDischargeSuperheat | EEV discharge superheat | 排气过热度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Eev discharge superheat of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.77 | hwFusionColMThSaturation | Th saturation | 吸气饱和温度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Th saturation of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.78 | hwFusionColMEevSuctSuperheat | EEV suct superheat | 吸气过热度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Eev suct superheat of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.79 | hwFusionColMInverterHeatSinkTemperature | Inverter heat sink temperature | 逆变温度 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Inverter heat sink temperature of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.80 | hwFusionColMHeat | Heat | 制热模式 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Heat of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.81 | hwFusionColMHumidity | Humidity | 加湿模式 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Humidity of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.82 | hwFusionColMDehumidityLowTempLimit | Dehumidity low temp limit | 除湿低温限制 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Dehumidity Low Temp Limit of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.83 | hwFusionColMAirSupplyLimit | Air supply limit | 送风限制 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Air Supply Limit of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.84 | hwFusionColMMaxSorRAirTempDiff | Max S/R air temp diff | 室内风机回送风温差最大值 | 0-Read_Only | 只读 | 10..200 | 10..200 | Max S/R Air Temp Diff of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.85 | hwFusionColMMinSorRAirTempDiff | Min S/R air temp diff | 室内风机回送风温差最小值 | 0-Read_Only | 只读 | 10..200 | 10..200 | Min S/R Air Temp Diff of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.86 | hwFusionColMDisHtDropTemp | Dis HT drop temp | 排气高温降频温度 | 0-Read_Only | 只读 | 900..1150 | 900..1150 | Dis HT Drop Temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.87 | hwFusionColMDisHtRiseLimitTemp | Dis HT rise limit temp | 排气高温限升频温度 | 0-Read_Only | 只读 | 900..1150 | 900..1150 | Dis HT Rise Limit Temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.88 | hwFusionColMHeatingTempDemand | Heating temp demand | 补热温度需求 | 0-Read_Only | 只读 | -100..0 | -100..0 | Heating Temp Demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.89 | hwFusionColMFreqRiseTempDemand | Freq rise temp demand | 启动温度需求 | 0-Read_Only | 只读 | 0..100 | 0..100 | Freq Rise Temp Demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.90 | hwFusionColMFreqDropTempDemand | Freq drop temp demand | 停机温度需求 | 0-Read_Only | 只读 | -100..0 | -100..0 | Freq Drop Temp Demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.91 | hwFusionColMCompressorRiseorDropRate | Compressor rise/drop rate | 压缩机升降频速率 | 0-Read_Only | 只读 | 1..10 | 1..10 | Compressor Rise/Drop Rate of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.92 | hwFusionColMCompressorMaxSpeed | Compressor max speed | 压缩机最大转速 | 0-Read_Only | 只读 | 720..4800 | 720..4800 | Compressor Max Speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.93 | hwFusionColMCompressorMinSpeed | Compressor min speed | 压缩机最小转速 | 0-Read_Only | 只读 | 720..4800 | 720..4800 | Compressor Min Speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.94 | hwFusionColMOilReturnSpeed | Oil return speed | 压缩机回油转速 | 0-Read_Only | 只读 | 720..4800 | 720..4800 | Oil Return Speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.95 | hwFusionColMStopVacuumSpeed | Stop vacuum speed | 压缩机停机转速 | 0-Read_Only | 只读 | 720..4800 | 720..4800 | Stop Vacuum Speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.96 | hwFusionColMStopVacuumPressure | Stop vacuum pressure | 停机抽空压力 | 0-Read_Only | 只读 | 0..150 | 0..150 | Stop Vacuum Pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.97 | hwFusionColMInfanMaxSpeed | In fan max speed | 室内风机最大转速 | 0-Read_Only | 只读 | 30..100 | 30..100 | InFan Max Speed of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.98 | hwFusionColMInfanMinSpeed | In fan min speed | 室内风机最小转速 | 0-Read_Only | 只读 | 30..100 | 30..100 | InFan Min Speed of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.99 | hwFusionColMDehumidSpeed | Dehumid speed | 室内风机除湿转速 | 0-Read_Only | 只读 | 30..100 | 30..100 | Dehumid Speed of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.100 | hwFusionColMEevMaxOpen | EEV max open | 电子膨胀阀最大开度 | 0-Read_Only | 只读 | 0..480 | 0..480 | EEV Max Open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.101 | hwFusionColMEevMinOpen | EEV min open | 电子膨胀阀最小开度 | 0-Read_Only | 只读 | 0..480 | 0..480 | EEV Min Open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.102 | hwFusionColMEevStandbyOpen | EEV standby open | 电子膨胀阀待机开度 | 0-Read_Only | 只读 | 0..480 | 0..480 | EEV Standby Open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.103 | hwFusionColMSuctSupperHeatSetPoint | Suct supper heat set point | 电子膨胀阀吸气过热度设定 | 0-Read_Only | 只读 | 20..200 | 20..200 | Suct Supper Heat Set Point of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.104 | hwFusionColMSuctSupperHeatDeadZone | Suct supper heat dead zone | 电子膨胀阀吸气过热度死区 | 0-Read_Only | 只读 | 0..50 | 0..50 | Suct Supper Heat Dead Zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.105 | hwFusionColMAdjustCycle | Adjust cycle | 电子膨胀阀调节周期 | 0-Read_Only | 只读 | 5..300 | 5..300 | Adjust Cycle of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.106 | hwFusionColMPBand | P-band | 电子膨胀阀比例系数 | 0-Read_Only | 只读 | 1..100 | 1..100 | P-band of the device config table for the FusionCol-M.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.107 | hwFusionColMIntegralTimeConstant | Integral time constant | 电子膨胀阀积分时间 | 0-Read_Only | 只读 | 1..999 | 1..999 | Integral Time Constant of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.108 | hwFusionColMDiffTimeConstant | Diff time constant | 电子膨胀阀微分时间 | 0-Read_Only | 只读 | 0..999 | 0..999 | Diff Time Constant of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.109 | hwFusionColMUltralowPressIniOpen | Ultralow press ini open | 电子膨胀阀超低压初始开度 | 0-Read_Only | 只读 | 0..480 | 0..480 | Ultralow Press Ini Open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.110 | hwFusionColMLowPressIniOpen | Low press ini open | 电子膨胀阀低压初始开度 | 0-Read_Only | 只读 | 0..480 | 0..480 | Low Press Ini Open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.111 | hwFusionColMMediumPressIniOpen | Medium press ini open | 电子膨胀阀中压初始开度 | 0-Read_Only | 只读 | 0..480 | 0..480 | Medium Press Ini Open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.112 | hwFusionColMHighPressIniOpen | High press ini open | 电子膨胀阀高压初始开度 | 0-Read_Only | 只读 | 0..480 | 0..480 | High Press Ini Open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.113 | hwFusionColMIniOpenRuntime | Ini open runtime | EEV初始开度运行时间 | 0-Read_Only | 只读 | 60..600 | 60..600 | Ini Open RunTime of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.114 | hwFusionColMLiquidSolenoidValOpenAhead | Liquid solenoid val open ahead | 液路电磁阀启动提前开始时间 | 0-Read_Only | 只读 | 0..99 | 0..99 | Liquid Solenoid Val Open ahead of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.115 | hwFusionColMLiquidSolenoidValCloseDelay | Liquid solenoid val close delay | 液路电磁阀停机延后关闭时间 | 0-Read_Only | 只读 | 0..99 | 0..99 | Liquid Solenoid Val Close Delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.116 | hwFusionColMForcedOilReturnCycle | Forced oil return cycle | 强制回油周期 | 0-Read_Only | 只读 | 2..24 | 2..24 | Forced Oil Return Cycle of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.117 | hwFusionColMOilReturnCycle | Oil return cycle | 回油周期 | 0-Read_Only | 只读 | 120..600 | 120..600 | Oil Return Cycle of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.118 | hwFusionColMMinStopTime | Min stop time | 压缩机最小停机时间 | 0-Read_Only | 只读 | 120..600 | 120..600 | Min Stop Time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.119 | hwFusionColMMinRunTime | Min run time | 压缩机最小开机时间 | 0-Read_Only | 只读 | 120..600 | 120..600 | Min Run Time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.120 | hwFusionColMLoadStartSpace | Load start space | 不同负载启动间隔时间 | 0-Read_Only | 只读 | 2..10 | 2..10 | Load Start Space of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.121 | hwFusionColMMinTempSet | Min temp set | 温度设定最小值 | 0-Read_Only | 只读 | 180..350 | 180..350 | Min Temp Set of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.122 | hwFusionColMMaxTempSet | Max temp set | 温度设定最大值 | 0-Read_Only | 只读 | 180..450 | 180..450 | Max Temp Set of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.123 | hwFusionColMMinHumidSet | Min humid set | 湿度设定最小值 | 0-Read_Only | 只读 | 200..700 | 200..700 | Min Humid Set of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.124 | hwFusionColMMaxHumidSet | Max humid set | 湿度设定最大值 | 0-Read_Only | 只读 | 200..1000 | 200..1000 | Max Humid Set of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.125 | hwFusionColMTempPBand | Temp p-band | 温度比例带 | 0-Read_Only | 只读 | 5..200 | 5..200 | Temp P-band of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.126 | hwFusionColMTempDeadzone | Temp dead zone | 温度死区 | 0-Read_Only | 只读 | 1..200 | 1..200 | Temp Dead zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.127 | hwFusionColMDehumPBand | Dehum p-band | 相对湿度除湿比例带 | 0-Read_Only | 只读 | 10..900 | 10..900 | Dehum P-band of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.128 | hwFusionColMHumidPBand | Humid p-band | 相对湿度加湿比例带 | 0-Read_Only | 只读 | 10..900 | 10..900 | Humid P-band of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.129 | hwFusionColMDehumDeadZone | Dehum dead zone | 相对湿度除湿死区 | 0-Read_Only | 只读 | 5..900 | 5..900 | Dehum Dead Zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.130 | hwFusionColMHumidDeadZone | Humid dead zone | 相对湿度加湿死区 | 0-Read_Only | 只读 | 5..900 | 5..900 | Humid Dead Zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.131 | hwFusionColMRtnAirTempCalibVal | Rtn air temp calibration value | 回风温度校准值 | 0-Read_Only | 只读 | -100..100 | -100..100 | Rtn Air Temp Calibration Value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.132 | hwFusionColMRtnAirHumidCalibVal | Rtn air humid calibration value | 回风湿度校准值 | 0-Read_Only | 只读 | -300..300 | -300..300 | Rtn Air Humid Calibration Value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.133 | hwFusionColMSupAirTempCalibVal | Sup air temp calibration value | 送风温度校准值 | 0-Read_Only | 只读 | -100..100 | -100..100 | Sup Air Temp Calibration Value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.134 | hwFusionColMSupAirHumidCalibVal | Sup air humid calibration value | 送风湿度校准值 | 0-Read_Only | 只读 | -300..300 | -300..300 | Sup Air Humid Calibration Value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.135 | hwFusionColMExhaustPressCalibVal | Exhaust press calibration value | 排气压力校准 | 0-Read_Only | 只读 | -50..50 | -50..50 | Exhaust Press Calibration Value of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.136 | hwFusionColMSuctionPressCalibVal | Suction press calibration value | 吸气压力校准 | 0-Read_Only | 只读 | -50..50 | -50..50 | Suction Press Calibration Value of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.137 | hwFusionColMExhaustTempCalibVal | Exhaust temp calibration value | 排气温度校准 | 0-Read_Only | 只读 | -200..200 | -200..200 | Exhaust Temp Calibration Value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.138 | hwFusionColMSuctionTempCalibVal | Suction temp calibration value | 吸气温度校准 | 0-Read_Only | 只读 | -200..200 | -200..200 | Suction Temp Calibration Value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.139 | hwFusionColMDehumiLimitTempOffset | Dehumi limit temp offset | 除湿低温限制偏差 | 0-Read_Only | 只读 | 5..200 | 5..200 | DeHumi Limit Temp Offset of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.140 | hwFusionColMDehumiLimitTempReturn | Dehumi limit temp return | 除湿低温限制回差 | 0-Read_Only | 只读 | 5..200 | 5..200 | DeHumi Limit Temp Return of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.141 | hwFusionColMDehumiLimitTempDeadzone | Dehumi limit temp dead zone | 除湿低温限制死区 | 0-Read_Only | 只读 | 5..100 | 5..100 | DeHumi Limit Temp Dead zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.142 | hwFusionColMDehumiRequireOnDemand | Dehumi require on demand | 除湿温度补偿开启需求 | 0-Read_Only | 只读 | -50..50 | -50..50 | DeHumi Require On Demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.143 | hwFusionColMDehumiRequireOffDemand | Dehumi require off demand | 除湿温度补偿关闭需求 | 0-Read_Only | 只读 | 0..100 | 0..100 | DeHumi Require Off Demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.144 | hwFusionColMLowShAlarmTemp | Low SH alarm temp | 低过热度报警温度 | 0-Read_Only | 只读 | 0..50 | 0..50 | Low SH Alarm Temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.145 | hwFusionColMLowShAlarmTime | Low SH alarm time | 低过热度报警时间 | 0-Read_Only | 只读 | 0..3600 | 0..3600 | Low SH Alarm Time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.146 | hwFusionColMCompRunTimeOutThres | Comp run time out thres | 压缩机运行超时告警阈值 | 0-Read_Only | 只读 | 20000..40000 | 20000..40000 | Comp Run Time Out Thres of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.147 | hwFusionColMInfanRunTimeOutThres | In fan run time out thres | 室内风机运行超时告警阈值 | 0-Read_Only | 只读 | 30000..80000 | 30000..80000 | InFan Run Time Out Thres of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.148 | hwFusionColMHumidiferTimeOutThres | Humidifer time out thres | 加湿湿膜运行超时告警阈值 | 0-Read_Only | 只读 | 4380..17520 | 4380..17520 | Humidifer Time Out Thres of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.149 | hwFusionColMAirFilterTimeOutThres | Air filter time out thres | 过滤网运行超时告警阈值 | 0-Read_Only | 只读 | 2160..6480 | 2160..6480 | Air Filter Time Out Thres of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.150 | hwFusionColMHeaterRunTimeOutThresLow | Heater run time out thres low | 电加热运行超时告警阈值 | 0-Read_Only | 只读 | 20000..40000 | 20000..40000 | Heater Run Time Out Thres Low of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.151 | hwFusionColMWaterSupplyAbnormalAlarm | Water supply abnormal alarm | 供水异常报警延时 | 0-Read_Only | 只读 | 0..999 | 0..999 | Water Supply Abnormal Alarm of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.152 | hwFusionColMInfanStartDelay | In fan start delay | 室内风机开机延时 | 0-Read_Only | 只读 | 0..99 | 0..99 | InFan Start Delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.153 | hwFusionColMInfanStopDelay | In fan stop delay | 室内风机停机延时 | 0-Read_Only | 只读 | 0..99 | 0..99 | InFan Stop Delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.154 | hwFusionColMTempHumidAlarmDelay | Temp humid alarm delay | 高低温湿度报警延时 | 0-Read_Only | 只读 | 5..999 | 5..999 | TempHumid Alarm Delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.155 | hwFusionColMStartLowPressMaskTime | Start low press mask time | 压缩机开机低压屏蔽时间 | 0-Read_Only | 只读 | 0..600 | 0..600 | Start Low Press Mask Time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.156 | hwFusionColMLowPressSwAlarmDelay | Low press sw alarm delay | 压缩机低压开关报警延时 | 0-Read_Only | 只读 | 3..10 | 3..10 | Low Press SW Alarm Delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.157 | hwFusionColMLowSuctionPressAlarmDelay | Low suction press alarm delay | 压缩机吸气低压告警延时 | 0-Read_Only | 只读 | 3..420 | 3..420 | Low Suction Press Alarm Delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.158 | hwFusionColMLowSuctionPressMaskTime | Low suction press mask time | 压缩机吸气低压屏蔽延时 | 0-Read_Only | 只读 | 3..420 | 3..420 | Low Suction Press Mask Time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.159 | hwFusionColMOvervoltThres | Overvolt thres | 电源过压告警阈值 | 0-Read_Only | 只读 | 100..112 | 100..112 | Overvolt Thres of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.160 | hwFusionColMUndervoltThres | Undervolt thres | 电源欠压告警阈值 | 0-Read_Only | 只读 | 83..100 | 83..100 | Undervolt Thres of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.161 | hwFusionColMOverFreqThres | Over freq thres | 电源高频告警阈值 | 0-Read_Only | 只读 | 61..63 | 61..63 | Over Freq Thres of the device config table for the FusionCol-M.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.162 | hwFusionColMUnderFreqThres | Under freq thres | 电源低频告警阈值 | 0-Read_Only | 只读 | 47..49 | 47..49 | Under Freq Thres of the device config table for the FusionCol-M.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.163 | hwFusionColMUnitInGroup | Unit in group | 群控机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Unit in group of the device config table for the FusionCol-M.SigUnitInfo:pcs.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.164 | hwFusionColMActiveUnitsInGroup | Active units in group | 群控运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Active units in group of the device config table for the FusionCol-M.SigUnitInfo:pcs.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.165 | hwFusionColMRotationType | Rotation type | 轮值类型 | 0-Read_Only | 只读 | times(1), address(2), unknown(255) | [时间=1]/[地址=2] | Rotation type of the device config table for the FusionCol-M. Value 1 indicate times Value 2 indicate address
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.166 | hwFusionColMRotationCycle | Rotation cycle | 轮值周期 | 0-Read_Only | 只读 | 1..30 | 1..30 | Rotation cycle of the device config table for the FusionCol-M.SigUnitInfo:day.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.167 | hwFusionColMRotationTimeHour | Rotation time hour | 轮值时刻小时 | 0-Read_Only | 只读 | 0..23 | 0..23 | Rotation time hour of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.168 | hwFusionColMRotationTimeMinute | Rotation time minute | 轮值时刻分钟 | 0-Read_Only | 只读 | 0..59 | 0..59 | Rotation time minute of the device config table for the FusionCol-M.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.169 | hwFusionColMTempForHtStartAll | Temp for HT start all | 高温同开值 | 0-Read_Only | 只读 | 240..450 | 240..450 | Temp for HT start all of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.170 | hwFusionColMTempForLtStartAll | Temp for LT start all | 低温同开值 | 0-Read_Only | 只读 | 100..180 | 100..180 | Temp for LT start all of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.171 | hwFusionColMYear | Year | 实时时钟-年 | 0-Read_Only | 只读 | 2000..2099 | 2000..2099 | Year of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.172 | hwFusionColMMonth | Month | 实时时钟-月 | 0-Read_Only | 只读 | 1..12 | 1..12 | Month of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.173 | hwFusionColMDate | Date | 实时时钟-日 | 0-Read_Only | 只读 | 1..31 | 1..31 | Date of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.174 | hwFusionColMHour | Hour | 实时时钟-时 | 0-Read_Only | 只读 | 0..23 | 0..23 | Hour of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.175 | hwFusionColMMinute | Minute | 实时时钟-分 | 0-Read_Only | 只读 | 0..59 | 0..59 | Minute of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.176 | hwFusionColMSecond | Second | 实时时钟-秒 | 0-Read_Only | 只读 | 0..59 | 0..59 | Second of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.177 | hwFusionColMOutfan1MaintainTime | Out fan 1 maintain time | 室外风机1维护时间 | 0-Read_Only | 只读 | 30000..80000 | 30000..80000 | OutFan 1 Maintain Time of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.178 | hwFusionColMOutfan2MaintainTime | Out fan 2 maintain time | 室外风机2维护时间 | 0-Read_Only | 只读 | 30000..80000 | 30000..80000 | OutFan 2 Maintain Time of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.179 | hwFusionColMHumidWaterPumpMaintainTime | Humid water pump maintain time | 加湿水泵维护时间 | 0-Read_Only | 只读 | 10000..50000 | 10000..50000 | Humid Water Pump Maintain Time of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.180 | hwFusionColMMinRunPressure | Min run pressure | 室外风机运行最低压力 | 0-Read_Only | 只读 | 100..350 | 100..350 | Min Run Pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.181 | hwFusionColMStartPressure | Start pressure | 室外风机运行启动压力 | 0-Read_Only | 只读 | 100..350 | 100..350 | Start Pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.182 | hwFusionColMMinSpeed | Min speed | 室外风机最小转速 | 0-Read_Only | 只读 | 1200..2400 | 1200..2400 | Min Speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.183 | hwFusionColMMaxRunPressure | Max run pressure | 室外风机运行最大压力 | 0-Read_Only | 只读 | 250..400 | 250..400 | Max Run Pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.184 | hwFusionColMMaxSpeed | Max speed | 室外风机最大转速 | 0-Read_Only | 只读 | 2400..6000 | 2400..6000 | Max Speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.185 | hwFusionColMDiagnosticMode | Diagnostic mode | 手动控制 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Diagnostic Mode of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.186 | hwFusionColMDiagnosticCompressor | Diagnostic compressor | 手动控制压缩机 | 0-Read_Only | 只读 | 0..4800 | 0..4800 | Diagnostic compressor of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.187 | hwFusionColMDiagnosticIndoorFan | Diagnostic indoor fan | 手动控制内风机 | 0-Read_Only | 只读 | 0..100 | 0..100 | Diagnostic Indoor Fan of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.188 | hwFusionColMDiagnosticLiquidSolenoidVal | Diagnostic liquid solenoid val | 手动控制液路电磁阀 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Diagnostic Liquid Solenoid Val of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.189 | hwFusionColMDiagnosticElectricHeater | Diagnostic electric heater | 手动控制电辅热 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Diagnostic Electric Heater of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.190 | hwFusionColMDiagnosticHumidifierWaterPump | Diagnostic humidifier water pump | 手动控制加湿水泵 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Diagnostic Humidifier Water Pump of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.191 | hwFusionColMDiagnosticWaterInletSolVal | Diagnostic water inlet sol val | 手动控制进水电磁阀 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Diagnostic Water Inlet Sol Val of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.192 | hwFusionColMDiagnosticOutdoorFan | Diagnostic outdoor fan | 手动控制外风机 | 0-Read_Only | 只读 | 0..100 | 0..100 | Diagnostic Outdoor Fan of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.193 | hwFusionColMDiagnosticWetFilmHumidifier | Diagnostic wet film humidifier | 手动控制湿膜加湿 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Diagnostic Wet Film Humidifier of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.194 | hwFusionColMInistialStartupPreheating | / | / | 0-Read_Only | 只读 | 4..24 | / | Initial Startup Preheating of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.195 | hwFusionColMLowLiquidSwTrigTime | Low liquid sw trig time | 低液位开关触发时间 | 0-Read_Only | 只读 | 0..200 | 0..200 | Low Liquid SW Trig Time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.196 | hwFusionColMOutUnitFanSpeed2 | Out unit fan speed 2 | 风机2运行转速 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | Out unit fan speed 2 of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.197 | hwFusionColMSpeedControl | Speed control | 控制转速 | 0-Read_Only | 只读 | 0..7200 | 0..7200 | Speed control of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.198 | hwFusionColMOilHeater | Oil heater | 油加热带控制 | 0-Read_Only | 只读 | close(1), open(2), invalid(3), unknown(255) | [关闭=1]/[开启=2]/[无效=3] | Oil Heater of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open Value 3 indicate invalid
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.199 | hwFusionColMForcedCooling | Forced cooling | 强制制冷设置 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Forced Cooling of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.200 | hwFusionColMHighTempStartAll | High temp start all | 高温同开设置 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | High Temp Start All of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.201 | hwFusionColMDriveVersion | Drive version | 驱动软件版本 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Drive version of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.202 | hwFusionColMDriveParameterVersion | Drive parameter version | 驱动参数版本 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Drive parameter version of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.1.1.300 | hwFusionColMRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2 | hwFusionColMRunning2Table | / | / |  |  | / | / | The running table of FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.1 | hwFusionColMRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.2 | hwFusionColMLowTemoStartAll | Low temp start all | 低温同开设置 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Low Temo Start All of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.3 | hwFusionColMDehumidifiying | Dehumidifying | 除湿功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Dehumidifying of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.4 | hwFusionColMHumidifiying | Humidifying | 加湿功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Humidifying of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.5 | hwFusionColMHeating | Heating | 加热功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Heating of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.6 | hwFusionColMTeamwork | Teamwork | 群控功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | TeamWork of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.7 | hwFusionColMRataion | Rotation | 轮询功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Rotation of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.8 | hwFusionColMEnableTeamworkResistor | Enable teamwork resistor | 群控匹配电阻开启 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable TeamWork Resistor of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.9 | hwFusionColMEnableMinotorResistor | Enable monitor resistor | 监控匹配电阻开启 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Monitor Resistor of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.10 | hwFusionColMEnableOutfan1MaintainAlarm | Enable out fan 1 maintain alarm | 室外风机1维护报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable out fan 1 maintain alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.11 | hwFusionColMEnableOutfan2MaintainAlarm | Enable out fan 2 maintain alarm | 室外风机2维护报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable OutFan 2 Maintain Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.12 | hwFusionColMEnableInfanMaintainAlarm | Enable in fan maintain alarm | 内风机维护报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable InFan Maintain Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.13 | hwFusionColMEnableCompressorMaintainAlarm | Enable compressor maintain alarm | 压缩机维护报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Compressor Maintain Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.14 | hwFusionColMEnableHumidiferMaintainAlarm | Enable humidifer maintain alarm | 加湿湿膜维护报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Humidifer Maintain Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.15 | hwFusionColMEnableAirFilterMaintainAlm | Enable air filter maintain alarm | 过滤网维护报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable air filter maintain alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.16 | hwFusionColMEnableHeatMaintainAlarm | Enable heat maintain alarm | 电加热维护报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Heat Maintain Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.17 | hwFusionColMWaterLeakageAlarmEnable | Water leakage alarm enable | 漏水报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Water Leakage Alarm Enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.18 | hwFusionColMEnableSomkeAlarm | Enable smoke alarm | 烟感报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Smoke Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.19 | hwFusionColMEnableFireAlarm | Enable fire alarm | 火感报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Fire Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.20 | hwFusionColMEnableCompressorPreheatAlarm | Enable compressor preheat alarm | 压缩机预热告警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Compressor preHeat Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.21 | hwFusionColMEnableHumidPumpOutAlarm | Enable humid pump out alarm | 加湿水泵维护报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Humid Pump Out Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.22 | hwFusionColMDrainagePump | Drainage pump | 强排水泵 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Drainage pump of the device config table for the FusionCol-M. Value 1 indicate No Value 2 indicate Yes
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.23 | hwFusionColMAirFilter | Air filter | 过滤网等级 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Air Filter of the device config table for the FusionCol-M. Value 1 indicate No Value 2 indicate Yes
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.24 | hwFusionColMLiquidSolenoidVal | Liquid solenoid val | 液路电磁阀 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Liquid Solenoid Val of the device config table for the FusionCol-M. Value 1 indicate No Value 2 indicate Yes
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.25 | hwFusionColMHeatHumid | Heat&humid | 加热加湿 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | HeatHumid of the device config table for the FusionCol-M. Value 1 indicate No Value 2 indicate Yes
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.26 | hwFusionColMDehumidificationTemperatureCompensation | Dehumidification temperature compensation | 除湿温度补偿功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Dehumidification temperature compensation of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.27 | hwFusionColMDehumidificationLowTemperatureLimiting | Dehumidification low temperature limiting | 除湿低温限制功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Dehumidification low temperature limiting of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.28 | hwFusionColMAirflowMissingAlarmEnable | Airflow missing alarm enable | 气流丢失报警使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Airflow missing alarm enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.29 | hwFusionColMCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the FusionCol-M. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.30 | hwFusionColMSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.31 | hwFusionColMHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.32 | hwFusionColMIndoorUnitSoftwareVersion | Indoor unit software version | 室内机软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Indoor Unit Software Version of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.33 | hwFusionColMEqualityOutput | / | / | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | / | Equality output of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.34 | hwFusionColMSystemStatus | System status | 系统状态 | 0-Read_Only | 只读 | receivingMonitoringCommand(1), upgradingInternalFirmware(2), upgradingExternalFirmware(3), unknown(255) | [接收监控命令=1]/[内部固件升级中=2]/[外部固件升级中=3] | System status of the device config table for the FusionCol-M. Value 1 indicate receiving monitoring command Value 2 indicate upgrading internal firmware Value 3 indicate upgrading external firmware
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.35 | hwFusionColMOutUnitPowerFactor | / | / | 0-Read_Only | 只读 | 0..100 | / | OutUnit power factor of the device config table for the FusionCol-M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.36 | hwFusionColMCondensationPressure | / | / | 0-Read_Only | 只读 | -30000..30000 | / | Condensation pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.37 | hwFusionColMPressureSetSpeed | / | / | 0-Read_Only | 只读 | 0..6000 | / | Pressure set speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.38 | hwFusionColMMinFanRunningFrequency | / | / | 0-Read_Only | 只读 | 0..6000 | / | OutUnit power factor of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.39 | hwFusionColMModbusSetSpeed | ModBus set speed | ModBus给定转速 | 0-Read_Only | 只读 | -6000..6000 | -6000..6000 | ModBus set speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.40 | hwFusionColMControlBoardSetSpeedControlMode | / | / | 0-Read_Only | 只读 | speedDifferenceControlMode(1), absoluteSpeedControlMode(2), unknown(255) | / | Control board set speed control mode of the device config table for the FusionCol-M. Value 1 indicate speed difference control mode Value 2 indicate absolute speed control mode
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.41 | hwFusionColMControlBoardSetAbsoluteSpeed | / | / | 0-Read_Only | 只读 | 0..6000 | / | Control board set absolute speed of the device config table for the FusionCol-M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.42 | hwFusionColMCompressorRunningStatus | Compressor running status | 压缩机运行状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Compressor running status of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.43 | hwFusionColMDCBusVoltage | / | / | 0-Read_Only | 只读 | 0..60000 | / | DC bus voltage of the device config table for the FusionCol-M.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.44 | hwFusionColMEnableAutomaticOperation | / | / | 0-Read_Only | 只读 | indicateDirectShutdownAfteraCommunicationFaultOccurs(1), indicateAutomaticRunningAfterACommunicationFaultOccurs(2), unknown(255) | / | Enable automatic operation of the device config table for the FusionCol-M. Value 1 indicate direct shutdown after a communication fault occurs Value 2 indicate Automatic running after a communication fault occurs
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.45 | hwFusionColMCompressorEmergencyStopControlMode | / | / | 0-Read_Only | 只读 | emergencyStop(1), slowStop(2), unknown(255) | / | Compressor emergency stop control mode of the device config table for the FusionCol-M. Value 1 indicate emergency stop Value 2 indicate slow stop
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.46 | hwFusionColMCompressorDriverSwitchControl | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | Compressor driver switch control of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.47 | hwFusionColMOutdoorFanType | Outdoor fan type | 当前风机类型 | 0-Read_Only | 只读 | indicateFactorySettingsRatedFrequency50Hz(1), indicateSingle6FFanRatedFrequency50Hz(2), indicateSingle6KFanRatedFrequency60Hz(3), indicateDual6FFansRatedFrequency50Hz(4), indicateDual6KFansRatedFrequency60Hz(5), unknown(255) | [出厂设置，额定频率50Hz=1]/[单6F风机，额定频率50Hz=2]/[单6K风机，额定频率60Hz=3]/[双6F风机，额定频率50Hz=4]/[双6K风机，额定频率60Hz=5] | Outdoor fan type of the device config table for the FusionCol-M. Value 1 indicate Factory settings, rated frequency 50Hz Value 2 indicate Single 6F fan, rated frequency 50Hz Value 3 indicate Single 6K fan, rated frequency 60Hz Value 4 indicate Dual 6F fans, rated frequency 50Hz Value 5 indicate Dual 6K fans, rated frequency 60Hz
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.48 | hwFusionColMSampOnOffStatus | On/Off status | 开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | On Off status of the device config table for the FusionCol-M. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.49 | hwFusionColMCoolChannelTemp1 | Cool channel temp 1 | 冷通道温度1 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Cool Channel Temp 1 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.50 | hwFusionColMCoolChannelTemp2 | Cool channel temp 2 | 冷通道温度2 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Cool Channel Temp 2 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.51 | hwFusionColMCoolChannelTemp3 | Cool channel temp 3 | 冷通道温度3 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Cool Channel Temp 3 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.52 | hwFusionColMHeatChannelTemp1 | Heat channel temp 1 | 热通道温度1 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Heat Channel Temp 1 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.53 | hwFusionColMHeatChannelTemp2 | Heat channel temp 2 | 热通道温度2 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Heat Channel Temp 2 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.54 | hwFusionColMHeatChannelTemp3 | Heat channel temp 3 | 热通道温度3 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Heat Channel Temp 3 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.55 | hwFusionColMCoolChannelHumid1 | Cool channel humid 1 | 冷通道湿度1 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Cool Channel Humid 1 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.56 | hwFusionColMCoolChannelHumid2 | Cool channel humid 2 | 冷通道湿度2 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Cool Channel Humid 2 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.57 | hwFusionColMCoolChannelHumid3 | Cool channel humid 3 | 冷通道湿度3 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Cool Channel Humid 3 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.58 | hwFusionColMHeatChannelHumid1 | Heat channel humid 1 | 热通道湿度1 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Heat Channel Humid 1 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.59 | hwFusionColMHeatChannelHumid2 | Heat channel humid 2 | 热通道湿度2 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Heat Channel Humid 2 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.60 | hwFusionColMHeatChannelHumid3 | Heat channel humid 3 | 热通道湿度3 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Heat Channel Humid 3 of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.61 | hwFusionColMColdAisleTHSensorFaultEnable | Cold aisle T/H sensor fault enable | 冷通道温湿度传感器故障使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold Aisle TH Sensor Fault Enable output of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.62 | hwFusionColMHotAisleTHSensorFaultEnable | Hot aisle T/H sensor fault enable | 热通道温湿度传感器故障使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold Aisle TH Sensor Fault Enable output of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.63 | hwFusionColMPowerOnSelfCheck | Power on self-check | 上电自检 | 0-Read_Only | 只读 | nottriggered(1), triggered(2), unknown(255) | [未触发=1]/[触发=2] | Power on self-check of the device config table for the FusionCol-M. Value 1 indicate notTriggered Value 2 indicate triggered
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.64 | hwFusionColMStop | Stop | 停机 | 0-Read_Only | 只读 | nottriggered(1), triggered(2), unknown(255) | [未触发=1]/[触发=2] | Stop of the device config table for the FusionCol-M. Value 1 indicate notTriggered Value 2 indicate triggered
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.65 | hwFusionColMRun | Run | 运行 | 0-Read_Only | 只读 | nottriggered(1), triggered(2), unknown(255) | [未触发=1]/[触发=2] | Run of the device config table for the FusionCol-M. Value 1 indicate notTriggered Value 2 indicate triggered
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.66 | hwFusionColMError | Error | 故障 | 0-Read_Only | 只读 | nottriggered(1), triggered(2), unknown(255) | [未触发=1]/[触发=2] | Error of the device config table for the FusionCol-M. Value 1 indicate notTriggered Value 2 indicate triggered
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.67 | hwFusionColMAlarm | Alarm | 告警 | 0-Read_Only | 只读 | nottriggered(1), triggered(2), unknown(255) | [未触发=1]/[触发=2] | Alarm of the device config table for the FusionCol-M. Value 1 indicate notTriggered Value 2 indicate triggered
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.68 | hwFusionColMModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.69 | hwFusionColMMotor1FaultCode | Motor 1 fault code | 电机1故障码 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Motor 1 fault code of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.70 | hwFusionColMMotor1PhaseCurrent | Motor 1 phase current | 电机1相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Motor 1 phase current of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.71 | hwFusionColMMotor2FaultCode | Motor 2 fault code | 电机2故障码 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Motor 2 fault code of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.72 | hwFusionColMMotor2PhaseCurrent | Motor 2 phase current | 电机2相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Motor 2 phase current of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.73 | hwFusionColMMotor3FaultCode | Motor 3 fault code | 电机3故障码 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Motor 3 fault code of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.74 | hwFusionColMMotor3PhaseCurrent | Motor 3 phase current | 电机3相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Motor 3 phase current of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.75 | hwFusionColMMotor4FaultCode | Motor 4 fault code | 电机4故障码 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Motor 4 fault code of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.76 | hwFusionColMMotor4PhaseCurrent | Motor 4 phase current | 电机4相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Motor 4 phase current of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.114.2.1.101 | hwFusionColMRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.3 | hwFusionColMConfig3Table | / | / |  |  | / | / | The config table of FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.1 | hwFusionColMConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.2 | hwFusionColMDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.3 | hwFusionColMPowerOnorOff | Power on/off | 开关机设置 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Power ON/OFF of the device config table for the FusionCol-M. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.4 | hwFusionColMTemperatureSetpoint | Temperature setpoint | 设定温度 | 1-Read_Write | 读写 | 180..350 | 180..350 | Temperature setpoint of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.5 | hwFusionColMHumiditySetpoint | Humidity setpoint | 设定湿度 | 1-Read_Write | 读写 | 200..1000 | 200..1000 | Humidity setpoint of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.6 | hwFusionColMReturnAirLtThres | Return air lt thres | 回风低温报警限值 | 1-Read_Write | 读写 | 50..240 | 50..240 | Return Air LT Thres of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.7 | hwFusionColMReturnAirHtThres | Return air ht thres | 回风高温报警限值 | 1-Read_Write | 读写 | 250..450 | 250..450 | Return Air HT Thres of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.8 | hwFusionColMLowHumidThres | Return air low humid thres | 回风低湿报警限值 | 1-Read_Write | 读写 | 50..350 | 50..350 | Low Humid Thres of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.9 | hwFusionColMHighHumidThres | Return air high humid thres | 回风高湿报警限值 | 1-Read_Write | 读写 | 650..950 | 650..950 | High Humid Thres of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.10 | hwFusionColMDiagnosticEevOpening | Diagnostic EEV opening | 手动控制电子膨胀阀 | 1-Read_Write | 读写 | 0..480 | 0..480 | Diagnostic EEV opening of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.11 | hwFusionColMClearCompressorRuntime | Clear compressor runtime | 压缩机运行时间清零 | 1-Read_Write | 读写 | invalid(1), zeroout(2), unknown(255) | [无效=1]/[清零=2] | Clear Compressor RunTime of the device config table for the FusionCol-M. Value 1 indicate invalid Value 2 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.12 | hwFusionColMClearIndoorFanRuntime | Clear indoor fan runtime | 内风机运行时间清零 | 1-Read_Write | 读写 | invalid(1), zeroout(2), unknown(255) | [无效=1]/[清零=2] | Clear Indoor Fan RunTime of the device config table for the FusionCol-M. Value 1 indicate invalid Value 2 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.13 | hwFusionColMClearWetFilmHumidifierRuntime | Clear wet film humidifier runtime | 加湿湿膜运行时间清零 | 1-Read_Write | 读写 | invalid(1), zeroout(2), unknown(255) | [无效=1]/[清零=2] | Clear Wet Film Humidifier RunTime of the device config table for the FusionCol-M. Value 1 indicate invalid Value 2 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.14 | hwFusionColMClearElectricHeaterRuntime | Clear electric heater runtime | 电加热运行时间清零 | 1-Read_Write | 读写 | invalid(1), zeroout(2), unknown(255) | [无效=1]/[清零=2] | Clear Electric Heater RunTime of the device config table for the FusionCol-M. Value 1 indicate invalid Value 2 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.15 | hwFusionColMClearAirFilterRuntime | Clear air filter runtime | 过滤网运行时间清零 | 1-Read_Write | 读写 | invalid(1), zeroout(2), unknown(255) | [无效=1]/[清零=2] | Clear Air Filter RunTime of the device config table for the FusionCol-M. Value 1 indicate invalid Value 2 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.16 | hwFusionColMClearOutdoorFan1Runtime | Clear outdoor fan 1 runtime | 外风机1运行时间清零 | 1-Read_Write | 读写 | invalid(1), zeroout(2), unknown(255) | [无效=1]/[清零=2] | Clear Outdoor Fan 1 RunTime of the device config table for the FusionCol-M. Value 1 indicate invalid Value 2 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.17 | hwFusionColMClearOutdoorFan2Runtime | Clear outdoor fan 2 runtime | 外风机2运行时间清零 | 1-Read_Write | 读写 | invalid(1), zeroout(2), unknown(255) | [无效=1]/[清零=2] | Clear Outdoor Fan 2 RunTime of the device config table for the FusionCol-M. Value 1 indicate invalid Value 2 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.18 | hwFusionColMClearHumidWaterPumpRuntime | Clear humid water pump runtime | 加湿泵运行时间清零 | 1-Read_Write | 读写 | invalid(1), zeroout(2), unknown(255) | [无效=1]/[清零=2] | Clear Humid Water Pump RunTime of the device config table for the FusionCol-M. Value 1 indicate invalid Value 2 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.19 | hwFusionColMClearLockAlarm | Clear lock alarm | 锁定故障清除 | 1-Read_Write | 读写 | zeroout(1), unknown(255) | [清零=1] | Clear Lock Alarm of the device config table for the FusionCol-M. Value 1 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.20 | hwFusionColMReset | Reset | 恢复出厂设置 | 1-Read_Write | 读写 | zeroout(1), unknown(255) | [清零=1] | Reset of the device config table for the FusionCol-M. Value 1 indicate zeroOut
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.21 | hwFusionColMEnableHighTempAlarm | Enable high temp alarm | 高温报警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable High Temp Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.22 | hwFusionColMEnableLowTempAlarm | Enable low temp alarm | 低温报警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Low Temp Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.23 | hwFusionColMEnableHighHumidAlarm | Enable high humid alarm | 高湿报警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable High Humid Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.24 | hwFusionColMEnableLowHumidAlarm | Enable low humid alarm | 低湿报警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable Low Humid Alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.25 | hwFusionColMControlmode | Control mode | 控制方式 | 1-Read_Write | 读写 | returnAirControl(1), supplyAirControl(2), coldAisleAverageValueControl(3), coldAisleMinimumValueControl(4), coldAisleMaximumValueControl(5), hotAisleAverageValueControl(6), hotAisleMinimumValueControl(7), hotAisleMaximumValueControl(8), unknown(255) | [回风控制=1]/[送风控制=2]/[冷通道平均值控制=3]/[冷通道最小值控制=4]/[冷通道最大值控制=5]/[热通道平均值控制=6]/[热通道最小值控制=7]/[热通道最大值控制=8] | Control mode of the device config table for the FusionCol-M. Value 1 indicate Return Air Control Value 2 indicate Supply Air Control Value 3 indicate Cold Aisle Average Value Control Value 4 indicate Cold Aisle Minimum Value Control Value 5 indicate Cold Aisle Maximum Value Control Value 6 indicate Hot Aisle Average Value Control Value 7 indicate Hot Aisle Minimum Value Control Value 8 indicate Hot Aisle Maximum Value Control
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.26 | hwFusionColMMedValOfTempDiffBetweenTheRetSupplyAirOfIndoorFans | Intermediate value of temp diff between the return/supply air of indoor fans | 室内风机回送风温差中间值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Intermediate Value Of Temp Diff Between The Return/Supply Air Of Indoor Fans of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.27 | hwFusionColMSetEqualityOutput | Equality output | 均匀输出使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Equality output of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.28 | hwFusionColMSetDehumidificationTemperatureCompensation | Dehumidification temperature compensation | 除湿温度补偿功能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Dehumidification temperature compensation of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.29 | hwFusionColMSetDehumidificationLowTemperatureLimiting | Dehumidification low temperature limiting | 除湿低温限制功能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Dehumidification low temperature limiting of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.30 | hwFusionColMSetMaxSorRAirTempDiff | Max S/R air temp diff | 室内风机回送风温差最大值 | 1-Read_Write | 读写 | 10..200 | 10..200 | Max S/R air temp diff of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.31 | hwFusionColMSetMinSorRAirTempDiff | Min S/R air temp diff | 室内风机回送风温差最小值 | 1-Read_Write | 读写 | 10..200 | 10..200 | Min S/R air temp diff of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.32 | hwFusionColMSetDisHtDropTemp | Dis HT drop temp | 排气高温降频温度 | 1-Read_Write | 读写 | 900..1150 | 900..1150 | Dis HT drop temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.33 | hwFusionColMSetDisHtRiseLimitTemp | Dis HT rise limit temp | 排气高温升频温度 | 1-Read_Write | 读写 | 900..1150 | 900..1150 | Dis HT rise limit temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.34 | hwFusionColMSetHeatingTempDemand | Heating temp demand | 补热温度需求 | 1-Read_Write | 读写 | -100..0 | -100..0 | Heating temp demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.35 | hwFusionColMSetFreqRiseTempDemand | Freq rise temp demand | 启动温度需求 | 1-Read_Write | 读写 | 0..100 | 0..100 | Freq rise temp demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.36 | hwFusionColMSetFreqDropTempDemand | Freq drop temp demand | 停机温度需求 | 1-Read_Write | 读写 | -100..0 | -100..0 | Freq drop temp demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.37 | hwFusionColMSetCompressorRiseorDropRate | Compressor rise/drop rate | 压缩机升降频速率 | 1-Read_Write | 读写 | 1..10 | 1..10 | Compressor rise/drop rate of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.38 | hwFusionColMSetCompressorMaxSpeed | Compressor max speed | 压缩机最大转速 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Compressor max speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.39 | hwFusionColMSetCompressorMinSpeed | Compressor min speed | 压缩机最小转速 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Compressor min speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.40 | hwFusionColMSetOilReturnSpeed | Oil return speed | 压缩机回油转速 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Oil return speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.41 | hwFusionColMSetStopVacuumSpeed | Stop vacuum speed | 压缩机停机转速 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Stop vacuum speed of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.42 | hwFusionColMSetStopVacuumPressure | Stop vacuum pressure | 停机抽空压力 | 1-Read_Write | 读写 | 0..150 | 0..150 | Stop vacuum pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.43 | hwFusionColMSetInfanMaxSpeed | In fan max speed | 室内风机最大转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | In fan max speed of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.44 | hwFusionColMSetInfanMinSpeed | In fan min speed | 室内风机最小转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | In fan min speed of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.45 | hwFusionColMSetDehumidSpeed | Dehumid speed | 室内风机除湿转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | Dehumid speed of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.46 | hwFusionColMSetEevMaxOpen | EEV max open | 电子膨胀阀最大开度 | 1-Read_Write | 读写 | 0..480 | 0..480 | EEV max open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.47 | hwFusionColMSetEevMinOpen | EEV min open | 电子膨胀阀最小开度 | 1-Read_Write | 读写 | 0..480 | 0..480 | EEV min open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.48 | hwFusionColMSetEevStandbyOpen | EEV standby open | 电子膨胀阀待机开度 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | EEV standby open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.49 | hwFusionColMSetSuctSupperHeatSetPoint | Suct supper heat set point | 电子膨胀阀吸气过热度设定 | 1-Read_Write | 读写 | 20..200 | 20..200 | Suct supper heat set point of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.50 | hwFusionColMSetSuctSupperHeatDeadZone | Suct supper heat dead zone | 电子膨胀阀吸气过热度死区 | 1-Read_Write | 读写 | 0..50 | 0..50 | Suct supper heat dead zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.51 | hwFusionColMSetAdjustCycle | Adjust cycle | 电子膨胀阀调节周期 | 1-Read_Write | 读写 | 5..300 | 5..300 | Adjust cycle of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.52 | hwFusionColMSetPBand | P-band | 电子膨胀阀比例系数 | 1-Read_Write | 读写 | 1..100 | 1..100 | P-band of the device config table for the FusionCol-M.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.53 | hwFusionColMSetIntegralTimeConstant | Integral time constant | 电子膨胀阀积分时间 | 1-Read_Write | 读写 | 1..999 | 1..999 | Integral time constant of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.54 | hwFusionColMSetDiffTimeConstant | Diff time constant | 电子膨胀阀微分时间 | 1-Read_Write | 读写 | 0..999 | 0..999 | Diff time constant of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.55 | hwFusionColMSetUltralowPressIniOpen | Ultralow press ini open | 电子膨胀阀超低压初始开度 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Ultralow press ini open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.56 | hwFusionColMSetLowPressIniOpen | Low press ini open | 电子膨胀阀低压初始开度 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Low press ini open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.57 | hwFusionColMSetMediumPressIniOpen | Medium press ini open | 电子膨胀阀中压初始开度 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Medium press ini open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.58 | hwFusionColMSetHighPressIniOpen | High press ini open | 电子膨胀阀高压初始开度 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | High press ini open of the device config table for the FusionCol-M.SigUnitInfo:P.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.59 | hwFusionColMSetIniOpenRuntime | Ini open runtime | EEV初始开度运行时间 | 1-Read_Write | 读写 | 60..600 | 60..600 | Ini open runtime of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.60 | hwFusionColMSetForcedOilReturnCycle | Forced oil return cycle | 强制回油周期 | 1-Read_Write | 读写 | 2..24 | 2..24 | Forced oil return cycle of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.61 | hwFusionColMSetOilReturnCycle | Oil return cycle | 回油周期 | 1-Read_Write | 读写 | 120..600 | 120..600 | Oil return cycle of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.62 | hwFusionColMSetMinStopTime | Min stop time | 压缩机最小停机时间 | 1-Read_Write | 读写 | 120..600 | 120..600 | Min stop time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.63 | hwFusionColMSetMinRunTime | Min run time | 压缩机最小开机时间 | 1-Read_Write | 读写 | 120..600 | 120..600 | Min run time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.64 | hwFusionColMSetLoadStartInterval | Load start interval | 不同负载启动间隔时间 | 1-Read_Write | 读写 | 2..10 | 2..10 | Load start interval of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.65 | hwFusionColMSetMinTempSet | Min temp set | 温度设定最小值 | 1-Read_Write | 读写 | 180..350 | 180..350 | Min temp set of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.66 | hwFusionColMSetMaxTempSet | Max temp set | 温度设定最大值 | 1-Read_Write | 读写 | 180..450 | 180..450 | Max temp set of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.67 | hwFusionColMSetMinHumidSet | Min humid set | 湿度设定最小值 | 1-Read_Write | 读写 | 200..700 | 200..700 | Min humid set of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.68 | hwFusionColMSetMaxHumidSet | Max humid set | 湿度设定最大值 | 1-Read_Write | 读写 | 200..1000 | 200..1000 | Max humid set of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.69 | hwFusionColMSetTempPBand | Temp p-band | 温度比例带 | 1-Read_Write | 读写 | 5..200 | 5..200 | Temp p-band of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.70 | hwFusionColMSetTempDeadzone | Temp dead zone | 温度死区 | 1-Read_Write | 读写 | 1..200 | 1..200 | Temp dead zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.71 | hwFusionColMSetDehumPBand | Dehum p-band | 相对湿度除湿比例带 | 1-Read_Write | 读写 | 10..900 | 10..900 | Dehum p-band of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.72 | hwFusionColMSetHumidPBand | Humid p-band | 相对湿度加湿比例带 | 1-Read_Write | 读写 | 10..900 | 10..900 | Humid p-band of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.73 | hwFusionColMSetDehumDeadZone | Dehum dead zone | 相对湿度除湿死区 | 1-Read_Write | 读写 | 5..900 | 5..900 | Dehum dead zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.74 | hwFusionColMSetHumidDeadZone | Humid dead zone | 相对湿度加湿死区 | 1-Read_Write | 读写 | 5..900 | 5..900 | Humid dead zone of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.75 | hwFusionColMSetRtnAirTempCalibVal | Rtn air temp calibration value | 回风温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Rtn air temp calibration value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.76 | hwFusionColMSetRtnAirHumidCalibVal | Rtn air humid calibration value | 回风湿度校准值 | 1-Read_Write | 读写 | -300..300 | -300..300 | Rtn air humid calibration value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.77 | hwFusionColMSetSupAirTempCalibVal | Sup air temp calibration value | 送风温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Sup air temp calibration value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.78 | hwFusionColMSetSupAirHumidCalibVal | Sup air humid calibration value | 送风湿度校准值 | 1-Read_Write | 读写 | -300..300 | -300..300 | Sup air humid calibration value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.79 | hwFusionColMSetExhaustPressCalibVal | Exhaust press calibration value | 排气压力校准 | 1-Read_Write | 读写 | -50..50 | -50..50 | Exhaust press calibration value of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.80 | hwFusionColMSetSuctionPressCalibVal | Suction press calibration value | 吸气压力校准 | 1-Read_Write | 读写 | -50..50 | -50..50 | Suction press calibration value of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.81 | hwFusionColMSetExhaustTempCalibVal | Exhaust temp calibration value | 排气温度校准 | 1-Read_Write | 读写 | -200..200 | -200..200 | Exhaust temp calibration value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.82 | hwFusionColMSetSuctionTempCalibVal | Suction temp calibration value | 吸气温度校准 | 1-Read_Write | 读写 | -200..200 | -200..200 | Suction temp calibration value of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.83 | hwFusionColMSetDehumiRequireOnDemand | Dehumi require on demand | 除湿温度补偿开启需求 | 1-Read_Write | 读写 | -50..50 | -50..50 | Dehumi require on demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.84 | hwFusionColMSetDehumiRequireOffDemand | Dehumi require off demand | 除湿温度补偿关闭需求 | 1-Read_Write | 读写 | 0..100 | 0..100 | Dehumi require off demand of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.85 | hwFusionColMSetLowShAlarmTemp | Low SH alarm temp | 低过热度报警温度 | 1-Read_Write | 读写 | 0..50 | 0..50 | Low SH alarm temp of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.86 | hwFusionColMSetLowShAlarmTime | Low SH alarm time | 低过热度报警时间 | 1-Read_Write | 读写 | 0..3600 | 0..3600 | Low SH alarm time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.87 | hwFusionColMSetInfanStartDelay | In fan start delay | 室内风机开机延时 | 1-Read_Write | 读写 | 0..99 | 0..99 | In fan start delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.88 | hwFusionColMSetInfanStopDelay | In fan stop delay | 室内风机停机延时 | 1-Read_Write | 读写 | 0..99 | 0..99 | In fan stop delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.89 | hwFusionColMSetTempHumidAlarmDelay | Temp humid alarm delay | 高低温湿度报警延时 | 1-Read_Write | 读写 | 5..999 | 5..999 | Temp&humid alarm delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.90 | hwFusionColMSetStartLowPressMaskTime | Start low press mask time | 压缩机开机低压屏蔽时间 | 1-Read_Write | 读写 | 0..600 | 0..600 | Start low press mask time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.91 | hwFusionColMSetLowPressSwAlarmDelay | Low press sw alarm delay | 压缩机低压开关报警延时 | 1-Read_Write | 读写 | 3..10 | 3..10 | Low press sw alarm delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.92 | hwFusionColMSetLowSuctionPressAlarmDelay | Low suction press alarm delay | 压缩机吸气低压告警延时 | 1-Read_Write | 读写 | 3..420 | 3..420 | Low suction press alarm delay of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.93 | hwFusionColMSetLowSuctionPressMaskTime | Low suction press mask time | 压缩机吸气低压屏蔽延时 | 1-Read_Write | 读写 | 3..420 | 3..420 | Low suction press mask time of the device config table for the FusionCol-M.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.94 | hwFusionColMSetOvervoltThres | Overvolt thres | 电源过压告警阈值 | 1-Read_Write | 读写 | 100..112 | 100..112 | Overvolt thres of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.95 | hwFusionColMSetUndervoltThres | Undervolt thres | 电源欠压告警阈值 | 1-Read_Write | 读写 | 83..100 | 83..100 | Undervolt thres of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.96 | hwFusionColMSetOverFreqThres | Over freq thres | 电源高频告警阈值 | 1-Read_Write | 读写 | 61..63 | 61..63 | Over freq thres of the device config table for the FusionCol-M.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.97 | hwFusionColMSetUnderFreqThres | Under freq thres | 电源低频告警阈值 | 1-Read_Write | 读写 | 47..49 | 47..49 | Under freq thres of the device config table for the FusionCol-M.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.98 | hwFusionColMSetUnitInGroup | Unit in group | 群控机组数目 | 1-Read_Write | 读写 | 1..32 | 1..32 | Unit in group of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.99 | hwFusionColMSetActiveUnitsInGroup | Active units in group | 群控运行机数目 | 1-Read_Write | 读写 | 1..32 | 1..32 | Active units in group of the device config table for the FusionCol-M.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.100 | hwFusionColMSetRotationType | Rotation type | 轮值类型 | 1-Read_Write | 读写 | times(1), address(2), unknown(255) | [时间=1]/[地址=2] | Rotation type of the device config table for the FusionCol-M. Value 1 indicate times Value 2 indicate address
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.101 | hwFusionColMSetRotationCycle | Rotation cycle | 轮值周期 | 1-Read_Write | 读写 | 1..30 | 1..30 | Rotation cycle of the device config table for the FusionCol-M.SigUnitInfo:day.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.102 | hwFusionColMSetRotationTimeHour | Rotation time hour | 轮值时刻小时 | 1-Read_Write | 读写 | 0..23 | 0..23 | Rotation time hour of the device config table for the FusionCol-M.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.103 | hwFusionColMSetRotationTimeMinute | Rotation time minute | 轮值时刻分钟 | 1-Read_Write | 读写 | 0..59 | 0..59 | Rotation time minute of the device config table for the FusionCol-M.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.104 | hwFusionColMSetTempForHtStartAll | Temp for HT start all | 高温同开值 | 1-Read_Write | 读写 | 240..450 | 240..450 | Temp for HT start all of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.105 | hwFusionColMSetTempForLtStartAll | Temp for LT start all | 低温同开值 | 1-Read_Write | 读写 | 100..180 | 100..180 | Temp for LT start all of the device config table for the FusionCol-M.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.106 | hwFusionColMSetForcedCooling | Forced Cooling | 强制制冷设置 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Forced Cooling of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.107 | hwFusionColMSetHighTempStartAll | High temp start all | 高温同开设置 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | High temp start all of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.108 | hwFusionColMSetDehumidifiying | Dehumidifying | 除湿功能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Dehumidifying of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.109 | hwFusionColMSetTeamwork | Teamwork | 群控功能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Teamwork of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.110 | hwFusionColMSetRataion | Rotation | 轮询功能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Rotation of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.111 | hwFusionColMSetEnableTeamworkResistor | Enable teamwork resistor | 群控匹配电阻开启 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable teamwork resistor of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.112 | hwFusionColMSetEnableMinotorResistor | Enable monitor resistor | 监控匹配电阻开启 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable monitor resistor of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.113 | hwFusionColMColdAisleTorHSensorFaultEnable | Cold aisle T/H sensor fault enable | 冷通道温湿度传感器故障使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold aisle T/H sensor fault enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.114 | hwFusionColMHotAisleTorHSensorFaultEnable | Hot aisle T/H sensor fault enable | 热通道温湿度传感器故障使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Hot aisle T/H sensor fault enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.115 | hwFusionColMSetEnableAirFilterMaintainAlm | Enable air filter maintain alarm | 过滤网维护报警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable air filter maintain alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.116 | hwFusionColMSetDrainagePump | Drainage pump | 漏水报警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Drainage pump of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.117 | hwFusionColMSetEnableCompressorPreheatAlarm | Enable compressor preheat alarm | 压缩机预热告警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable compressor preheat alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.118 | hwFusionColMSetDiagnosticMode | Diagnostic mode | 手动控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Diagnostic mode of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.119 | hwFusionColMSetDiagnosticCompressor | Diagnostic compressor | 手动控制压缩机 | 1-Read_Write | 读写 | 0..4800 | 0..4800 | Diagnostic compressor of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.120 | hwFusionColMSetDiagnosticIndoorFan | Diagnostic indoor fan | 手动控制内风机 | 1-Read_Write | 读写 | 0..100 | 0..100 | Diagnostic indoor fan of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.121 | hwFusionColMSetDiagnosticOutdoorFan | Diagnostic outdoor fan | 手动控制外风机 | 1-Read_Write | 读写 | 0..100 | 0..100 | Diagnostic outdoor fan of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.122 | hwFusionColMSetMinRunPressure | Min run pressure | 室外风机运行最低压力 | 1-Read_Write | 读写 | 100..350 | 100..350 | Min run pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.123 | hwFusionColMSetStartPressure | Start pressure | 室外风机运行启动压力 | 1-Read_Write | 读写 | 100..350 | 100..350 | Start pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.124 | hwFusionColMSetMaxRunPressure | Max run pressure | 室外风机运行最大压力 | 1-Read_Write | 读写 | 250..400 | 250..400 | Max run pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.125 | hwFusionColMSetMinSpeed | Min speed | 室外风机最小转速 | 1-Read_Write | 读写 | 600..2400 | 600..2400 | Min speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.126 | hwFusionColMSetMaxSpeed | Max speed | 室外风机最大转速 | 1-Read_Write | 读写 | 2400..6000 | 2400..6000 | Max speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.127 | hwFusionColMColdAisleTorHSensor1Enable | Cold aisle T/H sensor 1 enable | 冷通道温湿度传感器1使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold aisle T/H sensor 1 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.128 | hwFusionColMHotAisleTorHSensor1Enable | Hot aisle T/H sensor 1 enable | 热通道温湿度传感器1使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Hot aisle T/H sensor 1 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.129 | hwFusionColMColdAisleTorHSensor2Enable | Cold aisle T/H sensor 2 enable | 冷通道温湿度传感器2使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold aisle T/H sensor 2 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.130 | hwFusionColMColdAisleTorHSensor3Enable | Cold aisle T/H sensor 3 enable | 冷通道温湿度传感器3使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold aisle T/H sensor 3 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.131 | hwFusionColMHotAisleTorHSensor2Enable | Hot aisle T/H sensor 2 enable | 热通道温湿度传感器2使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Hot aisle T/H sensor 2 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.132 | hwFusionColMHotAisleTorHSensor3Enable | Hot aisle T/H sensor 3 enable | 热通道温湿度传感器3使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Hot aisle T/H sensor 3 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.300 | hwFusionColMConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of FusionCol-M.

## PMC-53A
PMC-53A
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.122 | PMC53A | PMC-53A | PMC-53A | / | / | / | / | PMC-53A Equipment.
1.3.6.1.4.1.2011.6.178.1.1.122.1 | hwPMC53ARunning1Table | / | / |  |  | / | / | The running table of PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.1 | hwPMC53ARunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.2 | hwPMC53APhaseAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase A voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.3 | hwPMC53APhaseBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase B voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.4 | hwPMC53APhaseCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase C voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.5 | hwPMC53AAveragePhaseVoltage | Average phase voltage | 平均相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Average phase voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.6 | hwPMC53ALineAbVoltage | Line AB voltage | AB线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Line AB voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.7 | hwPMC53ALineBcVoltage | Line BC voltage | BC线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Line BC voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.8 | hwPMC53ALineCaVoltage | Line CA voltage | CA线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Line CA voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.9 | hwPMC53AAverageLineVoltage | Average line voltage | 平均线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Average line voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.10 | hwPMC53APhaseACurrent | Phase A current | A相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase A current of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.11 | hwPMC53APhaseBCurrent | Phase B current | B相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase B current of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.12 | hwPMC53APhaseCCurrent | Phase C current | C相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase C current of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.13 | hwPMC53AAveragePhaseCurrent | Average phase current | 平均相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Average phase current of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.14 | hwPMC53APhaseAActivePower | Phase A active power | A相有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase A active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.15 | hwPMC53APhaseBActivePower | Phase B active power | B相有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase B active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.16 | hwPMC53APhaseCActivePower | Phase C active power | C相有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase C active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.17 | hwPMC53AThreePhaseActivePower | Three-phase active power | 三相有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Three-phase active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.18 | hwPMC53APhaseAReactivePower | Phase A reactive power | A相无功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase A reactive power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.19 | hwPMC53APhaseBReactivePower | Phase B reactive power | B相无功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase B reactive power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.20 | hwPMC53APhaseCReactivePower | Phase C reactive power | C相无功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase C reactive power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.21 | hwPMC53AThreePhaseReactivePower | Three-phase reactive power | 三相无功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Three-phase reactive power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.22 | hwPMC53APhaseAApparentPower | Phase A apparent power | A相视在功率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase A apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.23 | hwPMC53APhaseBApparentPower | Phase B apparent power | B相视在功率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase B apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.24 | hwPMC53APhaseCApparentPower | Phase C apparent power | C相视在功率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase C apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.25 | hwPMC53AThreePhaseApparentPower | Three-phase apparent power | 三相视在功率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Three-phase apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.26 | hwPMC53APhaseAPowerFactor | Phase A power factor | A相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase A power factor of the device config table for the PMC-53A.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.27 | hwPMC53APhaseBPowerFactor | Phase B power factor | B相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase B power factor of the device config table for the PMC-53A.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.28 | hwPMC53APhaseCPowerFactor | Phase C power factor | C相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase C power factor of the device config table for the PMC-53A.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.29 | hwPMC53ATotalPowerFactor | Total power factor | 总功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Total power factor of the device config table for the PMC-53A.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.30 | hwPMC53AFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Frequency of the device config table for the PMC-53A.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.31 | hwPMC53ACalculateNeutralLineCurrentInc | Calculate neutral line current Inc | 计算中性线电流Inc | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Calculate neutral line current Inc of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.32 | hwPMC53ADi1State | DI1 state | DI1状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI1 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.33 | hwPMC53ADi2State | DI2 state | DI2状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI2 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.34 | hwPMC53ADi3State | DI3 state | DI3状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI3 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.35 | hwPMC53ADi4State | DI4 state | DI4状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI4 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.36 | hwPMC53ADi5State | DI5 state | DI5状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI5 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.37 | hwPMC53ADi6State | DI6 state | DI6状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI6 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.38 | hwPMC53ADo1State | DO1 state | DO1状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DO1 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.39 | hwPMC53ADo2State | DO2 state | DO2状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DO2 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.40 | hwPMC53ADo3State | DO3 state | DO3状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DO3 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.41 | hwPMC53ADo4State | DO4 state | DO4状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DO4 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.42 | hwPMC53ATotalHarmonicActivePower | Total harmonic active power | 总谐波有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Total harmonic active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.43 | hwPMC53AThreePhaseActiveElectricEnergyTotalValue | Three-phase active electric energy total value | 三相有功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Three-phase active electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.44 | hwPMC53AThreePhaseReactiveElectricEnergyTotalValue | Three-phase reactive electric energy total value | 三相无功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Three-phase reactive electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.45 | hwPMC53AThreePhaseApparentElectricEnergy | Three-phase apparent electric energy | 三相视在电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Three-phase apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.46 | hwPMC53APhaseAActiveElectricEnergyTotalValue | Phase A active electric energy total value | A相有功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.47 | hwPMC53APhaseAReactiveElectricEnergyTotalValue | Phase A reactive electric energy total value | A相无功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A reactive electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.48 | hwPMC53APhaseAApparentElectricEnergy | Phase A apparent electric energy | A相视在电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.49 | hwPMC53APhaseBActiveElectricEnergyTotalValue | Phase B active electric energy total value | B相有功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.50 | hwPMC53APhaseBReactiveElectricEnergyTotalValue | Phase B reactive electric energy total value | B相无功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B reactive electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.51 | hwPMC53APhaseBApparentElectricEnergy | Phase B apparent electric energy | B相视在电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.52 | hwPMC53APhaseCActiveElectricEnergyTotalValue | Phase C active electric energy total value | C相有功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.53 | hwPMC53APhaseCReactiveElectricEnergyTotalValue | Phase C reactive electric energy total value | C相无功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C reactive electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.54 | hwPMC53APhaseCApparentElectricEnergy | Phase C apparent electric energy | C相视在电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.55 | hwPMC53AVoltageUnbalance | Voltage unbalance | 电压不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage unbalance of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.56 | hwPMC53ACurrentUnbalance | Current unbalance | 电流不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current unbalance of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.57 | hwPMC53APhaseACurrentThd | Phase A current THD | A相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.58 | hwPMC53APhaseBCurrentThd | Phase B current THD | B相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.59 | hwPMC53APhaseCCurrentThd | Phase C current THD | C相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.60 | hwPMC53APhaseAVoltageThd | Phase A voltage THD | A相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.61 | hwPMC53APhaseBVoltageThd | Phase B voltage THD | B相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B voltage THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.62 | hwPMC53APhaseCVoltageThd | Phase C voltage THD | C相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C voltage THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.63 | hwPMC53AVoltagePrimarySideRatedValue | Voltage primary side rated value | 电压一次侧额定值 | 0-Read_Only | 只读 | 1..1000000 | 1..1000000 | Voltage primary side rated value of the device config table for the PMC-53A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.64 | hwPMC53AVoltageSecondarySideRatedValue | Voltage secondary side rated value | 电压二次侧额定值 | 0-Read_Only | 只读 | 1..690 | 1..690 | Voltage secondary side rated value of the device config table for the PMC-53A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.65 | hwPMC53ACurrentPrimarySideRatedValue | Current primary side rated value | 电流一次侧额定值 | 0-Read_Only | 只读 | 1..30000 | 1..30000 | Current primary side rated value of the device config table for the PMC-53A.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.66 | hwPMC53ACurrentSecondarySideRatedValue | Current secondary side rated value | 电流二次侧额定值 | 0-Read_Only | 只读 | 1..5 | 1..5 | Current secondary side rated value of the device config table for the PMC-53A.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.67 | hwPMC53ACommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the PMC-53A. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.68 | hwPMC53APortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.69 | hwPMC53AModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.70 | hwPMC53ADeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.300 | hwPMC53ARunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PMC-53A.

## PZ96LE4
PZ96L-E4
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.3 | PZ96LE4 | PZ96L-E4 | PZ96L-E4 | / | / | / | / | PZ96L-E4 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1 | hwPZ96LE4RunningAndConfig1Table | / | / |  |  | / | / | The running table of PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.1 | hwPZ96LE4RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.2 | hwPZ96LE4NeutralCurrent | Neutral current | 中性线电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Neutral current of the device config table for the PZ96L-E4.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.3 | hwPZ96LE4PhaseVoltageUan | Phase voltage Uan | 相电压Uan | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage Uan of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.4 | hwPZ96LE4PhaseVoltageUbn | Phase voltage Ubn | 相电压Ubn | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage Ubn of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.5 | hwPZ96LE4PhaseVoltageUcn | Phase voltage Ucn | 相电压Ucn | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage Ucn of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.6 | hwPZ96LE4LineVoltageUab | Line voltage Uab | 线电压Uab | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage Uab of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.7 | hwPZ96LE4LineVoltageUbc | Line voltage Ubc | 线电压Ubc | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage Ubc of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.8 | hwPZ96LE4LineVoltageUac | Line voltage Uac | 线电压Uca | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage Uac of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.9 | hwPZ96LE4PhaseCurrentIa | Phase current Ia | 相电流Ia | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase current Ia of the device config table for the PZ96L-E4.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.10 | hwPZ96LE4PhaseCurrentIb | Phase current Ib | 相电流Ib | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase current Ib of the device config table for the PZ96L-E4.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.11 | hwPZ96LE4PhaseCurrentIc | Phase current Ic | 相电流Ic | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase current Ic of the device config table for the PZ96L-E4.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.12 | hwPZ96LE4FrequencyF | Frequency F | 频率F | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency F of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.13 | hwPZ96LE4PhaseAActivePowerPa | Phase A active power Pa | A相有功功率Pa | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active power Pa of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.14 | hwPZ96LE4PhaseBActivePowerPb | Phase B active power Pb | B相有功功率Pb | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active power Pb of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.15 | hwPZ96LE4PhaseCActivePowerPc | Phase C active power Pc | C相有功功率Pc | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active power Pc of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.16 | hwPZ96LE4TotalActivePowerP | Total active power P | 总有功功率P总 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total active power P of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.17 | hwPZ96LE4PhaseAReactivePowerQa | Phase A reactive power Qa | A相无功功率Qa | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A reactive power Qa of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.18 | hwPZ96LE4PhaseBReactivePowerQb | Phase B reactive power Qb | B相无功功率Qb | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B reactive power Qb of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.19 | hwPZ96LE4PhaseCReactivePowerQc | Phase C reactive power Qc | C相无功功率Qc | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C reactive power Qc of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.20 | hwPZ96LE4TotalReactivePowerQ | Total reactive power Q | 总无功功率Q总 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total reactive power Q of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.21 | hwPZ96LE4PhaseAApparentPowerSa | Phase A apparent power Sa | A相视在功率Sa | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A apparent power Sa of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.22 | hwPZ96LE4PhaseBApparentPowerSb | Phase B apparent power Sb | B相视在功率Sb | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B apparent power Sb of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.23 | hwPZ96LE4PhaseCApparentPowerSc | Phase C apparent power Sc | C相视在功率Sc | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C apparent power Sc of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.24 | hwPZ96LE4TotalApparentPowerS | Total apparent power S | 总视在功率S总 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total apparent power S of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.25 | hwPZ96LE4PhaseAPowerFactor | Phase A power factor | A相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A power factor of the device config table for the PZ96L-E4.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.26 | hwPZ96LE4PhaseBPowerFactor | Phase B power factor | B相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B power factor of the device config table for the PZ96L-E4.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.27 | hwPZ96LE4PhaseCPowerFactor | Phase C power factor | C相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C power factor of the device config table for the PZ96L-E4.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.28 | hwPZ96LE4TotalPowerFactor | Total power factor | 总功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total power factor of the device config table for the PZ96L-E4.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.29 | hwPZ96LE4UnbalanceFactorOfVoltage | Unbalance factor of voltage | 电压不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Unbalance factor of voltage of the device config table for the PZ96L-E4.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.30 | hwPZ96LE4UnbalanceFactorOfCurrent | Unbalance factor of current | 电流不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Unbalance factor of current of the device config table for the PZ96L-E4.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.31 | hwPZ96LE4ForwardActiveElectricEnergyEpi | Forward active Electric energy EPI | 正向有功电能EPI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Forward active Electric energy EPI of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.32 | hwPZ96LE4BackwardActiveElectricEnergyEpe | Backward active Electric energy EPE | 反向有功电能EPE | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Backward active Electric energy EPE of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.33 | hwPZ96LE4ForwardReactiveElectricEnergyEqi | Forward reactive Electric energy EQI | 正向无功电能EQL | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Forward reactive Electric energy EQI of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.34 | hwPZ96LE4BackwardReactiveElectricEnergyEqc | Backward reactive Electric energy EQC | 反向无功电能EQC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Backward reactive Electric energy EQC of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.35 | hwPZ96LE4APhaseVoltageTotalHarmonicDistortion | A phase voltage total harmonic distortion | A相电压总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A phase voltage total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.36 | hwPZ96LE4BPhaseVoltageTotalHarmonicDistortion | B phase voltage total harmonic distortion | B相电压总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B phase voltage total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.37 | hwPZ96LE4CPhaseVoltageTotalHarmonicDistortion | C phase voltage total harmonic distortion | C相电压总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | C phase voltage total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.38 | hwPZ96LE4APhaseCurrentTotalHarmonicDistortion | A phase current total harmonic distortion | A相电流总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A phase current total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.39 | hwPZ96LE4BPhaseCurrentTotalHarmonicDistortion | B phase current total harmonic distortion | B相电流总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B phase current total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.40 | hwPZ96LE4CPhaseCurrentTotalHarmonicDistortion | C phase current total harmonic distortion | C相电流总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | C phase current total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.41 | hwPZ96LE4CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the PZ96L-E4. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.42 | hwPZ96LE4PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.43 | hwPZ96LE4ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.44 | hwPZ96LE4DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.45 | hwPZ96LE4WiringMode | Wiring mode | 接线方式 | 1-Read_Write | 读写 | threePhaseThreeWire(1), threePhaseFourWire(2), unknown(255) | [3相3线=1]/[3相4线=2] | Wiring mode of the device config table for the PZ96L-E4. Value 1 indicate 3-phase 3-wire Value 2 indicate 3-phase 4-wire
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.46 | hwPZ96LE4VoltageLevel | Voltage level | 电压等级 | 1-Read_Write | 读写 | oneHundred(1), fourHundred(2), sixHundredAndSixty(3), unknown(255) | [100=1]/[400=2]/[660=3] | Voltage level of the device config table for the PZ96L-E4. Value 1 indicate 100 Value 2 indicate 400 Value 3 indicate 660SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.47 | hwPZ96LE4CurrentLevel | Current level | 电流等级 | 1-Read_Write | 读写 | one(1), five(2), unknown(255) | [1=1]/[5=2] | Current level of the device config table for the PZ96L-E4. Value 1 indicate 1 Value 2 indicate 5SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.48 | hwPZ96LE4VoltageTransformationRatio | Voltage transformation ratio | 电压变比 | 1-Read_Write | 读写 | 1..9999 | 1..9999 | Voltage transformation ratio of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.49 | hwPZ96LE4CurrentTransformationRatio | Current transformation ratio | 电流变比 | 1-Read_Write | 读写 | 1..9999 | 1..9999 | Current transformation ratio of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.50 | hwPZ96LE4HighFrequencyAlarmThreshold | High frequency alarm threshold | 频率过高告警点 | 1-Read_Write | 读写 | 4000..7000 | 4000..7000 | High frequency alarm threshold of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.51 | hwPZ96LE4LowFrequencyAlarmThreshold | Low frequency alarm threshold | 频率过低告警点 | 1-Read_Write | 读写 | 4000..7000 | 4000..7000 | Low frequency alarm threshold of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.52 | hwPZ96LE4PhaseOvervoltageAlarmThreshold | Phase overvoltage alarm threshold | 相电压过压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | Phase overvoltage alarm threshold of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.53 | hwPZ96LE4PhaseUndervoltageAlarmThreshold | Phase undervoltage alarm threshold | 相电压欠压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | Phase undervoltage alarm threshold of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.54 | hwPZ96LE4LineOvervoltageAlarmThreshold | Line overvoltage alarm threshold | 线电压过压告警点 | 1-Read_Write | 读写 | 500..6000 | 500..6000 | Line overvoltage alarm threshold of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.55 | hwPZ96LE4LineUndervoltageAlarmThreshold | Line undervoltage alarm threshold | 线电压欠压告警点 | 1-Read_Write | 读写 | 500..6000 | 500..6000 | Line undervoltage alarm threshold of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.300 | hwPZ96LE4RunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PZ96L-E4.

## Rack-mounted air conditioner HR
空调-机架式-HR04A
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.78 | rackmounted | Rack-mounted air conditioner HR04A | 空调-机架式-HR04A | / | / | / | / | rack_mounted Equipment.
1.3.6.1.4.1.2011.6.178.1.1.78.1 | hwRackmountedairconditionerHR04ARunning1Table | / | / |  |  | / | / | The running table of Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.1 | hwRackmountedairconditionerHR04ARunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.2 | hwRackmountedairconditionerHR04ALowLiquidLevelSwitch | Low liquid level switch | 低液位开关 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | Low liquid level switch of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.3 | hwRackmountedairconditionerHR04AHighLiquidLevelSwitch | High liquid level switch | 高液位开关 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | High liquid level switch of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.4 | hwRackmountedairconditionerHR04AElectricHeaterFault | Electric heater fault | 电加热故障 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | Electric heater fault of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.5 | hwRackmountedairconditionerHR04AWaterSensorFault | Water sensor fault | 水浸故障 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | Water sensor fault of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.6 | hwRackmountedairconditionerHR04AAirConditionerStatus | Air conditioner status | 机组状态 | 0-Read_Only | 只读 | stop(1), running(2), suspended(3), unknown(255) | [停止=1]/[运行=2]/[停机中=3] | Air conditioner status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running Value 3 indicate suspended
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.7 | hwRackmountedairconditionerHR04ACurrentOperatingStatus | Current operating status | 当前工作状态 | 0-Read_Only | 只读 | standby(1), cooling(2), dehumidification(3), dehumidificationtemperaturecompensation(4), antiCondensation(5), unknown(255) | [待机=1]/[制冷=2]/[除湿=3]/[除湿温度补偿=4]/[防凝露=5] | Current operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate standby Value 2 indicate cooling Value 3 indicate dehumidification Value 4 indicate dehumidification temperature compensation Value 5 indicate anti-condensation
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.8 | hwRackmountedairconditionerHR04ACompressorLogicalStatus | Compressor logical status | 压缩机逻辑状态 | 0-Read_Only | 只读 | off(1), manual(2), differentialpressure(3), oilreturn(4), highpressure(5), dischargehightemperature(6), lowsuction(7), highsuction(8), antiCondensation(9), dehumidification(10), forcedcooling(11), dischargetemperaturefrequencylimiting(12), normalcontrol(13), starting(14), unknown(255) | [关机=1]/[手动=2]/[压差=3]/[回油=4]/[高压=5]/[高排温=6]/[低吸气=7]/[高吸气=8]/[防凝露=9]/[除湿=10]/[强制制冷=11]/[排温限频=12]/[正常控制=13]/[启动过程=14] | Compressor logical status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate off Value 2 indicate manual Value 3 indicate differential pressure Value 4 indicate oil return Value 5 indicate high pressure Value 6 indicate discharge high temperature Value 7 indicate low suction Value 8 indicate high suction Value 9 indicate anti-condensation Value 10 indicate dehumidification Value 11 indicate forced cooling Value 12 indicate discharge temperature frequency limiting Value 13 indicate normal control Value 14 indicate starting
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.9 | hwRackmountedairconditionerHR04ATHStatus | T/H status | 温湿度状态 | 0-Read_Only | 只读 | normal(1), hightemperaturedeviation(2), lowtemperaturedeviation(3), highhumiditydeviation(4), lowhumiditydeviation(5), unknown(255) | [正常=1]/[高温偏差=2]/[低温偏差=3]/[高湿偏差=4]/[低湿偏差=5] | Temperature and humidity of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate normal Value 2 indicate high temperature deviation Value 3 indicate low temperature deviation Value 4 indicate high humidity deviation Value 5 indicate low humidity deviation
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.10 | hwRackmountedairconditionerHR04ACoolingRequirement | Cooling requirement | 制冷需求 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cooling requirement of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.11 | hwRackmountedairconditionerHR04ADehumidificationRequirement | Dehumidification requirement | 除湿需求 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Dehumidification requirement of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.12 | hwRackmountedairconditionerHR04ACompressorOperatingStatus | Compressor operating status | 压缩机工作状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Compressor operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.13 | hwRackmountedairconditionerHR04AElectricHeaterOperatingStatus | Electric heater operating status | 电加热工作状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Electric heater operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.14 | hwRackmountedairconditionerHR04AOutdoorHeatingBeltStatus | Outdoor heating belt status | 室外加热带状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Outdoor heating belt status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.15 | hwRackmountedairconditionerHR04AIndoorFanOperatingStatus | Indoor fan operating status | 室内风机工作状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Indoor fan operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.16 | hwRackmountedairconditionerHR04AOutdoorFanOperatingStatus | Outdoor fan operating status | 室外风机工作状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Outdoor fan operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.17 | hwRackmountedairconditionerHR04ACompressorSpeed | Compressor speed | 压缩机转速 | 0-Read_Only | 只读 | 0..1200 | 0..1200 | Compressor speed of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:rps.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.18 | hwRackmountedairconditionerHR04AIndoorFanSpeed | Indoor fan speed | 室内风机转速 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Indoor fan speed of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.19 | hwRackmountedairconditionerHR04AOutdoorFanSpeed | Outdoor fan speed | 室外风机转速 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Outdoor fan speed of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.20 | hwRackmountedairconditionerHR04AElectronicExpansionValveOpening | Electronic expansion valve opening | 电子膨胀阀开度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Electronic expansion valve opening of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.21 | hwRackmountedairconditionerHR04ASuperheatDegree | Superheat degree | 过热度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Superheat degree of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:K.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.22 | hwRackmountedairconditionerHR04AHotAisleTemperature | Hot aisle temperature | 热通道温度 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Hot aisle temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.23 | hwRackmountedairconditionerHR04AHotAisleHumidity | Hot aisle humidity | 热通道湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle humidity of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.24 | hwRackmountedairconditionerHR04ADewPointTemperature | Dew point temperature | 露点温度 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Dew point temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.25 | hwRackmountedairconditionerHR04AColdAisleTemperature | Cold aisle temperature | 冷通道温度 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Cold aisle temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.26 | hwRackmountedairconditionerHR04ADischargeTemperature | Discharge temperature | 排气温度 | 0-Read_Only | 只读 | -1000..1500 | -1000..1500 | Discharge temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.27 | hwRackmountedairconditionerHR04ASuctionTemperature | Suction temperature | 吸气温度 | 0-Read_Only | 只读 | -1000..1500 | -1000..1500 | Suction temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.28 | hwRackmountedairconditionerHR04ACondensingPressure | Condensing pressure | 冷凝压力 | 0-Read_Only | 只读 | 0..500 | 0..500 | Condensing pressure of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:bar.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.29 | hwRackmountedairconditionerHR04ALowPressure | Low pressure | 低压压力 | 0-Read_Only | 只读 | 0..300 | 0..300 | Low pressure of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:bar.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.30 | hwRackmountedairconditionerHR04AOutdoorAmbientTemperature | Outdoor ambient temperature | 室外环境温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Outdoor ambient temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.31 | hwRackmountedairconditionerHR04ACompressorIpmTemperature | Compressor IPM temperature | 压缩机IPM温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Compressor IPM temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.32 | hwRackmountedairconditionerHR04AFan | Fan | 风机 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Fan of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.33 | hwRackmountedairconditionerHR04ACompressor | Compressor | 压缩机 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Compressor of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.34 | hwRackmountedairconditionerHR04AElectricHeater | Electric heater | 电加热 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Electric heater of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.35 | hwRackmountedairconditionerHR04AWaterPump | Water pump | 水泵 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Water pump of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.36 | hwRackmountedairconditionerHR04AFault | Fault | 故障 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Fault of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.37 | hwRackmountedairconditionerHR04AHotAisleTemperature1 | Hot aisle temperature 1 | 热通道温度1 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Hot aisle temperature 1 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.38 | hwRackmountedairconditionerHR04AHotAisleHumidity1 | Hot aisle humidity 1 | 热通道湿度1 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle humidity 1 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.39 | hwRackmountedairconditionerHR04AHotAisleTemperature2 | Hot aisle temperature 2 | 热通道温度2 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Hot aisle temperature 2 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.40 | hwRackmountedairconditionerHR04AHotAisleHumidity2 | Hot aisle humidity 2 | 热通道湿度2 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle humidity 2 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.41 | hwRackmountedairconditionerHR04AColdAisleTemperature1 | Cold aisle temperature 1 | 冷通道温度1 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Cold aisle temperature 1 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.42 | hwRackmountedairconditionerHR04AColdAisleHumidity1 | Cold aisle humidity 1 | 冷通道湿度1 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle humidity 1 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.43 | hwRackmountedairconditionerHR04AColdAisleTemperature2 | Cold aisle temperature 2 | 冷通道温度2 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Cold aisle temperature 2 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.44 | hwRackmountedairconditionerHR04AColdAisleHumidity2 | Cold aisle humidity 2 | 冷通道湿度2 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle humidity 2 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.45 | hwRackmountedairconditionerHR04AControlTemperature | Control temperature | 控制温度 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Control temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.46 | hwRackmountedairconditionerHR04AControlHumidity | Control humidity | 控制湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Control humidity of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.47 | hwRackmountedairconditionerHR04ACommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.48 | hwRackmountedairconditionerHR04APortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.49 | hwRackmountedairconditionerHR04AModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.101 | hwRackmountedairconditionerHR04ARunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2 | hwRackmountedairconditionerHR04AConfig2Table | / | / |  |  | / | / | The config table of Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.1 | hwRackmountedairconditionerHR04AConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.2 | hwRackmountedairconditionerHR04ADeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.3 | hwRackmountedairconditionerHR04AIndoorFanRunningTime | Indoor fan running time | 内风机运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Indoor fan running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.4 | hwRackmountedairconditionerHR04ACompressorRunningTime | Compressor running time | 压缩机运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Compressor running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.5 | hwRackmountedairconditionerHR04AOutdoorFanRunningTime | Outdoor fan running time | 外风机运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Outdoor fan running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.6 | hwRackmountedairconditionerHR04AElectricHeaterRunningTime | Electric heater running time | 电加热运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Electric heater running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.7 | hwRackmountedairconditionerHR04AWaterPumpRunningTime | Water pump running time | 水泵运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Water pump running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.8 | hwRackmountedairconditionerHR04AReturnAirHighTemperatureAlarm | Return air high temperature alarm | 回风高温告警 | 1-Read_Write | 读写 | 250..500 | 250..500 | Return air high temperature alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.9 | hwRackmountedairconditionerHR04AReturnAirLowTemperatureAlarm | Return air low temperature alarm | 回风低温告警 | 1-Read_Write | 读写 | 0..250 | 0..250 | Return air low temperature alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.10 | hwRackmountedairconditionerHR04AReturnAirHighHumidityAlarm | Return air high humidity alarm | 回风高湿告警 | 1-Read_Write | 读写 | 650..900 | 650..900 | Return air high humidity alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.11 | hwRackmountedairconditionerHR04AReturnAirLowHumidityAlarm | Return air low humidity alarm | 回风低湿告警 | 1-Read_Write | 读写 | 100..350 | 100..350 | Return air low humidity alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.12 | hwRackmountedairconditionerHR04ASupplyAirHighTemperatureAlarm | Supply air high temperature alarm | 送风高温告警 | 1-Read_Write | 读写 | 150..350 | 150..350 | Supply air high temperature alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.13 | hwRackmountedairconditionerHR04ASupplyAirLowTemperatureAlarm | Supply air low temperature alarm | 送风低温告警 | 1-Read_Write | 读写 | 0..250 | 0..250 | Supply air low temperature alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.14 | hwRackmountedairconditionerHR04ASupplyAirHighHumidityAlarm | Supply air high humidity alarm | 送风高湿告警 | 1-Read_Write | 读写 | 650..900 | 650..900 | Supply air high humidity alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.15 | hwRackmountedairconditionerHR04ASupplyAirTemperatureSettings | Supply air temperature settings | 送风温度设定 | 1-Read_Write | 读写 | 130..250 | 130..250 | Supply air temperature settings of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.16 | hwRackmountedairconditionerHR04AReturnAirTemperatureSettings | Return air temperature settings | 回风温度设定 | 1-Read_Write | 读写 | 160..400 | 160..400 | Return air temperature settings of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.17 | hwRackmountedairconditionerHR04ADehumidificationSettings | Dehumidification settings | 除湿设定 | 1-Read_Write | 读写 | 200..800 | 200..800 | Dehumidification settings of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.18 | hwRackmountedairconditionerHR04ATemperatureControl | Temperature control | 温度控制 | 1-Read_Write | 读写 | returnAir(1), supplyAir(2), unknown(255) | [回风=1]/[送风=2] | Temperature control of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate return-air Value 2 indicate supply-air
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.19 | hwRackmountedairconditionerHR04AHostCommunicationAddress | Host communication address | 上位机通讯地址 | 1-Read_Write | 读写 | 1..255 | 1..255 | Host communication address of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.20 | hwRackmountedairconditionerHR04AHostCommunicationRate | Host communication rate | 上位机通讯速率 | 1-Read_Write | 读写 | baud4800(1), baud9600(2), baud19200(3), unknown(255) | [4800=1]/[9600=2]/[19200=3] | Host communication rate of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate 4800 Value 2 indicate 9600 Value 3 indicate 19200
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.21 | hwRackmountedairconditionerHR04AAutomaticStartupUponPowerOn | Automatic startup upon power-on | 来电自启动 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Automatic startup upon power-on of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.22 | hwRackmountedairconditionerHR04ANumberOfRotation | Number of rotation | 轮值个数 | 1-Read_Write | 读写 | 1..12 | 1..12 | Number of rotation of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.23 | hwRackmountedairconditionerHR04ARotationAddress | Rotation address | 轮值地址 | 1-Read_Write | 读写 | 0..11 | 0..11 | Rotation address of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.24 | hwRackmountedairconditionerHR04ARotationTime | Rotation time | 轮值时间 | 1-Read_Write | 读写 | 0..99 | 0..99 | Rotation time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.25 | hwRackmountedairconditionerHR04ARotationSettings | Rotation settings | 轮值设置 | 1-Read_Write | 读写 | disable(1), n1(2), n2(3), unknown(255) | [禁用=1]/[N1=2]/[N2=3] | Rotation settings of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate n+1 Value 3 indicate n+2
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.26 | hwRackmountedairconditionerHR04AHighTemperatureDeviation | High temperature deviation | 高温偏差 | 1-Read_Write | 读写 | 0..200 | 0..200 | High temperature deviation of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.27 | hwRackmountedairconditionerHR04AHighHumidityDeviation | High humidity deviation | 高湿偏差 | 1-Read_Write | 读写 | 0..500 | 0..500 | High humidity deviation of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.28 | hwRackmountedairconditionerHR04APowerOnorOff | Power on/off | 开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Power on/off of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.29 | hwRackmountedairconditionerHR04AReset | Reset | 故障复位 | 1-Read_Write | 读写 | nofaultoccurs(1), unknown(255) | [无故障=1] | Reset of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate no fault occurs
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.30 | hwRackmountedairconditionerHR04AHotAisleTHSensor1 | Hot aisle T/H sensor 1 | 热通道温湿度传感器1 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Hot aisle temperature and humidity sensor 1 of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.31 | hwRackmountedairconditionerHR04AHotAisleTHSensor2 | Hot aisle T/H sensor 2 | 热通道温湿度传感器2 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Hot aisle temperature and humidity sensor 2 of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.32 | hwRackmountedairconditionerHR04AColdAisleTHSensor1 | Cold aisle T/H sensor 1 | 冷通道温湿度传感器1 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Cold aisle temperature and humidity sensor 1 of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.33 | hwRackmountedairconditionerHR04AColdAisleTHSensor2 | Cold aisle T/H sensor 2 | 冷通道温湿度传感器2 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Cold aisle temperature and humidity sensor 2 of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.34 | hwRackmountedairconditionerHR04AControlSensor | Control sensor | 控制传感器 | 1-Read_Write | 读写 | builtIn(1), external(2), unknown(255) | [内置=1]/[外置=2] | Control sensor of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate built-in Value 2 indicate external
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.101 | hwRackmountedairconditionerHR04AConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Rack-mounted air conditioner HR04A.

## PowerMete-Renda-AMC7062HT-4(HI)
电量仪-任达-AMC7062HT-4(HI)
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.41 | RendaAMC | PowerMeter-Renda-AMC7062HT-4(HI) | 电量仪-任达-AMC7062HT-4(HI) | / | / | / | / | ATS Equipment.
1.3.6.1.4.1.2011.6.178.1.1.41.1 | hwRendaAMCRunningTable | / | / |  |  | / | / | The Running table of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.1 | hwRendaAMCRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.2 | hwRendaAMCCommState | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The CommState of hwRendaAMC. value 1 indicates Switch Normal. value 2 indicates Switch Abnormal.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.3 | hwRendaAMCCommPort | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The CommPort of hwRendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.4 | hwRendaAMCCommModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Comm Modbus Address of hwRendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.5 | hwRendaAMCNA1SwitchStatus | Mains 1 switch status | 主路1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.6 | hwRendaAMCNA1Current | Mains 1 current | 主路1电流 | 0-Read_Only | 只读 | 0..15000 | 0..15000 | The NA1 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.7 | hwRendaAMCNA1Voltage | Mains 1 voltage | 主路1电压 | 0-Read_Only | 只读 | -1000..0 | -1000..0 | The NA1 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.8 | hwRendaAMCNA1ActiveEnergy | Mains 1 active energy | 主路1有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.9 | hwRendaAMCNA1ActivePower | Mains 1 active power | 主路1有功功率 | 0-Read_Only | 只读 | 0..600 | 0..600 | The NA1 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.10 | hwRendaAMCNASPDStatus | SPD 1 status | 防雷器1状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NAS PDStatus of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.11 | hwRendaAMCNA2SwitchStatus | Mains 2 Switch status | 主路2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.12 | hwRendaAMCNA2Current | Mains 2 current | 主路2电流 | 0-Read_Only | 只读 | 0..15000 | 0..15000 | The NA2 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.13 | hwRendaAMCNA2Voltage | Mains 2 voltage | 主路2电压 | 0-Read_Only | 只读 | -1000..0 | -1000..0 | The NA2 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.14 | hwRendaAMCNA2ActiveEnergy | Mains 2 active energy | 主路2有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.15 | hwRendaAMCNA2ActivePower | Mains 2 active power | 主路2有功功率 | 0-Read_Only | 只读 | 0..600 | 0..600 | The NA2 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.16 | hwRendaAMCNBSPDStatus | SPD 2 status | 防雷器2状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NBS PDStatus of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.17 | hwRendaAMCNA1Branch1SwitchStatus | Branch 1 switch status | 支路1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 1 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.18 | hwRendaAMCNA1Branch2SwitchStatus | Branch 2 switch status | 支路2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 2 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.19 | hwRendaAMCNA1Branch3SwitchStatus | Branch 3 switch status | 支路3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 3 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.20 | hwRendaAMCNA1Branch4SwitchStatus | Branch 4 switch status | 支路4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 4 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.21 | hwRendaAMCNA1Branch5SwitchStatus | Branch 5 switch status | 支路5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 5 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.22 | hwRendaAMCNA1Branch6SwitchStatus | Branch 6 switch status | 支路6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 6 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.23 | hwRendaAMCNA1Branch7SwitchStatus | Branch 7 switch status | 支路7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 7 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.24 | hwRendaAMCNA1Branch8SwitchStatus | Branch 8 switch status | 支路8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 8 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.25 | hwRendaAMCNA1Branch9SwitchStatus | Branch 9 switch status | 支路9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 9 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.26 | hwRendaAMCNA1Branch10SwitchStatus | Branch 10 switch status | 支路10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 10 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.27 | hwRendaAMCNA1Branch11SwitchStatus | Branch 11 switch status | 支路11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 11 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.28 | hwRendaAMCNA1Branch12SwitchStatus | Branch 12 switch status | 支路12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 12 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.29 | hwRendaAMCNA1Branch13SwitchStatus | Branch 13 switch status | 支路13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 13 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.30 | hwRendaAMCNA1Branch14SwitchStatus | Branch 14 switch status | 支路14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 14 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.31 | hwRendaAMCNA1Branch15SwitchStatus | Branch 15 switch status | 支路15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 15 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.32 | hwRendaAMCNA1Branch1Current | Branch 1 current | 支路1电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 1 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.33 | hwRendaAMCNA1Branch2Current | Branch 2 current | 支路2电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 2 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.34 | hwRendaAMCNA1Branch3Current | Branch 3 current | 支路3电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 3 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.35 | hwRendaAMCNA1Branch4Current | Branch 4 current | 支路4电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 4 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.36 | hwRendaAMCNA1Branch5Current | Branch 5 current | 支路5电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 5 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.37 | hwRendaAMCNA1Branch6Current | Branch 6 current | 支路6电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 6 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.38 | hwRendaAMCNA1Branch7Current | Branch 7 current | 支路7电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 7 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.39 | hwRendaAMCNA1Branch8Current | Branch 8 current | 支路8电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 8 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.40 | hwRendaAMCNA1Branch9Current | Branch 9 current | 支路9电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 9 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.41 | hwRendaAMCNA1Branch10Current | Branch 10 current | 支路10电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 10 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.42 | hwRendaAMCNA1Branch11Current | Branch 11 current | 支路11电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 11 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.43 | hwRendaAMCNA1Branch12Current | Branch 12 current | 支路12电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 12 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.44 | hwRendaAMCNA1Branch13Current | Branch 13 current | 支路13电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 13 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.45 | hwRendaAMCNA1Branch14Current | Branch 14 current | 支路14电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 14 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.46 | hwRendaAMCNA1Branch15Current | Branch 15 current | 支路15电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 15 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.47 | hwRendaAMCNA1Branch1Voltage | Branch 1 voltage | 支路1电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 1 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.48 | hwRendaAMCNA1Branch2Voltage | Branch 2 voltage | 支路2电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 2 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.49 | hwRendaAMCNA1Branch3Voltage | Branch 3 voltage | 支路3电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 3 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.50 | hwRendaAMCNA1Branch4Voltage | Branch 4 voltage | 支路4电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 4 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.51 | hwRendaAMCNA1Branch5Voltage | Branch 5 voltage | 支路5电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 5 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.52 | hwRendaAMCNA1Branch6Voltage | Branch 6 voltage | 支路6电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 6 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.53 | hwRendaAMCNA1Branch7Voltage | Branch 7 voltage | 支路7电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 7 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.54 | hwRendaAMCNA1Branch8Voltage | Branch 8 voltage | 支路8电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 8 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.55 | hwRendaAMCNA1Branch9Voltage | Branch 9 voltage | 支路9电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 9 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.56 | hwRendaAMCNA1Branch10Voltage | Branch 10 voltage | 支路10电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 10 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.57 | hwRendaAMCNA1Branch11Voltage | Branch 11 voltage | 支路11电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 11 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.58 | hwRendaAMCNA1Branch12Voltage | Branch 12 voltage | 支路12电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 12 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.59 | hwRendaAMCNA1Branch13Voltage | Branch 13 voltage | 支路13电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 13 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.60 | hwRendaAMCNA1Branch14Voltage | Branch 14 voltage | 支路14电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 14 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.61 | hwRendaAMCNA1Branch15Voltage | Branch 15 voltage | 支路15电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 15 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.62 | hwRendaAMCNA1Branch1ActiveEnergy | Branch 1 active energy | 支路1有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 1 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.63 | hwRendaAMCNA1Branch2ActiveEnergy | Branch 2 active energy | 支路2有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 2 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.64 | hwRendaAMCNA1Branch3ActiveEnergy | Branch 3 active energy | 支路3有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 3 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.65 | hwRendaAMCNA1Branch4ActiveEnergy | Branch 4 active energy | 支路4有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 4 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.66 | hwRendaAMCNA1Branch5ActiveEnergy | Branch 5 active energy | 支路5有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 5 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.67 | hwRendaAMCNA1Branch6ActiveEnergy | Branch 6 active energy | 支路6有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 6 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.68 | hwRendaAMCNA1Branch7ActiveEnergy | Branch 7 active energy | 支路7有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 7 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.69 | hwRendaAMCNA1Branch8ActiveEnergy | Branch 8 active energy | 支路8有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 8 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.70 | hwRendaAMCNA1Branch9ActiveEnergy | Branch 9 active energy | 支路9有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 9 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.71 | hwRendaAMCNA1Branch10ActiveEnergy | Branch 10 active energy | 支路10有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 10 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.72 | hwRendaAMCNA1Branch11ActiveEnergy | Branch 11 active energy | 支路11有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 11 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.73 | hwRendaAMCNA1Branch12ActiveEnergy | Branch 12 active energy | 支路12有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 12 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.74 | hwRendaAMCNA1Branch13ActiveEnergy | Branch 13 active energy | 支路13有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 13 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.75 | hwRendaAMCNA1Branch14ActiveEnergy | Branch 14 active energy | 支路14有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 14 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.76 | hwRendaAMCNA1Branch15ActiveEnergy | Branch 15 active energy | 支路15有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 15 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.77 | hwRendaAMCNA1Branch1ActivePower | Branch 1 active power | 支路1有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 1 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.78 | hwRendaAMCNA1Branch2ActivePower | Branch 2 active power | 支路2有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 2 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.79 | hwRendaAMCNA1Branch3ActivePower | Branch 3 active power | 支路3有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 3 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.80 | hwRendaAMCNA1Branch4ActivePower | Branch 4 active power | 支路4有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 4 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.81 | hwRendaAMCNA1Branch5ActivePower | Branch 5 active power | 支路5有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 5 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.82 | hwRendaAMCNA1Branch6ActivePower | Branch 6 active power | 支路6有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 6 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.83 | hwRendaAMCNA1Branch7ActivePower | Branch 7 active power | 支路7有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 7 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.84 | hwRendaAMCNA1Branch8ActivePower | Branch 8 active power | 支路8有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 8 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.85 | hwRendaAMCNA1Branch9ActivePower | Branch 9 active power | 支路9有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 9 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.86 | hwRendaAMCNA1Branch10ActivePower | Branch 10 active power | 支路10有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 10 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.87 | hwRendaAMCNA1Branch11ActivePower | Branch 11 active power | 支路11有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 11 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.88 | hwRendaAMCNA1Branch12ActivePower | Branch 12 active power | 支路12有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 12 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.89 | hwRendaAMCNA1Branch13ActivePower | Branch 13 active power | 支路13有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 13 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.90 | hwRendaAMCNA1Branch14ActivePower | Branch 14 active power | 支路14有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 14 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.91 | hwRendaAMCNA1Branch15ActivePower | Branch 15 active power | 支路15有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 15 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.92 | hwRendaAMCNA2Branch1SwitchStatus | Branch 1 switch status | 支路1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 1 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.93 | hwRendaAMCNA2Branch2SwitchStatus | Branch 2 switch status | 支路2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 2 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.94 | hwRendaAMCNA2Branch3SwitchStatus | Branch 3 switch status | 支路3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 3 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.95 | hwRendaAMCNA2Branch4SwitchStatus | Branch 4 switch status | 支路4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 4 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.96 | hwRendaAMCNA2Branch5SwitchStatus | Branch 5 switch status | 支路5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 5 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.97 | hwRendaAMCNA2Branch6SwitchStatus | Branch 6 switch status | 支路6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 6 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.98 | hwRendaAMCNA2Branch7SwitchStatus | Branch 7 switch status | 支路7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 7 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.99 | hwRendaAMCNA2Branch8SwitchStatus | Branch 8 switch status | 支路8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 8 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.100 | hwRendaAMCNA2Branch9SwitchStatus | Branch 9 switch status | 支路9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 9 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.101 | hwRendaAMCNA2Branch10SwitchStatus | Branch 10 switch status | 支路10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 10 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.102 | hwRendaAMCNA2Branch11SwitchStatus | Branch 11 switch status | 支路11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 11 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.103 | hwRendaAMCNA2Branch12SwitchStatus | Branch 12 switch status | 支路12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 12 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.104 | hwRendaAMCNA2Branch13SwitchStatus | Branch 13 switch status | 支路13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 13 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.105 | hwRendaAMCNA2Branch14SwitchStatus | Branch 14 switch status | 支路14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 14 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.106 | hwRendaAMCNA2Branch15SwitchStatus | Branch 15 switch status | 支路15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 15 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.107 | hwRendaAMCNA2Branch1Current | Branch 1 current | 支路1电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 1 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.108 | hwRendaAMCNA2Branch2Current | Branch 2 current | 支路2电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 2 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.109 | hwRendaAMCNA2Branch3Current | Branch 3 current | 支路3电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 3 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.110 | hwRendaAMCNA2Branch4Current | Branch 4 current | 支路4电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 4 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.111 | hwRendaAMCNA2Branch5Current | Branch 5 current | 支路5电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 5 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.112 | hwRendaAMCNA2Branch6Current | Branch 6 current | 支路6电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 6 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.113 | hwRendaAMCNA2Branch7Current | Branch 7 current | 支路7电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 7 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.114 | hwRendaAMCNA2Branch8Current | Branch 8 current | 支路8电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 8 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.115 | hwRendaAMCNA2Branch9Current | Branch 9 current | 支路9电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 9 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.116 | hwRendaAMCNA2Branch10Current | Branch 10 current | 支路10电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 10 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.117 | hwRendaAMCNA2Branch11Current | Branch 11 current | 支路11电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 11 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.118 | hwRendaAMCNA2Branch12Current | Branch 12 current | 支路12电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 12 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.119 | hwRendaAMCNA2Branch13Current | Branch 13 current | 支路13电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 13 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.120 | hwRendaAMCNA2Branch14Current | Branch 14 current | 支路14电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 14 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.121 | hwRendaAMCNA2Branch15Current | Branch 15 current | 支路15电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 15 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.122 | hwRendaAMCNA2Branch1Voltage | Branch 1 voltage | 支路1电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 1 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.123 | hwRendaAMCNA2Branch2Voltage | Branch 2 voltage | 支路2电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 2 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.124 | hwRendaAMCNA2Branch3Voltage | Branch 3 voltage | 支路3电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 3 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.125 | hwRendaAMCNA2Branch4Voltage | Branch 4 voltage | 支路4电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 4 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.126 | hwRendaAMCNA2Branch5Voltage | Branch 5 voltage | 支路5电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 5 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.127 | hwRendaAMCNA2Branch6Voltage | Branch 6 voltage | 支路6电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 6 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.128 | hwRendaAMCNA2Branch7Voltage | Branch 7 voltage | 支路7电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 7 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.129 | hwRendaAMCNA2Branch8Voltage | Branch 8 voltage | 支路8电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 8 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.130 | hwRendaAMCNA2Branch9Voltage | Branch 9 voltage | 支路9电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 9 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.131 | hwRendaAMCNA2Branch10Voltage | Branch 10 voltage | 支路10电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 10 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.132 | hwRendaAMCNA2Branch11Voltage | Branch 11 voltage | 支路11电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 11 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.133 | hwRendaAMCNA2Branch12Voltage | Branch 12 voltage | 支路12电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 12 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.134 | hwRendaAMCNA2Branch13Voltage | Branch 13 voltage | 支路13电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 13 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.135 | hwRendaAMCNA2Branch14Voltage | Branch 14 voltage | 支路14电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 14 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.136 | hwRendaAMCNA2Branch15Voltage | Branch 15 voltage | 支路15电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 15 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.137 | hwRendaAMCNA2Branch1ActiveEnergy | Branch 1 active energy | 支路1有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 1 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.138 | hwRendaAMCNA2Branch2ActiveEnergy | Branch 2 active energy | 支路2有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 2 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.139 | hwRendaAMCNA2Branch3ActiveEnergy | Branch 3 active energy | 支路3有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 3 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.140 | hwRendaAMCNA2Branch4ActiveEnergy | Branch 4 active energy | 支路4有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 4 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.141 | hwRendaAMCNA2Branch5ActiveEnergy | Branch 5 active energy | 支路5有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 5 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.142 | hwRendaAMCNA2Branch6ActiveEnergy | Branch 6 active energy | 支路6有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 6 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.143 | hwRendaAMCNA2Branch7ActiveEnergy | Branch 7 active energy | 支路7有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 7 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.144 | hwRendaAMCNA2Branch8ActiveEnergy | Branch 8 active energy | 支路8有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 8 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.145 | hwRendaAMCNA2Branch9ActiveEnergy | Branch 9 active energy | 支路9有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 9 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.146 | hwRendaAMCNA2Branch10ActiveEnergy | Branch 10 active energy | 支路10有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 10 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.147 | hwRendaAMCNA2Branch11ActiveEnergy | Branch 11 active energy | 支路11有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 11 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.148 | hwRendaAMCNA2Branch12ActiveEnergy | Branch 12 active energy | 支路12有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 12 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.149 | hwRendaAMCNA2Branch13ActiveEnergy | Branch 13 active energy | 支路13有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 13 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.150 | hwRendaAMCNA2Branch14ActiveEnergy | Branch 14 active energy | 支路14有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 14 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.151 | hwRendaAMCNA2Branch15ActiveEnergy | Branch 15 active energy | 支路15有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 15 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.152 | hwRendaAMCNA2Branch1ActivePower | Branch 1 active power | 支路1有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 1 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.153 | hwRendaAMCNA2Branch2ActivePower | Branch 2 active power | 支路2有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 2 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.154 | hwRendaAMCNA2Branch3ActivePower | Branch 3 active power | 支路3有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 3 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.155 | hwRendaAMCNA2Branch4ActivePower | Branch 4 active power | 支路4有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 4 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.156 | hwRendaAMCNA2Branch5ActivePower | Branch 5 active power | 支路5有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 5 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.157 | hwRendaAMCNA2Branch6ActivePower | Branch 6 active power | 支路6有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 6 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.158 | hwRendaAMCNA2Branch7ActivePower | Branch 7 active power | 支路7有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 7 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.159 | hwRendaAMCNA2Branch8ActivePower | Branch 8 active power | 支路8有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 8 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.160 | hwRendaAMCNA2Branch9ActivePower | Branch 9 active power | 支路9有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 9 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.161 | hwRendaAMCNA2Branch10ActivePower | Branch 10 active power | 支路10有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 10 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.162 | hwRendaAMCNA2Branch11ActivePower | Branch 11 active power | 支路11有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 11 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.163 | hwRendaAMCNA2Branch12ActivePower | Branch 12 active power | 支路12有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 12 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.164 | hwRendaAMCNA2Branch13ActivePower | Branch 13 active power | 支路13有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 13 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.165 | hwRendaAMCNA2Branch14ActivePower | Branch 14 active power | 支路14有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 14 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.166 | hwRendaAMCNA2Branch15ActivePower | Branch 15 active power | 支路15有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 15 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.167 | hwRendaAMCDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device Name of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.200 | hwRendaAMCRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The rowstatus of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.2 | hwRendaAMCRunning2Table | / | / |  |  | [] | / | The Running table of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.1 | hwRendaAMCRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.2 | hwRendaAMCNA1Brauch16SwitchStatus | Branch 16 switch status | 支路16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 16 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.3 | hwRendaAMCNA1Brauch17SwitchStatus | Branch 17 switch status | 支路17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 17 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.4 | hwRendaAMCNA1Brauch18SwitchStatus | Branch 18 switch status | 支路18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 18 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.5 | hwRendaAMCNA1Brauch19SwitchStatus | Branch 19 switch status | 支路19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 19 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.6 | hwRendaAMCNA1Brauch20SwitchStatus | Branch 20 switch status | 支路20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 20 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.7 | hwRendaAMCNA1Brauch21SwitchStatus | Branch 21 switch status | 支路21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 21 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.8 | hwRendaAMCNA1Brauch22SwitchStatus | Branch 22 switch status | 支路22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 22 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.9 | hwRendaAMCNA1Brauch23SwitchStatus | Branch 23 switch status | 支路23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 23 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.10 | hwRendaAMCNA1Brauch24SwitchStatus | Branch 24 switch status | 支路24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 24 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.11 | hwRendaAMCNA1Brauch25SwitchStatus | Branch 25 switch status | 支路25开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 25 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.12 | hwRendaAMCNA1Brauch26SwitchStatus | Branch 26 switch status | 支路26开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 26 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.13 | hwRendaAMCNA1Brauch27SwitchStatus | Branch 27 switch status | 支路27开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 27 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.14 | hwRendaAMCNA1Brauch28SwitchStatus | Branch 28 switch status | 支路28开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 28 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.15 | hwRendaAMCNA1Brauch29SwitchStatus | Branch 29 switch status | 支路29开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 29 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.16 | hwRendaAMCNA1Brauch30SwitchStatus | Branch 30 switch status | 支路30开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 30 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.17 | hwRendaAMCNA1Brauch16Current | Branch 16 current | 支路16电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 16 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.18 | hwRendaAMCNA1Brauch17Current | Branch 17 current | 支路17电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 17 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.19 | hwRendaAMCNA1Brauch18Current | Branch 18 current | 支路18电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 18 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.20 | hwRendaAMCNA1Brauch19Current | Branch 19 current | 支路19电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 19 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.21 | hwRendaAMCNA1Brauch20Current | Branch 20 current | 支路20电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 20 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.22 | hwRendaAMCNA1Brauch21Current | Branch 21 current | 支路21电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 21 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.23 | hwRendaAMCNA1Brauch22Current | Branch 22 current | 支路22电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 22 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.24 | hwRendaAMCNA1Brauch23Current | Branch 23 current | 支路23电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 23 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.25 | hwRendaAMCNA1Brauch24Current | Branch 24 current | 支路24电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 24 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.26 | hwRendaAMCNA1Brauch25Current | Branch 25 current | 支路25电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 25 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.27 | hwRendaAMCNA1Brauch26Current | Branch 26 current | 支路26电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 26 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.28 | hwRendaAMCNA1Brauch27Current | Branch 27 current | 支路27电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 27 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.29 | hwRendaAMCNA1Brauch28Current | Branch 28 current | 支路28电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 28 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.30 | hwRendaAMCNA1Brauch29Current | Branch 29 current | 支路29电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 29 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.31 | hwRendaAMCNA1Brauch30Current | Branch 30 current | 支路30电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 30 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.32 | hwRendaAMCNA1Brauch16Voltage | Branch 16 voltage | 支路16电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 16 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.33 | hwRendaAMCNA1Brauch17Voltage | Branch 17 voltage | 支路17电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 17 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.34 | hwRendaAMCNA1Brauch18Voltage | Branch 18 voltage | 支路18电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 18 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.35 | hwRendaAMCNA1Brauch19Voltage | Branch 19 voltage | 支路19电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 19 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.36 | hwRendaAMCNA1Brauch20Voltage | Branch 20 voltage | 支路20电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 20 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.37 | hwRendaAMCNA1Brauch21Voltage | Branch 21 voltage | 支路21电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 21 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.38 | hwRendaAMCNA1Brauch22Voltage | Branch 22 voltage | 支路22电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 22 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.39 | hwRendaAMCNA1Brauch23Voltage | Branch 23 voltage | 支路23电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 23 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.40 | hwRendaAMCNA1Brauch24Voltage | Branch 24 voltage | 支路24电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 24 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.41 | hwRendaAMCNA1Brauch25Voltage | Branch 25 voltage | 支路25电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 25 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.42 | hwRendaAMCNA1Brauch26Voltage | Branch 26 voltage | 支路26电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 26 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.43 | hwRendaAMCNA1Brauch27Voltage | Branch 27 voltage | 支路27电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 27 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.44 | hwRendaAMCNA1Brauch28Voltage | Branch 28 voltage | 支路28电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 28 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.45 | hwRendaAMCNA1Brauch29Voltage | Branch 29 voltage | 支路29电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 29 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.46 | hwRendaAMCNA1Brauch30Voltage | Branch 30 voltage | 支路30电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 30 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.47 | hwRendaAMCNA1Branch16ActiveEnergy | Branch 16 active energy | 支路16有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 16 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.48 | hwRendaAMCNA1Branch17ActiveEnergy | Branch 17 active energy | 支路17有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 17 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.49 | hwRendaAMCNA1Branch18ActiveEnergy | Branch 18 active energy | 支路18有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 18 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.50 | hwRendaAMCNA1Branch19ActiveEnergy | Branch 19 active energy | 支路19有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 19 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.51 | hwRendaAMCNA1Branch20ActiveEnergy | Branch 20 active energy | 支路20有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 20 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.52 | hwRendaAMCNA1Branch21ActiveEnergy | Branch 21 active energy | 支路21有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 21 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.53 | hwRendaAMCNA1Branch22ActiveEnergy | Branch 22 active energy | 支路22有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 22 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.54 | hwRendaAMCNA1Branch23ActiveEnergy | Branch 23 active energy | 支路23有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 23 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.55 | hwRendaAMCNA1Branch24ActiveEnergy | Branch 24 active energy | 支路24有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 24 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.56 | hwRendaAMCNA1Branch25ActiveEnergy | Branch 25 active energy | 支路25有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 25 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.57 | hwRendaAMCNA1Branch26ActiveEnergy | Branch 26 active energy | 支路26有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 26 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.58 | hwRendaAMCNA1Branch27ActiveEnergy | Branch 27 active energy | 支路27有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 27 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.59 | hwRendaAMCNA1Branch28ActiveEnergy | Branch 28 active energy | 支路28有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 28 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.60 | hwRendaAMCNA1Branch29ActiveEnergy | Branch 29 active energy | 支路29有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 29 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.61 | hwRendaAMCNA1Branch30ActiveEnergy | Branch 30 active energy | 支路30有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 30 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.62 | hwRendaAMCNA1Brauch16ActivePower | Branch 16 active power | 支路16有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 16 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.63 | hwRendaAMCNA1Brauch17ActivePower | Branch 17 active power | 支路17有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 17 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.64 | hwRendaAMCNA1Brauch18ActivePower | Branch 18 active power | 支路18有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 18 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.65 | hwRendaAMCNA1Brauch19ActivePower | Branch 19 active power | 支路19有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 19 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.66 | hwRendaAMCNA1Brauch20ActivePower | Branch 20 active power | 支路20有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 20 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.67 | hwRendaAMCNA1Brauch21ActivePower | Branch 21 active power | 支路21有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 21 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.68 | hwRendaAMCNA1Brauch22ActivePower | Branch 22 active power | 支路22有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 22 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.69 | hwRendaAMCNA1Brauch23ActivePower | Branch 23 active power | 支路23有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 23 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.70 | hwRendaAMCNA1Brauch24ActivePower | Branch 24 active power | 支路24有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 24 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.71 | hwRendaAMCNA1Brauch25ActivePower | Branch 25 active power | 支路25有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 25 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.72 | hwRendaAMCNA1Brauch26ActivePower | Branch 26 active power | 支路26有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 26 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.73 | hwRendaAMCNA1Brauch27ActivePower | Branch 27 active power | 支路27有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 27 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.74 | hwRendaAMCNA1Brauch28ActivePower | Branch 28 active power | 支路28有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 28 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.75 | hwRendaAMCNA1Brauch29ActivePower | Branch 29 active power | 支路29有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 29 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.76 | hwRendaAMCNA1Brauch30ActivePower | Branch 30 active power | 支路30有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 30 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.77 | hwRendaAMCNA2Brauch16SwitchStatus | Branch 16 switch status | 支路16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 16 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.78 | hwRendaAMCNA2Brauch17SwitchStatus | Branch 17 switch status | 支路17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 17 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.79 | hwRendaAMCNA2Brauch18SwitchStatus | Branch 18 switch status | 支路18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 18 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.80 | hwRendaAMCNA2Brauch19SwitchStatus | Branch 19 switch status | 支路19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 19 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.81 | hwRendaAMCNA2Brauch20SwitchStatus | Branch 20 switch status | 支路20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 20 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.82 | hwRendaAMCNA2Brauch21SwitchStatus | Branch 21 switch status | 支路21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 21 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.83 | hwRendaAMCNA2Brauch22SwitchStatus | Branch 22 switch status | 支路22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 22 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.84 | hwRendaAMCNA2Brauch23SwitchStatus | Branch 23 switch status | 支路23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 23 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.85 | hwRendaAMCNA2Brauch24SwitchStatus | Branch 24 switch status | 支路24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 24 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.86 | hwRendaAMCNA2Brauch25SwitchStatus | Branch 25 switch status | 支路25开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 25 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.87 | hwRendaAMCNA2Brauch26SwitchStatus | Branch 26 switch status | 支路26开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 26 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.88 | hwRendaAMCNA2Brauch27SwitchStatus | Branch 27 switch status | 支路27开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 27 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.89 | hwRendaAMCNA2Brauch28SwitchStatus | Branch 28 switch status | 支路28开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 28 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.90 | hwRendaAMCNA2Brauch29SwitchStatus | Branch 29 switch status | 支路29开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 29 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.91 | hwRendaAMCNA2Brauch30SwitchStatus | Branch 30 switch status | 支路30开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 30 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.92 | hwRendaAMCNA2Brauch16Current | Branch 16 current | 支路16电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 16 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.93 | hwRendaAMCNA2Brauch17Current | Branch 17 current | 支路17电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 17 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.94 | hwRendaAMCNA2Brauch18Current | Branch 18 current | 支路18电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 18 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.95 | hwRendaAMCNA2Brauch19Current | Branch 19 current | 支路19电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 19 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.96 | hwRendaAMCNA2Brauch20Current | Branch 20 current | 支路20电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 20 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.97 | hwRendaAMCNA2Brauch21Current | Branch 21 current | 支路21电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 21 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.98 | hwRendaAMCNA2Brauch22Current | Branch 22 current | 支路22电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 22 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.99 | hwRendaAMCNA2Brauch23Current | Branch 23 current | 支路23电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 23 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.100 | hwRendaAMCNA2Brauch24Current | Branch 24 current | 支路24电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 24 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.101 | hwRendaAMCNA2Brauch25Current | Branch 25 current | 支路25电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 25 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.102 | hwRendaAMCNA2Brauch26Current | Branch 26 current | 支路26电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 26 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.103 | hwRendaAMCNA2Brauch27Current | Branch 27 current | 支路27电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 27 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.104 | hwRendaAMCNA2Brauch28Current | Branch 28 current | 支路28电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 28 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.105 | hwRendaAMCNA2Brauch29Current | Branch 29 current | 支路29电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 29 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.106 | hwRendaAMCNA2Brauch30Current | Branch 30 current | 支路30电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 30 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.107 | hwRendaAMCNA2Brauch16Voltage | Branch 16 voltage | 支路16电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 16 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.108 | hwRendaAMCNA2Brauch17Voltage | Branch 17 voltage | 支路17电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 17 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.109 | hwRendaAMCNA2Brauch18Voltage | Branch 18 voltage | 支路18电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 18 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.110 | hwRendaAMCNA2Brauch19Voltage | Branch 19 voltage | 支路19电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 19 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.111 | hwRendaAMCNA2Brauch20Voltage | Branch 20 voltage | 支路20电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 20 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.112 | hwRendaAMCNA2Brauch21Voltage | Branch 21 voltage | 支路21电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 21 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.113 | hwRendaAMCNA2Brauch22Voltage | Branch 22 voltage | 支路22电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 22 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.114 | hwRendaAMCNA2Brauch23Voltage | Branch 23 voltage | 支路23电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 23 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.115 | hwRendaAMCNA2Brauch24Voltage | Branch 24 voltage | 支路24电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 24 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.116 | hwRendaAMCNA2Brauch25Voltage | Branch 25 voltage | 支路25电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 25 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.117 | hwRendaAMCNA2Brauch26Voltage | Branch 26 voltage | 支路26电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 26 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.118 | hwRendaAMCNA2Brauch27Voltage | Branch 27 voltage | 支路27电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 27 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.119 | hwRendaAMCNA2Brauch28Voltage | Branch 28 voltage | 支路28电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 28 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.120 | hwRendaAMCNA2Brauch29Voltage | Branch 29 voltage | 支路29电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 29 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.121 | hwRendaAMCNA2Brauch30Voltage | Branch 30 voltage | 支路30电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 30 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.122 | hwRendaAMCNA2Branch16ActiveEnergy | Branch 16 active energy | 支路16有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 16 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.123 | hwRendaAMCNA2Branch17ActiveEnergy | Branch 17 active energy | 支路17有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 17 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.124 | hwRendaAMCNA2Branch18ActiveEnergy | Branch 18 active energy | 支路18有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 18 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.125 | hwRendaAMCNA2Branch19ActiveEnergy | Branch 19 active energy | 支路19有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 19 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.126 | hwRendaAMCNA2Branch20ActiveEnergy | Branch 20 active energy | 支路20有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 20 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.127 | hwRendaAMCNA2Branch21ActiveEnergy | Branch 21 active energy | 支路21有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 21 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.128 | hwRendaAMCNA2Branch22ActiveEnergy | Branch 22 active energy | 支路22有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 22 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.129 | hwRendaAMCNA2Branch23ActiveEnergy | Branch 23 active energy | 支路23有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 23 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.130 | hwRendaAMCNA2Branch24ActiveEnergy | Branch 24 active energy | 支路24有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 24 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.131 | hwRendaAMCNA2Branch25ActiveEnergy | Branch 25 active energy | 支路25有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 25 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.132 | hwRendaAMCNA2Branch26ActiveEnergy | Branch 26 active energy | 支路26有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 26 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.133 | hwRendaAMCNA2Branch27ActiveEnergy | Branch 27 active energy | 支路27有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 27 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.134 | hwRendaAMCNA2Branch28ActiveEnergy | Branch 28 active energy | 支路28有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 28 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.135 | hwRendaAMCNA2Branch29ActiveEnergy | Branch 29 active energy | 支路29有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 29 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.136 | hwRendaAMCNA2Branch30ActiveEnergy | Branch 30 active energy | 支路30有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 30 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.137 | hwRendaAMCNA2Brauch16ActivePower | Branch 16 active power | 支路16有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 16 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.138 | hwRendaAMCNA2Brauch17ActivePower | Branch 17 active power | 支路17有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 17 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.139 | hwRendaAMCNA2Brauch18ActivePower | Branch 18 active power | 支路18有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 18 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.140 | hwRendaAMCNA2Brauch19ActivePower | Branch 19 active power | 支路19有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 19 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.141 | hwRendaAMCNA2Brauch20ActivePower | Branch 20 active power | 支路20有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 20 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.142 | hwRendaAMCNA2Brauch21ActivePower | Branch 21 active power | 支路21有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 21 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.143 | hwRendaAMCNA2Brauch22ActivePower | Branch 22 active power | 支路22有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 22 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.144 | hwRendaAMCNA2Brauch23ActivePower | Branch 23 active power | 支路23有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 23 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.145 | hwRendaAMCNA2Brauch24ActivePower | Branch 24 active power | 支路24有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 24 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.146 | hwRendaAMCNA2Brauch25ActivePower | Branch 25 active power | 支路25有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 25 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.147 | hwRendaAMCNA2Brauch26ActivePower | Branch 26 active power | 支路26有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 26 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.148 | hwRendaAMCNA2Brauch27ActivePower | Branch 27 active power | 支路27有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 27 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.149 | hwRendaAMCNA2Brauch28ActivePower | Branch 28 active power | 支路28有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 28 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.150 | hwRendaAMCNA2Brauch29ActivePower | Branch 29 active power | 支路29有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 29 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.151 | hwRendaAMCNA2Brauch30ActivePower | Branch 30 active power | 支路30有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 30 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.200 | hwRendaAMCRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The rowstatus of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.3 | hwRendaAMCConfig3Table | / | / |  |  | / | / | The config table of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.3.1.1 | hwRendaAMCConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.3.1.2 | hwRendaAMCFirstBusBranchSet | First bus branch set | 母线1支路设置 | 1-Read_Write | 读写 | 15..30 | 15..30 | First bus branch set of the device config table for the RendaAMC
1.3.6.1.4.1.2011.6.178.1.1.41.3.1.3 | hwRendaAMCSecondBusBranchSet | Second bus branch set | 母线2支路设置 | 1-Read_Write | 读写 | 15..30 | 15..30 | Second bus branch set of the device config table for the RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.3.1.4 | hwRendaAMCRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The rowstatus of RendaAMC.

## rPDU-MPDU
rPDU-MPDU
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.48 | rPDUMPDU | rPDU-MPDU | rPDU-MPDU | / | / | / | / | rPDU-MPDU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.48.1 | hwrPDUMPDURunningTable | / | / |  |  | / | / | The running table of rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.1 | hwrPDUMPDURunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.2 | hwrPDUMPDUVoltageValue | Voltage value | 电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.3 | hwrPDUMPDUVoltageValueOfC1 | Voltage value of C1 | C1回路电压值 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value of C1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.4 | hwrPDUMPDUVoltageValueOfC2 | Voltage value of C2 | C2回路电压值 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value of C2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.5 | hwrPDUMPDUVoltageValueL1 | Voltage value L1 | L1相电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value L1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.6 | hwrPDUMPDUVoltageValueL2 | Voltage value L2 | L2相电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value L2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.7 | hwrPDUMPDUVoltageValueL3 | Voltage value L3 | L3相电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value L3 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.8 | hwrPDUMPDUCurrentValue | Current value | 电流 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.9 | hwrPDUMPDUCurrentValueOfC1 | Current value of C1 | C1回路电流值 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value of C1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.10 | hwrPDUMPDUCurrentValueOfC2 | Current value of C2 | C2回路电流值 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value of C2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.11 | hwrPDUMPDUCurrentValueL1 | Current value L1 | L1相电流 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value L1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.12 | hwrPDUMPDUCurrentValueL2 | Current value L2 | L2相电流 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value L2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.13 | hwrPDUMPDUCurrentValueL3 | Current value L3 | L3相电流 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value L3 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.14 | hwrPDUMPDUPowerValue | Power value | 有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.15 | hwrPDUMPDUPowerValueOfC1 | Power value of C1 | C1回路有功功率值 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value of C1 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.16 | hwrPDUMPDUPowerValueOfC2 | Power value of C2 | C2回路有功功率值 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value of C2 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.17 | hwrPDUMPDUPowerValueL1 | Power value L1 | L1相有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value L1 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.18 | hwrPDUMPDUPowerValueL2 | Power value L2 | L2相有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value L2 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.19 | hwrPDUMPDUPowerValueL3 | Power value L3 | L3相有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value L3 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.20 | hwrPDUMPDUPowerEnergyValue | Power energy value | 有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.21 | hwrPDUMPDUPowerEnergyValueOfC1 | Power energy value of C1 | C1回路电能值 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value of C1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.22 | hwrPDUMPDUPowerEnergyValueOfC2 | Power energy value of C2 | C2回路电能值 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value of C2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.23 | hwrPDUMPDUPowerEnergyValueL1 | Power energy value L1 | L1相有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value L1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.24 | hwrPDUMPDUPowerEnergyValueL2 | Power energy value L2 | L2相有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value L2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.25 | hwrPDUMPDUPowerEnergyValueL3 | Power energy value L3 | L3相有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value L3 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.26 | hwrPDUMPDUPowerFactorValue | Power factor value | 功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.27 | hwrPDUMPDUPowerFactorValueOfC1 | Power factor value of C1 | C1回路功率因数值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value of C1 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.28 | hwrPDUMPDUPowerFactorValueOfC2 | Power factor value of C2 | C2回路功率因数值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value of C2 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.29 | hwrPDUMPDUPowerFactorValueL1 | Power factor value L1 | L1相功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value L1 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.30 | hwrPDUMPDUPowerFactorValueL2 | Power factor value L2 | L2相功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value L2 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.31 | hwrPDUMPDUPowerFactorValueL3 | Power factor value L3 | L3相功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value L3 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.32 | hwrPDUMPDUQF1CurrentOfOutput | QF1 Current of output | QF1电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF1 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.33 | hwrPDUMPDUQF2CurrentOfOutput | QF2 Current of output | QF2电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF2 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.34 | hwrPDUMPDUQF3CurrentOfOutput | QF3 Current of output | QF3电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF3 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.35 | hwrPDUMPDUQF4CurrentOfOutput | QF4 Current of output | QF4电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF4 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.36 | hwrPDUMPDUQF5CurrentOfOutput | QF5 Current of output | QF5电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF5 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.37 | hwrPDUMPDUQF6CurrentOfOutput | QF6 Current of output | QF6电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF6 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.38 | hwrPDUMPDUQF7CurrentOfOutput | QF7 Current of output | QF7电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF7 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.39 | hwrPDUMPDUQF8CurrentOfOutput | QF8 Current of output | QF8电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF8 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.40 | hwrPDUMPDUQF9CurrentOfOutput | QF9 Current of output | QF9电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF9 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.41 | hwrPDUMPDUQF10CurrentOfOutput | QF10 Current of output | QF10电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF10 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.42 | hwrPDUMPDUQF11CurrentOfOutput | QF11 Current of output | QF11电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF11 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.43 | hwrPDUMPDUQF12CurrentOfOutput | QF12 Current of output | QF12电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF12 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.44 | hwrPDUMPDUQF13CurrentOfOutput | QF13 Current of output | QF13电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF13 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.45 | hwrPDUMPDUQF14CurrentOfOutput | QF14 Current of output | QF14电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF14 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.46 | hwrPDUMPDUQF15CurrentOfOutput | QF15 Current of output | QF15电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF15 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.47 | hwrPDUMPDUQF16CurrentOfOutput | QF16 Current of output | QF16电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF16 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.48 | hwrPDUMPDUQF17CurrentOfOutput | QF17 Current of output | QF17电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF17 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.49 | hwrPDUMPDUQF18CurrentOfOutput | QF18 Current of output | QF18电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF18 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.50 | hwrPDUMPDUQF19CurrentOfOutput | QF19 Current of output | QF19电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF19 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.51 | hwrPDUMPDUQF20CurrentOfOutput | QF20 Current of output | QF20电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF20 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.52 | hwrPDUMPDUQF21CurrentOfOutput | QF21 Current of output | QF21电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF21 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.53 | hwrPDUMPDUQF22CurrentOfOutput | QF22 Current of output | QF22电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF22 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.54 | hwrPDUMPDUQF23CurrentOfOutput | QF23 Current of output | QF23电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF23 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.55 | hwrPDUMPDUQF24CurrentOfOutput | QF24 Current of output | QF24电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF24 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.56 | hwrPDUMPDUQF1ElectricalEnergyOfOutput | QF1 Electrical energy of output | QF1电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF1 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.57 | hwrPDUMPDUQF1ApparentPowerOfOutput | QF1 Apparent power of output | QF1有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF1 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.58 | hwrPDUMPDUQF2ApparentPowerOfOutput | QF2 Apparent power of output | QF2有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF2 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.59 | hwrPDUMPDUQF3ApparentPowerOfOutput | QF3 Apparent power of output | QF3有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF3 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.60 | hwrPDUMPDUQF4ApparentPowerOfOutput | QF4 Apparent power of output | QF4有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF4 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.61 | hwrPDUMPDUQF5ApparentPowerOfOutput | QF5 Apparent power of output | QF5有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF5 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.62 | hwrPDUMPDUQF6ApparentPowerOfOutput | QF6 Apparent power of output | QF6有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF6 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.63 | hwrPDUMPDUQF7ApparentPowerOfOutput | QF7 Apparent power of output | QF7有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF7 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.64 | hwrPDUMPDUQF8ApparentPowerOfOutput | QF8 Apparent power of output | QF8有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF8 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.65 | hwrPDUMPDUQF9ApparentPowerOfOutput | QF9 Apparent power of output | QF9有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF9 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.66 | hwrPDUMPDUQF10ApparentPowerOfOutput | QF10 Apparent power of output | QF10有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF10 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.67 | hwrPDUMPDUQF11ApparentPowerOfOutput | QF11 Apparent power of output | QF11有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF11 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.68 | hwrPDUMPDUQF12ApparentPowerOfOutput | QF12 Apparent power of output | QF12有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF12 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.69 | hwrPDUMPDUQF13ApparentPowerOfOutput | QF13 Apparent power of output | QF13有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF13 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.70 | hwrPDUMPDUQF14ApparentPowerOfOutput | QF14 Apparent power of output | QF14有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF14 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.71 | hwrPDUMPDUQF15ApparentPowerOfOutput | QF15 Apparent power of output | QF15有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF15 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.72 | hwrPDUMPDUQF16ApparentPowerOfOutput | QF16 Apparent power of output | QF16有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF16 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.73 | hwrPDUMPDUQF17ApparentPowerOfOutput | QF17 Apparent power of output | QF17有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF17 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.74 | hwrPDUMPDUQF18ApparentPowerOfOutput | QF18 Apparent power of output | QF18有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF18 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.75 | hwrPDUMPDUQF19ApparentPowerOfOutput | QF19 Apparent power of output | QF19有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF19 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.76 | hwrPDUMPDUQF20ApparentPowerOfOutput | QF20 Apparent power of output | QF20有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF20 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.77 | hwrPDUMPDUQF21ApparentPowerOfOutput | QF21 Apparent power of output | QF21有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF21 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.78 | hwrPDUMPDUQF22ApparentPowerOfOutput | QF22 Apparent power of output | QF22有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF22 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.79 | hwrPDUMPDUQF23ApparentPowerOfOutput | QF23 Apparent power of output | QF23有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF23 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.80 | hwrPDUMPDUQF24ApparentPowerOfOutput | QF24 Apparent power of output | QF24有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF24 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.81 | hwrPDUMPDUQF2ElectricalEnergyOfOutput | QF2 Electrical energy of output | QF2电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF2 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.82 | hwrPDUMPDUQF3ElectricalEnergyOfOutput | QF3 Electrical energy of output | QF3电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF3 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.83 | hwrPDUMPDUQF4ElectricalEnergyOfOutput | QF4 Electrical energy of output | QF4电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF4 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.84 | hwrPDUMPDUQF5ElectricalEnergyOfOutput | QF5 Electrical energy of output | QF5电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF5 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.85 | hwrPDUMPDUQF6ElectricalEnergyOfOutput | QF6 Electrical energy of output | QF6电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF6 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.86 | hwrPDUMPDUQF7ElectricalEnergyOfOutput | QF7 Electrical energy of output | QF7电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF7 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.87 | hwrPDUMPDUQF8ElectricalEnergyOfOutput | QF8 Electrical energy of output | QF8电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF8 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.88 | hwrPDUMPDUQF9ElectricalEnergyOfOutput | QF9 Electrical energy of output | QF9电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF9 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.89 | hwrPDUMPDUQF10ElectricalEnergyOfOutput | QF10 Electrical energy of output | QF10电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF10 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.90 | hwrPDUMPDUQF11ElectricalEnergyOfOutput | QF11 Electrical energy of output | QF11电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF11 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.91 | hwrPDUMPDUQF12ElectricalEnergyOfOutput | QF12 Electrical energy of output | QF12电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF12 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.92 | hwrPDUMPDUQF13ElectricalEnergyOfOutput | QF13 Electrical energy of output | QF13电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF13 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.93 | hwrPDUMPDUQF14ElectricalEnergyOfOutput | QF14 Electrical energy of output | QF14电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF14 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.94 | hwrPDUMPDUQF15ElectricalEnergyOfOutput | QF15 Electrical energy of output | QF15电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF15 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.95 | hwrPDUMPDUQF16ElectricalEnergyOfOutput | QF16 Electrical energy of output | QF16电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF16 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.96 | hwrPDUMPDUQF17ElectricalEnergyOfOutput | QF17 Electrical energy of output | QF17电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF17 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.97 | hwrPDUMPDUQF18ElectricalEnergyOfOutput | QF18 Electrical energy of output | QF18电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF18 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.98 | hwrPDUMPDUQF19ElectricalEnergyOfOutput | QF19 Electrical energy of output | QF19电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF19 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.99 | hwrPDUMPDUQF20ElectricalEnergyOfOutput | QF20 Electrical energy of output | QF20电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF20 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.100 | hwrPDUMPDUQF21ElectricalEnergyOfOutput | QF21 Electrical energy of output | QF21电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF21 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.101 | hwrPDUMPDUQF22ElectricalEnergyOfOutput | QF22 Electrical energy of output | QF22电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF22 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.102 | hwrPDUMPDUQF23ElectricalEnergyOfOutput | QF23 Electrical energy of output | QF23电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF23 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.103 | hwrPDUMPDUQF24ElectricalEnergyOfOutput | QF24 Electrical energy of output | QF24电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF24 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.104 | hwrPDUMPDUQF1PowerFactorOfOutput | QF1 Power factor of output | QF1功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF1 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.105 | hwrPDUMPDUQF2PowerFactorOfOutput | QF2 Power factor of output | QF2功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF2 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.106 | hwrPDUMPDUQF3PowerFactorOfOutput | QF3 Power factor of output | QF3功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF3 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.107 | hwrPDUMPDUQF4PowerFactorOfOutput | QF4 Power factor of output | QF4功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF4 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.108 | hwrPDUMPDUQF5PowerFactorOfOutput | QF5 Power factor of output | QF5功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF5 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.109 | hwrPDUMPDUQF6PowerFactorOfOutput | QF6 Power factor of output | QF6功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF6 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.110 | hwrPDUMPDUQF7PowerFactorOfOutput | QF7 Power factor of output | QF7功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF7 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.111 | hwrPDUMPDUQF8PowerFactorOfOutput | QF8 Power factor of output | QF8功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF8 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.112 | hwrPDUMPDUQF9PowerFactorOfOutput | QF9 Power factor of output | QF9功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF9 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.113 | hwrPDUMPDUQF10PowerFactorOfOutput | QF10 Power factor of output | QF10功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF10 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.114 | hwrPDUMPDUQF11PowerFactorOfOutput | QF11 Power factor of output | QF11功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF11 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.115 | hwrPDUMPDUQF12PowerFactorOfOutput | QF12 Power factor of output | QF12功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF12 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.116 | hwrPDUMPDUQF13PowerFactorOfOutput | QF13 Power factor of output | QF13功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF13 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.117 | hwrPDUMPDUQF14PowerFactorOfOutput | QF14 Power factor of output | QF14功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF14 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.118 | hwrPDUMPDUQF15PowerFactorOfOutput | QF15 Power factor of output | QF15功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF15 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.119 | hwrPDUMPDUQF16PowerFactorOfOutput | QF16 Power factor of output | QF16功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF16 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.120 | hwrPDUMPDUQF17PowerFactorOfOutput | QF17 Power factor of output | QF17功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF17 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.121 | hwrPDUMPDUQF18PowerFactorOfOutput | QF18 Power factor of output | QF18功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF18 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.122 | hwrPDUMPDUQF19PowerFactorOfOutput | QF19 Power factor of output | QF19功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF19 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.123 | hwrPDUMPDUQF20PowerFactorOfOutput | QF20 Power factor of output | QF20功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF20 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.124 | hwrPDUMPDUQF21PowerFactorOfOutput | QF21 Power factor of output | QF21功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF21 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.125 | hwrPDUMPDUQF22PowerFactorOfOutput | QF22 Power factor of output | QF22功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF22 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.126 | hwrPDUMPDUQF23PowerFactorOfOutput | QF23 Power factor of output | QF23功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF23 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.127 | hwrPDUMPDUQF24PowerFactorOfOutput | QF24 Power factor of output | QF24功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF24 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.128 | hwrPDUMPDUQF1SwitchStatusOfOutput | QF1 Switch status of output | QF1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF1 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.129 | hwrPDUMPDUQF2SwitchStatusOfOutput | QF2 Switch status of output | QF2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF2 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.130 | hwrPDUMPDUQF3SwitchStatusOfOutput | QF3 Switch status of output | QF3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF3 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.131 | hwrPDUMPDUQF4SwitchStatusOfOutput | QF4 Switch status of output | QF4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF4 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.132 | hwrPDUMPDUQF5SwitchStatusOfOutput | QF5 Switch status of output | QF5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF5 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.133 | hwrPDUMPDUQF6SwitchStatusOfOutput | QF6 Switch status of output | QF6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF6 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.134 | hwrPDUMPDUQF7SwitchStatusOfOutput | QF7 Switch status of output | QF7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF7 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.135 | hwrPDUMPDUQF8SwitchStatusOfOutput | QF8 Switch status of output | QF8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF8 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.136 | hwrPDUMPDUQF9SwitchStatusOfOutput | QF9 Switch status of output | QF9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF9 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.137 | hwrPDUMPDUQF10SwitchStatusOfOutput | QF10 Switch status of output | QF10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF10 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.138 | hwrPDUMPDUQF11SwitchStatusOfOutput | QF11 Switch status of output | QF11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF11 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.139 | hwrPDUMPDUQF12SwitchStatusOfOutput | QF12 Switch status of output | QF12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF12 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.140 | hwrPDUMPDUQF13SwitchStatusOfOutput | QF13 Switch status of output | QF13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF13 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.141 | hwrPDUMPDUQF14SwitchStatusOfOutput | QF14 Switch status of output | QF14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF14 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.142 | hwrPDUMPDUQF15SwitchStatusOfOutput | QF15 Switch status of output | QF15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF15 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.143 | hwrPDUMPDUQF16SwitchStatusOfOutput | QF16 Switch status of output | QF16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF16 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.144 | hwrPDUMPDUQF17SwitchStatusOfOutput | QF17 Switch status of output | QF17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF17 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.145 | hwrPDUMPDUQF18SwitchStatusOfOutput | QF18 Switch status of output | QF18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF18 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.146 | hwrPDUMPDUQF19SwitchStatusOfOutput | QF19 Switch status of output | QF19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF19 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.147 | hwrPDUMPDUQF20SwitchStatusOfOutput | QF20 Switch status of output | QF20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF20 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.148 | hwrPDUMPDUQF21SwitchStatusOfOutput | QF21 Switch status of output | QF21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF21 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.149 | hwrPDUMPDUQF22SwitchStatusOfOutput | QF22 Switch status of output | QF22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF22 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.150 | hwrPDUMPDUQF23SwitchStatusOfOutput | QF23 Switch status of output | QF23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF23 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.151 | hwrPDUMPDUQF24SwitchStatusOfOutput | QF24 Switch status of output | QF24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF24 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.152 | hwrPDUMPDUCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the rPDU-MPDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.153 | hwrPDUMPDUPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.154 | hwrPDUMPDUModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.155 | hwrPDUMPDUSingleOrThreePhaseMark | Single/Three phase mark | 单/三相标识 | 0-Read_Only | 只读 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | Single or Three phase mark of the device config table for the rPDU-MPDU. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.156 | hwrPDUMPDUDeviceSeries | Device series | 设备系列 | 0-Read_Only | 只读 | a(1), b(2), c(3), d(4), unknown(255) | [A=1]/[B=2]/[C=3]/[D=4] | Device series of the device config table for the rPDU-MPDU. Value 1 indicate a Value 2 indicate b Value 3 indicate c Value 4 indicate d
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.157 | hwrPDUMPDUSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Software version of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.220 | hwrPDUMPDURunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2 | hwrPDUMPDUConfigTable | / | / |  |  | / | / | The config table of rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.1 | hwrPDUMPDUConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.2 | hwrPDUMPDUInputMode | Input mode | 输入模式 | 1-Read_Write | 读写 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | of the device config table for the rPDU-MPDU. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.3 | hwrPDUMPDUSwitchControlAllOutput | Switch control all output | 输出位总开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Switch control all output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.4 | hwrPDUMPDUQF1SwitchControlOutput | QF1 Switch control output | QF1开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF1 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.5 | hwrPDUMPDUQF2SwitchControlOutput | QF2 Switch control output | QF2开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF2 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.6 | hwrPDUMPDUQF3SwitchControlOutput | QF3 Switch control output | QF3开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF3 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.7 | hwrPDUMPDUQF4SwitchControlOutput | QF4 Switch control output | QF4开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF4 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.8 | hwrPDUMPDUQF5SwitchControlOutput | QF5 Switch control output | QF5开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF5 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.9 | hwrPDUMPDUQF6SwitchControlOutput | QF6 Switch control output | QF6开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF6 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.10 | hwrPDUMPDUQF7SwitchControlOutput | QF7 Switch control output | QF7开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF7 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.11 | hwrPDUMPDUQF8SwitchControlOutput | QF8 Switch control output | QF8开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF8 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.12 | hwrPDUMPDUQF9SwitchControlOutput | QF9 Switch control output | QF9开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF9 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.13 | hwrPDUMPDUQF10SwitchControlOutput | QF10 Switch control output | QF10开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF10 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.14 | hwrPDUMPDUQF11SwitchControlOutput | QF11 Switch control output | QF11开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF11 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.15 | hwrPDUMPDUQF12SwitchControlOutput | QF12 Switch control output | QF12开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF12 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.16 | hwrPDUMPDUQF13SwitchControlOutput | QF13 Switch control output | QF13开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF13 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.17 | hwrPDUMPDUQF14SwitchControlOutput | QF14 Switch control output | QF14开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF14 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.18 | hwrPDUMPDUQF15SwitchControlOutput | QF15 Switch control output | QF15开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF15 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.19 | hwrPDUMPDUQF16SwitchControlOutput | QF16 Switch control output | QF16开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF16 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.20 | hwrPDUMPDUQF17SwitchControlOutput | QF17 Switch control output | QF17开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF17 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.21 | hwrPDUMPDUQF18SwitchControlOutput | QF18 Switch control output | QF18开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF18 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.22 | hwrPDUMPDUQF19SwitchControlOutput | QF19 Switch control output | QF19开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF19 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.23 | hwrPDUMPDUQF20SwitchControlOutput | QF20 Switch control output | QF20开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF20 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.24 | hwrPDUMPDUQF21SwitchControlOutput | QF21 Switch control output | QF21开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF21 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.25 | hwrPDUMPDUQF22SwitchControlOutput | QF22 Switch control output | QF22开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF22 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.26 | hwrPDUMPDUQF23SwitchControlOutput | QF23 Switch control output | QF23开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF23 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.27 | hwrPDUMPDUQF24SwitchControlOutput | QF24 Switch control output | QF24开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF24 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.28 | hwrPDUMPDUClearTheTotalPowerEnergy | Clear the total power energy | 总电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear the total power energy of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.29 | hwrPDUMPDUClearTheTotalPowerEnergyOfC1 | Clear the total power energy of C1 | C1回路电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear the total power energy of C1 of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.30 | hwrPDUMPDUClearTheTotalPowerEnergyOfC2 | Clear the total power energy of C2 | C2回路电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear the total power energy of C2 of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.31 | hwrPDUMPDUQF1ClearPowerEnergyOfOutput | QF1 Clear power energy of output | QF1电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF1 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.32 | hwrPDUMPDUQF2ClearPowerEnergyOfOutput | QF2 Clear power energy of output | QF2电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF2 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.33 | hwrPDUMPDUQF3ClearPowerEnergyOfOutput | QF3 Clear power energy of output | QF3电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF3 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.34 | hwrPDUMPDUQF4ClearPowerEnergyOfOutput | QF4 Clear power energy of output | QF4电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF4 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.35 | hwrPDUMPDUQF5ClearPowerEnergyOfOutput | QF5 Clear power energy of output | QF5电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF5 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.36 | hwrPDUMPDUQF6ClearPowerEnergyOfOutput | QF6 Clear power energy of output | QF6电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF6 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.37 | hwrPDUMPDUQF7ClearPowerEnergyOfOutput | QF7 Clear power energy of output | QF7电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF7 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.38 | hwrPDUMPDUQF8ClearPowerEnergyOfOutput | QF8 Clear power energy of output | QF8电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF8 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.39 | hwrPDUMPDUQF9ClearPowerEnergyOfOutput | QF9 Clear power energy of output | QF9电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF9 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.40 | hwrPDUMPDUQF10ClearPowerEnergyOfOutput | QF10 Clear power energy of output | QF10电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF10 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.41 | hwrPDUMPDUQF11ClearPowerEnergyOfOutput | QF11 Clear power energy of output | QF11电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF11 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.42 | hwrPDUMPDUQF12ClearPowerEnergyOfOutput | QF12 Clear power energy of output | QF12电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF12 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.43 | hwrPDUMPDUQF13ClearPowerEnergyOfOutput | QF13 Clear power energy of output | QF13电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF13 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.44 | hwrPDUMPDUQF14ClearPowerEnergyOfOutput | QF14 Clear power energy of output | QF14电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF14 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.45 | hwrPDUMPDUQF15ClearPowerEnergyOfOutput | QF15 Clear power energy of output | QF15电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF15 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.46 | hwrPDUMPDUQF16ClearPowerEnergyOfOutput | QF16 Clear power energy of output | QF16电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF16 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.47 | hwrPDUMPDUQF17ClearPowerEnergyOfOutput | QF17 Clear power energy of output | QF17电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF17 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.48 | hwrPDUMPDUQF18ClearPowerEnergyOfOutput | QF18 Clear power energy of output | QF18电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF18 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.49 | hwrPDUMPDUQF19ClearPowerEnergyOfOutput | QF19 Clear power energy of output | QF19电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF19 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.50 | hwrPDUMPDUQF20ClearPowerEnergyOfOutput | QF20 Clear power energy of output | QF20电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF20 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.51 | hwrPDUMPDUQF21ClearPowerEnergyOfOutput | QF21 Clear power energy of output | QF21电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF21 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.52 | hwrPDUMPDUQF22ClearPowerEnergyOfOutput | QF22 Clear power energy of output | QF22电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF22 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.53 | hwrPDUMPDUQF23ClearPowerEnergyOfOutput | QF23 Clear power energy of output | QF23电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF23 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.54 | hwrPDUMPDUQF24ClearPowerEnergyOfOutput | QF24 Clear power energy of output | QF24电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF24 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.55 | hwrPDUMPDUUnifyDelayOfPowerOnOrOff | Unify Delay of power on/off | 统一上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | Unify Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.56 | hwrPDUMPDUQF1DelayOfPowerOnOrOff | QF1 Delay of power on/off | QF1上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF1 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.57 | hwrPDUMPDUQF2DelayOfPowerOnOrOff | QF2 Delay of power on/off | QF2上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF2 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.58 | hwrPDUMPDUQF3DelayOfPowerOnOrOff | QF3 Delay of power on/off | QF3上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF3 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.59 | hwrPDUMPDUQF4DelayOfPowerOnOrOff | QF4 Delay of power on/off | QF4上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF4 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.60 | hwrPDUMPDUQF5DelayOfPowerOnOrOff | QF5 Delay of power on/off | QF5上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF5 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.61 | hwrPDUMPDUQF6DelayOfPowerOnOrOff | QF6 Delay of power on/off | QF6上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF6 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.62 | hwrPDUMPDUQF7DelayOfPowerOnOrOff | QF7 Delay of power on/off | QF7上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF7 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.63 | hwrPDUMPDUQF8DelayOfPowerOnOrOff | QF8 Delay of power on/off | QF8上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF8 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.64 | hwrPDUMPDUQF9DelayOfPowerOnOrOff | QF9 Delay of power on/off | QF9上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF9 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.65 | hwrPDUMPDUQF10DelayOfPowerOnOrOff | QF10 Delay of power on/off | QF10上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF10 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.66 | hwrPDUMPDUQF11DelayOfPowerOnOrOff | QF11 Delay of power on/off | QF11上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF11 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.67 | hwrPDUMPDUQF12DelayOfPowerOnOrOff | QF12 Delay of power on/off | QF12上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF12 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.68 | hwrPDUMPDUQF13DelayOfPowerOnOrOff | QF13 Delay of power on/off | QF13上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF13 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.69 | hwrPDUMPDUQF14DelayOfPowerOnOrOff | QF14 Delay of power on/off | QF14上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF14 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.70 | hwrPDUMPDUQF15DelayOfPowerOnOrOff | QF15 Delay of power on/off | QF15上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF15 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.71 | hwrPDUMPDUQF16DelayOfPowerOnOrOff | QF16 Delay of power on/off | QF16上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF16 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.72 | hwrPDUMPDUQF17DelayOfPowerOnOrOff | QF17 Delay of power on/off | QF17上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF17 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.73 | hwrPDUMPDUQF18DelayOfPowerOnOrOff | QF18 Delay of power on/off | QF18上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF18 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.74 | hwrPDUMPDUQF19DelayOfPowerOnOrOff | QF19 Delay of power on/off | QF19上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF19 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.75 | hwrPDUMPDUQF20DelayOfPowerOnOrOff | QF20 Delay of power on/off | QF20上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF20 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.76 | hwrPDUMPDUQF21DelayOfPowerOnOrOff | QF21 Delay of power on/off | QF21上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF21 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.77 | hwrPDUMPDUQF22DelayOfPowerOnOrOff | QF22 Delay of power on/off | QF22上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF22 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.78 | hwrPDUMPDUQF23DelayOfPowerOnOrOff | QF23 Delay of power on/off | QF23上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF23 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.79 | hwrPDUMPDUQF24DelayOfPowerOnOrOff | QF24 Delay of power on/off | QF24上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF24 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.80 | hwrPDUMPDUMinVoltageValue | Min Voltage value | 电压下限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.81 | hwrPDUMPDUMinVoltageValueOfC1 | Min Voltage value of C1 | C1回路电压下限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of C1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.82 | hwrPDUMPDUMinVoltageValueOfC2 | Min Voltage value of C2 | C2回路电压下限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of C2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.83 | hwrPDUMPDUMinVoltageValueOfL1 | Min Voltage value of L1 | L1相电压最小值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of L1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.84 | hwrPDUMPDUMinVoltageValueOfL2 | Min Voltage value of L2 | L2相电压最小值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of L2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.85 | hwrPDUMPDUMinVoltageValueOfL3 | Min Voltage value of L3 | L3相电压最小值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of L3 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.86 | hwrPDUMPDUMaxVoltageValue | Max Voltage value | 电压上限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.87 | hwrPDUMPDUMaxVoltageValueOfC1 | Max Voltage value of C1 | C1回路电压上限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of C1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.88 | hwrPDUMPDUMaxVoltageValueOfC2 | Max Voltage value of C2 | C2回路电压上限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of C2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.89 | hwrPDUMPDUMaxVoltageValueOfL1 | Max Voltage value of L1 | L1相电压最大值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of L1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.90 | hwrPDUMPDUMaxVoltageValueOfL2 | Max Voltage value of L2 | L2相电压最大值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of L2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.91 | hwrPDUMPDUMaxVoltageValueOfL3 | Max Voltage value of L3 | L3相电压最大值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of L3 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.92 | hwrPDUMPDUMinCurrentValue | Min Current value | 电流下限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Min Current value of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.93 | hwrPDUMPDUMinCurrentValueOfC1 | Min Current value of C1 | C1回路电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Min Current value of C1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.94 | hwrPDUMPDUMinCurrentValueOfC2 | Min Current value of C2 | C2回路电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Min Current value of C2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.95 | hwrPDUMPDUMinCurrentValueOfL1 | Min Current value of L1 | L1相电流最小值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Min Current value of L1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.96 | hwrPDUMPDUMinCurrentValueOfL2 | Min Current value of L2 | L2相电流最小值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Min Current value of L2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.97 | hwrPDUMPDUMinCurrentValueOfL3 | Min Current value of L3 | L3相电流最小值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Min Current value of L3 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.98 | hwrPDUMPDUMaxCurrentValue | Max Current value | 电流上限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Max Current value of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.99 | hwrPDUMPDUMaxCurrentValueOfC1 | Max Current value of C1 | C1回路电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Max Current value of C1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.100 | hwrPDUMPDUMaxCurrentValueOfC2 | Max Current value of C2 | C2回路电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Max Current value of C2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.101 | hwrPDUMPDUMaxCurrentValueOfL1 | Max Current value of L1 | L1相电流最大值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Max Current value of L1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.102 | hwrPDUMPDUMaxCurrentValueOfL2 | Max Current value of L2 | L2相电流最大值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Max Current value of L2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.103 | hwrPDUMPDUMaxCurrentValueOfL3 | Max Current value of L3 | L3相电流最大值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Max Current value of L3 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.104 | hwrPDUMPDUQF1MinCurrentValueOfOutput | QF1 Min Current value of output | QF1电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF1 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.105 | hwrPDUMPDUQF2MinCurrentValueOfOutput | QF2 Min Current value of output | QF2电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF2 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.106 | hwrPDUMPDUQF3MinCurrentValueOfOutput | QF3 Min Current value of output | QF3电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF3 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.107 | hwrPDUMPDUQF4MinCurrentValueOfOutput | QF4 Min Current value of output | QF4电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF4 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.108 | hwrPDUMPDUQF5MinCurrentValueOfOutput | QF5 Min Current value of output | QF5电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF5 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.109 | hwrPDUMPDUQF6MinCurrentValueOfOutput | QF6 Min Current value of output | QF6电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF6 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.110 | hwrPDUMPDUQF7MinCurrentValueOfOutput | QF7 Min Current value of output | QF7电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF7 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.111 | hwrPDUMPDUQF8MinCurrentValueOfOutput | QF8 Min Current value of output | QF8电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF8 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.112 | hwrPDUMPDUQF9MinCurrentValueOfOutput | QF9 Min Current value of output | QF9电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF9 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.113 | hwrPDUMPDUQF10MinCurrentValueOfOutput | QF10 Min Current value of output | QF10电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF10 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.114 | hwrPDUMPDUQF11MinCurrentValueOfOutput | QF11 Min Current value of output | QF11电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF11 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.115 | hwrPDUMPDUQF12MinCurrentValueOfOutput | QF12 Min Current value of output | QF12电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF12 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.116 | hwrPDUMPDUQF13MinCurrentValueOfOutput | QF13 Min Current value of output | QF13电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF13 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.117 | hwrPDUMPDUQF14MinCurrentValueOfOutput | QF14 Min Current value of output | QF14电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF14 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.118 | hwrPDUMPDUQF15MinCurrentValueOfOutput | QF15 Min Current value of output | QF15电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF15 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.119 | hwrPDUMPDUQF16MinCurrentValueOfOutput | QF16 Min Current value of output | QF16电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF16 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.120 | hwrPDUMPDUQF17MinCurrentValueOfOutput | QF17 Min Current value of output | QF17电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF17 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.121 | hwrPDUMPDUQF18MinCurrentValueOfOutput | QF18 Min Current value of output | QF18电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF18 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.122 | hwrPDUMPDUQF19MinCurrentValueOfOutput | QF19 Min Current value of output | QF19电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF19 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.123 | hwrPDUMPDUQF20MinCurrentValueOfOutput | QF20 Min Current value of output | QF20电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF20 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.124 | hwrPDUMPDUQF21MinCurrentValueOfOutput | QF21 Min Current value of output | QF21电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF21 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.125 | hwrPDUMPDUQF22MinCurrentValueOfOutput | QF22 Min Current value of output | QF22电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF22 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.126 | hwrPDUMPDUQF23MinCurrentValueOfOutput | QF23 Min Current value of output | QF23电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF23 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.127 | hwrPDUMPDUQF24MinCurrentValueOfOutput | QF24 Min Current value of output | QF24电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF24 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.128 | hwrPDUMPDUQF1MaxCurrentValueOfOutput | QF1 Max Current value of output | QF1电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF1 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.129 | hwrPDUMPDUQF2MaxCurrentValueOfOutput | QF2 Max Current value of output | QF2电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF2 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.130 | hwrPDUMPDUQF3MaxCurrentValueOfOutput | QF3 Max Current value of output | QF3电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF3 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.131 | hwrPDUMPDUQF4MaxCurrentValueOfOutput | QF4 Max Current value of output | QF4电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF4 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.132 | hwrPDUMPDUQF5MaxCurrentValueOfOutput | QF5 Max Current value of output | QF5电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF5 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.133 | hwrPDUMPDUQF6MaxCurrentValueOfOutput | QF6 Max Current value of output | QF6电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF6 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.134 | hwrPDUMPDUQF7MaxCurrentValueOfOutput | QF7 Max Current value of output | QF7电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF7 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.135 | hwrPDUMPDUQF8MaxCurrentValueOfOutput | QF8 Max Current value of output | QF8电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF8 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.136 | hwrPDUMPDUQF9MaxCurrentValueOfOutput | QF9 Max Current value of output | QF9电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF9 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.137 | hwrPDUMPDUQF10MaxCurrentValueOfOutput | QF10 Max Current value of output | QF10电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF10 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.138 | hwrPDUMPDUQF11MaxCurrentValueOfOutput | QF11 Max Current value of output | QF11电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF11 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.139 | hwrPDUMPDUQF12MaxCurrentValueOfOutput | QF12 Max Current value of output | QF12电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF12 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.140 | hwrPDUMPDUQF13MaxCurrentValueOfOutput | QF13 Max Current value of output | QF13电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF13 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.141 | hwrPDUMPDUQF14MaxCurrentValueOfOutput | QF14 Max Current value of output | QF14电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF14 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.142 | hwrPDUMPDUQF15MaxCurrentValueOfOutput | QF15 Max Current value of output | QF15电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF15 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.143 | hwrPDUMPDUQF16MaxCurrentValueOfOutput | QF16 Max Current value of output | QF16电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF16 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.144 | hwrPDUMPDUQF17MaxCurrentValueOfOutput | QF17 Max Current value of output | QF17电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF17 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.145 | hwrPDUMPDUQF18MaxCurrentValueOfOutput | QF18 Max Current value of output | QF18电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF18 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.146 | hwrPDUMPDUQF19MaxCurrentValueOfOutput | QF19 Max Current value of output | QF19电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF19 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.147 | hwrPDUMPDUQF20MaxCurrentValueOfOutput | QF20 Max Current value of output | QF20电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF20 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.148 | hwrPDUMPDUQF21MaxCurrentValueOfOutput | QF21 Max Current value of output | QF21电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF21 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.149 | hwrPDUMPDUQF22MaxCurrentValueOfOutput | QF22 Max Current value of output | QF22电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF22 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.150 | hwrPDUMPDUQF23MaxCurrentValueOfOutput | QF23 Max Current value of output | QF23电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF23 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.151 | hwrPDUMPDUQF24MaxCurrentValueOfOutput | QF24 Max Current value of output | QF24电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF24 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.152 | hwrPDUMPDUParentDeviceId | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Parent device ID of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.153 | hwrPDUMPDUSingleOrThreePhaseMarkCfg | Single/Three phase mark | 单三相标识 | 1-Read_Write | 读写 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | Single or Three phase mark of the device config table for the rPDU-MPDU. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.154 | hwrPDUMPDUDevicename | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device name for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.220 | hwrPDUMPDUConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-MPDU.

## rPDU-PN
rPDU-PN
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.50 | rPDUPN | rPDU-PN | rPDU-PN | / | / | / | / | rPDU-PN Equipment.
1.3.6.1.4.1.2011.6.178.1.1.50.1 | hwrPDUPNRunningTable | / | / |  |  | / | / | The running table of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.1 | hwrPDUPNRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.2 | hwrPDUPNVoltageValue | Voltage value | 电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | Voltage value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.3 | hwrPDUPNCurrentValue | Current value | 电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.4 | hwrPDUPNActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Active power of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.5 | hwrPDUPNReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Reactive power of the device config table for the rPDU-PN. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.6 | hwrPDUPNPowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.7 | hwrPDUPNPowerEnergyValue | Power energy value | 有功电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Power energy value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.8 | hwrPDUPNFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 4500..6500 | 4500..6500 | Frequency of the device config table for the rPDU-PN.Multiple:100. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.9 | hwrPDUPNL1VoltageValue | L1 Voltage value | L1相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L1 Voltage value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.10 | hwrPDUPNL2VoltageValue | L2 Voltage value | L2相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L2 Voltage value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.11 | hwrPDUPNL3VoltageValue | L3 Voltage value | L3相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L3 Voltage value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.12 | hwrPDUPNL1CurrentValue | L1 Current value | L1相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L1 Current value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.13 | hwrPDUPNL2CurrentValue | L2 Current value | L2相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L2 Current value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.14 | hwrPDUPNL3CurrentValue | L3 Current value | L3相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L3 Current value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.15 | hwrPDUPNL1ActivePower | L1 Active power | L1相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 Active power of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.16 | hwrPDUPNL2ActivePower | L2 Active power | L2相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 Active power of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.17 | hwrPDUPNL3ActivePower | L3 Active power | L3相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 Active power of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.18 | hwrPDUPNL1ReactivePower | L1 Reactive power | L1相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 Reactive power of the device config table for the rPDU-PN. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.19 | hwrPDUPNL2ReactivePower | L2 Reactive power | L2相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 Reactive power of the device config table for the rPDU-PN. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.20 | hwrPDUPNL3ReactivePower | L3 Reactive power | L3相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 Reactive power of the device config table for the rPDU-PN. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.21 | hwrPDUPNL1PowerFactor | L1 Power factor | L1相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L1 Power factor of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.22 | hwrPDUPNL2PowerFactor | L2 Power factor | L2相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L2 Power factor of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.23 | hwrPDUPNL3PowerFactor | L3 Power factor | L3相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L3 Power factor of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.24 | hwrPDUPN1CurrentOfOutput | 1 Current of output | 输出位1电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 1 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.25 | hwrPDUPN2CurrentOfOutput | 2 Current of output | 输出位2电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 2 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.26 | hwrPDUPN3CurrentOfOutput | 3 Current of output | 输出位3电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 3 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.27 | hwrPDUPN4CurrentOfOutput | 4 Current of output | 输出位4电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 4 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.28 | hwrPDUPN5CurrentOfOutput | 5 Current of output | 输出位5电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 5 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.29 | hwrPDUPN6CurrentOfOutput | 6 Current of output | 输出位6电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 6 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.30 | hwrPDUPN7CurrentOfOutput | 7 Current of output | 输出位7电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 7 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.31 | hwrPDUPN8CurrentOfOutput | 8 Current of output | 输出位8电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 8 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.32 | hwrPDUPN9CurrentOfOutput | 9 Current of output | 输出位9电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 9 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.33 | hwrPDUPN10CurrentOfOutput | 10 Current of output | 输出位10电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 10 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.34 | hwrPDUPN11CurrentOfOutput | 11 Current of output | 输出位11电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 11 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.35 | hwrPDUPN12CurrentOfOutput | 12 Current of output | 输出位12电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 12 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.36 | hwrPDUPN13CurrentOfOutput | 13 Current of output | 输出位13电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 13 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.37 | hwrPDUPN14CurrentOfOutput | 14 Current of output | 输出位14电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 14 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.38 | hwrPDUPN15CurrentOfOutput | 15 Current of output | 输出位15电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 15 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.39 | hwrPDUPN16CurrentOfOutput | 16 Current of output | 输出位16电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 16 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.40 | hwrPDUPN17CurrentOfOutput | 17 Current of output | 输出位17电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 17 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.41 | hwrPDUPN18CurrentOfOutput | 18 Current of output | 输出位18电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 18 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.42 | hwrPDUPN19CurrentOfOutput | 19 Current of output | 输出位19电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 19 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.43 | hwrPDUPN20CurrentOfOutput | 20 Current of output | 输出位20电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 20 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.44 | hwrPDUPN21CurrentOfOutput | 21 Current of output | 输出位21电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 21 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.45 | hwrPDUPN22CurrentOfOutput | 22 Current of output | 输出位22电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 22 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.46 | hwrPDUPN23CurrentOfOutput | 23 Current of output | 输出位23电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 23 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.47 | hwrPDUPN24CurrentOfOutput | 24 Current of output | 输出位24电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 24 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.48 | hwrPDUPN25CurrentOfOutput | 25 Current of output | 输出位25电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 25 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.49 | hwrPDUPN26CurrentOfOutput | 26 Current of output | 输出位26电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 26 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.50 | hwrPDUPN27CurrentOfOutput | 27 Current of output | 输出位27电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 27 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.51 | hwrPDUPN28CurrentOfOutput | 28 Current of output | 输出位28电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 28 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.52 | hwrPDUPN29CurrentOfOutput | 29 Current of output | 输出位29电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 29 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.53 | hwrPDUPN30CurrentOfOutput | 30 Current of output | 输出位30电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 30 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.54 | hwrPDUPN31CurrentOfOutput | 31 Current of output | 输出位31电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 31 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.55 | hwrPDUPN32CurrentOfOutput | 32 Current of output | 输出位32电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 32 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.56 | hwrPDUPN33CurrentOfOutput | 33 Current of output | 输出位33电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 33 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.57 | hwrPDUPN34CurrentOfOutput | 34 Current of output | 输出位34电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 34 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.58 | hwrPDUPN35CurrentOfOutput | 35 Current of output | 输出位35电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 35 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.59 | hwrPDUPN36CurrentOfOutput | 36 Current of output | 输出位36电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 36 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.60 | hwrPDUPN1ElectricalEnergyOfOutput | 1 Electrical energy of output | 输出位1电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 1 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.61 | hwrPDUPN2ElectricalEnergyOfOutput | 2 Electrical energy of output | 输出位2电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 2 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.62 | hwrPDUPN3ElectricalEnergyOfOutput | 3 Electrical energy of output | 输出位3电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 3 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.63 | hwrPDUPN4ElectricalEnergyOfOutput | 4 Electrical energy of output | 输出位4电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 4 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.64 | hwrPDUPN5ElectricalEnergyOfOutput | 5 Electrical energy of output | 输出位5电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 5 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.65 | hwrPDUPN6ElectricalEnergyOfOutput | 6 Electrical energy of output | 输出位6电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 6 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.66 | hwrPDUPN7ElectricalEnergyOfOutput | 7 Electrical energy of output | 输出位7电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 7 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.67 | hwrPDUPN8ElectricalEnergyOfOutput | 8 Electrical energy of output | 输出位8电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 8 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.68 | hwrPDUPN9ElectricalEnergyOfOutput | 9 Electrical energy of output | 输出位9电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 9 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.69 | hwrPDUPN10ElectricalEnergyOfOutput | 10 Electrical energy of output | 输出位10电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 10 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.70 | hwrPDUPN11ElectricalEnergyOfOutput | 11 Electrical energy of output | 输出位11电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 11 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.71 | hwrPDUPN12ElectricalEnergyOfOutput | 12 Electrical energy of output | 输出位12电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 12 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.72 | hwrPDUPN13ElectricalEnergyOfOutput | 13 Electrical energy of output | 输出位13电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 13 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.73 | hwrPDUPN14ElectricalEnergyOfOutput | 14 Electrical energy of output | 输出位14电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 14 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.74 | hwrPDUPN15ElectricalEnergyOfOutput | 15 Electrical energy of output | 输出位15电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 15 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.75 | hwrPDUPN16ElectricalEnergyOfOutput | 16 Electrical energy of output | 输出位16电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 16 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.76 | hwrPDUPN17ElectricalEnergyOfOutput | 17 Electrical energy of output | 输出位17电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 17 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.77 | hwrPDUPN18ElectricalEnergyOfOutput | 18 Electrical energy of output | 输出位18电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 18 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.78 | hwrPDUPN19ElectricalEnergyOfOutput | 19 Electrical energy of output | 输出位19电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 19 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.79 | hwrPDUPN20ElectricalEnergyOfOutput | 20 Electrical energy of output | 输出位20电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 20 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.80 | hwrPDUPN21ElectricalEnergyOfOutput | 21 Electrical energy of output | 输出位21电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 21 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.81 | hwrPDUPN22ElectricalEnergyOfOutput | 22 Electrical energy of output | 输出位22电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 22 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.82 | hwrPDUPN23ElectricalEnergyOfOutput | 23 Electrical energy of output | 输出位23电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 23 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.83 | hwrPDUPN24ElectricalEnergyOfOutput | 24 Electrical energy of output | 输出位24电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 24 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.84 | hwrPDUPN25ElectricalEnergyOfOutput | 25 Electrical energy of output | 输出位25电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 25 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.85 | hwrPDUPN26ElectricalEnergyOfOutput | 26 Electrical energy of output | 输出位26电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 26 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.86 | hwrPDUPN27ElectricalEnergyOfOutput | 27 Electrical energy of output | 输出位27电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 27 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.87 | hwrPDUPN28ElectricalEnergyOfOutput | 28 Electrical energy of output | 输出位28电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 28 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.88 | hwrPDUPN29ElectricalEnergyOfOutput | 29 Electrical energy of output | 输出位29电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 29 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.89 | hwrPDUPN30ElectricalEnergyOfOutput | 30 Electrical energy of output | 输出位30电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 30 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.90 | hwrPDUPN31ElectricalEnergyOfOutput | 31 Electrical energy of output | 输出位31电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 31 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.91 | hwrPDUPN32ElectricalEnergyOfOutput | 32 Electrical energy of output | 输出位32电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 32 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.92 | hwrPDUPN33ElectricalEnergyOfOutput | 33 Electrical energy of output | 输出位33电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 33 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.93 | hwrPDUPN34ElectricalEnergyOfOutput | 34 Electrical energy of output | 输出位34电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 34 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.94 | hwrPDUPN35ElectricalEnergyOfOutput | 35 Electrical energy of output | 输出位35电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 35 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.95 | hwrPDUPN36ElectricalEnergyOfOutput | 36 Electrical energy of output | 输出位36电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 36 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.96 | hwrPDUPN1ActivePowerOfOutput | 1 Active power of output | 输出位1有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 1 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.97 | hwrPDUPN2ActivePowerOfOutput | 2 Active power of output | 输出位2有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 2 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.98 | hwrPDUPN3ActivePowerOfOutput | 3 Active power of output | 输出位3有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 3 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.99 | hwrPDUPN4ActivePowerOfOutput | 4 Active power of output | 输出位4有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 4 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.100 | hwrPDUPN5ActivePowerOfOutput | 5 Active power of output | 输出位5有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 5 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.101 | hwrPDUPN6ActivePowerOfOutput | 6 Active power of output | 输出位6有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 6 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.102 | hwrPDUPN7ActivePowerOfOutput | 7 Active power of output | 输出位7有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 7 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.103 | hwrPDUPN8ActivePowerOfOutput | 8 Active power of output | 输出位8有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 8 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.104 | hwrPDUPN9ActivePowerOfOutput | 9 Active power of output | 输出位9有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 9 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.105 | hwrPDUPN10ActivePowerOfOutput | 10 Active power of output | 输出位10有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 10 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.106 | hwrPDUPN11ActivePowerOfOutput | 11 Active power of output | 输出位11有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 11 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.107 | hwrPDUPN12ActivePowerOfOutput | 12 Active power of output | 输出位12有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 12 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.108 | hwrPDUPN13ActivePowerOfOutput | 13 Active power of output | 输出位13有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 13 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.109 | hwrPDUPN14ActivePowerOfOutput | 14 Active power of output | 输出位14有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 14 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.110 | hwrPDUPN15ActivePowerOfOutput | 15 Active power of output | 输出位15有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 15 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.111 | hwrPDUPN16ActivePowerOfOutput | 16 Active power of output | 输出位16有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 16 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.112 | hwrPDUPN17ActivePowerOfOutput | 17 Active power of output | 输出位17有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 17 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.113 | hwrPDUPN18ActivePowerOfOutput | 18 Active power of output | 输出位18有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 18 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.114 | hwrPDUPN19ActivePowerOfOutput | 19 Active power of output | 输出位19有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 19 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.115 | hwrPDUPN20ActivePowerOfOutput | 20 Active power of output | 输出位20有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 20 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.116 | hwrPDUPN21ActivePowerOfOutput | 21 Active power of output | 输出位21有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 21 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.117 | hwrPDUPN22ActivePowerOfOutput | 22 Active power of output | 输出位22有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 22 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.118 | hwrPDUPN23ActivePowerOfOutput | 23 Active power of output | 输出位23有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 23 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.119 | hwrPDUPN24ActivePowerOfOutput | 24 Active power of output | 输出位24有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 24 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.120 | hwrPDUPN25ActivePowerOfOutput | 25 Active power of output | 输出位25有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 25 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.121 | hwrPDUPN26ActivePowerOfOutput | 26 Active power of output | 输出位26有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 26 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.122 | hwrPDUPN27ActivePowerOfOutput | 27 Active power of output | 输出位27有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 27 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.123 | hwrPDUPN28ActivePowerOfOutput | 28 Active power of output | 输出位28有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 28 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.124 | hwrPDUPN29ActivePowerOfOutput | 29 Active power of output | 输出位29有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 29 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.125 | hwrPDUPN30ActivePowerOfOutput | 30 Active power of output | 输出位30有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 30 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.126 | hwrPDUPN31ActivePowerOfOutput | 31 Active power of output | 输出位31有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 31 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.127 | hwrPDUPN32ActivePowerOfOutput | 32 Active power of output | 输出位32有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 32 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.128 | hwrPDUPN33ActivePowerOfOutput | 33 Active power of output | 输出位33有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 33 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.129 | hwrPDUPN34ActivePowerOfOutput | 34 Active power of output | 输出位34有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 34 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.130 | hwrPDUPN35ActivePowerOfOutput | 35 Active power of output | 输出位35有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 35 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.131 | hwrPDUPN36ActivePowerOfOutput | 36 Active power of output | 输出位36有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 36 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.132 | hwrPDUPN1PowerFactorOfOutput | 1 Power factor of output | 输出位1功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 1 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.133 | hwrPDUPN2PowerFactorOfOutput | 2 Power factor of output | 输出位2功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 2 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.134 | hwrPDUPN3PowerFactorOfOutput | 3 Power factor of output | 输出位3功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 3 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.135 | hwrPDUPN4PowerFactorOfOutput | 4 Power factor of output | 输出位4功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 4 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.136 | hwrPDUPN5PowerFactorOfOutput | 5 Power factor of output | 输出位5功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 5 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.137 | hwrPDUPN6PowerFactorOfOutput | 6 Power factor of output | 输出位6功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 6 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.138 | hwrPDUPN7PowerFactorOfOutput | 7 Power factor of output | 输出位7功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 7 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.139 | hwrPDUPN8PowerFactorOfOutput | 8 Power factor of output | 输出位8功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 8 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.140 | hwrPDUPN9PowerFactorOfOutput | 9 Power factor of output | 输出位9功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 9 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.141 | hwrPDUPN10PowerFactorOfOutput | 10 Power factor of output | 输出位10功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 10 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.142 | hwrPDUPN11PowerFactorOfOutput | 11 Power factor of output | 输出位11功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 11 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.143 | hwrPDUPN12PowerFactorOfOutput | 12 Power factor of output | 输出位12功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 12 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.144 | hwrPDUPN13PowerFactorOfOutput | 13 Power factor of output | 输出位13功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 13 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.145 | hwrPDUPN14PowerFactorOfOutput | 14 Power factor of output | 输出位14功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 14 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.146 | hwrPDUPN15PowerFactorOfOutput | 15 Power factor of output | 输出位15功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 15 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.147 | hwrPDUPN16PowerFactorOfOutput | 16 Power factor of output | 输出位16功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 16 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.148 | hwrPDUPN17PowerFactorOfOutput | 17 Power factor of output | 输出位17功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 17 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.149 | hwrPDUPN18PowerFactorOfOutput | 18 Power factor of output | 输出位18功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 18 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.150 | hwrPDUPN19PowerFactorOfOutput | 19 Power factor of output | 输出位19功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 19 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.151 | hwrPDUPN20PowerFactorOfOutput | 20 Power factor of output | 输出位20功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 20 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.152 | hwrPDUPN21PowerFactorOfOutput | 21 Power factor of output | 输出位21功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 21 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.153 | hwrPDUPN22PowerFactorOfOutput | 22 Power factor of output | 输出位22功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 22 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.154 | hwrPDUPN23PowerFactorOfOutput | 23 Power factor of output | 输出位23功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 23 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.155 | hwrPDUPN24PowerFactorOfOutput | 24 Power factor of output | 输出位24功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 24 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.156 | hwrPDUPN25PowerFactorOfOutput | 25 Power factor of output | 输出位25功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 25 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.157 | hwrPDUPN26PowerFactorOfOutput | 26 Power factor of output | 输出位26功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 26 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.158 | hwrPDUPN27PowerFactorOfOutput | 27 Power factor of output | 输出位27功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 27 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.159 | hwrPDUPN28PowerFactorOfOutput | 28 Power factor of output | 输出位28功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 28 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.160 | hwrPDUPN29PowerFactorOfOutput | 29 Power factor of output | 输出位29功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 29 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.161 | hwrPDUPN30PowerFactorOfOutput | 30 Power factor of output | 输出位30功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 30 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.162 | hwrPDUPN31PowerFactorOfOutput | 31 Power factor of output | 输出位31功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 31 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.163 | hwrPDUPN32PowerFactorOfOutput | 32 Power factor of output | 输出位32功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 32 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.164 | hwrPDUPN33PowerFactorOfOutput | 33 Power factor of output | 输出位33功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 33 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.165 | hwrPDUPN34PowerFactorOfOutput | 34 Power factor of output | 输出位34功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 34 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.166 | hwrPDUPN35PowerFactorOfOutput | 35 Power factor of output | 输出位35功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 35 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.167 | hwrPDUPN36PowerFactorOfOutput | 36 Power factor of output | 输出位36功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 36 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.168 | hwrPDUPN1SwitchStatusOfOutput | 1 Switch status of output | 输出位1开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 1 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.169 | hwrPDUPN2SwitchStatusOfOutput | 2 Switch status of output | 输出位2开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 2 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.170 | hwrPDUPN3SwitchStatusOfOutput | 3 Switch status of output | 输出位3开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 3 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.171 | hwrPDUPN4SwitchStatusOfOutput | 4 Switch status of output | 输出位4开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 4 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.172 | hwrPDUPN5SwitchStatusOfOutput | 5 Switch status of output | 输出位5开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 5 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.173 | hwrPDUPN6SwitchStatusOfOutput | 6 Switch status of output | 输出位6开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 6 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.174 | hwrPDUPN7SwitchStatusOfOutput | 7 Switch status of output | 输出位7开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 7 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.175 | hwrPDUPN8SwitchStatusOfOutput | 8 Switch status of output | 输出位8开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 8 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.176 | hwrPDUPN9SwitchStatusOfOutput | 9 Switch status of output | 输出位9开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 9 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.177 | hwrPDUPN10SwitchStatusOfOutput | 10 Switch status of output | 输出位10开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 10 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.178 | hwrPDUPN11SwitchStatusOfOutput | 11 Switch status of output | 输出位11开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 11 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.179 | hwrPDUPN12SwitchStatusOfOutput | 12 Switch status of output | 输出位12开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 12 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.180 | hwrPDUPN13SwitchStatusOfOutput | 13 Switch status of output | 输出位13开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 13 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.181 | hwrPDUPN14SwitchStatusOfOutput | 14 Switch status of output | 输出位14开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 14 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.182 | hwrPDUPN15SwitchStatusOfOutput | 15 Switch status of output | 输出位15开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 15 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.183 | hwrPDUPN16SwitchStatusOfOutput | 16 Switch status of output | 输出位16开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 16 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.184 | hwrPDUPN17SwitchStatusOfOutput | 17 Switch status of output | 输出位17开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 17 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.185 | hwrPDUPN18SwitchStatusOfOutput | 18 Switch status of output | 输出位18开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 18 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.186 | hwrPDUPN19SwitchStatusOfOutput | 19 Switch status of output | 输出位19开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 19 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.187 | hwrPDUPN20SwitchStatusOfOutput | 20 Switch status of output | 输出位20开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 20 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.188 | hwrPDUPN21SwitchStatusOfOutput | 21 Switch status of output | 输出位21开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 21 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.189 | hwrPDUPN22SwitchStatusOfOutput | 22 Switch status of output | 输出位22开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 22 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.190 | hwrPDUPN23SwitchStatusOfOutput | 23 Switch status of output | 输出位23开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 23 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.191 | hwrPDUPN24SwitchStatusOfOutput | 24 Switch status of output | 输出位24开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 24 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.192 | hwrPDUPN25SwitchStatusOfOutput | 25 Switch status of output | 输出位25开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 25 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.193 | hwrPDUPN26SwitchStatusOfOutput | 26 Switch status of output | 输出位26开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 26 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.194 | hwrPDUPN27SwitchStatusOfOutput | 27 Switch status of output | 输出位27开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 27 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.195 | hwrPDUPN28SwitchStatusOfOutput | 28 Switch status of output | 输出位28开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 28 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.196 | hwrPDUPN29SwitchStatusOfOutput | 29 Switch status of output | 输出位29开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 29 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.197 | hwrPDUPN30SwitchStatusOfOutput | 30 Switch status of output | 输出位30开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 30 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.198 | hwrPDUPN31SwitchStatusOfOutput | 31 Switch status of output | 输出位31开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 31 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.199 | hwrPDUPN32SwitchStatusOfOutput | 32 Switch status of output | 输出位32开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 32 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.200 | hwrPDUPN33SwitchStatusOfOutput | 33 Switch status of output | 输出位33开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 33 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.201 | hwrPDUPN34SwitchStatusOfOutput | 34 Switch status of output | 输出位34开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 34 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.202 | hwrPDUPN35SwitchStatusOfOutput | 35 Switch status of output | 输出位35开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 35 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.203 | hwrPDUPN36SwitchStatusOfOutput | 36 Switch status of output | 输出位36开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 36 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.204 | hwrPDUPNCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the rPDU-PN. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.205 | hwrPDUPNPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.206 | hwrPDUPNModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.207 | hwrPDUPNSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Software version of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.208 | hwrPDUPNHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Hardware version of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.209 | hwrPDUPNType | Type | 型号 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Type of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.210 | hwrPDUPNRatedVoltage | Rated voltage | 额定电压 | 0-Read_Only | 只读 | 0..380 | 0..380 | Rated voltage of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.211 | hwrPDUPNRatedCurrent | Rated current | 额定电流 | 0-Read_Only | 只读 | 0..63 | 0..63 | Rated current of the device config table for the rPDU-PN. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.212 | hwrPDUPNRatedFrequency | Rated frequency | 额定频率 | 0-Read_Only | 只读 | 0..50 | 0..50 | Rated frequency of the device config table for the rPDU-PN. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.213 | hwrPDUPNNumbersOfOutput | Numbers of output | 输出位数 | 0-Read_Only | 只读 | 0..48 | 0..48 | Numbers of output of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.214 | hwrPDUPNSwitchFunctionOfOutput | Switch function of output | 输出位开关功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Switch function of output of the device config table for the rPDU-PN. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.215 | hwrPDUPNCurrentMeasuringFunctionOfOutput | Current measuring function of output | 输出位电流计量功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Current measuring function of output of the device config table for the rPDU-PN. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.216 | hwrPDUPNElectricalDegreeMeasuringFunctionOfOutput | Electrical degree measuring function of output | 输出位电度计量功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Electrical degree measuring function of output of the device config table for the rPDU-PN. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.220 | hwrPDUPNRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2 | hwrPDUPNConfigTable | / | / |  |  | / | / | The config table of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.1 | hwrPDUPNConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.2 | hwrPDUPNInputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | of the device config table for the rPDU-PN. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.3 | hwrPDUPNBuzzerSwitch | Buzzer switch | 蜂鸣器开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Buzzer switch of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.4 | hwrPDUPNAlarmDryContactSwitch | Alarm dry-contact switch | 报警干接点开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Alarm dry-contact switch of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.5 | hwrPDUPNCurrentUpperLimitAlarmSetValue | Current upper limit alarm set value | 电流上限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | Current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNCurrentUpperLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608,the new version is used. The value range of hwrPDUPNCurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNRatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.6 | hwrPDUPNCurrentDownLimitAlarmSetValue | Current down limit alarm set value | 电流下限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | Current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNCurrentDownLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNCurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNCurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.7 | hwrPDUPNL1CurrentUpperLimitAlarmSetValue | L1 Current upper limit alarm set value | L1相电流上限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L1 Current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL1CurrentUpperLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608,the new version is used. The value range of hwrPDUPNL1CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNRatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.8 | hwrPDUPNL1CurrentDownLimitAlarmSetValue | L1 Current down limit alarm set value | L1相电流下限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L1 Current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL1CurrentDownLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608,the new version is used. The value range of hwrPDUPNL1CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNL1CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.9 | hwrPDUPNL2CurrentUpperLimitAlarmSetValue | L2 Current upper limit alarm set value | L2相电流上限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L2 Current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL2CurrentUpperLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNL2CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNRatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.10 | hwrPDUPNL2CurrentDownLimitAlarmSetValue | L2 Current down limit alarm set value | L2相电流下限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L2 Current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10 Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL2CurrentDownLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNL2CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNL2CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.11 | hwrPDUPNL3CurrentUpperLimitAlarmSetValue | L3 Current upper limit alarm set value | L3相电流上限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L3 Current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL3CurrentUpperLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNL3CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNRatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.12 | hwrPDUPNL3CurrentDownLimitAlarmSetValue | L3 Current down limit alarm set value | L3相电流下限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L3 Current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL3CurrentDownLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNL3CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNL3CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.13 | hwrPDUPNOutput1CurrentUpperLimitAlarmSetValue | Output 1 current upper limit alarm set value | 输出位1电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 1 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput1CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput1CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput1RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.14 | hwrPDUPNOutput1CurrentDownLimitAlarmSetValue | Output 1 current down limit alarm set value | 输出位1电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 1 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608,the old version is used. The value range of hwrPDUPNOutput1CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput1CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput1CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.15 | hwrPDUPNOutput2CurrentUpperLimitAlarmSetValue | Output 2 current upper limit alarm set value | 输出位2电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 2 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput2CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput2CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput2RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.16 | hwrPDUPNOutput2CurrentDownLimitAlarmSetValue | Output 2 current down limit alarm set value | 输出位2电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 2 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput2CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput2CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput2CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.17 | hwrPDUPNOutput3CurrentUpperLimitAlarmSetValue | Output 3 current upper limit alarm set value | 输出位3电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 3 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput3CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput3CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput3RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.18 | hwrPDUPNOutput3CurrentDownLimitAlarmSetValue | Output 3 current down limit alarm set value | 输出位3电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 3 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput3CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput3CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput3CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.19 | hwrPDUPNOutput4CurrentUpperLimitAlarmSetValue | Output 4 current upper limit alarm set value | 输出位4电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 4 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput4CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput4CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput4RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.20 | hwrPDUPNOutput4CurrentDownLimitAlarmSetValue | Output 4 current down limit alarm set value | 输出位4电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 4 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput4CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput4CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput4CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.21 | hwrPDUPNOutput5CurrentUpperLimitAlarmSetValue | Output 5 current upper limit alarm set value | 输出位5电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 5 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput5CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput5CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput5RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.22 | hwrPDUPNOutput5CurrentDownLimitAlarmSetValue | Output 5 current down limit alarm set value | 输出位5电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 5 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput5CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput5CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput5CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.23 | hwrPDUPNOutput6CurrentUpperLimitAlarmSetValue | Output 6 current upper limit alarm set value | 输出位6电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | Output 6 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput6CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput6CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput6RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.24 | hwrPDUPNOutput6CurrentDownLimitAlarmSetValue | Output 6 current down limit alarm set value | 输出位6电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 6 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput6CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput6CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput6CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.25 | hwrPDUPNOutput7CurrentUpperLimitAlarmSetValue | Output 7 current upper limit alarm set value | 输出位7电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 7 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput7CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput7CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput7RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.26 | hwrPDUPNOutput7CurrentDownLimitAlarmSetValue | Output 7 current down limit alarm set value | 输出位7电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 7 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput7CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput7CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput7CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.27 | hwrPDUPNOutput8CurrentUpperLimitAlarmSetValue | Output 8 current upper limit alarm set value | 输出位8电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 8 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput8CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput8CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput8RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.28 | hwrPDUPNOutput8CurrentDownLimitAlarmSetValue | Output 8 current down limit alarm set value | 输出位8电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 8 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput8CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput8CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput8CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.29 | hwrPDUPNOutput9CurrentUpperLimitAlarmSetValue | Output 9 current upper limit alarm set value | 输出位9电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 9 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput9CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput9CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput9RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.30 | hwrPDUPNOutput9CurrentDownLimitAlarmSetValue | Output 9 current down limit alarm set value | 输出位9电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 9 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput9CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput9CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput9CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.31 | hwrPDUPNOutput10CurrentUpperLimitAlarmSetValue | Output 10 current upper limit alarm set value | 输出位10电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 10 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput10CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput10CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput10RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.32 | hwrPDUPNOutput10CurrentDownLimitAlarmSetValue | Output 10 current down limit alarm set value | 输出位10电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 10 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput10CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput10CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput10CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.33 | hwrPDUPNOutput11CurrentUpperLimitAlarmSetValue | Output 11 current upper limit alarm set value | 输出位11电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 11 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput11CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput11CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput11RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.34 | hwrPDUPNOutput11CurrentDownLimitAlarmSetValue | Output 11 current down limit alarm set value | 输出位11电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 11 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput11CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput11CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput11CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.35 | hwrPDUPNOutput12CurrentUpperLimitAlarmSetValue | Output 12 current upper limit alarm set value | 输出位12电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 12 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput12CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput12CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput12RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.36 | hwrPDUPNOutput12CurrentDownLimitAlarmSetValue | Output 12 current down limit alarm set value | 输出位12电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 12 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput2CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput12CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput12CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.37 | hwrPDUPNOutput13CurrentUpperLimitAlarmSetValue | Output 13 current upper limit alarm set value | 输出位13电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 13 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput13CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput13CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput13RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.38 | hwrPDUPNOutput13CurrentDownLimitAlarmSetValue | Output 13 current down limit alarm set value | 输出位13电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 13 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput13CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput13CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput13CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.39 | hwrPDUPNOutput14CurrentUpperLimitAlarmSetValue | Output 14 current upper limit alarm set value | 输出位14电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 14 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput14CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput14CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput14RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.40 | hwrPDUPNOutput14CurrentDownLimitAlarmSetValue | Output 14 current down limit alarm set value | 输出位14电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 14 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput14CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput14CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput14CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.41 | hwrPDUPNOutput15CurrentUpperLimitAlarmSetValue | Output 15 current upper limit alarm set value | 输出位15电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 15 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput15CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput15CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput15RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.42 | hwrPDUPNOutput15CurrentDownLimitAlarmSetValue | Output 15 current down limit alarm set value | 输出位15电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 15 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput15CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput15CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput15CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.43 | hwrPDUPNOutput16CurrentUpperLimitAlarmSetValue | Output 16 current upper limit alarm set value | 输出位16电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 16 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput16CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput16CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput16RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.44 | hwrPDUPNOutput16CurrentDownLimitAlarmSetValue | Output 16 current down limit alarm set value | 输出位16电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 16 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput16CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput16CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput16CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.45 | hwrPDUPNOutput17CurrentUpperLimitAlarmSetValue | Output 17 current upper limit alarm set value | 输出位17电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 17 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput17CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput17CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput17RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.46 | hwrPDUPNOutput17CurrentDownLimitAlarmSetValue | Output 17 current down limit alarm set value | 输出位17电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 17 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput17CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput17CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput17CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.47 | hwrPDUPNOutput18CurrentUpperLimitAlarmSetValue | Output 18 current upper limit alarm set value | 输出位18电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 18 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput18CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput18CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput18RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.48 | hwrPDUPNOutput18CurrentDownLimitAlarmSetValue | Output 18 current down limit alarm set value | 输出位18电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 18 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput18CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput18CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput18CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.49 | hwrPDUPNOutput19CurrentUpperLimitAlarmSetValue | Output 19 current upper limit alarm set value | 输出位19电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 19 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput19CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput19CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput19RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.50 | hwrPDUPNOutput19CurrentDownLimitAlarmSetValue | Output 19 current down limit alarm set value | 输出位19电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 19 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput19CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput19CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput19CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.51 | hwrPDUPNOutput20CurrentUpperLimitAlarmSetValue | Output 20 current upper limit alarm set value | 输出位20电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 20 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput20CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput20CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput20RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.52 | hwrPDUPNOutput20CurrentDownLimitAlarmSetValue | Output 20 current down limit alarm set value | 输出位20电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 20 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput20CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput20CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput20CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.53 | hwrPDUPNOutput21CurrentUpperLimitAlarmSetValue | Output 21 current upper limit alarm set value | 输出位21电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 21 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput21CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput21CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput21RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.54 | hwrPDUPNOutput21CurrentDownLimitAlarmSetValue | Output 21 current down limit alarm set value | 输出位21电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 21 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput21CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput21CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput21CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.55 | hwrPDUPNOutput22CurrentUpperLimitAlarmSetValue | Output 22 current upper limit alarm set value | 输出位22电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 22 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput22CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput22CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput22RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.56 | hwrPDUPNOutput22CurrentDownLimitAlarmSetValue | Output 22 current down limit alarm set value | 输出位22电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 22 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput22CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput22CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput22CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.57 | hwrPDUPNOutput23CurrentUpperLimitAlarmSetValue | Output 23 current upper limit alarm set value | 输出位23电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 23 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput23CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput23CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput23RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.58 | hwrPDUPNOutput23CurrentDownLimitAlarmSetValue | Output 23 current down limit alarm set value | 输出位23电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 23 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput23CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput23CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput23CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.59 | hwrPDUPNOutput24CurrentUpperLimitAlarmSetValue | Output 24 current upper limit alarm set value | 输出位24电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 24 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput24CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput24CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput24RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.60 | hwrPDUPNOutput24CurrentDownLimitAlarmSetValue | Output 24 current down limit alarm set value | 输出位24电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 24 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput24CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput24CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput24CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.61 | hwrPDUPNOutput25CurrentUpperLimitAlarmSetValue | Output 25 current upper limit alarm set value | 输出位25电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 25 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput25CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput25CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput25RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.62 | hwrPDUPNOutput25CurrentDownLimitAlarmSetValue | Output 25 current down limit alarm set value | 输出位25电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 25 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput25CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput25CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput25CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.63 | hwrPDUPNOutput26CurrentUpperLimitAlarmSetValue | Output 26 current upper limit alarm set value | 输出位26电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 26 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput26CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput26CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput26RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.64 | hwrPDUPNOutput26CurrentDownLimitAlarmSetValue | Output 26 current down limit alarm set value | 输出位26电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 26 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput26CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput26CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput26CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.65 | hwrPDUPNOutput27CurrentUpperLimitAlarmSetValue | Output 27 current upper limit alarm set value | 输出位27电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 27 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput27CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput27CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput27RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.66 | hwrPDUPNOutput27CurrentDownLimitAlarmSetValue | Output 27 current down limit alarm set value | 输出位27电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 27 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput27CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput27CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput27CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.67 | hwrPDUPNOutput28CurrentUpperLimitAlarmSetValue | Output 28 current upper limit alarm set value | 输出位28电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 28 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput28CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput28CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput28RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.68 | hwrPDUPNOutput28CurrentDownLimitAlarmSetValue | Output 28 current down limit alarm set value | 输出位28电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 28 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput28CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput28CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput28CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.69 | hwrPDUPNOutput29CurrentUpperLimitAlarmSetValue | Output 29 current upper limit alarm set value | 输出位29电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 29 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput29CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput29CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput29RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.70 | hwrPDUPNOutput29CurrentDownLimitAlarmSetValue | Output 29 current down limit alarm set value | 输出位29电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 29 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput29CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput29CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput29CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.71 | hwrPDUPNOutput30CurrentUpperLimitAlarmSetValue | Output 30 current upper limit alarm set value | 输出位30电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 30 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput30CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput30CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput30RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.72 | hwrPDUPNOutput30CurrentDownLimitAlarmSetValue | Output 30 current down limit alarm set value | 输出位30电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 30 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput30CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput30CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput30CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.73 | hwrPDUPNOutput31CurrentUpperLimitAlarmSetValue | Output 31 current upper limit alarm set value | 输出位31电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 31 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput31CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput31CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput31RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.74 | hwrPDUPNOutput31CurrentDownLimitAlarmSetValue | Output 31 current down limit alarm set value | 输出位31电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 31 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput31CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput31CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput31CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.75 | hwrPDUPNOutput32CurrentUpperLimitAlarmSetValue | Output 32 current upper limit alarm set value | 输出位32电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 32 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput32CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput32CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput32RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.76 | hwrPDUPNOutput32CurrentDownLimitAlarmSetValue | Output 32 current down limit alarm set value | 输出位32电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 32 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput32CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput32CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput32CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.77 | hwrPDUPNOutput33CurrentUpperLimitAlarmSetValue | Output 33 current upper limit alarm set value | 输出位33电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 33 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput33CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput33CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput33RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.78 | hwrPDUPNOutput33CurrentDownLimitAlarmSetValue | Output 33 current down limit alarm set value | 输出位33电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 33 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput33CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput33CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput33CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.79 | hwrPDUPNOutput34CurrentUpperLimitAlarmSetValue | Output 34 current upper limit alarm set value | 输出位34电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 34 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput34CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput34CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput34RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.80 | hwrPDUPNOutput34CurrentDownLimitAlarmSetValue | Output 34 current down limit alarm set value | 输出位34电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 34 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput34CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput34CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput34CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.81 | hwrPDUPNOutput35CurrentUpperLimitAlarmSetValue | Output 35 current upper limit alarm set value | 输出位35电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 35 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput35CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput35CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput35RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.82 | hwrPDUPNOutput35CurrentDownLimitAlarmSetValue | Output 35 current down limit alarm set value | 输出位35电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 35 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput35CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput35CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput35CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.83 | hwrPDUPNOutput36CurrentUpperLimitAlarmSetValue | Output 36 current upper limit alarm set value | 输出位36电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 36 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput36CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput36CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput36RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.84 | hwrPDUPNOutput36CurrentDownLimitAlarmSetValue | Output 36 current down limit alarm set value | 输出位36电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 36 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput36CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput36CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput36CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.85 | hwrPDUPNTemperature1CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 1 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.86 | hwrPDUPNTemperature1CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 1 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.87 | hwrPDUPNTemperature2CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 2 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.88 | hwrPDUPNTemperature2CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 2 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.89 | hwrPDUPNTemperature3CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 3 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.90 | hwrPDUPNTemperature3CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 3 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.91 | hwrPDUPNTemperature4CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 4 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.92 | hwrPDUPNTemperature4CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 4 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.93 | hwrPDUPNTemperature5CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 5 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.94 | hwrPDUPNTemperature5CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 5 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.95 | hwrPDUPNTemperature6CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 6 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.96 | hwrPDUPNTemperature6CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 6 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.97 | hwrPDUPNTemperature7CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 7 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.98 | hwrPDUPNTemperature7CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 7 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.99 | hwrPDUPNTemperature8CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 8 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.100 | hwrPDUPNTemperature8CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 8 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.101 | hwrPDUPNHumidity1CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 1 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.102 | hwrPDUPNHumidity1CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 1 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.103 | hwrPDUPNHumidity2CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 2 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.104 | hwrPDUPNHumidity2CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 2 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.105 | hwrPDUPNHumidity3CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 3 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.106 | hwrPDUPNHumidity3CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 3 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.107 | hwrPDUPNHumidity4CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 4 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.108 | hwrPDUPNHumidity4CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 4 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.109 | hwrPDUPNHumidity5CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 5 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.110 | hwrPDUPNHumidity5CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 5 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.111 | hwrPDUPNHumidity6CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 6 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.112 | hwrPDUPNHumidity6CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 6 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.113 | hwrPDUPNHumidity7CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 7 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.114 | hwrPDUPNHumidity7CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 7 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.115 | hwrPDUPNHumidity8CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 8 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.116 | hwrPDUPNHumidity8CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 8 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.117 | hwrPDUPNWindSpeedCurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..250 | / | Wind speed current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:m/s.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.118 | hwrPDUPNWindSpeedCurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..250 | / | Wind speed current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:m/s.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.119 | hwrPDUPNBranch1OutputOnOrOffControl | Branch 1 output on/off control | 第1路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 1 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.120 | hwrPDUPNBranch2OutputOnOrOffControl | Branch 2 output on/off control | 第2路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 2 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.121 | hwrPDUPNBranch3OutputOnOrOffControl | Branch 3 output on/off control | 第3路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 3 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.122 | hwrPDUPNBranch4OutputOnOrOffControl | Branch 4 output on/off control | 第4路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 4 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.123 | hwrPDUPNBranch5OutputOnOrOffControl | Branch 5 output on/off control | 第5路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 5 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.124 | hwrPDUPNBranch6OutputOnOrOffControl | Branch 6 output on/off control | 第6路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 6 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.125 | hwrPDUPNBranch7OutputOnOrOffControl | Branch 7 output on/off control | 第7路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 7 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.126 | hwrPDUPNBranch8OutputOnOrOffControl | Branch 8 output on/off control | 第8路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 8 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.127 | hwrPDUPNBranch9OutputOnOrOffControl | Branch 9 output on/off control | 第9路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 9 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.128 | hwrPDUPNBranch10OutputOnOrOffControl | Branch 10 output on/off control | 第10路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 10 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.129 | hwrPDUPNBranch11OutputOnOrOffControl | Branch 11 output on/off control | 第11路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 11 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.130 | hwrPDUPNBranch12OutputOnOrOffControl | Branch 12 output on/off control | 第12路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 12 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.131 | hwrPDUPNBranch13OutputOnOrOffControl | Branch 13 output on/off control | 第13路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 13 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.132 | hwrPDUPNBranch14OutputOnOrOffControl | Branch 14 output on/off control | 第14路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 14 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.133 | hwrPDUPNBranch15OutputOnOrOffControl | Branch 15 output on/off control | 第15路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 15 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.134 | hwrPDUPNBranch16OutputOnOrOffControl | Branch 16 output on/off control | 第16路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 16 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.135 | hwrPDUPNBranch17OutputOnOrOffControl | Branch 17 output on/off control | 第17路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 17 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.136 | hwrPDUPNBranch18OutputOnOrOffControl | Branch 18 output on/off control | 第18路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 18 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.137 | hwrPDUPNBranch19OutputOnOrOffControl | Branch 19 output on/off control | 第19路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 19 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.138 | hwrPDUPNBranch20OutputOnOrOffControl | Branch 20 output on/off control | 第20路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 20 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.139 | hwrPDUPNBranch21OutputOnOrOffControl | Branch 21 output on/off control | 第21路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 21 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.140 | hwrPDUPNBranch22OutputOnOrOffControl | Branch 22 output on/off control | 第22路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 22 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.141 | hwrPDUPNBranch23OutputOnOrOffControl | Branch 23 output on/off control | 第23路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 23 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.142 | hwrPDUPNBranch24OutputOnOrOffControl | Branch 24 output on/off control | 第24路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 24 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.143 | hwrPDUPNBranch25OutputOnOrOffControl | Branch 25 output on/off control | 第25路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 25 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.144 | hwrPDUPNBranch26OutputOnOrOffControl | Branch 26 output on/off control | 第26路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 26 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.145 | hwrPDUPNBranch27OutputOnOrOffControl | Branch 27 output on/off control | 第27路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 27 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.146 | hwrPDUPNBranch28OutputOnOrOffControl | Branch 28 output on/off control | 第28路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 28 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.147 | hwrPDUPNBranch29OutputOnOrOffControl | Branch 29 output on/off control | 第29路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 29 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.148 | hwrPDUPNBranch30OutputOnOrOffControl | Branch 30 output on/off control | 第30路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 30 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.149 | hwrPDUPNBranch31OutputOnOrOffControl | Branch 31 output on/off control | 第31路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 31 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.150 | hwrPDUPNBranch32OutputOnOrOffControl | Branch 32 output on/off control | 第32路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 32 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.151 | hwrPDUPNBranch33OutputOnOrOffControl | Branch 33 output on/off control | 第33路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 33 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.152 | hwrPDUPNBranch34OutputOnOrOffControl | Branch 34 output on/off control | 第34路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 34 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.153 | hwrPDUPNBranch35OutputOnOrOffControl | Branch 35 output on/off control | 第35路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 35 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.154 | hwrPDUPNBranch36OutputOnOrOffControl | Branch 36 output on/off control | 第36路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 36 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.155 | hwrPDUPNRestoreFactoryDefaults | Restore factory defaults | 恢复出厂默认值 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Restore factory defaults of the device config table for the rPDU-PN. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.156 | hwrPDUPNParentDeviceID | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.157 | hwrPDUPNVoltageUpperLimitAlarmSetValue | Voltage upper limit alarm set value | 电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Voltage Upper Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.158 | hwrPDUPNVoltageLowerLimitAlarmSetValue | Voltage lower limit alarm set value | 电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Voltage Lower Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.159 | hwrPDUPNL1VoltageUpperLimitAlarmSetValue | L1 Voltage upper limit alarm set value | L1相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1 Voltage Upper Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.160 | hwrPDUPNL1VoltageLowerLimitAlarmSetValue | L1 Voltage lower limit alarm set value | L1相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1 Voltage Lower Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.161 | hwrPDUPNL2VoltageUpperLimitAlarmSetValue | L2 Voltage upper limit alarm set value | L2相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2 Voltage Upper Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.162 | hwrPDUPNL2VoltageLowerLimitAlarmSetValue | L2 Voltage lower limit alarm set value | L2相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2 Voltage Lower Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.163 | hwrPDUPNL3VoltageUpperLimitAlarmSetValue | L3 Voltage upper limit alarm set value | L3相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3 Voltage Upper Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.164 | hwrPDUPNL3VoltageLowerLimitAlarmSetValue | L3 Voltage lower limit alarm set value | L3相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3 Voltage Lower Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.165 | hwrPDUPNSetRatedVoltage | Rated voltage | 额定电压 | 1-Read_Write | 读写 | 0..380 | 0..380 | Rated voltage of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.166 | hwrPDUPNSetNumbersOfOutput | Numbers of output | 输出位数 | 1-Read_Write | 读写 | 0..48 | 0..48 | Numbers of output of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.167 | hwrPDUPNDevicename | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device name for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.220 | hwrPDUPNConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.3 | hwrPDUPNRunning2table | / | / |  |  | / | / | The running 2 table of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.1 | hwrPDUPNRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.2 | hwrPDUPNHum1Value | Humidity value 1 | 湿度1 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 1 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.3 | hwrPDUPNHum2Value | Humidity value 2 | 湿度2 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 2 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.4 | hwrPDUPNHum3Value | Humidity value 3 | 湿度3 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 3 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.5 | hwrPDUPNHum4Value | Humidity value 4 | 湿度4 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 4 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.6 | hwrPDUPNHum5Value | Humidity value 5 | 湿度5 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 5 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.7 | hwrPDUPNHum6Value | Humidity value 6 | 湿度6 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 6 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.8 | hwrPDUPNHum7Value | Humidity value 7 | 湿度7 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 7 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.9 | hwrPDUPNHum8Value | Humidity value 8 | 湿度8 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 8 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.10 | hwrPDUPNTemp1Value | Temperature value 1 | 温度1 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 1 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.11 | hwrPDUPNTemp2Value | Temperature value 2 | 温度2 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 2 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.12 | hwrPDUPNTemp3Value | Temperature value 3 | 温度3 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 3 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.13 | hwrPDUPNTemp4Value | Temperature value 4 | 温度4 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 4 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.14 | hwrPDUPNTemp5Value | Temperature value 5 | 温度5 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 5 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.15 | hwrPDUPNTemp6Value | Temperature value 6 | 温度6 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 6 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.16 | hwrPDUPNTemp7Value | Temperature value 7 | 温度7 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 7 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.17 | hwrPDUPNTemp8Value | Temperature value 8 | 温度8 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 8 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.70 | hwrPDUPNActivePowerkW | Active power | 有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Active power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.71 | hwrPDUPNReactivePowerkvar | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Reactive power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.72 | hwrPDUPNL1ActivePowerkW | L1 Active power | L1相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 Active power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.73 | hwrPDUPNL2ActivePowerkW | L2 Active power | L2相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 Active power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.74 | hwrPDUPNL3ActivePowerkW | L3 Active power | L3相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 Active power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.75 | hwrPDUPNL1ReactivePowerkvar | L1 Reactive power | L1相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 Reactive power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.76 | hwrPDUPNL2ReactivePowerkvar | L2 Reactive power | L2相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 Reactive power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.77 | hwrPDUPNL3ReactivePowerkvar | L3 Reactive power | L3相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 Reactive power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.78 | hwrPDUPN1ActivePowerOfOutputkW | 1 Active power of output | 输出位1有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 1 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.79 | hwrPDUPN2ActivePowerOfOutputkW | 2 Active power of output | 输出位2有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 2 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.80 | hwrPDUPN3ActivePowerOfOutputkW | 3 Active power of output | 输出位3有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 3 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.81 | hwrPDUPN4ActivePowerOfOutputkW | 4 Active power of output | 输出位4有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 4 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.82 | hwrPDUPN5ActivePowerOfOutputkW | 5 Active power of output | 输出位5有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 5 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.83 | hwrPDUPN6ActivePowerOfOutputkW | 6 Active power of output | 输出位6有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 6 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.84 | hwrPDUPN7ActivePowerOfOutputkW | 7 Active power of output | 输出位7有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 7 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.85 | hwrPDUPN8ActivePowerOfOutputkW | 8 Active power of output | 输出位8有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 8 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.86 | hwrPDUPN9ActivePowerOfOutputkW | 9 Active power of output | 输出位9有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 9 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.87 | hwrPDUPN10ActivePowerOfOutputkW | 10 Active power of output | 输出位10有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 10 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.88 | hwrPDUPN11ActivePowerOfOutputkW | 11 Active power of output | 输出位11有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 11 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.89 | hwrPDUPN12ActivePowerOfOutputkW | 12 Active power of output | 输出位12有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 12 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.90 | hwrPDUPN13ActivePowerOfOutputkW | 13 Active power of output | 输出位13有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 13 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.91 | hwrPDUPN14ActivePowerOfOutputkW | 14 Active power of output | 输出位14有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 14 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.92 | hwrPDUPN15ActivePowerOfOutputkW | 15 Active power of output | 输出位15有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 15 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.93 | hwrPDUPN16ActivePowerOfOutputkW | 16 Active power of output | 输出位16有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 16 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.94 | hwrPDUPN17ActivePowerOfOutputkW | 17 Active power of output | 输出位17有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 17 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.95 | hwrPDUPN18ActivePowerOfOutputkW | 18 Active power of output | 输出位18有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 18 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.96 | hwrPDUPN19ActivePowerOfOutputkW | 19 Active power of output | 输出位19有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 19 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.97 | hwrPDUPN20ActivePowerOfOutputkW | 20 Active power of output | 输出位20有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 20 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.98 | hwrPDUPN21ActivePowerOfOutputkW | 21 Active power of output | 输出位21有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 21 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.99 | hwrPDUPN22ActivePowerOfOutputkW | 22 Active power of output | 输出位22有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 22 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.100 | hwrPDUPN23ActivePowerOfOutputkW | 23 Active power of output | 输出位23有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 23 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.101 | hwrPDUPN24ActivePowerOfOutputkW | 24 Active power of output | 输出位24有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 24 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.102 | hwrPDUPN25ActivePowerOfOutputkW | 25 Active power of output | 输出位25有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 25 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.103 | hwrPDUPN26ActivePowerOfOutputkW | 26 Active power of output | 输出位26有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 26 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.104 | hwrPDUPN27ActivePowerOfOutputkW | 27 Active power of output | 输出位27有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 27 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.105 | hwrPDUPN28ActivePowerOfOutputkW | 28 Active power of output | 输出位28有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 28 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.106 | hwrPDUPN29ActivePowerOfOutputkW | 29 Active power of output | 输出位29有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 29 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.107 | hwrPDUPN30ActivePowerOfOutputkW | 30 Active power of output | 输出位30有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 30 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.108 | hwrPDUPN31ActivePowerOfOutputkW | 31 Active power of output | 输出位31有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 31 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.109 | hwrPDUPN32ActivePowerOfOutputkW | 32 Active power of output | 输出位32有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 32 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.110 | hwrPDUPN33ActivePowerOfOutputkW | 33 Active power of output | 输出位33有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 33 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.111 | hwrPDUPN34ActivePowerOfOutputkW | 34 Active power of output | 输出位34有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 34 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.112 | hwrPDUPN35ActivePowerOfOutputkW | 35 Active power of output | 输出位35有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 35 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.113 | hwrPDUPN36ActivePowerOfOutputkW | 36 Active power of output | 输出位36有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 36 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.220 | hwrPDUPNRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-PN.

## rPDU
rPDU
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.125 | rPDU | rPDU | rPDU | / | / | / | / | rPDU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.125.1 | hwrPDURunning1Table | / | / |  |  | / | / | The running table of rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.1 | hwrPDURunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.2 | hwrPDUVoltageValue | Voltage value | 电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | Voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.3 | hwrPDUCurrentValue | Current value | 电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.4 | hwrPDUPowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.5 | hwrPDUPowerEnergyValue | Power energy value | 有功电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Power energy value of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.6 | hwrPDUFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 4500..6500 | 4500..6500 | Frequency of the device config table for the rPDU.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.7 | hwrPDUL1VoltageValue | L1 voltage value | L1相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L1 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.8 | hwrPDUL2VoltageValue | L2 voltage value | L2相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L2 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.9 | hwrPDUL3VoltageValue | L3 voltage value | L3相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L3 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.10 | hwrPDUL1CurrentValue | L1 current value | L1相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L1 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.11 | hwrPDUL2CurrentValue | L2 current value | L2相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L2 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.12 | hwrPDUL3CurrentValue | L3 current value | L3相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L3 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.13 | hwrPDUL1PowerFactor | L1 power factor | L1相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L1 power factor of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.14 | hwrPDUL2PowerFactor | L2 power factor | L2相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L2 power factor of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.15 | hwrPDUL3PowerFactor | L3 power factor | L3相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L3 power factor of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.16 | hwrPDUCurrentOfOutput1 | Current of output 1 | 输出位1电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.17 | hwrPDUCurrentOfOutput2 | Current of output 2 | 输出位2电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.18 | hwrPDUCurrentOfOutput3 | Current of output 3 | 输出位3电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.19 | hwrPDUCurrentOfOutput4 | Current of output 4 | 输出位4电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.20 | hwrPDUCurrentOfOutput5 | Current of output 5 | 输出位5电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 5 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.21 | hwrPDUCurrentOfOutput6 | Current of output 6 | 输出位6电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.22 | hwrPDUCurrentOfOutput7 | Current of output 7 | 输出位7电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.23 | hwrPDUCurrentOfOutput8 | Current of output 8 | 输出位8电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.24 | hwrPDUCurrentOfOutput9 | Current of output 9 | 输出位9电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.25 | hwrPDUCurrentOfOutput10 | Current of output 10 | 输出位10电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.26 | hwrPDUCurrentOfOutput11 | Current of output 11 | 输出位11电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.27 | hwrPDUCurrentOfOutput12 | Current of output 12 | 输出位12电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.28 | hwrPDUCurrentOfOutput13 | Current of output 13 | 输出位13电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.29 | hwrPDUCurrentOfOutput14 | Current of output 14 | 输出位14电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.30 | hwrPDUCurrentOfOutput15 | Current of output 15 | 输出位15电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.31 | hwrPDUCurrentOfOutput16 | Current of output 16 | 输出位16电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.32 | hwrPDUCurrentOfOutput17 | Current of output 17 | 输出位17电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.33 | hwrPDUCurrentOfOutput18 | Current of output 18 | 输出位18电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.34 | hwrPDUCurrentOfOutput19 | Current of output 19 | 输出位19电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.35 | hwrPDUCurrentOfOutput20 | Current of output 20 | 输出位20电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.36 | hwrPDUCurrentOfOutput21 | Current of output 21 | 输出位21电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.37 | hwrPDUCurrentOfOutput22 | Current of output 22 | 输出位22电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.38 | hwrPDUCurrentOfOutput23 | Current of output 23 | 输出位23电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.39 | hwrPDUCurrentOfOutput24 | Current of output 24 | 输出位24电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.40 | hwrPDUCurrentOfOutput25 | Current of output 25 | 输出位25电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.41 | hwrPDUCurrentOfOutput26 | Current of output 26 | 输出位26电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.42 | hwrPDUCurrentOfOutput27 | Current of output 27 | 输出位27电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.43 | hwrPDUCurrentOfOutput28 | Current of output 28 | 输出位28电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.44 | hwrPDUCurrentOfOutput29 | Current of output 29 | 输出位29电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.45 | hwrPDUCurrentOfOutput30 | Current of output 30 | 输出位30电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.46 | hwrPDUCurrentOfOutput31 | Current of output 31 | 输出位31电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.47 | hwrPDUCurrentOfOutput32 | Current of output 32 | 输出位32电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.48 | hwrPDUCurrentOfOutput33 | Current of output 33 | 输出位33电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.49 | hwrPDUCurrentOfOutput34 | Current of output 34 | 输出位34电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.50 | hwrPDUCurrentOfOutput35 | Current of output 35 | 输出位35电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.51 | hwrPDUCurrentOfOutput36 | Current of output 36 | 输出位36电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.52 | hwrPDUElectricalEnergyOfOutput1 | Electrical energy of output 1 | 输出位1电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.53 | hwrPDUElectricalEnergyOfOutput2 | Electrical energy of output 2 | 输出位2电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.54 | hwrPDUElectricalEnergyOfOutput3 | Electrical energy of output 3 | 输出位3电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.55 | hwrPDUElectricalEnergyOfOutput4 | Electrical energy of output 4 | 输出位4电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.56 | hwrPDUElectricalEnergyOfOutput5 | Electrical energy of output 5 | 输出位5电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.57 | hwrPDUElectricalEnergyOfOutput6 | Electrical energy of output 6 | 输出位6电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.58 | hwrPDUElectricalEnergyOfOutput7 | Electrical energy of output 7 | 输出位7电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 7 Electrical energy of output of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.59 | hwrPDUElectricalEnergyOfOutput8 | Electrical energy of output 8 | 输出位8电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.60 | hwrPDUElectricalEnergyOfOutput9 | Electrical energy of output 9 | 输出位9电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.61 | hwrPDUElectricalEnergyOfOutput10 | Electrical energy of output 10 | 输出位10电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.62 | hwrPDUElectricalEnergyOfOutput11 | Electrical energy of output 11 | 输出位11电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.63 | hwrPDUElectricalEnergyOfOutput12 | Electrical energy of output 12 | 输出位12电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.64 | hwrPDUElectricalEnergyOfOutput13 | Electrical energy of output 13 | 输出位13电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.65 | hwrPDUElectricalEnergyOfOutput14 | Electrical energy of output 14 | 输出位14电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.66 | hwrPDUElectricalEnergyOfOutput15 | Electrical energy of output 15 | 输出位15电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.67 | hwrPDUElectricalEnergyOfOutput16 | Electrical energy of output 16 | 输出位16电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.68 | hwrPDUElectricalEnergyOfOutput17 | Electrical energy of output 17 | 输出位17电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.69 | hwrPDUElectricalEnergyOfOutput18 | Electrical energy of output 18 | 输出位18电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.70 | hwrPDUElectricalEnergyOfOutput19 | Electrical energy of output 19 | 输出位19电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.71 | hwrPDUElectricalEnergyOfOutput20 | Electrical energy of output 20 | 输出位20电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.72 | hwrPDUElectricalEnergyOfOutput21 | Electrical energy of output 21 | 输出位21电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.73 | hwrPDUElectricalEnergyOfOutput22 | Electrical energy of output 22 | 输出位22电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.74 | hwrPDUElectricalEnergyOfOutput23 | Electrical energy of output 23 | 输出位23电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.75 | hwrPDUElectricalEnergyOfOutput24 | Electrical energy of output 24 | 输出位24电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.76 | hwrPDUElectricalEnergyOfOutput25 | Electrical energy of output 25 | 输出位25电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.77 | hwrPDUElectricalEnergyOfOutput26 | Electrical energy of output 26 | 输出位26电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.78 | hwrPDUElectricalEnergyOfOutput27 | Electrical energy of output 27 | 输出位27电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.79 | hwrPDUElectricalEnergyOfOutput28 | Electrical energy of output 28 | 输出位28电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.80 | hwrPDUElectricalEnergyOfOutput29 | Electrical energy of output 29 | 输出位29电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.81 | hwrPDUElectricalEnergyOfOutput30 | Electrical energy of output 30 | 输出位30电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.82 | hwrPDUElectricalEnergyOfOutput31 | Electrical energy of output 31 | 输出位31电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.83 | hwrPDUElectricalEnergyOfOutput32 | Electrical energy of output 32 | 输出位32电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.84 | hwrPDUElectricalEnergyOfOutput33 | Electrical energy of output 33 | 输出位33电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.85 | hwrPDUElectricalEnergyOfOutput34 | Electrical energy of output 34 | 输出位34电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.86 | hwrPDUElectricalEnergyOfOutput35 | Electrical energy of output 35 | 输出位35电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.87 | hwrPDUElectricalEnergyOfOutput36 | Electrical energy of output 36 | 输出位36电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.88 | hwrPDUPowerFactorOfOutput1 | Power factor of output 1 | 输出位1功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 1 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.89 | hwrPDUPowerFactorOfOutput2 | Power factor of output 2 | 输出位2功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 2 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.90 | hwrPDUPowerFactorOfOutput3 | Power factor of output 3 | 输出位3功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 3 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.91 | hwrPDUPowerFactorOfOutput4 | Power factor of output 4 | 输出位4功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 4 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.92 | hwrPDUPowerFactorOfOutput5 | Power factor of output 5 | 输出位5功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 5 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.93 | hwrPDUPowerFactorOfOutput6 | Power factor of output 6 | 输出位6功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 6 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.94 | hwrPDUPowerFactorOfOutput7 | Power factor of output 7 | 输出位7功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 7of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.95 | hwrPDUPowerFactorOfOutput8 | Power factor of output 8 | 输出位8功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 8 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.96 | hwrPDUPowerFactorOfOutput9 | Power factor of output 9 | 输出位9功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 9 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.97 | hwrPDUPowerFactorOfOutput10 | Power factor of output 10 | 输出位10功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 10 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.98 | hwrPDUPowerFactorOfOutput11 | Power factor of output 11 | 输出位11功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 11 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.99 | hwrPDUPowerFactorOfOutput12 | Power factor of output 12 | 输出位12功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 12 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.100 | hwrPDUPowerFactorOfOutput13 | Power factor of output 13 | 输出位13功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 13 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.101 | hwrPDUPowerFactorOfOutput14 | Power factor of output 14 | 输出位14功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 14 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.102 | hwrPDUPowerFactorOfOutput15 | Power factor of output 15 | 输出位15功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 15 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.103 | hwrPDUPowerFactorOfOutput16 | Power factor of output 16 | 输出位16功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 16 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.104 | hwrPDUPowerFactorOfOutput17 | Power factor of output 17 | 输出位17功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 17 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.105 | hwrPDUPowerFactorOfOutput18 | Power factor of output 18 | 输出位18功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 18 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.106 | hwrPDUPowerFactorOfOutput19 | Power factor of output 19 | 输出位19功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 19 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.107 | hwrPDUPowerFactorOfOutput20 | Power factor of output 20 | 输出位20功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 20 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.108 | hwrPDUPowerFactorOfOutput21 | Power factor of output 21 | 输出位21功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 21 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.109 | hwrPDUPowerFactorOfOutput22 | Power factor of output 22 | 输出位22功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 22 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.110 | hwrPDUPowerFactorOfOutput23 | Power factor of output 23 | 输出位23功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 23 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.111 | hwrPDUPowerFactorOfOutput24 | Power factor of output 24 | 输出位24功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 24 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.112 | hwrPDUPowerFactorOfOutput25 | Power factor of output 25 | 输出位25功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 25 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.113 | hwrPDUPowerFactorOfOutput26 | Power factor of output 26 | 输出位26功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 26 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.114 | hwrPDUPowerFactorOfOutput27 | Power factor of output 27 | 输出位27功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 27 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.115 | hwrPDUPowerFactorOfOutput28 | Power factor of output 28 | 输出位28功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 28 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.116 | hwrPDUPowerFactorOfOutput29 | Power factor of output 29 | 输出位29功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 29 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.117 | hwrPDUPowerFactorOfOutput30 | Power factor of output 30 | 输出位30功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 30 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.118 | hwrPDUPowerFactorOfOutput31 | Power factor of output 31 | 输出位31功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 31 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.119 | hwrPDUPowerFactorOfOutput32 | Power factor of output 32 | 输出位32功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 32 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.120 | hwrPDUPowerFactorOfOutput33 | Power factor of output 33 | 输出位33功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 33 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.121 | hwrPDUPowerFactorOfOutput34 | Power factor of output 34 | 输出位34功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 34 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.122 | hwrPDUPowerFactorOfOutput35 | Power factor of output 35 | 输出位35功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 35 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.123 | hwrPDUPowerFactorOfOutput36 | Power factor of output 36 | 输出位36功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 36 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.124 | hwrPDUHumidityValue1 | Humidity 1 value | 湿度1 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 1 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.125 | hwrPDUHumidityValue2 | Humidity 2 value | 湿度2 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 2 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.126 | hwrPDUHumidityValue3 | Humidity 3 value | 湿度3 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 3 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.127 | hwrPDUHumidityValue4 | Humidity 4 value | 湿度4 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 4 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.128 | hwrPDUHumidityValue5 | Humidity 5 value | 湿度5 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 5 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.129 | hwrPDUHumidityValue6 | Humidity 6 value | 湿度6 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 6 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.130 | hwrPDUHumidityValue7 | Humidity 7 value | 湿度7 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 7 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.131 | hwrPDUHumidityValue8 | Humidity 8 value | 湿度8 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 8 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.132 | hwrPDUTemperatureValue1 | Temperature value 1 | 温度1 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 1 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.133 | hwrPDUTemperatureValue2 | Temperature value 2 | 温度2 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 2 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.134 | hwrPDUTemperatureValue3 | Temperature value 3 | 温度3 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 3 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.135 | hwrPDUTemperatureValue4 | Temperature value 4 | 温度4 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 4 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.136 | hwrPDUTemperatureValue5 | Temperature value 5 | 温度5 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 5 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.137 | hwrPDUTemperatureValue6 | Temperature value 6 | 温度6 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 6 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.138 | hwrPDUTemperatureValue7 | Temperature value 7 | 温度7 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 7 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.139 | hwrPDUTemperatureValue8 | Temperature value 8 | 温度8 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 8 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.140 | hwrPDUSwitchStatusOfOutput1 | Switch status of output 1 | 输出位1开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 1 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.141 | hwrPDUSwitchStatusOfOutput2 | Switch status of output 2 | 输出位2开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 2 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.142 | hwrPDUSwitchStatusOfOutput3 | Switch status of output 3 | 输出位3开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 3 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.143 | hwrPDUSwitchStatusOfOutput4 | Switch status of output 4 | 输出位4开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 4 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.144 | hwrPDUSwitchStatusOfOutput5 | Switch status of output 5 | 输出位5开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 5 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.145 | hwrPDUSwitchStatusOfOutput6 | Switch status of output 6 | 输出位6开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 6 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.146 | hwrPDUSwitchStatusOfOutput7 | Switch status of output 7 | 输出位7开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 7 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.147 | hwrPDUSwitchStatusOfOutput8 | Switch status of output 8 | 输出位8开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 8 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.148 | hwrPDUSwitchStatusOfOutput9 | Switch status of output 9 | 输出位9开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 9 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.149 | hwrPDUSwitchStatusOfOutput10 | Switch status of output 10 | 输出位10开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 10 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.150 | hwrPDUSwitchStatusOfOutput11 | Switch status of output 11 | 输出位11开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 11 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.151 | hwrPDUSwitchStatusOfOutput12 | Switch status of output 12 | 输出位12开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 12 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.152 | hwrPDUSwitchStatusOfOutput13 | Switch status of output 13 | 输出位13开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 13 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.153 | hwrPDUSwitchStatusOfOutput14 | Switch status of output 14 | 输出位14开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 14 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.154 | hwrPDUSwitchStatusOfOutput15 | Switch status of output 15 | 输出位15开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 15 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.155 | hwrPDUSwitchStatusOfOutput16 | Switch status of output 16 | 输出位16开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 16 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.156 | hwrPDUSwitchStatusOfOutput17 | Switch status of output 17 | 输出位17开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 17 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.157 | hwrPDUSwitchStatusOfOutput18 | Switch status of output 18 | 输出位18开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 18 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.158 | hwrPDUSwitchStatusOfOutput19 | Switch status of output 19 | 输出位19开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 19 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.159 | hwrPDUSwitchStatusOfOutput20 | Switch status of output 20 | 输出位20开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 20 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.160 | hwrPDUSwitchStatusOfOutput21 | Switch status of output 21 | 输出位21开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 21 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.161 | hwrPDUSwitchStatusOfOutput22 | Switch status of output 22 | 输出位22开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 22 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.162 | hwrPDUSwitchStatusOfOutput23 | Switch status of output 23 | 输出位23开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 23 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.163 | hwrPDUSwitchStatusOfOutput24 | Switch status of output 24 | 输出位24开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 24 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.164 | hwrPDUSwitchStatusOfOutput25 | Switch status of output 25 | 输出位25开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 25 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.165 | hwrPDUSwitchStatusOfOutput26 | Switch status of output 26 | 输出位26开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 26 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.166 | hwrPDUSwitchStatusOfOutput27 | Switch status of output 27 | 输出位27开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 27 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.167 | hwrPDUSwitchStatusOfOutput28 | Switch status of output 28 | 输出位28开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 28 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.168 | hwrPDUSwitchStatusOfOutput29 | Switch status of output 29 | 输出位29开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 29 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.169 | hwrPDUSwitchStatusOfOutput30 | Switch status of output 30 | 输出位30开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 30 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.170 | hwrPDUSwitchStatusOfOutput31 | Switch status of output 31 | 输出位31开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 31 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.171 | hwrPDUSwitchStatusOfOutput32 | Switch status of output 32 | 输出位32开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 32 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.172 | hwrPDUSwitchStatusOfOutput33 | Switch status of output 33 | 输出位33开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 33 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.173 | hwrPDUSwitchStatusOfOutput34 | Switch status of output 34 | 输出位34开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 34 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.174 | hwrPDUSwitchStatusOfOutput35 | Switch status of output 35 | 输出位35开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 35 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.175 | hwrPDUSwitchStatusOfOutput36 | Switch status of output 36 | 输出位36开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 36 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.176 | hwrPDUNumberOfOutputs | Number of outputs | 输出位数 | 0-Read_Only | 只读 | 0..48 | 0..48 | Number of outputs of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.177 | hwrPDUSwitchFunctionOfOutput | Switch function of output | 输出位开关功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Switch function of output of the device config table for the rPDU. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.178 | hwrPDUCurrentMeasuringFunctionOfOutput | Current measuring function of output | 输出位电流计量功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Current measuring function of output of the device config table for the rPDU. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.179 | hwrPDUElectricalDegreeMeasuringFunctionOfOutput | Electrical degree measuring function of output | 输出位电度计量功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Electrical degree measuring function of output of the device config table for the rPDU. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.180 | hwrPDURatedCurrentOfOutput1 | Rated current of output 1 | 输出位1额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.181 | hwrPDURatedCurrentOfOutput2 | Rated current of output 2 | 输出位2额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.182 | hwrPDURatedCurrentOfOutput3 | Rated current of output 3 | 输出位3额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.183 | hwrPDURatedCurrentOfOutput4 | Rated current of output 4 | 输出位4额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.184 | hwrPDURatedCurrentOfOutput5 | Rated current of output 5 | 输出位5额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 5 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.185 | hwrPDURatedCurrentOfOutput6 | Rated current of output 6 | 输出位6额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.186 | hwrPDURatedCurrentOfOutput7 | Rated current of output 7 | 输出位7额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.187 | hwrPDURatedCurrentOfOutput8 | Rated current of output 8 | 输出位8额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.188 | hwrPDURatedCurrentOfOutput9 | Rated current of output 9 | 输出位9额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.189 | hwrPDURatedCurrentOfOutput10 | Rated current of output 10 | 输出位10额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.190 | hwrPDURatedCurrentOfOutput11 | Rated current of output 11 | 输出位11额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.191 | hwrPDURatedCurrentOfOutput12 | Rated current of output 12 | 输出位12额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.192 | hwrPDURatedCurrentOfOutput13 | Rated current of output 13 | 输出位13额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.193 | hwrPDURatedCurrentOfOutput14 | Rated current of output 14 | 输出位14额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.194 | hwrPDURatedCurrentOfOutput15 | Rated current of output 15 | 输出位15额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.195 | hwrPDURatedCurrentOfOutput16 | Rated current of output 16 | 输出位16额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.196 | hwrPDURatedCurrentOfOutput17 | Rated current of output 17 | 输出位17额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.197 | hwrPDURatedCurrentOfOutput18 | Rated current of output 18 | 输出位18额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.198 | hwrPDURatedCurrentOfOutput19 | Rated current of output 19 | 输出位19额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.199 | hwrPDURatedCurrentOfOutput20 | Rated current of output 20 | 输出位20额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.200 | hwrPDURatedCurrentOfOutput21 | Rated current of output 21 | 输出位21额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.201 | hwrPDURatedCurrentOfOutput22 | Rated current of output 22 | 输出位22额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.202 | hwrPDURatedCurrentOfOutput23 | Rated current of output 23 | 输出位23额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.203 | hwrPDURatedCurrentOfOutput24 | Rated current of output 24 | 输出位24额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.204 | hwrPDURatedCurrentOfOutput25 | Rated current of output 25 | 输出位25额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.205 | hwrPDURatedCurrentOfOutput26 | Rated current of output 26 | 输出位26额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.206 | hwrPDURatedCurrentOfOutput27 | Rated current of output 27 | 输出位27额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.207 | hwrPDURatedCurrentOfOutput28 | Rated current of output 28 | 输出位28额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.208 | hwrPDURatedCurrentOfOutput29 | Rated current of output 29 | 输出位29额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.209 | hwrPDURatedCurrentOfOutput30 | Rated current of output 30 | 输出位30额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.210 | hwrPDURatedCurrentOfOutput31 | Rated current of output 31 | 输出位31额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.211 | hwrPDURatedCurrentOfOutput32 | Rated current of output 32 | 输出位32额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.212 | hwrPDURatedCurrentOfOutput33 | Rated current of output 33 | 输出位33额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.213 | hwrPDURatedCurrentOfOutput34 | Rated current of output 34 | 输出位34额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.214 | hwrPDURatedCurrentOfOutput35 | Rated current of output 35 | 输出位35额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.215 | hwrPDURatedCurrentOfOutput36 | Rated current of output 36 | 输出位36额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.216 | hwrPDUNumberOfPhases | Number of phases | 相位数 | 0-Read_Only | 只读 | singlephase(1), duallivewire(2), threephase(3), threelivewire(4), unknown(255) | [单相=1]/[双火线=2]/[三相=3]/[三火线=4] | Number of phases of the device config table for the rPDU. Value 1 indicate singlephase Value 2 indicate dual-live wire Value 3 indicate threephase Value 4 is three-live wire
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.217 | hwrPDUNumberOfLoops | Number of loops | 回路数 | 0-Read_Only | 只读 | 0..12 | 0..12 | Number of loops of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.218 | hwrPDULoop1Current | Loop 1 current | 回路1电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 1 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.219 | hwrPDULoop2Current | Loop 2 current | 回路2电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 2 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.220 | hwrPDULoop3Current | Loop 3 current | 回路3电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 3 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.221 | hwrPDULoop4Current | Loop 4 current | 回路4电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 4 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.222 | hwrPDULoop5Current | Loop 5 current | 回路5电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 5 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.223 | hwrPDULoop6Current | Loop 6 current | 回路6电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 6 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.224 | hwrPDULoop7Current | Loop 7 current | 回路7电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 7 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.225 | hwrPDULoop8Current | Loop 8 current | 回路8电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 8 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.226 | hwrPDULoop9Current | Loop 9 current | 回路9电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 9 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.227 | hwrPDULoop10Current | Loop 10 current | 回路10电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 10 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.228 | hwrPDULoop11Current | Loop 11 current | 回路11电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 11 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.229 | hwrPDULoop12Current | Loop 12 current | 回路12电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 12 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.230 | hwrPDUActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.231 | hwrPDUReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Reactive power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.232 | hwrPDUL1ActivePower | L1 active power | L1相有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L1 active power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.233 | hwrPDUL2ActivePower | L2 active power | L2相有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L2 active power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.234 | hwrPDUL3ActivePower | L3 active power | L3相有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L3 active power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.235 | hwrPDUL1ReactivePower | L1 reactive power | L1相无功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L1 reactive power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.236 | hwrPDUL2ReactivePower | L2 reactive power | L2相无功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L2 reactive power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.237 | hwrPDUL3ReactivePower | L3 reactive power | L3相无功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L3 reactive power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.238 | hwrPDUActivePowerOfOutput1 | Active power of output 1 | 输出位1有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 1 of output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.239 | hwrPDUActivePowerOfOutput2 | Active power of output 2 | 输出位2有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 2 output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.240 | hwrPDUActivePowerOfOutput3 | Active power of output 3 | 输出位3有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 3 output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.241 | hwrPDUActivePowerOfOutput4 | Active power of output 4 | 输出位4有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 4 of output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.242 | hwrPDUActivePowerOfOutput5 | Active power of output 5 | 输出位5有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 5 of output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.243 | hwrPDUActivePowerOfOutput6 | Active power of output 6 | 输出位6有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 6 of output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.244 | hwrPDUActivePowerOfOutput7 | Active power of output 7 | 输出位7有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 7 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.245 | hwrPDUActivePowerOfOutput8 | Active power of output 8 | 输出位8有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 8 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.246 | hwrPDUActivePowerOfOutput9 | Active power of output 9 | 输出位9有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 9 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.247 | hwrPDUActivePowerOfOutput10 | Active power of output 10 | 输出位10有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 10 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.248 | hwrPDUActivePowerOfOutput11 | Active power of output 11 | 输出位11有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 11 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.249 | hwrPDUActivePowerOfOutput12 | Active power of output 12 | 输出位12有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 12 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.250 | hwrPDUActivePowerOfOutput13 | Active power of output 13 | 输出位13有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 13 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.251 | hwrPDUActivePowerOfOutput14 | Active power of output 14 | 输出位14有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 14 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.252 | hwrPDUActivePowerOfOutput15 | Active power of output 15 | 输出位15有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 15 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.253 | hwrPDUActivePowerOfOutput16 | Active power of output 16 | 输出位16有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 16 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.254 | hwrPDUActivePowerOfOutput17 | Active power of output 17 | 输出位17有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 17 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.255 | hwrPDUActivePowerOfOutput18 | Active power of output 18 | 输出位18有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 18 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.256 | hwrPDUActivePowerOfOutput19 | Active power of output 19 | 输出位19有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 19 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.257 | hwrPDUActivePowerOfOutput20 | Active power of output 20 | 输出位20有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 20 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.258 | hwrPDUActivePowerOfOutput21 | Active power of output 21 | 输出位21有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 21 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.259 | hwrPDUActivePowerOfOutput22 | Active power of output 22 | 输出位22有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 22 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.260 | hwrPDUActivePowerOfOutput23 | Active power of output 23 | 输出位23有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 23 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.261 | hwrPDUActivePowerOfOutput24 | Active power of output 24 | 输出位24有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 24 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.262 | hwrPDUActivePowerOfOutput25 | Active power of output 25 | 输出位25有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 25 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.263 | hwrPDUActivePowerOfOutput26 | Active power of output 26 | 输出位26有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 26 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.264 | hwrPDUActivePowerOfOutput27 | Active power of output 27 | 输出位27有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 27 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.265 | hwrPDUActivePowerOfOutput28 | Active power of output 28 | 输出位28有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 28 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.266 | hwrPDUActivePowerOfOutput29 | Active power of output 29 | 输出位29有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 29 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.267 | hwrPDUActivePowerOfOutput30 | Active power of output 30 | 输出位30有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 30 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.268 | hwrPDUActivePowerOfOutput31 | Active power of output 31 | 输出位31有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 31 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.269 | hwrPDUActivePowerOfOutput32 | Active power of output 32 | 输出位32有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 32 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.270 | hwrPDUActivePowerOfOutput33 | Active power of output 33 | 输出位33有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 33 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.271 | hwrPDUActivePowerOfOutput34 | Active power of output 34 | 输出位34有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 34 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.272 | hwrPDUActivePowerOfOutput35 | Active power of output 35 | 输出位35有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 35 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.273 | hwrPDUActivePowerOfOutput36 | Active power of output 36 | 输出位36有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 36 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.274 | hwrPDUCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the rPDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.275 | hwrPDUPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.276 | hwrPDUModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.277 | hwrPDUSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.278 | hwrPDUHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.279 | hwrPDUModel | Model | 型号 | 0-Read_Only | 只读 | 0..33 | 0..33 | Model of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.280 | hwrPDURatedVoltage | Rated voltage | 额定电压 | 0-Read_Only | 只读 | 0..380 | 0..380 | Rated voltage of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.281 | hwrPDURatedCurrent | Rated current | 额定电流 | 0-Read_Only | 只读 | 0..63 | 0..63 | Rated current of the device config table for the rPDU.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.282 | hwrPDURatedFrequency | Rated frequency | 额定频率 | 0-Read_Only | 只读 | 0..50 | 0..50 | Rated frequency of the device config table for the rPDU.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.283 | hwrPDUDetailModel | Detail model | 详细机型 | 0-Read_Only | 只读 | cLEVERPDU(1), hPXINPDU(2), unknown(255) | [克莱沃=1]/[海鹏信=2] | Detail model of the device config table for the rPDU. Value 1 indicate CLEVER PDU Value 2 indicate HPXIN PDU
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.284 | hwrPDUL1L2VoltageValue | L1-L2 line voltage | L1L2线电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L1-L2 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.285 | hwrPDUL2L3VoltageValue | L2-L3 line voltage | L2L3线电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L2-L3 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.286 | hwrPDUL3L1VoltageValue | L3-L1 line voltage | L3L1线电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L3-L1 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.287 | hwrPDUrPDUType | rPDU type | rPDU分类 | 0-Read_Only | 只读 | monitoringtype(1), switchingtype(2), unknown(255) | [主路监测型=1]/[开关型=2] | Type of the device config table for the rPDU. Value 1 indicate monitoring type Value 2 indicate switching type
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.288 | hwrPDUL1L2CurrentValue | L1-L2 line current | L1L2线电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L1-L2 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.289 | hwrPDUL2L3CurrentValue | L2-L3 line current | L2L3线电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L2-L3 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.290 | hwrPDUL3L1CurrentValue | L3-L1 line current | L3L1线电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L3-L1 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.291 | hwrPDULeakageCurrent | Leakage current | 漏电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Leakage current value of the device config table for the rPDU.SigUnitInfo:mA.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.300 | hwrPDURunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2 | hwrPDUConfig2Table | / | / |  |  | / | / | The config table of rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.1 | hwrPDUConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.2 | hwrPDUDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.3 | hwrPDUInputMode | Input mode | 输入模式 | 1-Read_Write | 读写 | singlephase(1), duallivewire(2), threephase(3), threelivewire(4), unknown(255) | [单相=1]/[双火线=2]/[三相=3]/[三火线=4] | Input mode of the device config table for the rPDU. Value 1 indicate singlephase Value 2 indicate dual-live wire Value 3 indicate threephase Value 4 is three-live wire
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.4 | hwrPDUParentDeviceId | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Parent device ID of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.5 | hwrPDUBuzzerSwitch | Buzzer switch | 蜂鸣器开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Buzzer switch of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.6 | hwrPDUAlarmDryContactSwitch | Alarm dry-contact switch | 报警干接点开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Alarm dry-contact switch of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.7 | hwrPDUCurrentUpperLimitAlarmSetValue | Current upper limit alarm set value | 电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.8 | hwrPDUCurrentLowerLimitAlarmSetValue | Current lower limit alarm set value | 电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.9 | hwrPDUL1CurrentUpperLimitAlarmSetValue | L1 current upper limit alarm set value | L1相电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L1 Current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.10 | hwrPDUL1CurrentLowerLimitAlarmSetValue | L1 current lower limit alarm set value | L1相电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L1 Current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.11 | hwrPDUL2CurrentUpperLimitAlarmSetValue | L2 current upper limit alarm set value | L2相电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L2 Current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.12 | hwrPDUL2CurrentLowerLimitAlarmSetValue | L2 current lower limit alarm set value | L2相电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L2 Current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.13 | hwrPDUL3CurrentUpperLimitAlarmSetValue | L3 current upper limit alarm set value | L3相电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L3 Current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.14 | hwrPDUL3CurrentLowerLimitAlarmSetValue | L3 current lower limit alarm set value | L3相电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L3 Current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.15 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput1 | Current upper limit alarm set value of output 1 | 输出位1电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.16 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput1 | Current lower limit alarm set value of output 1 | 输出位1电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.17 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput2 | Current upper limit alarm set value of output 2 | 输出位2电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.18 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput2 | Current lower limit alarm set value of output 2 | 输出位2电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.19 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput3 | Current upper limit alarm set value of output 3 | 输出位3电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.20 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput3 | Current lower limit alarm set value of output 3 | 输出位3电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.21 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput4 | Current upper limit alarm set value of output 4 | 输出位4电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.22 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput4 | Current lower limit alarm set value of output 4 | 输出位4电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.23 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput5 | Current upper limit alarm set value of output 5 | 输出位5电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 5 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.24 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput5 | Current lower limit alarm set value of output 5 | 输出位5电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 5 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.25 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput6 | Current upper limit alarm set value of output 6 | 输出位6电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.26 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput6 | Current lower limit alarm set value of output 6 | 输出位6电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.27 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput7 | Current upper limit alarm set value of output 7 | 输出位7电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.28 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput7 | Current lower limit alarm set value of output 7 | 输出位7电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.29 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput8 | Current upper limit alarm set value of output 8 | 输出位8电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.30 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput8 | Current lower limit alarm set value of output 8 | 输出位8电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.31 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput9 | Current upper limit alarm set value of output 9 | 输出位9电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.32 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput9 | Current lower limit alarm set value of output 9 | 输出位9电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.33 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput10 | Current upper limit alarm set value of output 10 | 输出位10电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.34 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput10 | Current lower limit alarm set value of output 10 | 输出位10电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.35 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput11 | Current upper limit alarm set value of output 11 | 输出位11电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.36 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput11 | Current lower limit alarm set value of output 11 | 输出位11电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.37 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput12 | Current upper limit alarm set value of output 12 | 输出位12电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.38 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput12 | Current lower limit alarm set value of output 12 | 输出位12电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.39 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput13 | Current upper limit alarm set value of output 13 | 输出位13电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.40 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput13 | Current lower limit alarm set value of output 13 | 输出位13电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.41 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput14 | Current upper limit alarm set value of output 14 | 输出位14电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.42 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput14 | Current lower limit alarm set value of output 14 | 输出位14电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.43 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput15 | Current upper limit alarm set value of output 15 | 输出位15电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.44 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput15 | Current lower limit alarm set value of output 15 | 输出位15电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.45 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput16 | Current upper limit alarm set value of output 16 | 输出位16电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.46 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput16 | Current lower limit alarm set value of output 16 | 输出位16电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.47 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput17 | Current upper limit alarm set value of output 17 | 输出位17电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.48 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput17 | Current lower limit alarm set value of output 17 | 输出位17电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.49 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput18 | Current upper limit alarm set value of output 18 | 输出位18电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.50 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput18 | Current lower limit alarm set value of output 18 | 输出位18电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.51 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput19 | Current upper limit alarm set value of output 19 | 输出位19电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.52 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput19 | Current lower limit alarm set value of output 19 | 输出位19电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.53 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput20 | Current upper limit alarm set value of output 20 | 输出位20电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.54 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput20 | Current lower limit alarm set value of output 20 | 输出位20电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.55 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput21 | Current upper limit alarm set value of output 21 | 输出位21电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.56 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput21 | Current lower limit alarm set value of output 21 | 输出位21电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.57 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput22 | Current upper limit alarm set value of output 22 | 输出位22电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.58 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput22 | Current lower limit alarm set value of output 22 | 输出位22电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.59 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput23 | Current upper limit alarm set value of output 23 | 输出位23电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.60 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput23 | Current lower limit alarm set value of output 23 | 输出位23电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.61 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput24 | Current upper limit alarm set value of output 24 | 输出位24电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.62 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput24 | Current lower limit alarm set value of output 24 | 输出位24电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.63 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput25 | Current upper limit alarm set value of output 25 | 输出位25电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.64 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput25 | Current lower limit alarm set value of output 25 | 输出位25电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.65 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput26 | Current upper limit alarm set value of output 26 | 输出位26电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.66 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput26 | Current lower limit alarm set value of output 26 | 输出位26电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.67 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput27 | Current upper limit alarm set value of output 27 | 输出位27电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.68 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput27 | Current lower limit alarm set value of output 27 | 输出位27电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.69 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput28 | Current upper limit alarm set value of output 28 | 输出位28电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.70 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput28 | Current lower limit alarm set value of output 28 | 输出位28电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.71 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput29 | Current upper limit alarm set value of output 29 | 输出位29电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.72 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput29 | Current lower limit alarm set value of output 29 | 输出位29电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.73 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput30 | Current upper limit alarm set value of output 30 | 输出位30电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.74 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput30 | Current lower limit alarm set value of output 30 | 输出位30电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.75 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput31 | Current upper limit alarm set value of output 31 | 输出位31电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.76 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput31 | Current lower limit alarm set value of output 31 | 输出位31电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.77 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput32 | Current upper limit alarm set value of output 32 | 输出位32电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.78 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput32 | Current lower limit alarm set value of output 32 | 输出位32电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.79 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput33 | Current upper limit alarm set value of output 33 | 输出位33电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.80 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput33 | Current lower limit alarm set value of output 33 | 输出位33电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.81 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput34 | Current upper limit alarm set value of output 34 | 输出位34电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.82 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput34 | Current lower limit alarm set value of output 34 | 输出位34电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.83 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput35 | Current upper limit alarm set value of output 35 | 输出位35电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.84 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput35 | Current lower limit alarm set value of output 35 | 输出位35电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.85 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput36 | Current upper limit alarm set value of output 36 | 输出位36电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.86 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput36 | Current lower limit alarm set value of output 36 | 输出位36电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.87 | hwrPDUBranch1OutputOnorOffControl | Branch 1 output on/off control | 第1路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 1 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.88 | hwrPDUBranch2OutputOnorOffControl | Branch 2 output on/off control | 第2路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 2 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.89 | hwrPDUBranch3OutputOnorOffControl | Branch 3 output on/off control | 第3路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 3 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.90 | hwrPDUBranch4OutputOnorOffControl | Branch 4 output on/off control | 第4路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 4 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.91 | hwrPDUBranch5OutputOnorOffControl | Branch 5 output on/off control | 第5路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 5 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.92 | hwrPDUBranch6OutputOnorOffControl | Branch 6 output on/off control | 第6路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 6 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.93 | hwrPDUBranch7OutputOnorOffControl | Branch 7 output on/off control | 第7路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 7 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.94 | hwrPDUBranch8OutputOnorOffControl | Branch 8 output on/off control | 第8路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 8 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.95 | hwrPDUBranch9OutputOnorOffControl | Branch 9 output on/off control | 第9路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 9 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.96 | hwrPDUBranch10OutputOnorOffControl | Branch 10 output on/off control | 第10路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 10 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.97 | hwrPDUBranch11OutputOnorOffControl | Branch 11 output on/off control | 第11路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 11 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.98 | hwrPDUBranch12OutputOnorOffControl | Branch 12 output on/off control | 第12路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 12 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.99 | hwrPDUBranch13OutputOnorOffControl | Branch 13 output on/off control | 第13路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 13 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.100 | hwrPDUBranch14OutputOnorOffControl | Branch 14 output on/off control | 第14路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 14 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.101 | hwrPDUBranch15OutputOnorOffControl | Branch 15 output on/off control | 第15路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 15 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.102 | hwrPDUBranch16OutputOnorOffControl | Branch 16 output on/off control | 第16路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 16 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.103 | hwrPDUBranch17OutputOnorOffControl | Branch 17 output on/off control | 第17路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 17 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.104 | hwrPDUBranch18OutputOnorOffControl | Branch 18 output on/off control | 第18路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 18 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.105 | hwrPDUBranch19OutputOnorOffControl | Branch 19 output on/off control | 第19路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 19 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.106 | hwrPDUBranch20OutputOnorOffControl | Branch 20 output on/off control | 第20路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 20 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.107 | hwrPDUBranch21OutputOnorOffControl | Branch 21 output on/off control | 第21路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 21 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.108 | hwrPDUBranch22OutputOnorOffControl | Branch 22 output on/off control | 第22路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 22 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.109 | hwrPDUBranch23OutputOnorOffControl | Branch 23 output on/off control | 第23路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 23 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.110 | hwrPDUBranch24OutputOnorOffControl | Branch 24 output on/off control | 第24路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 24 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.111 | hwrPDUBranch25OutputOnorOffControl | Branch 25 output on/off control | 第25路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 25 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.112 | hwrPDUBranch26OutputOnorOffControl | Branch 26 output on/off control | 第26路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 26 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.113 | hwrPDUBranch27OutputOnorOffControl | Branch 27 output on/off control | 第27路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 27 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.114 | hwrPDUBranch28OutputOnorOffControl | Branch 28 output on/off control | 第28路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 28 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.115 | hwrPDUBranch29OutputOnorOffControl | Branch 29 output on/off control | 第29路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 29 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.116 | hwrPDUBranch30OutputOnorOffControl | Branch 30 output on/off control | 第30路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 30 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.117 | hwrPDUBranch31OutputOnorOffControl | Branch 31 output on/off control | 第31路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 31 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.118 | hwrPDUBranch32OutputOnorOffControl | Branch 32 output on/off control | 第32路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 32 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.119 | hwrPDUBranch33OutputOnorOffControl | Branch 33 output on/off control | 第33路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 33 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.120 | hwrPDUBranch34OutputOnorOffControl | Branch 34 output on/off control | 第34路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 34 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.121 | hwrPDUBranch35OutputOnorOffControl | Branch 35 output on/off control | 第35路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 35 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.122 | hwrPDUBranch36OutputOnorOffControl | Branch 36 output on/off control | 第36路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 36 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.123 | hwrPDUVoltageUpperLimitAlarmSetValue | Voltage upper limit alarm set value | 电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.124 | hwrPDUVoltageLowerLimitAlarmSetValue | Voltage lower limit alarm set value | 电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.125 | hwrPDUL1VoltageUpperLimitAlarmSetValue | L1 voltage upper limit alarm set value | L1相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1 Voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.126 | hwrPDUL1VoltageLowerLimitAlarmSetValue | L1 voltage lower limit alarm set value | L1相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1 Voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.127 | hwrPDUL2VoltageUpperLimitAlarmSetValue | L2 voltage upper limit alarm set value | L2相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2 Voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.128 | hwrPDUL2VoltageLowerLimitAlarmSetValue | L2 voltage lower limit alarm set value | L2相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2 Voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.129 | hwrPDUL3VoltageUpperLimitAlarmSetValue | L3 voltage upper limit alarm set value | L3相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3 Voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.130 | hwrPDUL3VoltageLowerLimitAlarmSetValue | L3 voltage lower limit alarm set value | L3相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3 Voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.131 | hwrPDULoop1CurrentUpperAlarmSetValue | Loop 1 current upper limit alarm set value | 回路1电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 1 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.132 | hwrPDULoop2CurrentUpperAlarmSetValue | Loop 2 current upper limit alarm set value | 回路2电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 2 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.133 | hwrPDULoop3CurrentUpperAlarmSetValue | Loop 3 current upper limit alarm set value | 回路3电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 3 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.134 | hwrPDULoop4CurrentUpperAlarmSetValue | Loop 4 current upper limit alarm set value | 回路4电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 4 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.135 | hwrPDULoop5CurrentUpperAlarmSetValue | Loop 5 current upper limit alarm set value | 回路5电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 5 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.136 | hwrPDULoop6CurrentUpperAlarmSetValue | Loop 6 current upper limit alarm set value | 回路6电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 6 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.137 | hwrPDULoop7CurrentUpperAlarmSetValue | Loop 7 current upper limit alarm set value | 回路7电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 7 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.138 | hwrPDULoop8CurrentUpperAlarmSetValue | Loop 8 current upper limit alarm set value | 回路8电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 8 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.139 | hwrPDULoop9CurrentUpperAlarmSetValue | Loop 9 current upper limit alarm set value | 回路9电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 9 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.140 | hwrPDULoop10CurrentUpperAlarmSetValue | Loop 10 current upper limit alarm set value | 回路10电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 10 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.141 | hwrPDULoop11CurrentUpperAlarmSetValue | Loop 11 current upper limit alarm set value | 回路11电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 11 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.142 | hwrPDULoop12CurrentUpperAlarmSetValue | Loop 12 current upper limit alarm set value | 回路12电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 12 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.143 | hwrPDULoop1CurrentLowerAlarmSetValue | Loop 1 current lower limit alarm set value | 回路1电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 1 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.144 | hwrPDULoop2CurrentLowerAlarmSetValue | Loop 2 current lower limit alarm set value | 回路2电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 2 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.145 | hwrPDULoop3CurrentLowerAlarmSetValue | Loop 3 current lower limit alarm set value | 回路3电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 3 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.146 | hwrPDULoop4CurrentLowerAlarmSetValue | Loop 4 current lower limit alarm set value | 回路4电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 4 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.147 | hwrPDULoop5CurrentLowerAlarmSetValue | Loop 5 current lower limit alarm set value | 回路5电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 5 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.148 | hwrPDULoop6CurrentLowerAlarmSetValue | Loop 6 current lower limit alarm set value | 回路6电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 6 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.149 | hwrPDULoop7CurrentLowerAlarmSetValue | Loop 7 current lower limit alarm set value | 回路7电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 7 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.150 | hwrPDULoop8CurrentLowerAlarmSetValue | Loop 8 current lower limit alarm set value | 回路8电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 8 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.151 | hwrPDULoop9CurrentLowerAlarmSetValue | Loop 9 current lower limit alarm set value | 回路9电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 9 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.152 | hwrPDULoop10CurrentLowerAlarmSetValue | Loop 10 current lower limit alarm set value | 回路10电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 10 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.153 | hwrPDULoop11CurrentLowerAlarmSetValue | Loop 11 current lower limit alarm set value | 回路11电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 11 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.154 | hwrPDULoop12CurrentLowerAlarmSetValue | Loop 12 current lower limit alarm set value | 回路12电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 12 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.155 | hwrPDULoopNumber | Number of loops | 回路数 | 1-Read_Write | 读写 | 0..12 | 0..12 | Loop number of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.156 | hwrPDUL1L2CurrentUpperLimitAlarmSetValue | L1-L2 current upper limit alarm set value | L1L2线电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L1-L2 current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.157 | hwrPDUL1L2CurrentLowerLimitAlarmSetValue | L1-L2 current lower limit alarm set value | L1L2线电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L1-L2 current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.158 | hwrPDUL2L3CurrentUpperLimitAlarmSetValue | L2-L3 current upper limit alarm set value | L2L3线电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L2-L3 current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.159 | hwrPDUL2L3CurrentLowerLimitAlarmSetValue | L2-L3 current lower limit alarm set value | L2L3线电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L2-L3 current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.160 | hwrPDUL3L1CurrentUpperLimitAlarmSetValue | L3-L1 current upper limit alarm set value | L3L1线电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L3-L1 current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.161 | hwrPDUL3L1CurrentLowerLimitAlarmSetValue | L3-L1 current lower limit alarm set value | L3L1线电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L3-L1 current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.162 | hwrPDULineVoltageUpperLimitAlarmSetValue | Line voltage upper limit alarm set value | 线电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Line voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.163 | hwrPDULineVoltageLowerLimitAlarmSetValue | Line voltage lower limit alarm set value | 线电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Line voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.164 | hwrPDUL1L2VoltageUpperLimitAlarmSetValue | L1-L2 voltage upper limit alarm set value | L1L2线电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1L2 voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.165 | hwrPDUL1L2VoltageLowerLimitAlarmSetValue | L1-L2 voltage lower limit alarm set value | L1L2线电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1-L2 voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.166 | hwrPDUL2L3VoltageUpperLimitAlarmSetValue | L2-L3 voltage upper limit alarm set value | L2L3线电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2-L3 voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.167 | hwrPDUL2L3VoltageLowerLimitAlarmSetValue | L2-L3 voltage lower limit alarm set value | L2L3线电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2-L3 voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.168 | hwrPDUL3L1VoltageUpperLimitAlarmSetValue | L3-L1 voltage upper limit alarm set value | L3L1线电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3-L1 voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.169 | hwrPDUL3L1VoltageLowerLimitAlarmSetValue | L3-L1 voltage upper limit alarm set value | L3L1线电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3-L1 voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.170 | hwrPDULeakageCurrentAlarmSetting | Leakage current alarm setting | 漏电流告警设定值 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | Leakage current alarm setting value of the device config table for the rPDU.SigUnitInfo:mA.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.300 | hwrPDUConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU.

## rPDU-Clever-IPPDUV1
rPDU-克莱沃-IPPDUV1
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.72 | rpduippduActuator | rPDU-Clever-IPPDUV1 | rPDU-克莱沃-IPPDUV1 | / | / | / | / | rpdu_ippduActuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.72.1 | hwrPDUCleverIPPDUV1Running1Table | / | / |  |  | / | / | The running table of rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.1 | hwrPDUCleverIPPDUV1Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.2 | hwrPDUCleverIPPDUV1VoltageL1 | L1 voltage value | L1电压值 | 0-Read_Only | 只读 | 80..276 | 80..276 | Voltage L1 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.3 | hwrPDUCleverIPPDUV1VoltageL2 | L2 voltage value | L2电压值 | 0-Read_Only | 只读 | 80..276 | 80..276 | Voltage L2 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.4 | hwrPDUCleverIPPDUV1VoltageL3 | L3 voltage value | L3电压值 | 0-Read_Only | 只读 | 80..276 | 80..276 | Voltage L3 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.5 | hwrPDUCleverIPPDUV1CurrentL1 | L1 current value | L1电流值 | 0-Read_Only | 只读 | 0..320 | 0..320 | Current L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.6 | hwrPDUCleverIPPDUV1CurrentL2 | L2 current value | L2电流值 | 0-Read_Only | 只读 | 0..320 | 0..320 | Current L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.7 | hwrPDUCleverIPPDUV1CurrentL3 | L3 current value | L3电流值 | 0-Read_Only | 只读 | 0..320 | 0..320 | Current L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.8 | hwrPDUCleverIPPDUV1PowerL1 | L1 power value | L1功率值 | 0-Read_Only | 只读 | 0..90 | 0..90 | Power L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.9 | hwrPDUCleverIPPDUV1PowerL2 | L2 power value | L2功率值 | 0-Read_Only | 只读 | 0..90 | 0..90 | Power L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.10 | hwrPDUCleverIPPDUV1PowerL3 | L3 power value | L3功率值 | 0-Read_Only | 只读 | 0..90 | 0..90 | Power L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.11 | hwrPDUCleverIPPDUV1FrequencyL1 | L1 frequency value | L1频率值 | 0-Read_Only | 只读 | 40..60 | 40..60 | Frequency L1 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.12 | hwrPDUCleverIPPDUV1FrequencyL2 | L2 frequency value | L2频率值 | 0-Read_Only | 只读 | 40..60 | 40..60 | Frequency L2 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.13 | hwrPDUCleverIPPDUV1FrequencyL3 | L3 frequency value | L3频率值 | 0-Read_Only | 只读 | 40..60 | 40..60 | Frequency L3 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.14 | hwrPDUCleverIPPDUV1EnergyL1 | L1 energy value | L1电能值 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Energy L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.15 | hwrPDUCleverIPPDUV1EnergyL2 | L2 energy value | L2电能值 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Energy L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.16 | hwrPDUCleverIPPDUV1EnergyL3 | L3 energy value | L3电能值 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Energy L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.17 | hwrPDUCleverIPPDUV1Temperature | Temperature value | 温度值 | 0-Read_Only | 只读 | 0..99 | 0..99 | Temperature of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.18 | hwrPDUCleverIPPDUV1Humidity | Humidity value | 湿度值 | 0-Read_Only | 只读 | 0..99 | 0..99 | Humidity of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.19 | hwrPDUCleverIPPDUV1Voltage | Voltage value | 电压值 | 0-Read_Only | 只读 | 80..276 | 80..276 | Voltage of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.20 | hwrPDUCleverIPPDUV1Current | Current value | 电流值 | 0-Read_Only | 只读 | 0..320 | 0..320 | Current of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.21 | hwrPDUCleverIPPDUV1Power | Power value | 功率值 | 0-Read_Only | 只读 | 0..90 | 0..90 | Power of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.22 | hwrPDUCleverIPPDUV1Frequency | Frequency value | 频率值 | 0-Read_Only | 只读 | 40..60 | 40..60 | Frequency of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.23 | hwrPDUCleverIPPDUV1Energy | Energy value | 电能值 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Energy of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.24 | hwrPDUCleverIPPDUV1CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the rPDU-Clever-IPPDUV1. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.25 | hwrPDUCleverIPPDUV1PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.26 | hwrPDUCleverIPPDUV1ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.27 | hwrPDUCleverIPPDUV1SoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.28 | hwrPDUCleverIPPDUV1InputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Input mode of the device config table for the rPDU-Clever-IPPDUV1. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.101 | hwrPDUCleverIPPDUV1Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2 | hwrPDUCleverIPPDUV1Config2Table | / | / |  |  | / | / | The config table of rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.1 | hwrPDUCleverIPPDUV1Config2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.2 | hwrPDUCleverIPPDUSetV1InputMode | Input mode | 输入模式 | 1-Read_Write | 读写 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Input Mode of the device config table for the rPDU-Clever-IPPDUV1. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.3 | hwrPDUCleverIPPDUV1DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.4 | hwrPDUCleverIPPDUV1ParentDeviceId | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Parent DeviceId of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.5 | hwrPDUCleverIPPDUV1VoltageMinL1 | L1 Min voltage value | L1电压下限告警值 | 1-Read_Write | 读写 | 80..275 | 80..275 | Voltage MIN L1 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.6 | hwrPDUCleverIPPDUV1VoltageMaxL1 | L1 Max voltage value | L1电压上限告警值 | 1-Read_Write | 读写 | 81..276 | 81..276 | Voltage MAX L1 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.7 | hwrPDUCleverIPPDUV1VoltageMinL2 | L2 Min voltage value | L2电压下限告警值 | 1-Read_Write | 读写 | 80..275 | 80..275 | Voltage MIN L2 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.8 | hwrPDUCleverIPPDUV1VoltageMaxL2 | L2 Max voltage value | L2电压上限告警值 | 1-Read_Write | 读写 | 81..276 | 81..276 | Voltage MAX L2 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.9 | hwrPDUCleverIPPDUV1VoltageMinL3 | L3 Min voltage value | L3电压下限告警值 | 1-Read_Write | 读写 | 80..275 | 80..275 | Voltage MIN L3 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.10 | hwrPDUCleverIPPDUV1VoltageMaxL3 | L3 Max voltage value | L3电压上限告警值 | 1-Read_Write | 读写 | 81..276 | 81..276 | Voltage MAX L3 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.11 | hwrPDUCleverIPPDUV1CurrentMinL1 | L1 Min current value | L1电流下限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MIN L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.12 | hwrPDUCleverIPPDUV1CurrentMaxL1 | L1 Max current value | L1电流上限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MAX L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.13 | hwrPDUCleverIPPDUV1CurrentMinL2 | L2 Min current value | L2电流下限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MIN L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.14 | hwrPDUCleverIPPDUV1CurrentMaxL2 | L2 Max current value | L2电流上限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MAX L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.15 | hwrPDUCleverIPPDUV1CurrentMinL3 | L3 Min current value | L3电流下限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MIN L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.16 | hwrPDUCleverIPPDUV1CurrentMaxL3 | L3 Max current value | L3电流上限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MAX L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.17 | hwrPDUCleverIPPDUV1VoltageMinimum | Min voltage value | 电压下限告警值 | 1-Read_Write | 读写 | 80..275 | 80..275 | Voltage minimum of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.18 | hwrPDUCleverIPPDUV1VoltageMaximum | Max voltage value | 电压上限告警值 | 1-Read_Write | 读写 | 81..276 | 81..276 | Voltage maximum of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.19 | hwrPDUCleverIPPDUV1CurrentMinimum | Min current value | 电流下限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current minimum of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.20 | hwrPDUCleverIPPDUV1CurrentMaximum | Max current value | 电流上限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current maximum of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.21 | hwrPDUCleverIPPDUV1TemperatureMin | Min temperature value | 温度值下限值 | 1-Read_Write | 读写 | 0..90 | 0..90 | Temperature MIN of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.22 | hwrPDUCleverIPPDUV1TemperatureMax | Max temperature value | 温度值上限值 | 1-Read_Write | 读写 | 0..90 | 0..90 | Temperature MAX of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.23 | hwrPDUCleverIPPDUV1HumidityMin | Min humidity value | 湿度值下限值 | 1-Read_Write | 读写 | 0..90 | 0..90 | Humidity MIN of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.24 | hwrPDUCleverIPPDUV1HumidityMax | Max humidity value | 湿度值上限值 | 1-Read_Write | 读写 | 0..90 | 0..90 | Humidity MAX of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.101 | hwrPDUCleverIPPDUV1Config2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-Clever-IPPDUV1.

## Schneider_MTZ1_IFM_Module
Schneider_MTZ1_IFM_Module
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.127 | SchneiderMTZ1IFMModule | Schneider_MTZ1_IFM_Module | Schneider_MTZ1_IFM_Module | / | / | / | / | Schneider_MTZ1_IFM_Module Equipment.
1.3.6.1.4.1.2011.6.178.1.1.127.1 | hwSchneiderMTZ1IFMModuleRunning1Table | / | / |  |  | / | / | The running table of Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.1 | hwSchneiderMTZ1IFMModuleRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.2 | hwSchneiderMTZ1IFMModuleBreakerStatus | / | / | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | / | Breaker status of the device config table for the Schneider_MTZ1_IFM_Module. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.3 | hwSchneiderMTZ1IFMModuleBreakerMode | / | / | 0-Read_Only | 只读 | manual(1), auto(2), unknown(255) | / | Breaker mode of the device config table for the Schneider_MTZ1_IFM_Module. Value 1 indicate manual Value 2 indicate auto
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.4 | hwSchneiderMTZ1IFMModuleLineAbVoltage | / | / | 0-Read_Only | 只读 | 416..22500 | / | Line AB voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.5 | hwSchneiderMTZ1IFMModuleLineBcVoltage | / | / | 0-Read_Only | 只读 | 416..22500 | / | Line BC voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.6 | hwSchneiderMTZ1IFMModuleLineCaVoltage | / | / | 0-Read_Only | 只读 | 416..22500 | / | Line CA voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.7 | hwSchneiderMTZ1IFMModuleAverageLineVoltage | / | / | 0-Read_Only | 只读 | 416..22500 | / | Average line voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.8 | hwSchneiderMTZ1IFMModulePhaseAVoltage | / | / | 0-Read_Only | 只读 | 240..15000 | / | Phase A voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.9 | hwSchneiderMTZ1IFMModulePhaseBVoltage | / | / | 0-Read_Only | 只读 | 240..15000 | / | Phase B voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.10 | hwSchneiderMTZ1IFMModulePhaseCVoltage | / | / | 0-Read_Only | 只读 | 240..15000 | / | Phase C voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.11 | hwSchneiderMTZ1IFMModuleAveragePhaseVoltage | / | / | 0-Read_Only | 只读 | 240..15000 | / | Average phase voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.12 | hwSchneiderMTZ1IFMModulePhaseACurrent | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase A current of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.13 | hwSchneiderMTZ1IFMModulePhaseBCurrent | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase B current of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.14 | hwSchneiderMTZ1IFMModulePhaseCCurrent | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase C current of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.15 | hwSchneiderMTZ1IFMModuleNeutralCurrent | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Neutral current of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.16 | hwSchneiderMTZ1IFMModuleFrequency | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Frequency of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.17 | hwSchneiderMTZ1IFMModulePhaseAActivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase A active power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.18 | hwSchneiderMTZ1IFMModulePhaseBActivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase B active power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.19 | hwSchneiderMTZ1IFMModulePhaseCActivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase C active power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.20 | hwSchneiderMTZ1IFMModuleTotalActivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total active power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.21 | hwSchneiderMTZ1IFMModulePhaseAReactivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase A reactive power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Var.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.22 | hwSchneiderMTZ1IFMModulePhaseBReactivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase B reactive power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Var.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.23 | hwSchneiderMTZ1IFMModulePhaseCReactivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase C reactive power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Var.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.24 | hwSchneiderMTZ1IFMModuleTotalReactivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total reactive power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Var.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.25 | hwSchneiderMTZ1IFMModulePhaseAApparentPower | / | / | 0-Read_Only | 只读 | 0..160000000 | / | Phase A apparent power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.26 | hwSchneiderMTZ1IFMModulePhaseBApparentPower | / | / | 0-Read_Only | 只读 | 0..160000000 | / | Phase B apparent power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.27 | hwSchneiderMTZ1IFMModulePhaseCApparentPower | / | / | 0-Read_Only | 只读 | 0..160000000 | / | Phase C apparent power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.28 | hwSchneiderMTZ1IFMModuleTotalApparentPower | / | / | 0-Read_Only | 只读 | 0..160000000 | / | Total apparent power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.29 | hwSchneiderMTZ1IFMModuleTotalActiveElectricEnergy | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total active electric energy of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Wh.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.30 | hwSchneiderMTZ1IFMModuleTotalApparentElectricEnergy | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total apparent electric energy of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Varh.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.31 | hwSchneiderMTZ1IFMModuleTotalReactiveElectricEnergy | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total reactive electric energy of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Vah.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.32 | hwSchneiderMTZ1IFMModuleTotalPowerFactor | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total power factor of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.33 | hwSchneiderMTZ1IFMModuleCommunicationStatus | / | / | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | / | Communication status of the device config table for the Schneider_MTZ1_IFM_Module. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.34 | hwSchneiderMTZ1IFMModulePortNo | / | / | 0-Read_Only | 只读 | 1..8 | / | Port No. of the device config table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.35 | hwSchneiderMTZ1IFMModuleModbusAddress | / | / | 0-Read_Only | 只读 | 1..255 | / | Modbus address of the device config table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.300 | hwSchneiderMTZ1IFMModuleRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.2 | hwSchneiderMTZ1IFMModuleConfig2Table | / | / |  |  | / | / | The config table of Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.2.1.1 | hwSchneiderMTZ1IFMModuleConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.2.1.2 | hwSchneiderMTZ1IFMModuleDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.2.1.300 | hwSchneiderMTZ1IFMModuleConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Schneider_MTZ1_IFM_Module.

## Smart U Space Manager
智能U位管理器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.46 | SmartUSpaceManager | Smart U Space Manager | 智能U位管理器 | / | / | / | / | SmartUSpaceManager Equipment.
1.3.6.1.4.1.2011.6.178.1.1.46.1 | hwSmartUSpaceManagerRunningTable | / | / |  |  | / | / | The running table of Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.1 | hwSmartUSpaceManagerRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.2 | hwSmartUSpaceManagerCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the Smart U Space Manager. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.4 | hwSmartUSpaceManagerPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.5 | hwSmartUSpaceManagerModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.6 | hwSmartUSpaceManagerUSpaceQuantity | U space quantity | U位数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | U space quantity of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.7 | hwSmartUSpaceManagerSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Software version of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.9 | hwSmartUSpaceManager1USpaceUsageInformation | 1 U space usage information | 1U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 1 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.10 | hwSmartUSpaceManager2USpaceUsageInformation | 2 U space usage information | 2U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 2 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.11 | hwSmartUSpaceManager3USpaceUsageInformation | 3 U space usage information | 3U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 3 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.12 | hwSmartUSpaceManager4USpaceUsageInformation | 4 U space usage information | 4U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 4 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.13 | hwSmartUSpaceManager5USpaceUsageInformation | 5 U space usage information | 5U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 5 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.14 | hwSmartUSpaceManager6USpaceUsageInformation | 6 U space usage information | 6U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 6 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.15 | hwSmartUSpaceManager7USpaceUsageInformation | 7 U space usage information | 7U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 7 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.16 | hwSmartUSpaceManager8USpaceUsageInformation | 8 U space usage information | 8U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 8 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.17 | hwSmartUSpaceManager9USpaceUsageInformation | 9 U space usage information | 9U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 9 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.18 | hwSmartUSpaceManager10USpaceUsageInformation | 10 U space usage information | 10U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 10 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.19 | hwSmartUSpaceManager11USpaceUsageInformation | 11 U space usage information | 11U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 11 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.20 | hwSmartUSpaceManager12USpaceUsageInformation | 12 U space usage information | 12U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 12 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.21 | hwSmartUSpaceManager13USpaceUsageInformation | 13 U space usage information | 13U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 13 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.22 | hwSmartUSpaceManager14USpaceUsageInformation | 14 U space usage information | 14U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 14 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.23 | hwSmartUSpaceManager15USpaceUsageInformation | 15 U space usage information | 15U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 15 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.24 | hwSmartUSpaceManager16USpaceUsageInformation | 16 U space usage information | 16U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 16 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.25 | hwSmartUSpaceManager17USpaceUsageInformation | 17 U space usage information | 17U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 17 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.26 | hwSmartUSpaceManager18USpaceUsageInformation | 18 U space usage information | 18U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 18 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.27 | hwSmartUSpaceManager19USpaceUsageInformation | 19 U space usage information | 19U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 19 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.28 | hwSmartUSpaceManager20USpaceUsageInformation | 20 U space usage information | 20U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 20 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.29 | hwSmartUSpaceManager21USpaceUsageInformation | 21 U space usage information | 21U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 21 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.30 | hwSmartUSpaceManager22USpaceUsageInformation | 22 U space usage information | 22U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 22 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.31 | hwSmartUSpaceManager23USpaceUsageInformation | 23 U space usage information | 23U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 23 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.32 | hwSmartUSpaceManager24USpaceUsageInformation | 24 U space usage information | 24U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 24 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.33 | hwSmartUSpaceManager25USpaceUsageInformation | 25 U space usage information | 25U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 25 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.34 | hwSmartUSpaceManager26USpaceUsageInformation | 26 U space usage information | 26U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 26 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.35 | hwSmartUSpaceManager27USpaceUsageInformation | 27 U space usage information | 27U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 27 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.36 | hwSmartUSpaceManager28USpaceUsageInformation | 28 U space usage information | 28U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 28 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.37 | hwSmartUSpaceManager29USpaceUsageInformation | 29 U space usage information | 29U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 29 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.38 | hwSmartUSpaceManager30USpaceUsageInformation | 30 U space usage information | 30U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 30 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.39 | hwSmartUSpaceManager31USpaceUsageInformation | 31 U space usage information | 31U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 31 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.40 | hwSmartUSpaceManager32USpaceUsageInformation | 32 U space usage information | 32U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 32 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.41 | hwSmartUSpaceManager33USpaceUsageInformation | 33 U space usage information | 33U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 33 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.42 | hwSmartUSpaceManager34USpaceUsageInformation | 34 U space usage information | 34U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 34 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.43 | hwSmartUSpaceManager35USpaceUsageInformation | 35 U space usage information | 35U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 35 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.44 | hwSmartUSpaceManager36USpaceUsageInformation | 36 U space usage information | 36U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 36 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.45 | hwSmartUSpaceManager37USpaceUsageInformation | 37 U space usage information | 37U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 37 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.46 | hwSmartUSpaceManager38USpaceUsageInformation | 38 U space usage information | 38U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 38 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.47 | hwSmartUSpaceManager39USpaceUsageInformation | 39 U space usage information | 39U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 39 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.48 | hwSmartUSpaceManager40USpaceUsageInformation | 40 U space usage information | 40U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 40 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.49 | hwSmartUSpaceManager41USpaceUsageInformation | 41 U space usage information | 41U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 41 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.50 | hwSmartUSpaceManager42USpaceUsageInformation | 42 U space usage information | 42U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 42 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.51 | hwSmartUSpaceManager43USpaceUsageInformation | 43 U space usage information | 43U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 43 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.52 | hwSmartUSpaceManager44USpaceUsageInformation | 44 U space usage information | 44U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 44 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.53 | hwSmartUSpaceManager45USpaceUsageInformation | 45 U space usage information | 45U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 45 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.54 | hwSmartUSpaceManager46USpaceUsageInformation | 46 U space usage information | 46U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 46 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.55 | hwSmartUSpaceManager47USpaceUsageInformation | 47 U space usage information | 47U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 47 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.56 | hwSmartUSpaceManager48USpaceUsageInformation | 48 U space usage information | 48U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 48 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.57 | hwSmartUSpaceManager49USpaceUsageInformation | 49 U space usage information | 49U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 49 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.58 | hwSmartUSpaceManager50USpaceUsageInformation | 50 U space usage information | 50U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 50 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.59 | hwSmartUSpaceManager51USpaceUsageInformation | 51 U space usage information | 51U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 51 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.60 | hwSmartUSpaceManager52USpaceUsageInformation | 52 U space usage information | 52U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 52 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.61 | hwSmartUSpaceManager53USpaceUsageInformation | 53 U space usage information | 53U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 53 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.62 | hwSmartUSpaceManager54USpaceUsageInformation | 54 U space usage information | 54U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 54 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.63 | hwSmartUSpaceManager55USpaceUsageInformation | 55 U space usage information | 55U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 55 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.64 | hwSmartUSpaceManager56USpaceUsageInformation | 56 U space usage information | 56U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 56 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.65 | hwSmartUSpaceManager57USpaceUsageInformation | 57 U space usage information | 57U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 57 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.66 | hwSmartUSpaceManager58USpaceUsageInformation | 58 U space usage information | 58U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 58 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.67 | hwSmartUSpaceManager59USpaceUsageInformation | 59 U space usage information | 59U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 59 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.68 | hwSmartUSpaceManager60USpaceUsageInformation | 60 U space usage information | 60U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 60 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.69 | hwSmartUSpaceManager61USpaceUsageInformation | 61 U space usage information | 61U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 61 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.70 | hwSmartUSpaceManager62USpaceUsageInformation | 62 U space usage information | 62U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 62 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.71 | hwSmartUSpaceManager63USpaceUsageInformation | 63 U space usage information | 63U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 63 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.72 | hwSmartUSpaceManager64USpaceUsageInformation | 64 U space usage information | 64U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 64 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.137 | hwSmartUSpaceManager1USpaceLabelId | 1 U space label ID | 1U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 1 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.138 | hwSmartUSpaceManager2USpaceLabelId | 2 U space label ID | 2U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 2 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.139 | hwSmartUSpaceManager3USpaceLabelId | 3 U space label ID | 3U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 3 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.140 | hwSmartUSpaceManager4USpaceLabelId | 4 U space label ID | 4U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 4 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.141 | hwSmartUSpaceManager5USpaceLabelId | 5 U space label ID | 5U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 5 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.142 | hwSmartUSpaceManager6USpaceLabelId | 6 U space label ID | 6U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 6 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.143 | hwSmartUSpaceManager7USpaceLabelId | 7 U space label ID | 7U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 7 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.144 | hwSmartUSpaceManager8USpaceLabelId | 8 U space label ID | 8U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 8 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.145 | hwSmartUSpaceManager9USpaceLabelId | 9 U space label ID | 9U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 9 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.146 | hwSmartUSpaceManager10USpaceLabelId | 10 U space label ID | 10U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 10 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.147 | hwSmartUSpaceManager11USpaceLabelId | 11 U space label ID | 11U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 11 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.148 | hwSmartUSpaceManager12USpaceLabelId | 12 U space label ID | 12U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 12 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.149 | hwSmartUSpaceManager13USpaceLabelId | 13 U space label ID | 13U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 13 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.150 | hwSmartUSpaceManager14USpaceLabelId | 14 U space label ID | 14U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 14 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.151 | hwSmartUSpaceManager15USpaceLabelId | 15 U space label ID | 15U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 15 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.152 | hwSmartUSpaceManager16USpaceLabelId | 16 U space label ID | 16U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 16 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.153 | hwSmartUSpaceManager17USpaceLabelId | 17 U space label ID | 17U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 17 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.154 | hwSmartUSpaceManager18USpaceLabelId | 18 U space label ID | 18U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 18 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.155 | hwSmartUSpaceManager19USpaceLabelId | 19 U space label ID | 19U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 19 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.156 | hwSmartUSpaceManager20USpaceLabelId | 20 U space label ID | 20U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 20 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.157 | hwSmartUSpaceManager21USpaceLabelId | 21 U space label ID | 21U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 21 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.158 | hwSmartUSpaceManager22USpaceLabelId | 22 U space label ID | 22U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 22 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.159 | hwSmartUSpaceManager23USpaceLabelId | 23 U space label ID | 23U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 23 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.160 | hwSmartUSpaceManager24USpaceLabelId | 24 U space label ID | 24U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 24 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.161 | hwSmartUSpaceManager25USpaceLabelId | 25 U space label ID | 25U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 25 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.162 | hwSmartUSpaceManager26USpaceLabelId | 26 U space label ID | 26U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 26 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.163 | hwSmartUSpaceManager27USpaceLabelId | 27 U space label ID | 27U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 27 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.164 | hwSmartUSpaceManager28USpaceLabelId | 28 U space label ID | 28U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 28 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.165 | hwSmartUSpaceManager29USpaceLabelId | 29 U space label ID | 29U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 29 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.166 | hwSmartUSpaceManager30USpaceLabelId | 30 U space label ID | 30U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 30 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.167 | hwSmartUSpaceManager31USpaceLabelId | 31 U space label ID | 31U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 31 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.168 | hwSmartUSpaceManager32USpaceLabelId | 32 U space label ID | 32U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 32 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.169 | hwSmartUSpaceManager33USpaceLabelId | 33 U space label ID | 33U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 33 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.170 | hwSmartUSpaceManager34USpaceLabelId | 34 U space label ID | 34U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 34 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.171 | hwSmartUSpaceManager35USpaceLabelId | 35 U space label ID | 35U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 35 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.172 | hwSmartUSpaceManager36USpaceLabelId | 36 U space label ID | 36U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 36 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.173 | hwSmartUSpaceManager37USpaceLabelId | 37 U space label ID | 37U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 37 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.174 | hwSmartUSpaceManager38USpaceLabelId | 38 U space label ID | 38U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 38 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.175 | hwSmartUSpaceManager39USpaceLabelId | 39 U space label ID | 39U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 39 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.176 | hwSmartUSpaceManager40USpaceLabelId | 40 U space label ID | 40U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 40 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.177 | hwSmartUSpaceManager41USpaceLabelId | 41 U space label ID | 41U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 41 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.178 | hwSmartUSpaceManager42USpaceLabelId | 42 U space label ID | 42U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 42 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.179 | hwSmartUSpaceManager43USpaceLabelId | 43 U space label ID | 43U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 43 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.180 | hwSmartUSpaceManager44USpaceLabelId | 44 U space label ID | 44U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 44 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.181 | hwSmartUSpaceManager45USpaceLabelId | 45 U space label ID | 45U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 45 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.182 | hwSmartUSpaceManager46USpaceLabelId | 46 U space label ID | 46U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 46 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.183 | hwSmartUSpaceManager47USpaceLabelId | 47 U space label ID | 47U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 47 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.184 | hwSmartUSpaceManager48USpaceLabelId | 48 U space label ID | 48U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 48 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.185 | hwSmartUSpaceManager49USpaceLabelId | 49 U space label ID | 49U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 49 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.186 | hwSmartUSpaceManager50USpaceLabelId | 50 U space label ID | 50U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 50 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.187 | hwSmartUSpaceManager51USpaceLabelId | 51 U space label ID | 51U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 51 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.188 | hwSmartUSpaceManager52USpaceLabelId | 52 U space label ID | 52U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 52 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.189 | hwSmartUSpaceManager53USpaceLabelId | 53 U space label ID | 53U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 53 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.190 | hwSmartUSpaceManager54USpaceLabelId | 54 U space label ID | 54U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 54 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.191 | hwSmartUSpaceManager55USpaceLabelId | 55 U space label ID | 55U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 55 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.192 | hwSmartUSpaceManager56USpaceLabelId | 56 U space label ID | 56U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 56 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.193 | hwSmartUSpaceManager57USpaceLabelId | 57 U space label ID | 57U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 57 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.194 | hwSmartUSpaceManager58USpaceLabelId | 58 U space label ID | 58U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 58 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.195 | hwSmartUSpaceManager59USpaceLabelId | 59 U space label ID | 59U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 59 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.196 | hwSmartUSpaceManager60USpaceLabelId | 60 U space label ID | 60U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 60 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.197 | hwSmartUSpaceManager61USpaceLabelId | 61 U space label ID | 61U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 61 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.198 | hwSmartUSpaceManager62USpaceLabelId | 62 U space label ID | 62U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 62 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.199 | hwSmartUSpaceManager63USpaceLabelId | 63 U space label ID | 63U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 63 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.200 | hwSmartUSpaceManager64USpaceLabelId | 64 U space label ID | 64U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 64 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.201 | hwSmartUSpaceManagerQuantityofIdleUSpace | Quantity of idle U space | 空闲U位数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The quantity of idle U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.220 | hwSmartUSpaceManagerRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.2 | hwSmartUSpaceManagerConfigTable | / | / |  |  | / | / | The config table of Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.1 | hwSmartUSpaceManagerConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.2 | hwSmartUSpaceManagerDevicename | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device name for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.88 | hwSmartUSpaceManagerBlink | / | / | 1-Read_Write | 读写 | yes(1), unknown(255) | / | Blink of the device config table for the Smart U Space Manager. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.89 | hwSmartUSpaceManagerFactoryType |  |  | 1-Read_Write | 读写 | xDUD(1), iADU(2), unknown(255) | [共济U位=1]/[龙控U位=2] | The factory type for the Smart U Space Manager. Value 1 indicate XDUD Value 2 indicate IADU
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.220 | hwSmartUSpaceManagerConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Smart U Space Manager.

## SMU11B
SMU11B
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.120 | SMU11B | SMU11B | SMU11B | / | / | / | / | SMU11B Equipment.
1.3.6.1.4.1.2011.6.178.1.1.120.1 | hwSMU11BRunning1Table | / | / |  |  | / | / | The running table of SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.1 | hwSMU11BRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.2 | hwSMU11BSystemDcVoltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | System DC voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.3 | hwSMU11BCommunicationStatus | / | / | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | / | Communication status of the device config table for the SMU11B. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.4 | hwSMU11BPortNo | / | / | 0-Read_Only | 只读 | 1..8 | / | Port No. of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.5 | hwSMU11BModbusAddress | / | / | 0-Read_Only | 只读 | 1..255 | / | Modbus address of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.6 | hwSMU11BTotalDcLoadCurrent | / | / | 0-Read_Only | 只读 | 0..10000 | / | Total DC load current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.7 | hwSMU11BAcVoltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | AC voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.8 | hwSMU11BAcCurrent | / | / | 0-Read_Only | 只读 | 0..10000 | / | AC current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.9 | hwSMU11BPhaseL1Voltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L1 voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.10 | hwSMU11BPhaseL2Voltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L2 voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.11 | hwSMU11BPhaseL3Voltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L3 voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.12 | hwSMU11BPhaseL1Current | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L1 current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.13 | hwSMU11BPhaseL2Current | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L2 current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.14 | hwSMU11BPhaseL3Current | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L3 current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.15 | hwSMU11BAcFrequency | / | / | 0-Read_Only | 只读 | 0..100 | / | AC frequency of the device config table for the SMU11B.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.16 | hwSMU11BEquipmentAreaTemperature | / | / | 0-Read_Only | 只读 | 0..100 | / | Equipment area temperature of the device config table for the SMU11B.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.17 | hwSMU11BRectifierTotalOutputCurrent | / | / | 0-Read_Only | 只读 | 0..10000 | / | Rectifier total output current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.18 | hwSMU11BRectifierAmount | / | / | 0-Read_Only | 只读 | 0..12 | / | Rectifier amount of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.19 | hwSMU11BRectifierTotalDcPower | / | / | 0-Read_Only | 只读 | 0..10000 | / | Rectifier total DC power of the device config table for the SMU11B.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.20 | hwSMU11BBatteryStatus | / | / | 0-Read_Only | 只读 | floatcharging(1), equalizedcharging(2), discharge(3), hibernation(4), unknown(255) | / | Battery status of the device config table for the SMU11B. Value 1 indicate float charging Value 2 indicate equalized charging Value 3 indicate discharge Value 4 indicate hibernation
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.21 | hwSMU11BTotalBatteryCurrent | / | / | 0-Read_Only | 只读 | 0..10000 | / | Total battery current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.22 | hwSMU11BTotalRemainingCapacityPercent | / | / | 0-Read_Only | 只读 | 0..100 | / | Total remaining capacity percent of the device config table for the SMU11B.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.23 | hwSMU11BBatteryTemperature | / | / | 0-Read_Only | 只读 | 0..100 | / | Battery temperature of the device config table for the SMU11B.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.24 | hwSMU11BAmbientTemperature | / | / | 0-Read_Only | 只读 | 0..100 | / | Ambient temperature of the device config table for the SMU11B.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.25 | hwSMU11BHourlyMainsPowerConsumption | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Hourly mains power consumption of the device config table for the SMU11B.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.26 | hwSMU11BHourlyTotalDcLoadPowerConsumption | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Hourly total DC load power consumption of the device config table for the SMU11B.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.27 | hwSMU11BCumulativeMainsPowerConsumption | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Cumulative mains power consumption of the device config table for the SMU11B.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.28 | hwSMU11BCumulativeTotalDcLoadPowerConsumption | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Cumulative total DC load power consumption of the device config table for the SMU11B.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.300 | hwSMU11BRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2 | hwSMU11BConfig2Table | / | / |  |  | / | / | The config table of SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.1 | hwSMU11BConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.2 | hwSMU11BYear | / | / | 1-Read_Write | 读写 | 2000..2037 | / | Year of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.3 | hwSMU11BMonth | / | / | 1-Read_Write | 读写 | 1..12 | / | Month of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.4 | hwSMU11BDay | / | / | 1-Read_Write | 读写 | 1..31 | / | Day of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.5 | hwSMU11BHour | / | / | 1-Read_Write | 读写 | 0..23 | / | Hour of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.6 | hwSMU11BMinute | / | / | 1-Read_Write | 读写 | 0..59 | / | Minute of the device config table for the SMU11B.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.7 | hwSMU11BSecond | / | / | 1-Read_Write | 读写 | 0..59 | / | Second of the device config table for the SMU11B.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.8 | hwSMU11BLlvd1Enable | / | / | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | / | LLVD1 enable of the device config table for the SMU11B. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.9 | hwSMU11BLlvd1Voltage | / | / | 1-Read_Write | 读写 | 360..560 | / | LLVD1 voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.10 | hwSMU11BLlvd1ConnectionVoltage | / | / | 1-Read_Write | 读写 | 370..580 | / | LLVD1 connection voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.11 | hwSMU11BAcOvervoltageThreshold | / | / | 1-Read_Write | 读写 | 60..300 | / | AC overvoltage threshold of the device config table for the SMU11B.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.12 | hwSMU11BAcUndervoltageThreshold | / | / | 1-Read_Write | 读写 | 60..300 | / | AC undervoltage threshold of the device config table for the SMU11B.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.13 | hwSMU11BDcOvervoltageThreshold | / | / | 1-Read_Write | 读写 | 530..600 | / | DC overvoltage threshold of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.14 | hwSMU11BDcUndervoltageThreshold | / | / | 1-Read_Write | 读写 | 350..570 | / | DC undervoltage threshold of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.15 | hwSMU11BAcOverfrequencyAlarmthreshold | / | / | 1-Read_Write | 读写 | 66..70 | / | AC overfrequency alarm threshold of the device config table for the SMU11B.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.16 | hwSMU11BAcUnderfrequencyAlarmThreshold | / | / | 1-Read_Write | 读写 | 45..70 | / | AC underfrequency alarm threshold of the device config table for the SMU11B.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.17 | hwSMU11BLlvd1DisconnectMode | / | / | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | / | LLVD1 disconnect mode of the device config table for the SMU11B. Value 1 indicate voltage mode Value 2 indicate time mode Value 3 indicate capacity mode
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.18 | hwSMU11BLlvd1DisconnectTime | / | / | 1-Read_Write | 读写 | 0..50000 | / | LLVD1 disconnect time of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.19 | hwSMU11BLlvd1DisconnectCapacity | / | / | 1-Read_Write | 读写 | 0..990 | / | LLVD1 disconnect capacity of the device config table for the SMU11B.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.20 | hwSMU11BLlvd1HighTempDisconnectEnable | / | / | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | / | LLVD1 high temp disconnect enable of the device config table for the SMU11B. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.21 | hwSMU11BLlvd1HighTempDisconnectTemperature | / | / | 1-Read_Write | 读写 | 250..800 | / | LLVD1 high temp disconnect temperature of the device config table for the SMU11B.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.22 | hwSMU11BAc2OvervoltageThreshold | / | / | 1-Read_Write | 读写 | 60..300 | / | AC 2 overvoltage threshold of the device config table for the SMU11B.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.23 | hwSMU11BAc2UndervoltageThreshold | / | / | 1-Read_Write | 读写 | 60..300 | / | AC 2 undervoltage threshold of the device config table for the SMU11B.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.24 | hwSMU11BBatteryRatedCapacity | / | / | 1-Read_Write | 读写 | 5..10000 | / | Battery rated capacity of the device config table for the SMU11B.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.25 | hwSMU11BFloatChargingVoltage | / | / | 1-Read_Write | 读写 | 420..580 | / | Float charging voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.26 | hwSMU11BBoostChargingVoltage | / | / | 1-Read_Write | 读写 | 420..580 | / | Boost charging voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.27 | hwSMU11BBlvdEnable | / | / | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | / | BLVD enable of the device config table for the SMU11B. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.28 | hwSMU11BBlvdVoltage | / | / | 1-Read_Write | 读写 | 360..560 | / | BLVD voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.29 | hwSMU11BBlvdConnectionVoltage | / | / | 1-Read_Write | 读写 | 370..580 | / | BLVD connection voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.30 | hwSMU11BChargeCurrentLimitCoefficient | / | / | 1-Read_Write | 读写 | 5..25 | / | Charge current limit coefficient of the device config table for the SMU11B.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.31 | hwSMU11BBlvdDisconnectMode | / | / | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | / | BLVD disconnect mode of the device config table for the SMU11B. Value 1 indicate voltage mode Value 2 indicate time mode Value 3 indicate capacity mode
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.32 | hwSMU11BBlvdDisconnectTime | / | / | 1-Read_Write | 读写 | 0..10000 | / | BLVD disconnect time of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.33 | hwSMU11BBlvdDisconnectCapacity | / | / | 1-Read_Write | 读写 | 0..990 | / | BLVD disconnect capacity of the device config table for the SMU11B.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.34 | hwSMU11BResetControl | / | / | 1-Read_Write | 读写 | 0..65535 | / | Reset control of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.300 | hwSMU11BConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SMU11B.

## Air Conditioner-Separate Subrac
空调-分体插框-XR005A
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.70 | splitsubrackActuator | Air Conditioner-Separate Subrack-XR005A | 空调-分体插框-XR005A | / | / | / | / | split_subrackActuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.70.1 | hwSplitSubrackRunning1Table | / | / |  |  | / | / | The running table of Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.1 | hwSplitSubrackRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.2 | hwSplitSubrack1ReturnAirTemperature | 1#Return air temperature | 1#回风温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | 1Return air temperature of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.3 | hwSplitSubrack1OutletTemperature | 1#Outlet temperature | 1#出风温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | 1Outlet temperature of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.4 | hwSplitSubrack1ReturnAirHumidity | 1#Return air humidity | 1#回风湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | 1Return air humidity of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.5 | hwSplitSubrackIndoorFanState | Indoor fan state | 内风机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Indoor fan state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.6 | hwSplitSubrackCompressorState | Compressor state | 压缩机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Compressor state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.7 | hwSplitSubrack1HeaterState | 1#Heater state | 1#电加热状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | 1#Heater state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.8 | hwSplitSubrackOutdoorFanState | Outdoor fan state | 外风机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Outdoor fan state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.9 | hwSplitSubrackSystemOnorOffState | System On/Off state | 系统开关机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | System On/Off state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.10 | hwSplitSubrackCoolingState | Cooling state | 制冷状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Cooling state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.11 | hwSplitSubrackHeatState | Heat state | 加热状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Heat state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.12 | hwSplitSubrackDehumidificationState | Dehumidification state | 除湿状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Dehumidification state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.13 | hwSplitSubrackCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Split Subrack. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.14 | hwSplitSubrackPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.15 | hwSplitSubrackModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.16 | hwSplitSubrackSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | SOftware version of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.17 | hwSplitSubrackFrontTempOfTheIntegratedCabinet | Front temperature of the integrated cabinet | 综合柜前温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | Front temperature of the integrated cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.18 | hwSplitSubrackFrontHumidOfTheIntegratedCabinet | Front humidity of the integrated cabinet | 综合柜前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Front humidity of the integrated cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.19 | hwSplitSubrackRearTempOfTheIntegratedCabinet | Rear temperature of the integrated cabinet | 综合柜后温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | Rear temperature of the integrated cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.20 | hwSplitSubrackRearHumidOfTheIntegratedCabinet | Rear humidity of the integrated cabinet | 综合柜后湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rear humidity of the integrated cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.21 | hwSplitSubrackFrontTempofTheCabinet | Front temperature of the cabinet | 机柜前温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | Front temperature of the cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.22 | hwSplitSubrackCabinetFrontHumidity | Front humidity of the cabinet | 机柜前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cabinet front humidity of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.23 | hwSplitSubrackRearTempOfTheCabinet | Rear temperature of the cabinet | 机柜后温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | Rear temperature of the cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.24 | hwSplitSubrackRearHumidityOfTheCabinet | Rear humidity of the cabinet | 机柜后湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rear humidity of the cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.101 | hwSplitSubrackRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.2 | hwSplitSubrackConfig2Table | / | / |  |  | / | / | The config table of Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.1 | hwSplitSubrackConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.2 | hwSplitSubrackDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.3 | hwSplitSubrackTemperatureSetPoint | Temperature set point | 温度设定点 | 1-Read_Write | 读写 | 70..400 | 70..400 | Temperature set point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.4 | hwSplitSubrackHumiditySetPoint | Humidity set point | 湿度设定点 | 1-Read_Write | 读写 | 100..900 | 100..900 | Humidity set point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.5 | hwSplitSubrackHighTemperatureAlarmPoint | High temperature alarm point | 高温告警点 | 1-Read_Write | 读写 | 200..700 | 200..700 | High temperature alarm point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.6 | hwSplitSubrackLowTemperatureAlarmPoint | Low temperature alarm point | 低温告警点 | 1-Read_Write | 读写 | -200..200 | -200..200 | Low temperature alarm point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.7 | hwSplitSubrackHighHumiditySetPoint | High humidity alarm point | 高湿告警点 | 1-Read_Write | 读写 | 500..900 | 500..900 | High humidity set point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.8 | hwSplitSubrackLowHumiditySetPoint | Low humidity alarm point | 低湿告警点 | 1-Read_Write | 读写 | 100..600 | 100..600 | Low humidity set point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.9 | hwSplitSubrackOutletHighTemperatureAlarmPoint | Outlet High temperature alarm point | 出风高温告警点 | 1-Read_Write | 读写 | 200..700 | 200..700 | Outlet High temperature alarm point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.10 | hwSplitSubrackOutletLowTemperatureAlarmPoint | Outlet Low temperature alarm point | 出风低温告警点 | 1-Read_Write | 读写 | -200..200 | -200..200 | Outlet Low temperature alarm point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.11 | hwSplitSubrackMonitoringOnorOff | Monitoring On/Off | 监控开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Monitoring On/Off of the device config table for the Split Subrack. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.101 | hwSplitSubrackConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Split Subrack.

## SVG-APF-NOVTIUM
SVG-APF-新能动力
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.119 | SVGAPFNOVTIUM | SVG-APF-NOVTIUM | SVG-APF-新能动力 | / | / | / | / | SVG-APF-NOVTIUM Equipment.
1.3.6.1.4.1.2011.6.178.1.1.119.1 | hwSVGAPFNOVTIUMRunning1Table | / | / |  |  | / | / | The running table of SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.1 | hwSVGAPFNOVTIUMRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.2 | hwSVGAPFNOVTIUMStartorStopStatus | Start / stop status | 启动/停机状态 | 0-Read_Only | 只读 | suspension(1), startup(2), unknown(255) | [停机=1]/[启动=2] | Start / stop status of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate suspension Value 2 indicate startup
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.3 | hwSVGAPFNOVTIUMSystemStandbyState | System standby state | 系统待机状态 | 0-Read_Only | 只读 | nostandby(1), standbystatus(2), unknown(255) | [无待机=1]/[待机状态=2] | System standby state of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate no standby Value 2 indicate standby status
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.4 | hwSVGAPFNOVTIUMGridVoltage | Grid voltage | 源侧电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid voltage of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.5 | hwSVGAPFNOVTIUMLoadCurrent | Load current | 负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.6 | hwSVGAPFNOVTIUMEquipmentCurrent | Equipment current | 设备电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Equipment current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.7 | hwSVGAPFNOVTIUMDcVoltage | DC voltage+- | 直流电压+- | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | DC voltage+- of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.8 | hwSVGAPFNOVTIUMRadiatorTemperature | Radiator temperature | 散热器温度 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Radiator temperature of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.9 | hwSVGAPFNOVTIUMUnitTemperature | Unit temperature | 单元温度 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Unit temperature of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.10 | hwSVGAPFNOVTIUMGridFrequency | Grid frequency | 源侧频率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid frequency of the device config table for the SVG-APF-NOVTIUM.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.11 | hwSVGAPFNOVTIUMActivePowerOfGrid | Active power of grid | 电网有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Active power of grid of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.12 | hwSVGAPFNOVTIUMReactivePowerOfGrid | Reactive power of grid | 电网无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Reactive power of grid of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.13 | hwSVGAPFNOVTIUMPowerFactorOfGrid | Power factor of grid | 源侧功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Power factor of grid of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.14 | hwSVGAPFNOVTIUMDcVoltageN | DC voltage+N | 直流电压+N | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | DC voltage+N of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.15 | hwSVGAPFNOVTIUMUsedCapacity | Used capacity | 已用容量 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Used capacity of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.16 | hwSVGAPFNOVTIUMApparentPowerOfGrid | Apparent power of grid | 电网视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Apparent power of grid of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.17 | hwSVGAPFNOVTIUMPhaseAVoltage | Phase A voltage of grid | 源侧A相电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A voltage of grid of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.18 | hwSVGAPFNOVTIUMPhaseBVoltage | Phase B voltage of grid | 源侧B相电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B voltage of grid of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.19 | hwSVGAPFNOVTIUMPhaseCVoltage | Phase C voltage of grid | 源侧C相电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C voltage of grid of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.20 | hwSVGAPFNOVTIUMPhaseALoadCurrent | Phase A load current | 负载侧A相电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.21 | hwSVGAPFNOVTIUMPhaseBLoadCurrent | Phase B load current | 负载侧B相电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.22 | hwSVGAPFNOVTIUMPhaseCLoadCurrent | Phase C load current | 负载侧C相电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.23 | hwSVGAPFNOVTIUMPhaseAEquipmentCurrent | Phase A compensation current | A相补偿电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A compensation current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.24 | hwSVGAPFNOVTIUMPhaseBEquipmentCurrent | Phase B compensation current | B相补偿电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B compensation current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.25 | hwSVGAPFNOVTIUMPhaseCEquipmentCurrent | Phase C compensation current | C相补偿电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C compensation current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.26 | hwSVGAPFNOVTIUMPhaseAGridCurrent | Phase A grid current | A相电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.27 | hwSVGAPFNOVTIUMPhaseBGridCurrent | Phase B grid current | B相电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.28 | hwSVGAPFNOVTIUMPhaseCGridCurrent | Phase C grid current | C相电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.29 | hwSVGAPFNOVTIUMHighSideGridVoltage | High side grid voltage | 高压侧电网电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | High side grid voltage of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.30 | hwSVGAPFNOVTIUMHighSideGridCurrent | High side grid current | 高压侧电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | High side grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.31 | hwSVGAPFNOVTIUMHighSideLoadCurrent | High side load current | 高压侧负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | High side load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.32 | hwSVGAPFNOVTIUMHighSideEquipmentCurrent | High side equipment current | 高压侧设备电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | High side equipment current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.33 | hwSVGAPFNOVTIUMGridVoltageDistortionRate | Grid voltage distortion rate | 源侧电压畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid voltage distortion rate of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.34 | hwSVGAPFNOVTIUMGridCurrentDistortionRate | Grid current distortion rate | 源侧电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid current distortion rate of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.35 | hwSVGAPFNOVTIUMLoadCurrentDistortionRate | Load current distortion rate | 负载电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load current distortion rate of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.36 | hwSVGAPFNOVTIUMGridVoltageDistortionRateOfPhaseA | Grid THDU of phase A | 源侧A相THDU | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid THDU of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.37 | hwSVGAPFNOVTIUMGridVoltageDistortionRateOfPhaseB | Grid THDU of phase B | 源侧B相THDU | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid THDU of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.38 | hwSVGAPFNOVTIUMGridVoltageDistortionRateOfPhaseC | Grid THDU of phase C | 源侧C相THDU | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid THDU of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.39 | hwSVGAPFNOVTIUMGridCurrentDistortionRateOfPhaseA | Grid THDI of phase A | 源侧A相THDI | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid THDI of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.40 | hwSVGAPFNOVTIUMGridCurrentDistortionRateOfPhaseB | Grid THDI of phase B | 源侧B相THDI | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid THDI of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.41 | hwSVGAPFNOVTIUMGridCurrentDistortionRateOfPhaseC | Grid THDI of phase C | 源侧C相THDI | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid THDI of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.42 | hwSVGAPFNOVTIUMLoadCurrentDistortionRateOfPhaseA | Load THDI of phase A | 负载侧A相THDI | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load THDI of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.43 | hwSVGAPFNOVTIUMLoadCurrentDistortionRateOfPhaseB | Load THDI of phase B | 负载侧B相THDI | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load THDI of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.44 | hwSVGAPFNOVTIUMLoadCurrentDistortionRateOfPhaseC | Load THDI of phase C | 负载侧C相THDI | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load THDI of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.45 | hwSVGAPFNOVTIUMGridCurrent | Grid current | 电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.46 | hwSVGAPFNOVTIUMNLineGridCurrent | N-line grid current | N线电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | N-line grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.47 | hwSVGAPFNOVTIUMNLineLoadCurrent | N-line load current | N线负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | N-line load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.48 | hwSVGAPFNOVTIUMGridActivePowerOfPhaseA | Grid active power of phase A | A相电网有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid active power of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.49 | hwSVGAPFNOVTIUMGridActivePowerOfPhaseB | Grid active power of phase B | B相电网有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid active power of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.50 | hwSVGAPFNOVTIUMGridActivePowerOfPhaseC | Grid active power of phase C | C相电网有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid active power of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.51 | hwSVGAPFNOVTIUMGridReactivePowerOfPhaseA | Grid reactive power of phase A | A相电网无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid reactive power of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.52 | hwSVGAPFNOVTIUMGridReactivePowerOfPhaseB | Grid reactive power of phase B | B相电网无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid reactive power of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.53 | hwSVGAPFNOVTIUMGridReactivePowerOfPhaseC | Grid reactive power of phase C | C相电网无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid reactive power of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.54 | hwSVGAPFNOVTIUMGridApparentPowerOfPhaseA | Grid apparent power of phase A | A相电网视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid apparent power of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.55 | hwSVGAPFNOVTIUMGridApparentPowerOfPhaseB | Grid apparent power of phase B | B相电网视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid apparent power of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.56 | hwSVGAPFNOVTIUMGridApparentPowerOfPhaseC | Grid apparent power of phase C | C相电网视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid apparent power of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.57 | hwSVGAPFNOVTIUMGridPowerFactorOfPhaseA | Grid power factor of phase A | 源侧A相功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid power factor of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.58 | hwSVGAPFNOVTIUMGridPowerFactorOfPhaseB | Grid power factor of phase B | 源侧B相功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid power factor of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.59 | hwSVGAPFNOVTIUMGridPowerFactorOfPhaseC | Grid power factor of phase C | 源侧C相功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid power factor of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.60 | hwSVGAPFNOVTIUMAPhaseLoadActivePower | A phase load active power | A相负载有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | A phase load active power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.61 | hwSVGAPFNOVTIUMBPhaseLoadActivePower | B phase load active power | B相负载有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | B phase load active power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.62 | hwSVGAPFNOVTIUMCPhaseLoadActivePower | C phase load active power | C相负载有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | C phase load active power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.63 | hwSVGAPFNOVTIUMLoadPowerFactorOfPhaseA | Load power factor of phase A | 负载侧A相无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load power factor of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.64 | hwSVGAPFNOVTIUMLoadPowerFactorOfPhaseB | Load power factor of phase B | 负载侧B相无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load power factor of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.65 | hwSVGAPFNOVTIUMLoadPowerFactorOfPhaseC | Load power factor of phase C | 负载侧C相无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load power factor of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.66 | hwSVGAPFNOVTIUMLoadApparentPowerOfPhaseA | Load apparent power of phase A | A相负载视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load apparent power of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.67 | hwSVGAPFNOVTIUMLoadApparentPowerOfPhaseB | Load apparent power of phase B | B相负载视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load apparent power of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.68 | hwSVGAPFNOVTIUMLoadApparentPowerOfPhaseC | Load apparent power of phase C | C相负载视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load apparent power of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.69 | hwSVGAPFNOVTIUMPhaseALoadPowerFactor | Phase A load power factor | A相负载功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A load power factor of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.70 | hwSVGAPFNOVTIUMPhaseBLoadPowerFactor | Phase B load power factor | B相负载功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B load power factor of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.71 | hwSVGAPFNOVTIUMPhaseCLoadPowerFactor | Phase C load power factor | C相负载功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C load power factor of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.72 | hwSVGAPFNOVTIUMUnbalanceDegreeOfGridCurrent | Unbalance degree of grid current | 电网电流不平衡度 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Unbalance degree of grid current of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.73 | hwSVGAPFNOVTIUMPrimaryGridVoltageA | Primary grid voltage A | 一次电网电压A | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid voltage A of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.74 | hwSVGAPFNOVTIUMPrimaryGridVoltageB | Primary grid voltage B | 一次电网电压B | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid voltage B of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.75 | hwSVGAPFNOVTIUMPrimaryGridVoltageC | Primary grid voltage C | 一次电网电压C | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid voltage C of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.76 | hwSVGAPFNOVTIUMPrimaryGridCurrentA | Primary grid current A | 一次电网电流A | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid current A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.77 | hwSVGAPFNOVTIUMPrimaryGridCurrentB | Primary grid current B | 一次电网电流B | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid current B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.78 | hwSVGAPFNOVTIUMPrimaryGridCurrentC | Primary grid current C | 一次电网电流C | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid current C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.79 | hwSVGAPFNOVTIUMPrimaryEquipmentCurrentA | Primary equipment current A | 一次设备电流A | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary equipment current A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.80 | hwSVGAPFNOVTIUMPrimaryEquipmentCurrentB | Primary equipment current B | 一次设备电流B | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary equipment current B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.81 | hwSVGAPFNOVTIUMPrimaryEquipmentCurrentC | Primary equipment current C | 一次设备电流C | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary equipment current C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.82 | hwSVGAPFNOVTIUMPrimaryLoadCurrentA | Primary load current A | 一次负载电流A | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary load current A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.83 | hwSVGAPFNOVTIUMPrimaryLoadCurrentB | Primary load current B | 一次负载电流B | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary load current B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.84 | hwSVGAPFNOVTIUMPrimaryLoadCurrentC | Primary load current C | 一次负载电流C | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary load current C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.85 | hwSVGAPFNOVTIUMCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.86 | hwSVGAPFNOVTIUMPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.87 | hwSVGAPFNOVTIUMModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.300 | hwSVGAPFNOVTIUMRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.2 | hwSVGAPFNOVTIUMConfig2Table | / | / |  |  | / | / | The config table of SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.1 | hwSVGAPFNOVTIUMConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.2 | hwSVGAPFNOVTIUMDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.3 | hwSVGAPFNOVTIUMStartOperation | Start operation | 系统启动 | 1-Read_Write | 读写 | startup(1), unknown(255) | [启动=1] | Start operation of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate startup
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.4 | hwSVGAPFNOVTIUMStopOperation | Stop operation | 系统停机 | 1-Read_Write | 读写 | startup(1), unknown(255) | [启动=1] | Stop operation of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate startup
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.5 | hwSVGAPFNOVTIUMResetOperation | Reset operation | 系统复位 | 1-Read_Write | 读写 | startup(1), unknown(255) | [启动=1] | Reset operation of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate startup
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.6 | hwSVGAPFNOVTIUMCompensationcurrentLoadRateOfPhaseA | Compensation current load rate of phase A | A相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.7 | hwSVGAPFNOVTIUMCompensationcurrentLoadRateOfPhaseB | Compensation current load rate of phase B | B相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.8 | hwSVGAPFNOVTIUMCompensationcurrentLoadRateOfPhaseC | Compensation current load rate of phase C | C相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.9 | hwSVGAPFNOVTIUMGridFrequencyOfPhaseA | Grid frequency of phase A | 源侧A相频率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid frequency of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.10 | hwSVGAPFNOVTIUMGridFrequencyOfPhaseB | Grid frequency of phase B | 源侧B相频率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid frequency of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.11 | hwSVGAPFNOVTIUMGridFrequencyOfPhaseC | Grid frequency of phase C | 源侧C相频率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid frequency of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.300 | hwSVGAPFNOVTIUMConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG-APF-NOVTIUM.

## SVG-In-Power
SVG-英博电气
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.108 | SVGInPower | SVG-In-Power | SVG-英博电气 | / | / | / | / | SVG-In-Power Equipment.
1.3.6.1.4.1.2011.6.178.1.1.108.1 | hwSVGInPowerRunning1Table | / | / |  |  | / | / | The running table of SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.1 | hwSVGInPowerRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.2 | hwSVGInPowerDeviceStatus | Device status | 装置状态 | 0-Read_Only | 只读 | fault(1), run(2), suspended(3), unknown(255) | [故障=1]/[运行=2]/[停机=3] | Device status of the device config table for the SVG-In-Power. Value 1 indicate fault Value 2 indicate run Value 3 indicate suspended
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.3 | hwSVGInPowerCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the SVG-In-Power. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.4 | hwSVGInPowerPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.5 | hwSVGInPowerModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..247 | 1..247 | Modbus address of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.6 | hwSVGInPowerDeviceCompensationCurrentA | Device compensation current A | 装置补偿电流A | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Device compensation current A of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.7 | hwSVGInPowerDeviceCompensationCurrentB | Device compensation current B | 装置补偿电流B | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Device compensation current B of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.8 | hwSVGInPowerDeviceCompensationCurrentC | Device compensation current C | 装置补偿电流C | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Device compensation current C of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.9 | hwSVGInPowerTemperatureOfTheDevice | Temperature of the device | 装置温度 | 0-Read_Only | 只读 | -100..200 | -100..200 | Temperature of the device of the device config table for the SVG-In-Power.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.10 | hwSVGInPowerEffectiveValueOfLoadCurrentA | Effective value of load current A | 负载电流有效值A | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current A of the device config table for the SVG-In-Power.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.11 | hwSVGInPowerEffectiveValueOfLoadCurrentB | Effective value of load current B | 负载电流有效值B | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current B of the device config table for the SVG-In-Power.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.12 | hwSVGInPowerEffectiveValueOfLoadCurrentC | Effective value of load current C | 负载电流有效值C | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current C of the device config table for the SVG-In-Power.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.13 | hwSVGInPowerEffectiveValueOfLineVoltageAb | Effective value of line voltage AB | 线电压有效值AB | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Effective value of line voltage AB of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.14 | hwSVGInPowerEffectiveValueOfLineVoltageBc | Effective value of line voltage BC | 线电压有效值BC | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Effective value of line voltage BC of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.15 | hwSVGInPowerEffectiveValueOfLineVoltageCa | Effective value of line voltage CA | 线电压有效值CA | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Effective value of line voltage CA of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.16 | hwSVGInPowerSystemCurrentDistortionRate | System current distortion rate | 系统电流畸变率 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | System current distortion rate of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.17 | hwSVGInPowerSystemPowerFactor | System power factor | 系统功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | System power factor of the device config table for the SVG-In-Power.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.18 | hwSVGInPowerEquipmentLoadRate | Equipment load rate | 设备负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Equipment load rate of the device config table for the SVG-In-Power.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.19 | hwSVGInPowerHmiVersion | HMI version | HMI版本 | 0-Read_Only | 只读 | 0..6 | 0..6 | HMI version of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.101 | hwSVGInPowerRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.2 | hwSVGInPowerConfig2Table | / | / |  |  | / | / | The config table of SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.1 | hwSVGInPowerConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.2 | hwSVGInPowerDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.3 | hwSVGInPowerStartAndStopControl | Start and stop control | 启停控制 | 1-Read_Write | 读写 | localcontrol(1), startfromafar(2), stopfromafar(3), unknown(255) | [就地控制=1]/[远方启动=2]/[远方停止=3] | Start and stop control of the device config table for the SVG-In-Power. Value 1 indicate local control Value 2 indicate start from afar Value 3 indicate stop from afar
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.4 | hwSVGInPowerSetDetailModel | Detail model | 详细机型 | 1-Read_Write | 读写 | eightHundredAndOneThousandMm(1), sixHundredAndOneThousandMm(2), unknown(255) | [800 * 1000 mm=1]/[600 * 1000 mm=2] | Detail model of the device config table for the SVG-In-Power. Value 1 indicate 800 * 1000 mm Value 2 indicate 600 * 1000 mm
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.5 | hwSVGInPowerPhAVoltageOfGrid | Phase A voltage of grid | 源侧A相电压 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase A voltage of grid of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.6 | hwSVGInPowerPhBVoltageOfGrid | Phase B voltage of grid | 源侧B相电压 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase B voltage of grid of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.7 | hwSVGInPowerPhCVoltageOfGrid | Phase C voltage of grid | 源侧C相电压 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase C voltage of grid of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.8 | hwSVGInPowerPhALoadCurr | Phase A load current | 负载侧A相电流 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase A load current of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.9 | hwSVGInPowerPhBLoadCurr | Phase B load current | 负载侧B相电流 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase B load current of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.10 | hwSVGInPowerPhCLoadCurr | Phase C load current | 负载侧C相电流 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase C load current of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.11 | hwSVGInPowerPhACompCurr | Phase A compensation current | A相补偿电流 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase A compensation current of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.12 | hwSVGInPowerPhBCompCurr | Phase B compensation current | B相补偿电流 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase B compensation current of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.13 | hwSVGInPowerPhCCompCurr | Phase C compensation current | C相补偿电流 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Phase C compensation current of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.14 | hwSVGInPowerGridTHDUOfPhA | Grid THDU of phase A | 源侧A相THDU | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Grid THDU of phase A of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.15 | hwSVGInPowerGridTHDUOfPhB | Grid THDU of phase B | 源侧B相THDU | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Grid THDU of phase B of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.16 | hwSVGInPowerGridTHDUOfPhC | Grid THDU of phase C | 源侧C相THDU | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Grid THDU of phase C of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.17 | hwSVGInPowerGridTHDIOfPhA | Grid THDI of phase A | 源侧A相THDI | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Grid THDI of phase A of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.18 | hwSVGInPowerGridTHDIOfPhB | Grid THDI of phase B | 源侧B相THDI | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Grid THDI of phase B of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.19 | hwSVGInPowerGridTHDIOfPhC | Grid THDI of phase C | 源侧C相THDI | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Grid THDI of phase C of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.20 | hwSVGInPowerLoadTHDIOfPhA | Load THDI of phase A | 负载侧A相THDI | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Load THDI of phase A of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.21 | hwSVGInPowerLoadTHDIOfPhB | Load THDI of phase B | 负载侧B相THDI | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Load THDI of phase B of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.22 | hwSVGInPowerLoadTHDIOfPhC | Load THDI of phase C | 负载侧C相THDI | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Load THDI of phase C of the device config table for the SVG-In-Power.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.23 | hwSVGInPowerLoadReactivePowerOfPhaseA | Load reactive power of phase A | 负载侧A相无功功率 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Load reactive power of phase A of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.24 | hwSVGInPowerLoadReactivePowerOfPhaseB | Load reactive power of phase B | 负载侧B相无功功率 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Load reactive power of phase B of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.25 | hwSVGInPowerLoadReactivePowerOfPhaseC | Load reactive power of phase C | 负载侧C相无功功率 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Load reactive power of phase C of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.26 | hwSVGInPowerGridPowerFactorOfPhA | Grid power factor of phase A | 源侧A相功率因数 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Grid power factor of phase A of the device config table for the SVG-In-Power.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.27 | hwSVGInPowerGridPowerFactorOfPhB | Grid power factor of phase B | 源侧B相功率因数 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Grid power factor of phase B of the device config table for the SVG-In-Power.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.28 | hwSVGInPowerGridPowerFactorOfPhC | Grid power factor of phase C | 源侧C相功率因数 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Grid power factor of phase C of the device config table for the SVG-In-Power.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.29 | hwSVGInPowerGridFrOfPhA | Grid frequency of phase A | 源侧A相频率 | 0-Read_Only | 只读 | 0..327 | 0..327 | Grid frequency of phase A of the device config table for the SVG-In-Power.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.30 | hwSVGInPowerGridFrOfPhB | Grid frequency of phase B | 源侧B相频率 | 0-Read_Only | 只读 | 0..327 | 0..327 | Grid frequency of phase B of the device config table for the SVG-In-Power.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.31 | hwSVGInPowerGridFrOfPhC | Grid frequency of phase C | 源侧C相频率 | 0-Read_Only | 只读 | 0..327 | 0..327 | Grid frequency of phase C of the device config table for the SVG-In-Power.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.32 | hwSVGInPowerCompCurrLoadRateOfSVGPhA | Compensation current load rate of SVG phase A | SVG A相补偿电流负载率 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Compensation current load rate of SVG phase A of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.33 | hwSVGInPowerCompCurrLoadRateOfSVGPhB | Compensation current load rate of SVG phase B | SVG B相补偿电流负载率 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Compensation current load rate of SVG phase B of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.34 | hwSVGInPowerCompCurrLoadRateOfSVGPhC | Compensation current load rate of SVG phase C | SVG C相补偿电流负载率 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Compensation current load rate of SVG phase C of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.35 | hwSVGInPowerCompCurrLoadRateOfAPFPhA | Compensation current load rate of APF phase A | APF A相补偿电流负载率 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Compensation current load rate of APF phase A of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.36 | hwSVGInPowerCompCurrLoadRateOfAPFPhB | Compensation current load rate of APF phase B | APF B相补偿电流负载率 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Compensation current load rate of APF phase B of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.37 | hwSVGInPowerCompCurrLoadRateOfAPFPhC | Compensation current load rate of APF phase C | APF C相补偿电流负载率 | 0-Read_Only | 只读 | 0..3276 | 0..3276 | Compensation current load rate of APF phase C of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.38 | hwSVGInPoweSwitchType | Switch type | 开关类型 | 1-Read_Write | 读写 | ABB(1), HUAWEI(2), unknown(255) | [ABB=1]/[华为=2] | Switch type of the device config table for the SVG-In-Power. Value 1 indicate ABB Value 2 indicate HUAWEI
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.101 | hwSVGInPowerConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG-In-Power.

## Tap-off Unit
密集母线插接箱
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.121 | TapoffUnit | Tap-off Unit | 密集母线插接箱 | / | / | / | / | Tap-off Unit Equipment.
1.3.6.1.4.1.2011.6.178.1.1.121.1 | hwTapoffUnitRunning1Table | / | / |  |  | / | / | The running table of Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.1 | hwTapoffUnitRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.2 | hwTapoffUnitL1PhaseVoltage | L1 phase voltage | L1相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 phase voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.3 | hwTapoffUnitL1InputCopperBarTemperature | L1 input copper bar temperature | L1输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.4 | hwTapoffUnitL1ThdU | L1 THD-u | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.5 | hwTapoffUnitSwitchStatus | Switch status | 开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [断开=1]/[闭合=2] | Switch status of the device config table for the Tap-off Unit. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.6 | hwTapoffUnitCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Tap-off Unit. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.7 | hwTapoffUnitPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.8 | hwTapoffUnitModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.9 | hwTapoffUnitL2PhaseVoltage | L2 phase voltage | L2相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 phase voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.10 | hwTapoffUnitL3PhaseVoltage | L3 phase voltage | L3相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 phase voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.11 | hwTapoffUnitL1L2LineVoltage | L1-L2 line voltage | L1-L2线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1-L2 line voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.12 | hwTapoffUnitL2L3LineVoltage | L2-L3 line voltage | L2-L3线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2-L3 line voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.13 | hwTapoffUnitL3L1LineVoltage | L3-L1 line voltage | L3-L1线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3-L1 line voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.14 | hwTapoffUnitNPeVoltage | N-PE voltage | N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | N-PE voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.15 | hwTapoffUnitL1Current | L1 current | L1电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L1 current of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.16 | hwTapoffUnitL2Current | L2 current | L2电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L2 current of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.17 | hwTapoffUnitL3Current | L3 current | L3电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L3 current of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.18 | hwTapoffUnitNCurrent | N current | N线电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | N current of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.19 | hwTapoffUnitFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Frequency of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.20 | hwTapoffUnitL1ActivePower | L1 active power | L1有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 active power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.21 | hwTapoffUnitL2ActivePower | L2 active power | L2有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 active power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.22 | hwTapoffUnitL3ActivePower | L3 active power | L3有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 active power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.23 | hwTapoffUnitL1AppearancePower | L1 appearance power | L1视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 appearance power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.24 | hwTapoffUnitL2AppearancePower | L2 appearance power | L2视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 appearance power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.25 | hwTapoffUnitL3AppearancePower | L3 appearance power | L3视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 appearance power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.26 | hwTapoffUnitL1ReactivePower | L1 reactive power | L1无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 reactive power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.27 | hwTapoffUnitL2ReactivePower | L2 reactive power | L2无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 reactive power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.28 | hwTapoffUnitL3ReactivePower | L3 reactive power | L3无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 reactive power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.29 | hwTapoffUnitL1PowerFactor | L1 power factor | L1功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L1 power factor of the device config table for the Tap-off Unit.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.30 | hwTapoffUnitL2PowerFactor | L2 power factor | L2功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L2 power factor of the device config table for the Tap-off Unit.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.31 | hwTapoffUnitL3PowerFactor | L3 power factor | L3功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L3 power factor of the device config table for the Tap-off Unit.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.32 | hwTapoffUnitActiveEnergy | Active energy | 有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active energy of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.33 | hwTapoffUnitL1LoadRatio | L1 load ratio | L1负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L1 load ratio of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.34 | hwTapoffUnitL2LoadRatio | L2 load ratio | L2负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L2 load ratio of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.35 | hwTapoffUnitL3LoadRatio | L3 load ratio | L3负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L3 load ratio of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.36 | hwTapoffUnitL2ThdU | L2 THD-u | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.37 | hwTapoffUnitL3ThdU | L3 THD-u | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.38 | hwTapoffUnitL15ThThdU | L1 5th THD-u | L1 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.39 | hwTapoffUnitL25ThThdU | L2 5th THD-u | L2 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.40 | hwTapoffUnitL35ThThdU | L3 5th THD-u | L3 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.41 | hwTapoffUnitL17ThThdU | L1 7th THD-u | L1 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.42 | hwTapoffUnitL27ThThdU | L2 7th THD-u | L2 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.43 | hwTapoffUnitL37ThThdU | L3 7th THD-u | L3 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.44 | hwTapoffUnitL111ThThdU | L1 11th THD-u | L1 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.45 | hwTapoffUnitL211ThThdU | L2 11th THD-u | L2 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.46 | hwTapoffUnitL311ThThdU | L3 11th THD-u | L3 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.47 | hwTapoffUnitL1ThdI | L1 THD-i | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.48 | hwTapoffUnitL2ThdI | L2 THD-i | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.49 | hwTapoffUnitL3ThdI | L3 THD-i | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.50 | hwTapoffUnitL15ThThdI | L1 5th THD-i | L1 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.51 | hwTapoffUnitL25ThThdI | L2 5th THD-i | L2 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.52 | hwTapoffUnitL35ThThdI | L3 5th THD-i | L3 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.53 | hwTapoffUnitL17ThThdI | L1 7th THD-i | L1 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.54 | hwTapoffUnitL27ThThdI | L2 7th THD-i | L2 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.55 | hwTapoffUnitL37ThThdI | L3 7th THD-i | L3 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.56 | hwTapoffUnitL111ThThdI | L1 11th THD-i | L1 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.57 | hwTapoffUnitL211ThThdI | L2 11th THD-i | L2 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.58 | hwTapoffUnitL311ThThdI | L3 11th THD-i | L3 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.59 | hwTapoffUnitTotalOutputActivePower | Total output active power | 总输出有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output active power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.60 | hwTapoffUnitTotalOutputAppearancePower | Total output appearance power | 总输出视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output appearance power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.61 | hwTapoffUnitTotalOutputReactivePower | Total output reactive power | 总输出无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output reactive power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.62 | hwTapoffUnitL2InputCopperBarTemperature | L2 input copper bar temperature | L2输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.63 | hwTapoffUnitL3InputCopperBarTemperature | L3 input copper bar temperature | L3输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.64 | hwTapoffUnitL1OutputCopperBarTemperature | L1 output copper bar temperature | L1输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.65 | hwTapoffUnitL2OutputCopperBarTemperature | L2 output copper bar temperature | L2输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.66 | hwTapoffUnitL3OutputCopperBarTemperature | L3 output copper bar temperature | L3输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.67 | hwTapoffUnitCopperBarEnvironmentTemperature | Copper bar environment temperature | 铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Copper bar environment temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.68 | hwTapoffUnitL1OutputCopperBarPredictedTemperature | L1 output copper bar predicted temperature | L1输出铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output copper bar predicted temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.69 | hwTapoffUnitL2OutputCopperBarPredictedTemperature | L2 output copper bar predicted temperature | L2输出铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output copper bar predicted temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.70 | hwTapoffUnitL3OutputCopperBarPredictedTemperature | L3 output copper bar predicted temperature | L3输出铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output copper bar predicted temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.71 | hwTapoffUnitTrippingStatus | Tripping status | 脱扣状态 | 0-Read_Only | 只读 | normal(1), tripping(2), unknown(255) | [正常=1]/[脱扣=2] | Tripping status of the device config table for the Tap-off Unit. Value 1 indicate normal Value 2 indicate tripping
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.72 | hwTapoffUnitRunningIndicatorStatus | Running indicator status | 运行灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Running indicator status of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.73 | hwTapoffUnitAlarmIndicatorStatus | Alarm indicator status | 告警灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Alarm indicator status of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.74 | hwTapoffUnitAcInputSwitchIndicator | AC input switch indicator | AC输入开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC input switch indicator of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.75 | hwTapoffUnitAcOutputSwitchIndicator | AC output switch indicator | AC输出开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC output switch indicator of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.76 | hwTapoffUnitSoftwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.77 | hwTapoffUnitHardwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.78 | hwTapoffUnitELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E label of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.79 | hwTapoffUnitESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.80 | hwTapoffUnitM3MeterChipSoftwareVersion | M3 meter chip software version | M3电表芯片软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | M3 meter chip software version of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.300 | hwTapoffUnitRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.2 | hwTapoffUnitConfig2Table | / | / |  |  | / | / | The config table of Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.1 | hwTapoffUnitConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.2 | hwTapoffUnitDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.3 | hwTapoffUnitOpenPhaseThreshold | Open phase threshold | 缺相告警阈值 | 1-Read_Write | 读写 | 0..60 | 0..60 | Open phase threshold of the device config table for the Tap-off Unit.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.4 | hwTapoffUnitHarmonicAlarm | Harmonic alarm | 谐波告警 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Harmonic alarm of the device config table for the Tap-off Unit. Value 1 indicate forbid Value 2 indicate enabled
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.5 | hwTapoffUnitVoltageHarmonicAlarmThreshold | Voltage harmonic alarm threshold | 电压谐波告警阈值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Voltage harmonic alarm threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.6 | hwTapoffUnitCurrentHarmonicAlarmThreshold | Current harmonic alarm threshold | 电流谐波告警阈值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Current harmonic alarm threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.7 | hwTapoffUnitOvervoltageThreshold | Overvoltage threshold | 过压告警阈值 | 1-Read_Write | 读写 | 1050..1300 | 1050..1300 | Overvoltage threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.8 | hwTapoffUnitOvervoltageAcknowledgeTime | Overvoltage acknowledge time | 过压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overvoltage acknowledge time of the device config table for the Tap-off Unit.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.9 | hwTapoffUnitUndervoltageThreshold | Undervoltage threshold | 欠压告警阈值 | 1-Read_Write | 读写 | 750..950 | 750..950 | Undervoltage threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.10 | hwTapoffUnitUndervoltageAcknowledgeTime | Undervoltage acknowledge time | 欠压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Undervoltage acknowledge time of the device config table for the Tap-off Unit.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.11 | hwTapoffUnitOverloadThreshold | Overload threshold | 负载过载阈值 | 1-Read_Write | 读写 | 100..120 | 100..120 | Overload threshold of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.12 | hwTapoffUnitOverloadAcknowledgeTime | Overload acknowledge time | 负载过载确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overload acknowledge time of the device config table for the Tap-off Unit.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.13 | hwTapoffUnitOverfrequencyThreshold | Overfrequency threshold | 频率越限阈值 | 1-Read_Write | 读写 | 10..100 | 10..100 | Overfrequency threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.14 | hwTapoffUnitOverfrequencyAcknowledgeTime | Overfrequency acknowledge time | 频率越限确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overfrequency acknowledge time of the device config table for the Tap-off Unit.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.15 | hwTapoffUnitThreePhaseLoadImbalance | Three-phase load imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..50 | 0..50 | Three-phase load imbalance of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.16 | hwTapoffUnitOvercurrentThreshold | Overcurrent threshold | 电流高阈值 | 1-Read_Write | 读写 | 40..100 | 40..100 | Overcurrent threshold of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.17 | hwTapoffUnitUndercurrentThreshold | Undercurrent threshold | 电流低阈值 | 1-Read_Write | 读写 | 30..80 | 30..80 | Undercurrent threshold of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.300 | hwTapoffUnitConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Tap-off Unit.

## Transformer_LD-B10
变压器_LD-B10
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.106 | Transformer | Transformer_LD-B10 | 变压器_LD-B10 | / | / | / | / | Transformer Equipment.
1.3.6.1.4.1.2011.6.178.1.1.106.1 | hwTransformerRunning1Table | / | / |  |  | / | / | The running table of Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.1 | hwTransformerRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.2 | hwTransformerCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the Transformer. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.3 | hwTransformerPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.4 | hwTransformerModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.5 | hwTransformerAPhaseWindingTemperature | A phase winding temperature | A相温度 | 0-Read_Only | 只读 | -300..2400 | -300..2400 | A phase winding temperature of the device config table for the Transformer.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.6 | hwTransformerBPhaseWindingTemperature | B phase winding temperature | B相温度 | 0-Read_Only | 只读 | -300..2400 | -300..2400 | B phase winding temperature of the device config table for the Transformer.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.7 | hwTransformerCPhaseWindingTemperature | C phase winding temperature | C相温度 | 0-Read_Only | 只读 | -300..2400 | -300..2400 | C phase winding temperature of the device config table for the Transformer.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.101 | hwTransformerRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.2 | hwTransformerConfig2Table | / | / |  |  | / | / | The config table of Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.1 | hwTransformerConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.2 | hwTransformerDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.3 | hwTransformerTransformerHighTemperatureAlarmThreshold | Transformer high temperature alarm threshold | 变压器高温报警阈值 | 1-Read_Write | 读写 | 800..2400 | 800..2400 | Transformer high temperature alarm threshold of the device config table for the Transformer.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.4 | hwTransformerTransformerInputVoltage | Transformer input voltage | 变压器输入电压 | 1-Read_Write | 读写 | 95..385 | 95..385 | Transformer input voltage of the device config table for the Transformer.Multiple:10.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.5 | hwTransformerTransformerOutputVoltage | Transformer output voltage | 变压器输出电压 | 1-Read_Write | 读写 | 3800..4150 | 3800..4150 | Transformer output voltage of the device config table for the Transformer.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.6 | hwTransformerGridCapacity | Grid capacity | 电网容量 | 1-Read_Write | 读写 | 5000..100000 | 5000..100000 | Grid capacity of the device config table for the Transformer.Multiple:100.SigUnitInfo:MVA.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.7 | hwTransformerTransformerCapacity | Transformer capacity | 变压器容量 | 1-Read_Write | 读写 | 1250..2500 | 1250..2500 | Transformer capacity of the device config table for the Transformer.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.8 | hwTransformerTransformerImpedance | Transformer impedance | 变压器阻抗 | 1-Read_Write | 读写 | 600..800 | 600..800 | Transformer impedance of the device config table for the Transformer.Multiple:10000.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.9 | hwTransformerSetDetailModel | Detail model | 详细机型 | 1-Read_Write | 读写 | transformer1(1), transformer2(2), transformer3(3), transformer4(4), transformer5(5), transformer6(6), transformer7(7), transformer8(8), unknown(255) | [变压器1(2400 * 1700 mm)=1]/[变压器2(2200 * 1400 mm)=2]/[变压器3(2400 * 1650 mm)=3]/[变压器4(2200 * 1500 mm)=4]/[变压器5(2300 * 1600 mm)=5]/[变压器6(2000 * 1400 mm)=6]/[变压器7(2200 * 1600 mm)=7]/[变压器8(2484 * 1575 mm)=8] | Detail model of the device config table for the Transformer. Value 1 indicate transformer 1(2400 * 1700 mm) Value 2 indicate transformer 2(2200 * 1400 mm) Value 3 indicate transformer 3(2400 * 1650 mm) Value 4 indicate transformer 4(2200 * 1500 mm) Value 5 indicate transformer 5(2300 * 1600 mm) Value 6 indicate transformer 6(2000 * 1400 mm) Value 7 indicate transformer 7(2200 * 1600 mm) Value 8 indicate transformer 8(2484 * 1575 mm)
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.101 | hwTransformerConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Transformer.

## Transformer-ABB-SCB11-2000
变压器-ABB-SCB11-2000
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.118 | TransformerAbbScb112000 | Transformer-ABB-SCB11-2000 | 变压器-ABB-SCB11-2000 | / | / | / | / | Transformer ABB SCB11 2000 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.118.1 | hwTransformerAbbScb112000Running1Table | / | / |  |  | / | / | The running table of Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.1 | hwTransformerAbbScb112000Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.2 | hwTransformerAbbScb112000APhaseTemperature | A phase temperature | A相温度 | 0-Read_Only | 只读 | -30..240 | -30..240 | A phase temperature of the device config table for the Transformer ABB SCB11 2000.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.3 | hwTransformerAbbScb112000CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Transformer ABB SCB11 2000. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.4 | hwTransformerAbbScb112000PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.5 | hwTransformerAbbScb112000ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.6 | hwTransformerAbbScb112000BPhaseTemperature | B phase temperature | B相温度 | 0-Read_Only | 只读 | -30..240 | -30..240 | B phase temperature of the device config table for the Transformer ABB SCB11 2000.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.7 | hwTransformerAbbScb112000CPhaseTemperature | C phase temperature | C相温度 | 0-Read_Only | 只读 | -30..240 | -30..240 | C phase temperature of the device config table for the Transformer ABB SCB11 2000.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.8 | hwTransformerAbbScb112000DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.9 | hwTransformerAbbScb112000Model | Transformer model | 变压器型号 | 1-Read_Write | 读写 | transformer1(1), transformer2(2), transformer3(3), transformer4(4), transformer5(5), transformer6(6), unknown(255) | [变压器1(2400 * 1500 mm)=1]/[变压器2(2200 * 1400 mm)=2]/[变压器3(2000 * 1400 mm)=3]/[变压器4(2200 * 1500 mm)=4]/[变压器5(2300 * 1600 mm)=5]/[变压器6(2400 * 1600 mm)=6] | Transformer model of the device config table for the Transformer ABB SCB11 2000. Value 1 indicate Transformer 1(2400 * 1500 mm) Value 2 indicate Transformer 2(2200 * 1400 mm) Value 3 indicate Transformer 3(2000 * 1400 mm) Value 4 indicate Transformer 4(2200 * 1500 mm) Value 5 indicate Transformer 5(2300 * 1600 mm) Value 6 indicate Transformer 6(2400 * 1600 mm)
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.10 | hwTransformerAbbScb112000TransformerInputVoltage | Transformer input voltage | 变压器输入电压 | 1-Read_Write | 读写 | 95..385 | 95..385 | Transformer input voltage of the device config table for the Transformer ABB SCB11 2000.Multiple:10.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.11 | hwTransformerAbbScb112000TransformerOutputVoltage | Transformer output voltage | 变压器输出电压 | 1-Read_Write | 读写 | 3800..4150 | 3800..4150 | Transformer output voltage of the device config table for the Transformer ABB SCB11 2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.12 | hwTransformerAbbScb112000GridCapacity | Grid capacity | 电网容量 | 1-Read_Write | 读写 | 5000..100000 | 5000..100000 | Grid capacity of the device config table for the Transformer ABB SCB11 2000.Multiple:100.SigUnitInfo:MVA.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.13 | hwTransformerAbbScb112000TransformerCapacity | Transformer capacity | 变压器容量 | 1-Read_Write | 读写 | 1250..2500 | 1250..2500 | Transformer capacity of the device config table for the Transformer ABB SCB11 2000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.14 | hwTransformerAbbScb112000TransformerImpedance | Transformer impedance | 变压器阻抗 | 1-Read_Write | 读写 | 600..800 | 600..800 | Transformer impedance of the device config table for the Transformer ABB SCB11 2000.Multiple:10000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.15 | hwTransformerAbbScb112000FanStatus | Fan status | 风机状态 | 0-Read_Only | 只读 | Stopped(1), Started(2), unknown(255) | [未开风机=1]/[已开风机=2] | Fan status of the device config table for the Transformer ABB SCB11 2000. Value 1 indicate the fan is Stopped Value 2 indicate the fan is Started
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.101 | hwTransformerAbbScb112000Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Transformer ABB SCB11 2000.

## UPS2000G-L
UPS2000G_L
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.7 | UPS2000GL | UPS2000G_L | UPS2000G_L | / | / | / | / | UPS2000G_L Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1 | hwUPS2000GLRunningAndConfig1Table | / | / |  |  | / | / | The running table of UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.1 | hwUPS2000GLRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.2 | hwUPS2000GLInputVoltage | Input voltage | 输入电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Input voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.3 | hwUPS2000GLInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..7000 | 0..7000 | Input frequency of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.4 | hwUPS2000GLBypassVoltage | Bypass voltage | 旁路电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Bypass voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.5 | hwUPS2000GLBypassFrequency | Bypass frequency | 旁路频率 | 0-Read_Only | 只读 | 0..7000 | 0..7000 | Bypass frequency of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.6 | hwUPS2000GLOutputVoltage | Output voltage | 输出电压 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Output voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.7 | hwUPS2000GLOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..7000 | 0..7000 | Output frequency of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.8 | hwUPS2000GLOutputCurrent | Output current | 输出电流 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Output current of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.9 | hwUPS2000GLOutputLoadPercent | Output load percent | 输出负载百分比 | 0-Read_Only | 只读 | 0..200 | 0..200 | Output load percent of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.10 | hwUPS2000GLPBatteryVoltage | P battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..6600 | 0..6600 | P battery voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.11 | hwUPS2000GLOutputActivePower | Output active power | 输出有功功率 | 0-Read_Only | 只读 | 0..12000 | 0..12000 | Output active power of the device config table for the UPS2000G_L.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.12 | hwUPS2000GLOutputApparentPower | Output apparent power | 输出视在功率 | 0-Read_Only | 只读 | 0..12000 | 0..12000 | Output apparent power of the device config table for the UPS2000G_L.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.13 | hwUPS2000GLBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery capacity of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.14 | hwUPS2000GLBatteryCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | 0..200 | 0..200 | Battery current of the device config table for the UPS2000G_L.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.15 | hwUPS2000GLUpsModeInquiry | UPS mode inquiry | UPS模式查询 | 0-Read_Only | 只读 | powerOnMode(1), standbyMode(2), bypassMode(3), lineMode(4), batteryMode(5), batteryTestMode(6), faultMode(7), ecoMode(8), transferMode(9), shutdownMode(10), unknown(255) | [上电模式=1]/[待机模式=2]/[旁路模式=3]/[市电模式=4]/[电池模式=5]/[电池测试模式=6]/[故障模式=7]/[ECO模式=8]/[转换模式=9]/[关机模式=10] | UPS mode inquiry of the device config table for the UPS2000G_L. Value 1 indicate power on mode Value 2 indicate standby mode Value 3 indicate bypass mode Value 4 indicate line mode Value 5 indicate battery mode Value 6 indicate battery test mode Value 7 indicate fault mode Value 8 indicate eco mode Value 9 indicate transfer mode Value 10 indicate shutdown mode
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.16 | hwUPS2000GLBmsBatteryVoltage | BMS battery voltage | 锂电池电压 | 0-Read_Only | 只读 | 0..600 | 0..600 | BMS battery voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.17 | hwUPS2000GLBmsSoc | BMS SOC | 锂电池SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | BMS SOC of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.18 | hwUPS2000GLBmsBackupTime | BMS backup time | 锂电池备电时间 | 0-Read_Only | 只读 | 0..990 | 0..990 | BMS backup time of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:H.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.19 | hwUPS2000GLBmsBatteryNumber | BMS battery number | 锂电池数量 | 0-Read_Only | 只读 | 0..16 | 0..16 | BMS battery number of the device config table for the UPS2000G_L.SigUnitInfo:pcs.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.20 | hwUPS2000GLBmsBatteryTotalCapacity | BMS battery total capacity | 锂电池总容量 | 0-Read_Only | 只读 | 0..2400 | 0..2400 | BMS battery total capacity of the device config table for the UPS2000G_L.SigUnitInfo:AH.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.21 | hwUPS2000GLBmsBatterySoh | BMS battery SOH | 锂电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | BMS battery SOH of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.22 | hwUPS2000GLProtocolIdInquiry | Protocol id inquiry | 协议ID查询 | 0-Read_Only | 只读 | 0..3 | 0..3 | Protocol id inquiry of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.23 | hwUPS2000GLMainCpuFirmwareVersion | Main CPU firmware version | 主CPU固件版本 | 0-Read_Only | 只读 | 0..20 | 0..20 | Main CPU firmware version of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.24 | hwUPS2000GLModbusFirmwareVersion | Modbus firmware version | Modbus固件版本 | 0-Read_Only | 只读 | 0..4 | 0..4 | Modbus firmware version of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.25 | hwUPS2000GLSerialNumber | Serial number | 序列号 | 0-Read_Only | 只读 | 0..14 | 0..14 | Serial number of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.26 | hwUPS2000GLUpsOutputStatus | UPS output status | UPS输出状态 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | UPS output status of the device config table for the UPS2000G_L. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.27 | hwUPS2000GLUpsBatteryStatus | UPS battery status | UPS电池状态 | 0-Read_Only | 只读 | nothing(1), charging(2), discharging(3), unknown(255) | [无=1]/[充电=2]/[放电=3] | UPS battery status of the device config table for the UPS2000G_L. Value 1 indicate nothing Value 2 indicate charging Value 3 indicate discharging
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.28 | hwUPS2000GLCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the UPS2000G_L. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.29 | hwUPS2000GLSlotNo | Slot No. | 槽位号 | 0-Read_Only | 只读 | 0..6 | 0..6 | Slot No. of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.30 | hwUPS2000GLPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.31 | hwUPS2000GLModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.32 | hwUPS2000GLDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.33 | hwUPS2000GLAcOutputRatingVoltage | AC output rating voltage | 输出额定电压 | 1-Read_Write | 读写 | twoHundredAndTwenty(1), twoHundredAndThirty(2), twoHundredAndForty(3), unknown(255) | [220=1]/[230=2]/[240=3] | AC output rating voltage of the device config table for the UPS2000G_L. Value 1 indicate 220 Value 2 indicate 230 Value 3 indicate 240
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.34 | hwUPS2000GLBatteryBulkVoltage | Battery bulk voltage | 电池均充电压 | 1-Read_Write | 读写 | 535..570 | 535..570 | Battery bulk voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.35 | hwUPS2000GLBatteryFloatVoltage | Battery float voltage | 电池浮充电压 | 1-Read_Write | 读写 | 510..560 | 510..560 | Battery float voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.36 | hwUPS2000GLBatteryUnderVoltage | Battery under voltage | 电池截止电压 | 1-Read_Write | 读写 | 440..460 | 440..460 | Battery under voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.37 | hwUPS2000GLCurrentMaxChargingCurrent | Current max charging current | 最大充电电流 | 1-Read_Write | 读写 | 10..60 | 10..60 | Current max charging current of the device config table for the UPS2000G_L.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.38 | hwUPS2000GLParallelNumber | Parallel number | 并机数量 | 1-Read_Write | 读写 | 1..4 | 1..4 | Parallel number of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.39 | hwUPS2000GLOperationLogic | Operation logic | ECO模式使能 | 1-Read_Write | 读写 | onLineMode(1), ecoMode(2), unknown(255) | [联机模式=1]/[ECO模式=2] | Operation logic of the device config table for the UPS2000G_L. Value 1 indicate on-line mode Value 2 indicate eco mode
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.40 | hwUPS2000GLBatteryMaxDischargingTime | Battery max discharging time | 电池最大放电时间 | 1-Read_Write | 读写 | 0..48 | 0..48 | Battery max discharging time of the device config table for the UPS2000G_L.SigUnitInfo:H.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.41 | hwUPS2000GLBatteryTestCapacity | Battery test capacity | 电池测试容量 | 1-Read_Write | 读写 | 10..50 | 10..50 | Battery test capacity of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.42 | hwUPS2000GLSettingBmsBatteryRatedCapacity | Setting BMS battery rated capacity | 锂电池额定容量 | 1-Read_Write | 读写 | 50..2400 | 50..2400 | Setting BMS battery rated capacity of the device config table for the UPS2000G_L.SigUnitInfo:AH.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.300 | hwUPS2000GLRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS2000G_L.

## UPS5000-H
UPS5000-H
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.112 | UPS5000H | UPS5000-H | UPS5000-H | / | / | / | / | UPS5000-H Equipment.
1.3.6.1.4.1.2011.6.178.1.1.112.1 | hwUPS5000HRunning1Table | / | / |  |  | / | / | The running table of UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.1 | hwUPS5000HRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.2 | hwUPS5000HPowerSupplyStatus | Power supply status | 供电状态 | 0-Read_Only | 只读 | nopowersupplied(1), bypassmode(2), normalmode(3), batterymode(4), sourcesharemode(5), mainseco(6), batteryeco(7), unknown(255) | [均不供电=1]/[旁路供电=2]/[主路逆变供电=3]/[电池逆变供电=4]/[联合供电=5]/[市电ECO=6]/[电池ECO=7] | Power supply status of the device config table for the UPS5000-H. Value 1 indicate no power supplied Value 2 indicate bypass mode Value 3 indicate normal mode Value 4 indicate battery mode Value 5 indicate source-share mode Value 6 indicate mains eco Value 7 indicate battery eco
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.3 | hwUPS5000HPhaseAInputVoltage | Phase A input voltage | A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase A input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.4 | hwUPS5000HBpmPhaseAInputVoltage | BPM phase A input voltage | 旁路A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase A input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.5 | hwUPS5000HPositiveBatteryVoltage | Positive battery voltage | 正组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Positive battery voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.6 | hwUPS5000HRackPhaseAOutputVoltage | Ph. A output volt. | A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase A output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.7 | hwUPS5000HAmbientTemperature | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Ambient temperature of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.8 | hwUPS5000HAmbientHumidity | Ambient humidity | 环境湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Ambient humidity of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.9 | hwUPS5000HCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the UPS5000-H. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.10 | hwUPS5000HELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.11 | hwUPS5000HSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.12 | hwUPS5000HMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.13 | hwUPS5000HIp | IP | IP地址 | 0-Read_Only | 只读 |  |  | IP of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.14 | hwUPS5000HEsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.15 | hwUPS5000HSystemCapacity | System capacity | 整机机型容量 | 0-Read_Only | 只读 | 20..3000 | 20..3000 | System capacity of the device config table for the UPS5000-H.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.16 | hwUPS5000HRunningStatus | Running status | 运行状态 | 0-Read_Only | 只读 | single(1), parallel(2), singleeco(3), paralleleco(4), selfloadmode(5), convertermode(6), singleseco(7), parallelseco(8), unknown(255) | [单机=1]/[并机=2]/[单机ECO=3]/[并机ECO=4]/[自老化模式=5]/[变频器模式=6]/[单机智能在线模式=7]/[并机智能在线模式=8] | Running status of the device config table for the UPS5000-H. Value 1 indicate single Value 2 indicate parallel Value 3 indicate single eco Value 4 indicate parallel eco Value 5 indicate self-load mode Value 6 indicate converter mode Value 7 indicate single s-eco Value 8 indicate parallel s-eco
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.17 | hwUPS5000HBatteryStatus | Battery status | 电池状态 | 0-Read_Only | 只读 | notconnected(1), nonchargingnondischarge(2), hibernation(3), floatcharging(4), equalizedcharging(5), discharging(6), charging(7), unknown(255) | [未接入=1]/[非充非放=2]/[休眠=3]/[浮充=4]/[均充=5]/[放电=6]/[充电=7] | Battery status of the device config table for the UPS5000-H. Value 1 indicate not connected Value 2 indicate non-charging non-discharge Value 3 indicate hibernation Value 4 indicate float charging Value 5 indicate equalized charging Value 6 indicate discharging Value 7 indicate charging
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.18 | hwUPS5000HPhaseBInputVoltage | Phase B input voltage | B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase B input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.19 | hwUPS5000HPhaseCInputVoltage | Phase C input voltage | C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase C input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.20 | hwUPS5000HAbInputLineVoltage | AB input line voltage | AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | AB input line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.21 | hwUPS5000HBcInputLineVoltage | BC input line voltage | BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BC input line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.22 | hwUPS5000HCaInputLineVoltage | CA input line voltage | CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | CA input line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.23 | hwUPS5000HPhaseAInputCurrent | Phase A input current | A相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Phase A input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.24 | hwUPS5000HPhaseBInputCurrent | Phase B input current | B相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Phase B input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.25 | hwUPS5000HPhaseCInputCurrent | Phase C input current | C相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Phase C input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.26 | hwUPS5000HInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input frequency of the device config table for the UPS5000-H.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.27 | hwUPS5000HPhaseAInputPowerFactor | Phase A input power factor | A相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase A input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.28 | hwUPS5000HPhaseBInputPowerFactor | Phase B input power factor | B相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase B input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.29 | hwUPS5000HPhaseCInputPowerFactor | Phase C input power factor | C相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase C input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.30 | hwUPS5000HPositiveBusVoltage | Positive bus voltage | 正母线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Positive bus voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.31 | hwUPS5000HNegativeBusVoltage | Negative bus voltage | 负母线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Negative bus voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.32 | hwUPS5000HZeroSequenceCurrent | Zero sequence current | 零序电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Zero sequence current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.33 | hwUPS5000HModuleTemperature | Module temperature | 模块温度 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Module temperature of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.34 | hwUPS5000HBpmPhaseBInputVoltage | BPM phase B input voltage | 旁路B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase B input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.35 | hwUPS5000HBpmPhaseCInputVoltage | BPM phase C input voltage | 旁路C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase C input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.36 | hwUPS5000HBpmAbLineVoltage | BPM AB line voltage | 旁路AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM AB line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.37 | hwUPS5000HBpmBcLineVoltage | BPM BC line voltage | 旁路BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM BC line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.38 | hwUPS5000HBpmCaLineVoltage | BPM CA line voltage | 旁路CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM CA line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.39 | hwUPS5000HBpmInputFrequency | BPM input frequency | 旁路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM input frequency of the device config table for the UPS5000-H.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.40 | hwUPS5000HBpmPhaseAOutputVoltage | BPM phase A output voltage | 旁路A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase A output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.41 | hwUPS5000HBpmPhaseBOutputVoltage | BPM phase B output voltage | 旁路B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase B output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.42 | hwUPS5000HBpmPhaseCOutputVoltage | BPM phase C output voltage | 旁路C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase C output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.43 | hwUPS5000HBpmAbOutputLineVoltage | BPM AB output line voltage | 旁路AB输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM AB output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.44 | hwUPS5000HBpmBcOutputLineVoltage | BPM BC output line voltage | 旁路BC输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM BC output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.45 | hwUPS5000HBpmCaOutputLineVoltage | BPM CA output line voltage | 旁路CA输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM CA output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.46 | hwUPS5000HBpmPhaseAInputCurrent | BPM phase A input current | 旁路A相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM phase A input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.47 | hwUPS5000HBpmPhaseBInputCurrent | BPM phase B input current | 旁路B相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM phase B input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.48 | hwUPS5000HBpmPhaseCInputCurrent | BPM phase C input current | 旁路C相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM phase C input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.49 | hwUPS5000HRackPhaseBOutputVoltage | Ph. B output volt. | B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase B output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.50 | hwUPS5000HRackPhaseCOutputVoltage | Ph. C output volt. | C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase C output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.51 | hwUPS5000HRackAbOutputLineVoltage | Rack AB output line voltage | 机架AB输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack AB output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.52 | hwUPS5000HRackBcOutputLineVoltage | Rack BC output line voltage | 机架BC输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack BC output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.53 | hwUPS5000HRackCaOutputLineVoltage | Rack CA output line voltage | 机架CA输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack CA output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.54 | hwUPS5000HRackPhaseAOutputCurrent | Ph. A output cur. | A相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Rack phase A output current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.55 | hwUPS5000HRackPhaseBOutputCurrent | Ph. B output cur. | B相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Rack phase B output current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.56 | hwUPS5000HRackPhaseCOutputCurrent | Ph. C output cur. | C相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Rack phase C output current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.57 | hwUPS5000HRackOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack output frequency of the device config table for the UPS5000-H.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.58 | hwUPS5000HRackPhaseAOutputActivePower | Ph. A output active power | A相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.59 | hwUPS5000HRackPhaseBOutputActivePower | Ph. B output active power | B相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.60 | hwUPS5000HRackPhaseCOutputActivePower | Ph. C output active power | C相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.61 | hwUPS5000HRackPhaseAOutputApparentPower | Ph. A output apparent power | A相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.62 | hwUPS5000HRackPhaseBOutputApparentPower | Ph. B output apparent power | B相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.63 | hwUPS5000HRackPhaseCOutputApparentPower | Ph. C output apparent power | C相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.64 | hwUPS5000HRackPhaseAOutputReactivePower | Rack phase A output reactive power | A相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.65 | hwUPS5000HRackPhaseBOutputReactivePower | Rack phase B output reactive power | B相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.66 | hwUPS5000HRackPhaseCOutputReactivePower | Rack phase C output reactive power | C相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.67 | hwUPS5000HRackPhaseAOutputPowerFactor | Ph. A output power factor | A相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Rack phase A output power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.68 | hwUPS5000HRackPhaseBOutputPowerFactor | Ph. B output power factor | B相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Rack phase B output power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.69 | hwUPS5000HRackPhaseCOutputPowerFactor | Ph. C output power factor | C相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Rack phase C output power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.70 | hwUPS5000HRackPhaseAOutputLoadPercentage | Ph. A output load ratio | A相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Rack phase A output load percentage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.71 | hwUPS5000HRackPhaseBOutputLoadPercentage | Ph. B output load ratio | B相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Rack phase B output load percentage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.72 | hwUPS5000HRackPhaseCOutputLoadPercentage | Ph. C output load ratio | C相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Rack phase C output load percentage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.73 | hwUPS5000HRackPhaseAOutputCurrCrestRatio | Rack phase A output curr. crest ratio | 机架A相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack phase A output crest ratio of the device config table for the UPS5000-H.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.74 | hwUPS5000HRackPhaseBOutputCurrCrestRatio | Rack phase B output curr. crest ratio | 机架B相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack phase B output crest ratio of the device config table for the UPS5000-H.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.75 | hwUPS5000HRackPhaseCOutputCurrCrestRatio | Rack phase C output curr. crest ratio | 机架C相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack phase C output crest ratio of the device config table for the UPS5000-H.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.76 | hwUPS5000HSystemPhaseAOutputActivePower | System phase A output active power | 系统A相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase A output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.77 | hwUPS5000HSystemPhaseBOutputActivePower | System phase B output active power | 系统B相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase B output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.78 | hwUPS5000HSystemPhaseCOutputActivePower | System phase C output active power | 系统C相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase C output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.79 | hwUPS5000HSystemPhaseAOutputApparentPower | System phase A output apparent power | 系统A相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase A output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.80 | hwUPS5000HSystemPhaseBOutputApparentPower | System phase B output apparent power | 系统B相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase B output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.81 | hwUPS5000HSystemPhaseCOutputApparentPower | System phase C output apparent power | 系统C相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase C output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.82 | hwUPS5000HSystemPhaseAOutputReactivePower | System phase A output reactive power | 系统A相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase A output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.83 | hwUPS5000HSystemPhaseBOutputReactivePower | System phase B output reactive power | 系统B相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase B output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.84 | hwUPS5000HSystemPhaseCOutputReactivePower | System phase C output reactive power | 系统C相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase C output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.85 | hwUPS5000HNegativeBatteryVoltage | Negative battery voltage | 负组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Negative battery voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.86 | hwUPS5000HPositiveBatteryCurrent | Positive battery current | 正组电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | Positive battery current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.87 | hwUPS5000HNegativeBatteryCurrent | Negative battery current | 负组电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | Negative battery current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.88 | hwUPS5000HBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -200..800 | -200..800 | Battery temperature of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.90 | hwUPS5000HBatteryRemainingCapacity | Battery remaining capacity | 电池剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery remaining capacity of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.91 | hwUPS5000HNumberOfOnlineModules | Number of online modules | 在线模块个数 | 0-Read_Only | 只读 | 0..20 | 0..20 | Number of online modules of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.92 | hwUPS5000HModuleOnlineStatus | Module online status | 模块在位状态 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Module online status of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.93 | hwUPS5000HEnergyFlowDiagram1 | Energy flow diagram 1 | 能量流图1 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 1 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.94 | hwUPS5000HEnergyFlowDiagram2 | Energy flow diagram 2 | 能量流图2 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 2 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.95 | hwUPS5000HEnergyFlowDiagram3 | Energy flow diagram 3 | 能量流图3 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 3 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.96 | hwUPS5000HEnergyFlowDiagram4 | Energy flow diagram 4 | 能量流图4 | 0-Read_Only | 只读 | hollow(1), solid(2), downwardflow(3), upwardflow(4), unknown(255) | [空心=1]/[实心=2]/[向下流动=3]/[向上流动=4] | Energy flow diagram 4 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate downward flow Value 4 indicate upward flow
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.97 | hwUPS5000HEnergyFlowDiagram5 | Energy flow diagram 5 | 能量流图5 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 5 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.98 | hwUPS5000HEnergyFlowDiagram6 | Energy flow diagram 6 | 能量流图6 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 6 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.99 | hwUPS5000HEnergyFlowDiagram7 | Energy flow diagram 7 | 能量流图7 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), Leftflow(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[向左流动=4] | Energy flow diagram 7 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate left flow
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.100 | hwUPS5000HEnergyFlowDiagram8 | Energy flow diagram 8 | 能量流图8 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), Leftflow(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[向左流动=4] | Energy flow diagram 8 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate left flow
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.101 | hwUPS5000HBatterySoh | Battery SOH | 电池SOH | 0-Read_Only | 只读 | good(1), maintain(2), abnormal(3), unknown(255) | [良好=1]/[需维护=2]/[异常=3] | Battery SOH of the device config table for the UPS5000-H. Value 1 indicate good Value 2 indicate maintain Value 3 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.102 | hwUPS5000HVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.103 | hwUPS5000HCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | Current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.104 | hwUPS5000HCoupledInductorSideCabinet | Voltage format | 电压制式 | 0-Read_Only | 只读 | threePhasefourWire(1), threePhasethreeWire(2), unknown(255) | [三相四线=1]/[三相三线=2] | Coupled inductor side cabinet of the device config table for the UPS5000-H. Value 1 indicate three-phase four-wire Value 2 indicate three-phase three-wire
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.105 | hwUPS5000HSwitchSideCabinet | Switch side cabinet | 开关边柜 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Switch side cabinet of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.106 | hwUPS5000HTopAirFlowSideCabinet | Top air flow side cabinet | 顶出风边柜 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Top air flow side cabinet of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.107 | hwUPS5000HBottomCablingSideCabinet | Bottom cabling side cabinet | 进线边柜 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Bottom cabling side cabinet of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.108 | hwUPS5000HMainsInputACopperBarTemp | Mains input A copper bar temp | 主路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.109 | hwUPS5000HMainsInputBCopperBarTemp | Mains input B copper bar temp | 主路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.110 | hwUPS5000HMainsInputCCopperBarTemp | Mains input C copper bar temp | 主路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.111 | hwUPS5000HMainsInputNCopperBarTemp | Mains input N copper bar temp | 主路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.112 | hwUPS5000HMainsInputCopperBarEnvTemp | Mains input copper bar env temp | 主路输入铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.113 | hwUPS5000HOutputACopperBarTemp | Output A copper bar temp | 输出A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.114 | hwUPS5000HOutputBCopperBarTemp | Output B copper bar temp | 输出B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.115 | hwUPS5000HOutputCCopperBarTemp | Output C copper bar temp | 输出C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.116 | hwUPS5000HOutputNCopperBarTemp | Output N copper bar temp | 输出N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.117 | hwUPS5000HOutputCopperBarEnvTemp | Output copper bar env temp | 输出环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.118 | hwUPS5000HBypassInputACopperBarTemp | Bypass input A copper bar temp | 旁路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.119 | hwUPS5000HBypassInputBCopperBarTemp | Bypass input B copper bar temp | 旁路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.120 | hwUPS5000HBypassInputCCopperBarTemp | Bypass input C copper bar temp | 旁路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.121 | hwUPS5000HBypassInputNCopperBarTemp | Bypass input N copper bar temp | 旁路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.122 | hwUPS5000HBypassInputCopperEnvironmentTemp | Bypass input copper environment temp | 旁路输入铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input copper environment temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.123 | hwUPS5000HBattPositCopperBarTemp | Batt posit copper bar temp | 电池正铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt posit copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.124 | hwUPS5000HBattNegativeCopperBarTemp | Batt negative copper bar temp | 电池负铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt negative copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.125 | hwUPS5000HBattCopperCopperBarEnvTemp | Batt copper bar ambient temp | 电池铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt copper copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.126 | hwUPS5000HSwitchCabinetMainsInputACopperBarTemp | Switch cabinet mains input A copper bar temp | 开关柜主路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.127 | hwUPS5000HSwitchCabinetMainsInputBCopperBarTemp | Switch cabinet mains input B copper bar temp | 开关柜主路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.128 | hwUPS5000HSwitchCabinetMainsInputCCopperBarTemp | Switch cabinet mains input C copper bar temp | 开关柜主路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.129 | hwUPS5000HSwitchCabinetMainsInputNCopperBarTemp | Switch cabinet mains input N copper bar temp | 开关柜主路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.130 | hwUPS5000HSwitchCabinetMainsInputCopperBarEnvBarTemp | Switch cabinet mains input copper bar env bar temp | 开关柜主路输入铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input copper bar env bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.131 | hwUPS5000HSwitchCabinetOutputACopperBarTemp | Switch cabinet output A copper bar temp | 开关柜输出A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.132 | hwUPS5000HSwitchCabinetOutputBCopperBarTemp | Switch cabinet output B copper bar temp | 开关柜输出B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.133 | hwUPS5000HSwitchCabinetOutputCCopperBarTemp | Switch cabinet output C copper bar temp | 开关柜输出C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.134 | hwUPS5000HSwitchCabinetOutputNCopperBarTemp | Switch cabinet output N copper bar temp | 开关柜输出N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.135 | hwUPS5000HSwitchCabinetOutputCopperBarEnvTemp | Switch cabinet output copper bar env temp | 开关柜输出环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.136 | hwUPS5000HSwitchCabinetBypassInputACopperBarTemp | Switch cabinet bypass input A copper bar temp | 开关柜旁路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.137 | hwUPS5000HSwitchCabinetBypassInputBCopperBarTemp | Switch cabinet bypass input B copper bar temp | 开关柜旁路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.138 | hwUPS5000HSwitchCabinetBypassInputCCopperBarTemp | Switch cabinet bypass input C copper bar temp | 开关柜旁路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.139 | hwUPS5000HSwitchCabinetBypassInputNCopperBarTemp | Switch cabinet bypass input N copper bar temp | 开关柜旁路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.140 | hwUPS5000HSwitchCabinetBypassInputCopperBarEnvTemp | Switch cabinet bypass input copper bar env temp | 开关柜旁路输入环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.141 | hwUPS5000HOutputSwitchTemp | Output switch temp | 输出开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output switch temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.142 | hwUPS5000HBypassInputSwitchTemp | Bypass input switch temp | 旁路输入开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input switch temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.143 | hwUPS5000HMainsInputSwitchTemp | Mains input switch temp | 主路输入开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input switch temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.144 | hwUPS5000HMainsInputACopperBarPredictTemp | Mains input A copper bar predict temp | 主路输入A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.145 | hwUPS5000HMainsInputBCopperBarPredictTemp | Mains input B copper bar predict temp | 主路输入B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.146 | hwUPS5000HMainsInputCCopperBarPredictTemp | Mains input C copper bar predict temp | 主路输入C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.147 | hwUPS5000HOutputACopperBarPredictTemp | Output A copper bar predict temp | 输出A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.148 | hwUPS5000HOutputBCopperBarPredictTemp | Output B copper bar predict temp | 输出B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.149 | hwUPS5000HOutputCCopperBarPredictTemp | Output C copper bar predict temp | 输出C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.150 | hwUPS5000HBypassInputACopperBarPredictTemp | Bypass input A copper bar predict temp | 旁路输入A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.151 | hwUPS5000HBypassInputBCopperBarPredictTemp | Bypass input B copper bar predict temp | 旁路输入B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.152 | hwUPS5000HBypassInputCCopperBarPredictTemp | Bypass input C copper bar predict temp | 旁路输入C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.153 | hwUPS5000HBattPositCopperBarPredictTemp | Batt posit copper bar predict temp | 电池正铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt posit copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.154 | hwUPS5000HBattNegativeCopperBarPredictTemp | Batt negative copper bar predict temp | 电池负铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt negative copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.155 | hwUPS5000HSwitchCabinetMainsInputACopperBarPredictTemp | Switch cabinet mains input A copper bar predict temp | 开关柜主路输入A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.156 | hwUPS5000HSwitchCabinetMainsInputBCopperBarPredictTemp | Switch cabinet mains input B copper bar predict temp | 开关柜主路输入B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.157 | hwUPS5000HSwitchCabinetMainsInputCCopperBarPredictTemp | Switch cabinet mains input C copper bar predict temp | 开关柜主路输入C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.158 | hwUPS5000HSwitchCabinetOutputACopperBarPredictTemp | Switch cabinet output A copper bar predict temp | 开关柜输出A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.159 | hwUPS5000HSwitchCabinetOutputBCopperBarPredictTemp | Switch cabinet output B copper bar predict temp | 开关柜输出B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.160 | hwUPS5000HSwitchCabinetOutputCCopperBarPredictTemp | Switch cabinet output C copper bar predict temp | 开关柜输出C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.161 | hwUPS5000HSwitchCabinetBypassInputACopperBarPredictTemp | Switch cabinet bypass input A copper bar predict temp | 开关柜旁路输入A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.162 | hwUPS5000HSwitchCabinetBypassInputBCopperBarPredictTemp | Switch cabinet bypass input B copper bar predict temp | 开关柜旁路输入B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.163 | hwUPS5000HSwitchCabinetBypassInputCCopperBarPredictTemp | Switch cabinet bypass input C copper bar predict temp | 开关柜旁路输入C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.164 | hwUPS5000HPowerVersion | Power Version | 功率版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Power Version of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.165 | hwUPS5000HBatteryType | Battery type | 电池类型 | 0-Read_Only | 只读 | vrla(1), lithiumbattery(2), unknown(255) | [铅酸电池=1]/[锂电电池=2] | Battery type of the device config table for the UPS5000-H. Value 1 indicate vrla Value 2 indicate lithium battery
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.166 | hwUPS5000HBatteryBackupTime | Backup time | 备电时间 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery backup time of the device config table for the UPS5000-H.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.167 | hwUPS5000HVoltageLevel | Voltage level | 电压等级 | 0-Read_Only | 只读 | twoHundred(1), twoHundredAndEight(2), twoHundredAndTwenty(3), threeHundredAndEighty(4), fourHundred(5), fourHundredAndFifteen(6), fourHundredAndEighty(7), sixHundred(8), sixHundredAndNinety(9), threeHundredAndSixty(10), twoHundredAndThirty(11), fourHundredAndTwenty(12), twoHundredAndTen(13), unknown(255) | [200=1]/[208=2]/[220=3]/[380=4]/[400=5]/[415=6]/[480=7]/[600=8]/[690=9]/[360=10]/[230=11]/[420=12]/[210=13] | Voltage level of the device config table for the UPS5000-H. Value 1 indicate 200 Value 2 indicate 208 Value 3 indicate 220 Value 4 indicate 380 Value 5 indicate 400 Value 6 indicate 415 Value 7 indicate 480 Value 8 indicate 600 Value 9 indicate 690 Value 10 indicate 360 Value 11 indicate 230 Value 12 indicate 420 Value 13 indicate 210SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.168 | hwUPS5000HSystemOutputFrequency | System output frequency | 系统输出频率 | 0-Read_Only | 只读 | fifty(1), sixty(2), unknown(255) | [50=1]/[60=2] | System output frequency of the device config table for the UPS5000-H. Value 1 indicate 50 Value 2 indicate 60SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.169 | hwUPS5000HBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 5..9999 | 5..9999 | Battery capacity of the device config table for the UPS5000-H.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.170 | hwUPS5000HWorkMode | Work mode | 工作模式 | 0-Read_Only | 只读 | normalmode(1), eco(2), selfloadmode(3), convertermode(4), seco(5), unknown(255) | [正常模式=1]/[ECO=2]/[自老化模式=3]/[变频器模式=4]/[智能在线模式=5] | Work mode of the device config table for the UPS5000-H. Value 1 indicate normal mode Value 2 indicate eco Value 3 indicate self-load mode Value 4 indicate converter mode Value 5 indicate s-eco
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.201 | hwUPS5000HRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.2 | hwUPS5000HConfig2Table | / | / |  |  | / | / | The config table of UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.1 | hwUPS5000HConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.2 | hwUPS5000HDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.3 | hwUPS5000HTemperaturePrediction | Temperature prewarning | 温度预警 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Temperature Prediction of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.4 | hwUPS5000HSchedShallowDisTest | Sched. shallow dis. test | 定时浅放电测试 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Sched. shallow dis. test of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.5 | hwUPS5000HSchedShallowDisTestTime | Sched. shallow dis. test time | 定时浅放电测试时间段 | 1-Read_Write | 读写 | zeroToSixHourly(1), sixToTwelveHourly(2), twelveToEighteenHourly(3), eighteenToTwentyfourHourly(4), unknown(255) | [00:00~06:00=1]/[06:00~12:00=2]/[12:00~18:00=3]/[18:00~24:00=4] | Sched. shallow dis. test time of the device config table for the UPS5000-H. Value 1 indicate 00:00~06:00 Value 2 indicate 06:00~12:00 Value 3 indicate 12:00~18:00 Value 4 indicate 18:00~24:00
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.6 | hwUPS5000HSchedShallowDisTestInterval | Sched. shallow dis. test interval | 定时浅放电测试间隔 | 1-Read_Write | 读写 | 30..90 | 30..90 | Sched. shallow dis. test interval of the device config table for the UPS5000-H.SigUnitInfo:days.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.7 | hwUPS5000HShallowDisTestDisRatio | Shallow dis. test dis. ratio | 浅放电测试放电百分比 | 1-Read_Write | 读写 | 10..50 | 10..50 | Shallow dis. test dis. ratio of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.8 | hwUPS5000HSmartParallelSleepMode | Smart parallel sleep mode | 智能并机休眠模式 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Smart parallel sleep mode of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.9 | hwUPS5000HSupportedOrNotPeakShaving | Supported or not peak shaving | 是否支持削峰填谷 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Supported or not peak shaving of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.10 | hwUPS5000HPeakShaving | Peak shaving | 削峰填谷 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Peak shaving of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.11 | hwUPS5000HVrlaBatteryVoltageToExitPeakShaving | hwUPS5000HVrlaBatteryVoltageToExitPeakShaving | 铅酸退出削峰填谷模式的电压 | 1-Read_Write | 读写 | 160..230 | 160..230 | VRLA battery voltage to exit peak shaving of the device config table for the UPS5000-H.Multiple:100.SigUnitInfo:V/cell.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.12 | hwUPS5000HPeakShavingRepetitionMethodSunday | Peak shaving repetition method-Sunday | 削峰填谷重复方式-星期天 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Sunday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.13 | hwUPS5000HPeakShavingRepetitionMethodMonday | Peak shaving repetition method-Monday | 削峰填谷重复方式-星期一 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Monday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.14 | hwUPS5000HPeakShavingRepetitionMethodTuesday | Peak shaving repetition method-Tuesday | 削峰填谷重复方式-星期二 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Tuesday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.15 | hwUPS5000HPeakShavingRepetitionMethodWednesday | Peak shaving repetition method-Wednesday | 削峰填谷重复方式-星期三 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Wednesday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.16 | hwUPS5000HPeakShavingRepetitionMethodThursday | Peak shaving repetition method-Thursday | 削峰填谷重复方式-星期四 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Thursday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.17 | hwUPS5000HPeakShavingRepetitionMethodFriday | Peak shaving repetition method-Friday | 削峰填谷重复方式-星期五 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Friday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.18 | hwUPS5000HPeakShavingRepetitionMethodSaturday | Peak shaving repetition method-Saturday | 削峰填谷重复方式-星期六 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Saturday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.19 | hwUPS5000HNormalBackupTimeReservedForPeakShaving | Normal backup time reserved for peak shaving | 削峰填谷预留正常备电时间 | 1-Read_Write | 读写 | 5..600 | 5..600 | Normal backup time reserved for peak shaving of the device config table for the UPS5000-H.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.20 | hwUPS5000HSocThresholdToExitPeakShaving | SOC threshold to exit peak shaving | 退出削峰填谷模式的SOC阈值 | 1-Read_Write | 读写 | 0..100 | 0..100 | SOC threshold to exit peak shaving of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.27 | hwUPS5000HInputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | onePowerSource(1), twoPowerSources(2), unknown(255) | [主旁同源=1]/[主旁不同源=2] | Input mode of the device config table for the UPS5000-H. Value 1 indicate one power source Value 2 indicate two power sources
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.28 | hwUPS5000HBatterySohPercentage | Battery SOH | 电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery SOH Percentage of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.66 | hwUPS5000HTotalChargeEnergy | Total charge energy | 总充电电度 | 0-Read_Only | 只读 | 0..429496720 | 0..429496720 | Total charge energy of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.67 | hwUPS5000HTotalDischargeEnergy | Total discharge energy | 总放电电度 | 0-Read_Only | 只读 | 0..429496720 | 0..429496720 | Total discharge energy of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.68 | hwUPS5000HSavedElectricityBills | Saved electricity bills | 节省电费 | 0-Read_Only | 只读 | 0..429496720 | 0..429496720 | Saved electricity bills of the device config table for the UPS5000-H.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.69 | hwUPS5000HMaintenanceBypassSwitchTemp | Maintenance bypass switch temp | 维修旁路开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Maintenance bypass switch temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.70 | hwUPS5000HMainsInputSwitchHealth | Mains input switch health | 主路输入开关健康度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Mains input switch health of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.71 | hwUPS5000HBypassInputSwitchHealth | Bypass input switch health | 旁路输入开关健康度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Bypass input switch health of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.72 | hwUPS5000HOutputSwitchHealth | Output switch health | 输出开关健康度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Output switch health of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.73 | hwUPS5000HRackOutputTotalElectricityEnergy | Rack output total electricity energy | 机架输出总电能 | 0-Read_Only | 只读 | 0..429496720 | 0..429496720 | Rack output total electricity energy of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.74 | hwUPS5000HPeakShavingCurrentElectricityPrice | Peak shaving current electricity price | 削峰填谷当前电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Peak shaving current electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.75 | hwUPS5000HPeakShavingDischargeStartTime1 | Peak shaving discharge start time 1 | 削峰填谷放电起始时间1 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 1 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.76 | hwUPS5000HPeakShavingDischargeEndTime1 | Peak shaving discharge end time 1 | 削峰填谷放电结束时间1 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 1 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.77 | hwUPS5000HPeakShavingDischargeStartTime2 | Peak shaving discharge start time 2 | 削峰填谷放电起始时间2 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 2 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.78 | hwUPS5000HPeakShavingDischargeEndTime2 | Peak shaving discharge end time 2 | 削峰填谷放电结束时间2 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 2 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.79 | hwUPS5000HPeakShavingDischargeStartTime3 | Peak shaving discharge start time 3 | 削峰填谷放电起始时间3 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 3 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.80 | hwUPS5000HPeakShavingDischargeEndTime3 | Peak shaving discharge end time 3 | 削峰填谷放电结束时间3 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 3 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.81 | hwUPS5000HPeakShavingDischargeStartTime4 | Peak shaving discharge start time 4 | 削峰填谷放电起始时间4 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 4 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.82 | hwUPS5000HPeakShavingDischargeEndTime4 | Peak shaving discharge end time 4 | 削峰填谷放电结束时间4 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 4 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.83 | hwUPS5000HPeakShavingDischargeStartTime5 | Peak shaving discharge start time 5 | 削峰填谷放电起始时间5 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 5 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.84 | hwUPS5000HPeakShavingDischargeEndTime5 | Peak shaving discharge end time 5 | 削峰填谷放电结束时间5 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 5 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.85 | hwUPS5000HPeakShavingDischargeStartTime6 | Peak shaving discharge start time 6 | 削峰填谷放电起始时间6 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 6 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.86 | hwUPS5000HPeakShavingDischargeEndTime6 | Peak shaving discharge end time 6 | 削峰填谷放电结束时间6 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 6 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.87 | hwUPS5000HPeakShavingChargeStartTime1 | Peak shaving charge start time 1 | 削峰填谷充电起始时间1 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge start time 1 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.88 | hwUPS5000HPeakShavingChargeEndTime1 | Peak shaving charge end time 1 | 削峰填谷充电结束时间1 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge end time 1 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.89 | hwUPS5000HPeakShavingChargeStartTime2 | Peak shaving charge start time 2 | 削峰填谷充电起始时间2 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge start time 2 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.90 | hwUPS5000HPeakShavingChargeEndTime2 | Peak shaving charge end time 2 | 削峰填谷充电结束时间2 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge end time 2 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.91 | hwUPS5000HPeakShavingChargeStartTime3 | Peak shaving charge start time 3 | 削峰填谷充电起始时间3 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge start time 3 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.92 | hwUPS5000HPeakShavingChargeEndTime3 | Peak shaving charge end time 3 | 削峰填谷充电结束时间3 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge end time 3 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.93 | hwUPS5000HPeakShavingChargeStartTime4 | Peak shaving charge start time 4 | 削峰填谷充电起始时间4 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge start time 4 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.94 | hwUPS5000HPeakShavingChargeEndTime4 | Peak shaving charge end time 4 | 削峰填谷充电结束时间4 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge end time 4 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.95 | hwUPS5000HPeakShavingChargeStartTime5 | Peak shaving charge start time 5 | 削峰填谷充电起始时间5 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge start time 5 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.96 | hwUPS5000HPeakShavingChargeEndTime5 | Peak shaving charge end time 5 | 削峰填谷充电结束时间5 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge end time 5 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.97 | hwUPS5000HPeakShavingChargeStartTime6 | Peak shaving charge start time 6 | 削峰填谷充电起始时间6 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge start time 6 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.98 | hwUPS5000HPeakShavingChargeEndTime6 | Peak shaving charge end time 6 | 削峰填谷充电结束时间6 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving charge end time 6 of the device config table for the UPS5000-H.SigUnitInfo:HH:mm:ss.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.99 | hwUPS5000HPeriod1BatteryPowerSupplyRatio | Period 1 battery power supply ratio | 时间段1电池供电百分比 | 0-Read_Only | 只读 | 0..1500 | 0..1500 | Period 1 battery power supply ratio of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.100 | hwUPS5000HPeriod2BatteryPowerSupplyRatio | Period 2 battery power supply ratio | 时间段2电池供电百分比 | 0-Read_Only | 只读 | 0..1500 | 0..1500 | Period 2 battery power supply ratio of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.101 | hwUPS5000HPeriod3BatteryPowerSupplyRatio | Period 3 battery power supply ratio | 时间段3电池供电百分比 | 0-Read_Only | 只读 | 0..1500 | 0..1500 | Period 3 battery power supply ratio of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.102 | hwUPS5000HPeriod4BatteryPowerSupplyRatio | Period 4 battery power supply ratio | 时间段4电池供电百分比 | 0-Read_Only | 只读 | 0..1500 | 0..1500 | Period 4 battery power supply ratio of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.103 | hwUPS5000HPeriod5BatteryPowerSupplyRatio | Period 5 battery power supply ratio | 时间段5电池供电百分比 | 0-Read_Only | 只读 | 0..1500 | 0..1500 | Period 5 battery power supply ratio of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.104 | hwUPS5000HPeriod6BatteryPowerSupplyRatio | Period 6 battery power supply ratio | 时间段6电池供电百分比 | 0-Read_Only | 只读 | 0..1500 | 0..1500 | Period 6 battery power supply ratio of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.105 | hwUPS5000HDischargePeriod1ElectricityPrice | Discharge period 1 electricity price | 削峰填谷放电时段1电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Discharge period 1 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.106 | hwUPS5000HDischargePeriod2ElectricityPrice | Discharge period 2 electricity price | 削峰填谷放电时段2电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Discharge period 2 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.107 | hwUPS5000HDischargePeriod3ElectricityPrice | Discharge period 3 electricity price | 削峰填谷放电时段3电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Discharge period 3 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.108 | hwUPS5000HDischargePeriod4ElectricityPrice | Discharge period 4 electricity price | 削峰填谷放电时段4电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Discharge period 4 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.109 | hwUPS5000HDischargePeriod5ElectricityPrice | Discharge period 5 electricity price | 削峰填谷放电时段5电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Discharge period 5 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.110 | hwUPS5000HDischargePeriod6ElectricityPrice | Discharge period 6 electricity price | 削峰填谷放电时段6电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Discharge period 6 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.111 | hwUPS5000HChargePeriod1ElectricityPrice | Charge period 1 electricity price | 削峰填谷充电时段1电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Charge period 1 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.112 | hwUPS5000HChargePeriod2ElectricityPrice | Charge period 2 electricity price | 削峰填谷充电时段2电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Charge period 2 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.113 | hwUPS5000HChargePeriod3ElectricityPrice | Charge period 3 electricity price | 削峰填谷充电时段3电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Charge period 3 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.114 | hwUPS5000HChargePeriod4ElectricityPrice | Charge period 4 electricity price | 削峰填谷充电时段4电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Charge period 4 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.115 | hwUPS5000HChargePeriod5ElectricityPrice | Charge period 5 electricity price | 削峰填谷充电时段5电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Charge period 5 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.116 | hwUPS5000HChargePeriod6ElectricityPrice | Charge period 6 electricity price | 削峰填谷充电时段6电价 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Charge period 6 electricity price of the device config table for the UPS5000-H.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.118 | hwUPS5000HBpmPhaseAInputPowerFactor | BPM ph. A input power factor | 旁路A相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM phase A input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.119 | hwUPS5000HBpmPhaseBInputPowerFactor | BPM ph. B input power factor | 旁路B相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM phase B input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.120 | hwUPS5000HBpmPhaseCInputPowerFactor | BPM ph. C input power factor | 旁路C相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM phase C input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.201 | hwUPS5000HConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS5000-H.

## UIM
UIM
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.88 | UIM | UIM | UIM | / | / | / | / | AIDI Equipment.
1.3.6.1.4.1.2011.6.178.1.1.88.1 | hwUIMRunning1Table | / | / |  |  | / | / | The running table of UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.1 | hwUIMRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.2 | hwUIMCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the UIM. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.3 | hwUIMMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.4 | hwUIMIp | IP | IP地址 | 0-Read_Only | 只读 | 1..65535 | 1..65535 | IP of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.5 | hwUIMEsn | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.6 | hwUIMSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..6 | 0..6 | Software version of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.7 | hwUIMHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..6 | 0..6 | Hardware version of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.8 | hwUIMAiorDi1AiValue | AI/DI_1 AI value | AI/DI_1 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | AI/DI_1 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.9 | hwUIMAiorDi1DiStatus | AI/DI_1 DI status | AI/DI_1 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_1 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.10 | hwUIMAiorDi1PowerStatus | AI/DI_1 power status | AI/DI_1 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_1 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.11 | hwUIMAiorDi2AiValue | AI/DI_2 AI value | AI/DI_2 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | AI/DI_2 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.12 | hwUIMAiorDi2DiStatus | AI/DI_2 DI status | AI/DI_2 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_2 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.13 | hwUIMAiorDi2PowerStatus | AI/DI_2 power status | AI/DI_2 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_2 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.14 | hwUIMAiorDi3AiValue | AI/DI_3 AI value | AI/DI_3 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | AI/DI_3 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.15 | hwUIMAiorDi3DiStatus | AI/DI_3 DI status | AI/DI_3 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_3 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.16 | hwUIMAiorDi3PowerStatus | AI/DI_3 power status | AI/DI_3 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_3 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.17 | hwUIMAiorDi4AiValue | AI/DI_4 AI value | AI/DI_4 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | AI/DI_4 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.18 | hwUIMAiorDi4DiStatus | AI/DI_4 DI status | AI/DI_4 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_4 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.19 | hwUIMAiorDi4PowerStatus | AI/DI_4 power status | AI/DI_4 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_4 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.20 | hwUIMAiorDi5AiValue | AI/DI_5 AI value | AI/DI_5 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | AI/DI_5 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.21 | hwUIMAiorDi5DiStatus | AI/DI_5 DI status | AI/DI_5 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_5 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.22 | hwUIMAiorDi5PowerStatus | AI/DI_5 power status | AI/DI_5 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_5 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.23 | hwUIMAiorDi6AiValue | AI/DI_6 AI value | AI/DI_6 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | AI/DI_6 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.24 | hwUIMAiorDi6DiStatus | AI/DI_6 DI status | AI/DI_6 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_6 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.25 | hwUIMAiorDi6PowerStatus | AI/DI_6 power status | AI/DI_6 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_6 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.26 | hwUIMAiorDi7AiValue | AI/DI_7 AI value | AI/DI_7 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | AI/DI_7 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.27 | hwUIMAiorDi7DiStatus | AI/DI_7 DI status | AI/DI_7 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_7 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.28 | hwUIMAiorDi7PowerStatus | AI/DI_7 power status | AI/DI_7 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_7 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.29 | hwUIMAiorDi8AiValue | AI/DI_8 AI value | AI/DI_8 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | AI/DI_8 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.30 | hwUIMAiorDi8DiStatus | AI/DI_8 DI status | AI/DI_8 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_8 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.31 | hwUIMAiorDi8PowerStatus | AI/DI_8 power status | AI/DI_8 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_8 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.101 | hwUIMRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2 | hwUIMConfig2Table | / | / |  |  | / | / | The config table of UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.1 | hwUIMConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.2 | hwUIMAiorDi1Sensor | AI/DI_1 sensor | AI/DI_1 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_1 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.3 | hwUIMAiorDi1SensorType | AI/DI_1 sensor type | AI/DI_1 传感器类型 | 1-Read_Write | 读写 | normalOpen(1), normalClose(2), doorSensor(3), smokeSensor(4), smokeSensorNc(5), leakSensor(6), leakSensorRope(7), leakSensorNc(8), ntc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_1 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.4 | hwUIMAiorDi1MeasurementUnit | AI/DI_1 measurement unit | AI/DI_1 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_1 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.5 | hwUIMAiorDi1UpperMeasurementThresh | AI/DI_1 upper measurement thresh. | AI/DI_1 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_1 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.6 | hwUIMAiorDi1LowerMeasurementThresh | AI/DI_1 lower measurement thresh. | AI/DI_1 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_1 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.7 | hwUIMAiorDi1UpperAlarmThreshold | AI/DI_1 upper alarm threshold | AI/DI_1 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_1 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.8 | hwUIMAiorDi1LowerAlarmThreshold | AI/DI_1 lower alarm threshold | AI/DI_1 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_1 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.9 | hwUIMAiorDi2Sensor | AI/DI_2 sensor | AI/DI_2 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_2 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.10 | hwUIMAiorDi2SensorType | AI/DI_2 sensor type | AI/DI_2 传感器类型 | 1-Read_Write | 读写 | normalOpen(1), normalClose(2), doorSensor(3), smokeSensor(4), smokeSensorNc(5), leakSensor(6), leakSensorRope(7), leakSensorNc(8), ntc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_2 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.11 | hwUIMAiorDi2MeasurementUnit | AI/DI_2 measurement unit | AI/DI_2 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_2 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.12 | hwUIMAiorDi2UpperMeasurementThresh | AI/DI_2 upper measurement thresh. | AI/DI_2 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_2 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.13 | hwUIMAiorDi2LowerMeasurementThresh | AI/DI_2 lower measurement thresh. | AI/DI_2 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_2 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.14 | hwUIMAiorDi2UpperAlarmThreshold | AI/DI_2 upper alarm threshold | AI/DI_2 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_2 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.15 | hwUIMAiorDi2LowerAlarmThreshold | AI/DI_2 lower alarm threshold | AI/DI_2 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_2 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.16 | hwUIMAiorDi3Sensor | AI/DI_3 sensor | AI/DI_3 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_3 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.17 | hwUIMAiorDi3SensorType | AI/DI_3 sensor type | AI/DI_3 传感器类型 | 1-Read_Write | 读写 | normalOpen(1), normalClose(2), doorSensor(3), smokeSensor(4), smokeSensorNc(5), leakSensor(6), leakSensorRope(7), leakSensorNc(8), ntc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_3 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.18 | hwUIMAiorDi3MeasurementUnit | AI/DI_3 measurement unit | AI/DI_3 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_3 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.19 | hwUIMAiorDi3UpperMeasurementThresh | AI/DI_3 upper measurement thresh. | AI/DI_3 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_3 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.20 | hwUIMAiorDi3LowerMeasurementThresh | AI/DI_3 lower measurement thresh. | AI/DI_3 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_3 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.21 | hwUIMAiorDi3UpperAlarmThreshold | AI/DI_3 upper alarm threshold | AI/DI_3 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_3 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.22 | hwUIMAiorDi3LowerAlarmThreshold | AI/DI_3 lower alarm threshold | AI/DI_3 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_3 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.23 | hwUIMAiorDi4Sensor | AI/DI_4 sensor | AI/DI_4 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_4 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.24 | hwUIMAiorDi4SensorType | AI/DI_4 sensor type | AI/DI_4 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_4 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.25 | hwUIMAiorDi4MeasurementUnit | AI/DI_4 measurement unit | AI/DI_4 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_4 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.26 | hwUIMAiorDi4UpperMeasurementThresh | AI/DI_4 upper measurement thresh. | AI/DI_4 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_4 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.27 | hwUIMAiorDi4LowerMeasurementThresh | AI/DI_4 lower measurement thresh. | AI/DI_4 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_4 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.28 | hwUIMAiorDi4UpperAlarmThreshold | AI/DI_4 upper alarm threshold | AI/DI_4 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_4 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.29 | hwUIMAiorDi4LowerAlarmThreshold | AI/DI_4 lower alarm threshold | AI/DI_4 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_4 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.30 | hwUIMAiorDi5Sensor | AI/DI_5 sensor | AI/DI_5 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_5 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.31 | hwUIMAiorDi5SensorType | AI/DI_5 sensor type | AI/DI_5 传感器类型 | 1-Read_Write | 读写 | normalOpen(1), normalClose(2), doorSensor(3), smokeSensor(4), smokeSensorNc(5), leakSensor(6), leakSensorRope(7), leakSensorNc(8), ntc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_5 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.32 | hwUIMAiorDi5MeasurementUnit | AI/DI_5 measurement unit | AI/DI_5 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_5 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.33 | hwUIMAiorDi5UpperMeasurementThresh | AI/DI_5 upper measurement thresh. | AI/DI_5 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_5 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.34 | hwUIMAiorDi5LowerMeasurementThresh | AI/DI_5 lower measurement thresh. | AI/DI_5 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_5 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.35 | hwUIMAiorDi5UpperAlarmThreshold | AI/DI_5 upper alarm threshold | AI/DI_5 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_5 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.36 | hwUIMAiorDi5LowerAlarmThreshold | AI/DI_5 lower alarm threshold | AI/DI_5 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_5 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.37 | hwUIMAiorDi6Sensor | AI/DI_6 sensor | AI/DI_6 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_6 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.38 | hwUIMAiorDi6SensorType | AI/DI_6 sensor type | AI/DI_6 传感器类型 | 1-Read_Write | 读写 | normalOpen(1), normalClose(2), doorSensor(3), smokeSensor(4), smokeSensorNc(5), leakSensor(6), leakSensorRope(7), leakSensorNc(8), ntc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_6 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.39 | hwUIMAiorDi6MeasurementUnit | AI/DI_6 measurement unit | AI/DI_6 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_6 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.40 | hwUIMAiorDi6UpperMeasurementThresh | AI/DI_6 upper measurement thresh. | AI/DI_6 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_6 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.41 | hwUIMAiorDi6LowerMeasurementThresh | AI/DI_6 lower measurement thresh. | AI/DI_6 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_6 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.42 | hwUIMAiorDi6UpperAlarmThreshold | AI/DI_6 upper alarm threshold | AI/DI_6 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_6 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.43 | hwUIMAiorDi6LowerAlarmThreshold | AI/DI_6 lower alarm threshold | AI/DI_6 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_6 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.44 | hwUIMAiorDi7Sensor | AI/DI_7 sensor | AI/DI_7 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_7 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.45 | hwUIMAiorDi7SensorType | AI/DI_7 sensor type | AI/DI_7 传感器类型 | 1-Read_Write | 读写 | normalOpen(1), normalClose(2), doorSensor(3), smokeSensor(4), smokeSensorNc(5), leakSensor(6), leakSensorRope(7), leakSensorNc(8), ntc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_7 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.46 | hwUIMAiorDi7MeasurementUnit | AI/DI_7 measurement unit | AI/DI_7 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_7 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.47 | hwUIMAiorDi7UpperMeasurementThresh | AI/DI_7 upper measurement thresh. | AI/DI_7 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_7 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.48 | hwUIMAiorDi7LowerMeasurementThresh | AI/DI_7 lower measurement thresh. | AI/DI_7 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_7 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.49 | hwUIMAiorDi7UpperAlarmThreshold | AI/DI_7 upper alarm threshold | AI/DI_7 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_7 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.50 | hwUIMAiorDi7LowerAlarmThreshold | AI/DI_7 lower alarm threshold | AI/DI_7 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_7 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.51 | hwUIMAiorDi8Sensor | AI/DI_8 sensor | AI/DI_8 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_8 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.52 | hwUIMAiorDi8SensorType | AI/DI_8 sensor type | AI/DI_8 传感器类型 | 1-Read_Write | 读写 | normalOpen(1), normalClose(2), doorSensor(3), smokeSensor(4), smokeSensorNc(5), leakSensor(6), leakSensorRope(7), leakSensorNc(8), ntc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_8 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.53 | hwUIMAiorDi8MeasurementUnit | AI/DI_8 measurement unit | AI/DI_8 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_8 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.54 | hwUIMAiorDi8UpperMeasurementThresh | AI/DI_8 upper measurement thresh. | AI/DI_8 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_8 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.55 | hwUIMAiorDi8LowerMeasurementThresh | AI/DI_8 lower measurement thresh. | AI/DI_8 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_8 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.56 | hwUIMAiorDi8UpperAlarmThreshold | AI/DI_8 upper alarm threshold | AI/DI_8 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | AI/DI_8 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.57 | hwUIMAiorDi8LowerAlarmThreshold | AI/DI_8 lower alarm threshold | AI/DI_8 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_8 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.58 | hwUIMCom1BaudRate | COM1 baud rate | COM1 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM1 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.59 | hwUIMCom1DataBit | COM1 data bit | COM1 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM1 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.60 | hwUIMCom1StopBit | COM1 stop bit | COM1 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM1 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.61 | hwUIMCom1Parity | COM1 parity | COM1 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM1 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.62 | hwUIMCom2BaudRate | COM2 baud rate | COM2 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM2 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.63 | hwUIMCom2DataBit | COM2 data bit | COM2 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM2 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.64 | hwUIMCom2StopBit | COM2 stop bit | COM2 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM2 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.65 | hwUIMCom2Parity | COM2 parity | COM2 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM2 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.66 | hwUIMCom3BaudRate | COM3 baud rate | COM3 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM3 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.67 | hwUIMCom3DataBit | COM3 data bit | COM3 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM3 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.68 | hwUIMCom3StopBit | COM3 stop bit | COM3 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM3 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.69 | hwUIMCom3Parity | COM3 parity | COM3 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM3 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.70 | hwUIMCom4BaudRate | COM4 baud rate | COM4 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM4 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.71 | hwUIMCom4DataBit | COM4 data bit | COM4 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM4 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.72 | hwUIMCom4StopBit | COM4 stop bit | COM4 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM4 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.73 | hwUIMCom4Parity | COM4 parity | COM4 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM4 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.74 | hwUIMCom5BaudRate | COM5 baud rate | COM5 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM5 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.75 | hwUIMCom5DataBit | COM5 data bit | COM5 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM5 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.76 | hwUIMCom5StopBit | COM5 stop bit | COM5 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM5 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.77 | hwUIMCom5Parity | COM5 parity | COM5 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM5 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.78 | hwUIMCom6BaudRate | COM6 baud rate | COM6 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM6 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.79 | hwUIMCom6DataBit | COM6 data bit | COM6 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM6 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.80 | hwUIMCom6StopBit | COM6 stop bit | COM6 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM6 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.81 | hwUIMCom6Parity | COM6 parity | COM6 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM6 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.82 | hwUIMCom7BaudRate | COM7 baud rate | COM7 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM7 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.83 | hwUIMCom7DataBit | COM7 data bit | COM7 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM7 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.84 | hwUIMCom7StopBit | COM7 stop bit | COM7 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM7 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.85 | hwUIMCom7Parity | COM7 parity | COM7 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM7 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.86 | hwUIMCom8BaudRate | COM8 baud rate | COM8 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM8 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.87 | hwUIMCom8DataBit | COM8 data bit | COM8 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM8 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.88 | hwUIMCom8StopBit | COM8 stop bit | COM8 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM8 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.89 | hwUIMCom8Parity | COM8 parity | COM8 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM8 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.101 | hwUIMConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UIM.

## YD-DEMS AC Meter
YD-DEMS AC Meter
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.1 | YDDEMSACMeter | YD-DEMS AC Meter | YD-DEMS AC Meter | / | / | / | / | YD-DEMS AC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1 | hwYDDEMSACMeterRunning1Table | / | / |  |  | / | / | The running table of YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.1 | hwYDDEMSACMeterRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.2 | hwYDDEMSACMeterPhaseAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.3 | hwYDDEMSACMeterPhaseBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.4 | hwYDDEMSACMeterPhaseCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.5 | hwYDDEMSACMeterAverageThreePhasePhaseVoltage | Average three-phase phase voltage | 三相平均相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase phase voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.6 | hwYDDEMSACMeterABLineVoltage | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A-B line voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.7 | hwYDDEMSACMeterBCLineVoltage | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B-C line voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.8 | hwYDDEMSACMeterCALineVoltage | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | C-A line voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.9 | hwYDDEMSACMeterAverageThreePhaseLineVoltage | Average three-phase line voltage | 三相平均线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase line voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.10 | hwYDDEMSACMeterPhaseACurrent | Phase A current | A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.11 | hwYDDEMSACMeterPhaseBCurrent | Phase B current | B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.12 | hwYDDEMSACMeterPhaseCCurrent | Phase C current | C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.13 | hwYDDEMSACMeterAverageThreePhaseCurrent | Average three-phase current | 三相平均电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.14 | hwYDDEMSACMeterNeutralWireCurrent | Neutral wire current | 零线电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Neutral wire current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.15 | hwYDDEMSACMeterPhaseAActivePower | Phase A active power | A相有功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.16 | hwYDDEMSACMeterPhaseBActivePower | Phase B active power | B相有功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.17 | hwYDDEMSACMeterPhaseCActivePower | Phase C active power | C相有功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.18 | hwYDDEMSACMeterSystemActivePower | System active power | 系统有功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System active power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.19 | hwYDDEMSACMeterPhaseAReactivePower | Phase A reactive power | A相无功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A reactive power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.20 | hwYDDEMSACMeterPhaseBReactivePower | Phase B reactive power | B相无功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B reactive power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.21 | hwYDDEMSACMeterPhaseCReactivePower | Phase C reactive power | C相无功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C reactive power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.22 | hwYDDEMSACMeterSystemReactivePower | System reactive power | 系统无功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System reactive power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.23 | hwYDDEMSACMeterPhaseAApparentPower | Phase A apparent power | A相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.24 | hwYDDEMSACMeterPhaseBApparentPower | Phase B apparent power | B相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.25 | hwYDDEMSACMeterPhaseCApparentPower | Phase C apparent power | C相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.26 | hwYDDEMSACMeterSystemApparentPower | System apparent power | 系统视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.27 | hwYDDEMSACMeterPhaseAPowerFactor | Phase A power factor | A相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.28 | hwYDDEMSACMeterPhaseBPowerFactor | Phase B power factor | B相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.29 | hwYDDEMSACMeterPhaseCPowerFactor | Phase C power factor | C相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.30 | hwYDDEMSACMeterSystemPowerFactor | System power factor | 系统功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.31 | hwYDDEMSACMeterFrequency | Frequency | 频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.32 | hwYDDEMSACMeterVoltageImbalance | Voltage imbalance | 电压不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage imbalance of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.33 | hwYDDEMSACMeterCurrentImbalance | Current imbalance | 电流不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current imbalance of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.34 | hwYDDEMSACMeterPhaseAVoltagePositiveSequence | Phase A voltage positive sequence | A相电压正序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage positive sequence of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.35 | hwYDDEMSACMeterPhaseAVoltageNegativeSequence | Phase A voltage negative sequence | A相电压负序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage negative sequence of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.36 | hwYDDEMSACMeterPhaseAVoltageZeroSequence | Phase A voltage zero sequence | A相电压零序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage zero sequence of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.37 | hwYDDEMSACMeterPhaseACurrentPositiveSequence | Phase A current positive sequence | A相电流正序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current positive sequence of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.38 | hwYDDEMSACMeterPhaseACurrentNegativeSequence | Phase A current negative sequence | A相电流负序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current negative sequence of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.39 | hwYDDEMSACMeterPhaseACurrentZeroSequence | Phase A current zero sequence | A相电流零序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current zero sequence of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.40 | hwYDDEMSACMeterNeutralGroundVoltage | Neutral-ground voltage | 零地电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Neutral-ground voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.41 | hwYDDEMSACMeterLeakageCurrent | Leakage current | 漏电电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Leakage current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.42 | hwYDDEMSACMeterPositiveActiveEnergy | Positive active energy | 正向有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.43 | hwYDDEMSACMeterNegativeActiveEnergy | Negative active energy | 负向有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.44 | hwYDDEMSACMeterPositiveReactiveEnergy | Positive reactive energy | 正向无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.45 | hwYDDEMSACMeterNegativeReactiveEnergy | Negative reactive energy | 负向无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.46 | hwYDDEMSACMeterPhaseAActivePowerDemand | Phase A active power demand | A相有功功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active power demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.47 | hwYDDEMSACMeterPhaseBActivePowerDemand | Phase B active power demand | B相有功功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active power demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.48 | hwYDDEMSACMeterPhaseCActivePowerDemand | Phase C active power demand | C相有功功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active power demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.49 | hwYDDEMSACMeterSystemActivePowerDemand | System active power demand | 系统有功功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System active power demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.50 | hwYDDEMSACMeterPhaseACurrentRequirement | Phase A current requirement | A相电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current requirement of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.51 | hwYDDEMSACMeterPhaseBCurrentRequirement | Phase B current requirement | B相电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current requirement of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.52 | hwYDDEMSACMeterPhaseCCurrentRequirement | Phase C current requirement | C相电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current requirement of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.53 | hwYDDEMSACMeterThreePhaseAverageCurrentDemand | Three-phase average current demand | 三相平均电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Three-phase average current demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.54 | hwYDDEMSACMeterPhaseAVoltagePercentage | Phase A voltage percentage | A相电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.55 | hwYDDEMSACMeterPhaseBVoltagePercentage | Phase B voltage percentage | B相电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B voltage percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.56 | hwYDDEMSACMeterPhaseCVoltagePercentage | Phase C voltage percentage | C相电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C voltage percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.57 | hwYDDEMSACMeterAverageThreePhaseVoltagePercentage | Average three-phase voltage percentage | 三相平均电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase voltage percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.58 | hwYDDEMSACMeterPhaseACurrentPercentage | Phase A current percentage | A相电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.59 | hwYDDEMSACMeterPhaseBCurrentPercentage | Phase B current percentage | B相电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.60 | hwYDDEMSACMeterPhaseCCurrentPercentage | Phase C current percentage | C相电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.61 | hwYDDEMSACMeterAverageThreePhaseCurrentPercentage | Average three-phase current percentage | 三相平均电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.62 | hwYDDEMSACMeterBranchQf01SwitchOf | Branch QF01 switch OF | 支路QF01开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch QF01 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.63 | hwYDDEMSACMeterBranchAqf01SwitchOf | Branch AQF01 switch OF | 支路AQF01开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF01 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.64 | hwYDDEMSACMeterBranchAqf02SwitchOf | Branch AQF02 switch OF | 支路AQF02开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF02 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.65 | hwYDDEMSACMeterBranchAqf03SwitchOf | Branch AQF03 switch OF | 支路AQF03开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF03 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.66 | hwYDDEMSACMeterBranchAqf04SwitchOf | Branch AQF04 switch OF | 支路AQF04开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF04 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.67 | hwYDDEMSACMeterBranchAqf05SwitchOf | Branch AQF05 switch OF | 支路AQF05开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF05 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.68 | hwYDDEMSACMeterBranchAqf06SwitchOf | Branch AQF06 switch OF | 支路AQF06开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF06 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.69 | hwYDDEMSACMeterBranchAqf07SwitchOf | Branch AQF07 switch OF | 支路AQF07开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF07 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.70 | hwYDDEMSACMeterBranchAqf08SwitchOf | Branch AQF08 switch OF | 支路AQF08开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF08 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.71 | hwYDDEMSACMeterBranchAqf09SwitchOf | Branch AQF09 switch OF | 支路AQF09开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF09 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.72 | hwYDDEMSACMeterBranchAqf10SwitchOf | Branch AQF10 switch OF | 支路AQF10开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF10 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.73 | hwYDDEMSACMeterBranchAqf11SwitchOf | Branch AQF11 switch OF | 支路AQF11开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF11 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.74 | hwYDDEMSACMeterBranchAqf12SwitchOf | Branch AQF12 switch OF | 支路AQF12开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF12 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.75 | hwYDDEMSACMeterBranchAqf13SwitchOf | Branch AQF13 switch OF | 支路AQF13开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF13 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.76 | hwYDDEMSACMeterBranchAqf14SwitchOf | Branch AQF14 switch OF | 支路AQF14开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF14 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.77 | hwYDDEMSACMeterBranchAqf15SwitchOf | Branch AQF15 switch OF | 支路AQF15开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF15 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.78 | hwYDDEMSACMeterBranchBqf01SwitchOf | Branch BQF01 switch OF | 支路BQF01开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF01 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.79 | hwYDDEMSACMeterBranchBqf02SwitchOf | Branch BQF02 switch OF | 支路BQF02开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF02 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.80 | hwYDDEMSACMeterBranchBqf03SwitchOf | Branch BQF03 switch OF | 支路BQF03开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF03 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.81 | hwYDDEMSACMeterBranchBqf04SwitchOf | Branch BQF04 switch OF | 支路BQF04开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF04 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.82 | hwYDDEMSACMeterBranchBqf05SwitchOf | Branch BQF05 switch OF | 支路BQF05开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF05 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.83 | hwYDDEMSACMeterBranchBqf06SwitchOf | Branch BQF06 switch OF | 支路BQF06开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF06 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.84 | hwYDDEMSACMeterBranchBqf07SwitchOf | Branch BQF07 switch OF | 支路BQF07开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF07 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.85 | hwYDDEMSACMeterBranchBqf08SwitchOf | Branch BQF08 switch OF | 支路BQF08开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF08 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.86 | hwYDDEMSACMeterBranchBqf09SwitchOf | Branch BQF09 switch OF | 支路BQF09开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF09 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.87 | hwYDDEMSACMeterBranchBqf10SwitchOf | Branch BQF10 switch OF | 支路BQF10开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF10 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.88 | hwYDDEMSACMeterBranchBqf11SwitchOf | Branch BQF11 switch OF | 支路BQF11开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF11 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.89 | hwYDDEMSACMeterBranchBqf12SwitchOf | Branch BQF12 switch OF | 支路BQF12开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF12 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.90 | hwYDDEMSACMeterBranchBqf13SwitchOf | Branch BQF13 switch OF | 支路BQF13开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF13 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.91 | hwYDDEMSACMeterBranchBqf14SwitchOf | Branch BQF14 switch OF | 支路BQF14开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF14 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.92 | hwYDDEMSACMeterBranchBqf15SwitchOf | Branch BQF15 switch OF | 支路BQF15开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF15 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.93 | hwYDDEMSACMeterBranchCqf01SwitchOf | Branch CQF01 switch OF | 支路CQF01开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF01 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.94 | hwYDDEMSACMeterBranchCqf02SwitchOf | Branch CQF02 switch OF | 支路CQF02开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF02 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.95 | hwYDDEMSACMeterBranchCqf03SwitchOf | Branch CQF03 switch OF | 支路CQF03开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF03 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.96 | hwYDDEMSACMeterBranchCqf04SwitchOf | Branch CQF04 switch OF | 支路CQF04开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF04 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.97 | hwYDDEMSACMeterBranchCqf05SwitchOf | Branch CQF05 switch OF | 支路CQF05开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF05 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.98 | hwYDDEMSACMeterBranchCqf06SwitchOf | Branch CQF06 switch OF | 支路CQF06开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF06 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.99 | hwYDDEMSACMeterBranchCqf07SwitchOf | Branch CQF07 switch OF | 支路CQF07开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF07 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.100 | hwYDDEMSACMeterBranchCqf08SwitchOf | Branch CQF08 switch OF | 支路CQF08开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF08 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.101 | hwYDDEMSACMeterBranchCqf09SwitchOf | Branch CQF09 switch OF | 支路CQF09开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF09 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.102 | hwYDDEMSACMeterBranchCqf10SwitchOf | Branch CQF10 switch OF | 支路CQF10开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF10 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.103 | hwYDDEMSACMeterBranchCqf11SwitchOf | Branch CQF11 switch OF | 支路CQF11开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF11 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.104 | hwYDDEMSACMeterBranchCqf12SwitchOf | Branch CQF12 switch OF | 支路CQF12开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF12 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.105 | hwYDDEMSACMeterBranchCqf13SwitchOf | Branch CQF13 switch OF | 支路CQF13开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF13 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.106 | hwYDDEMSACMeterBranchCqf14SwitchOf | Branch CQF14 switch OF | 支路CQF14开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF14 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.107 | hwYDDEMSACMeterBranchCqf15SwitchOf | Branch CQF15 switch OF | 支路CQF15开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF15 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.108 | hwYDDEMSACMeterInputSwitchStatus | Input switch status | 进线开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Input switch status of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.109 | hwYDDEMSACMeterInputSwitchFaultStatus | Input switch fault status | 进线开关故障状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Input switch fault status of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.110 | hwYDDEMSACMeterSpdStatus | SPD status | 防雷器状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | SPD status of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.111 | hwYDDEMSACMeterQf01ALoopVoltage | QF01-A loop voltage | QF01-A回路电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.112 | hwYDDEMSACMeterQf01ALoopCurrent | QF01-A loop current | QF01-A回路电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.113 | hwYDDEMSACMeterQf01ALoopCurrentPercentage | QF01-A loop current percentage | QF01-A回路电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.114 | hwYDDEMSACMeterQf01ALoopActivePower | QF01-A loop active power | QF01-A回路有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.115 | hwYDDEMSACMeterQf01ALoopReactivePower | QF01-A loop reactive power | QF01-A回路无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop reactive power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.116 | hwYDDEMSACMeterQf01ALoopApparentPower | QF01-A loop apparent power | QF01-A回路视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.117 | hwYDDEMSACMeterQf01ALoopActiveEnergy | QF01-A loop active energy | QF01-A回路有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.118 | hwYDDEMSACMeterQf01ALoopReactiveEnergy | QF01-A loop reactive energy | QF01-A回路无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.119 | hwYDDEMSACMeterQf01ALoopPowerFactor | QF01-A loop power factor | QF01-A回路功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.120 | hwYDDEMSACMeterQf01BLoopVoltage | QF01-B loop voltage | QF01-B回路电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.121 | hwYDDEMSACMeterQf01BLoopCurrent | QF01-B loop current | QF01-B回路电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.122 | hwYDDEMSACMeterQf01BLoopCurrentPercentage | QF01-B loop current percentage | QF01-B回路电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.123 | hwYDDEMSACMeterQf01BLoopActivePower | QF01-B loop active power | QF01-B回路有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.124 | hwYDDEMSACMeterQf01BLoopReactivePower | QF01-B loop reactive power | QF01-B回路无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop reactive power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.125 | hwYDDEMSACMeterQf01BLoopApparentPower | QF01-B loop apparent power | QF01-B回路视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.126 | hwYDDEMSACMeterQf01BLoopActiveEnergy | QF01-B loop active energy | QF01-B回路有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.127 | hwYDDEMSACMeterQf01BLoopReactiveEnergy | QF01-B loop reactive energy | QF01-B回路无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.128 | hwYDDEMSACMeterQf01BLoopPowerFactor | QF01-B loop power factor | QF01-B回路功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.129 | hwYDDEMSACMeterQf01CLoopVoltage | QF01-C loop voltage | QF01-C回路电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.130 | hwYDDEMSACMeterQf01CLoopCurrent | QF01-C loop current | QF01-C回路电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.131 | hwYDDEMSACMeterQf01CLoopCurrentPercentage | QF01-C loop current percentage | QF01-C回路电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.132 | hwYDDEMSACMeterQf01CLoopActivePower | QF01-C loop active power | QF01-C回路有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.133 | hwYDDEMSACMeterQf01CLoopReactivePower | QF01-C loop reactive power | QF01-C回路无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop reactive power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.134 | hwYDDEMSACMeterQf01CLoopApparentPower | QF01-C loop apparent power | QF01-C回路视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.135 | hwYDDEMSACMeterQf01CLoopActiveEnergy | QF01-C loop active energy | QF01-C回路有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.136 | hwYDDEMSACMeterQf01CLoopReactiveEnergy | QF01-C loop reactive energy | QF01-C回路无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.137 | hwYDDEMSACMeterQf01CLoopPowerFactor | QF01-C loop power factor | QF01-C回路功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.138 | hwYDDEMSACMeterAqf01Voltage | AQF01 voltage | AQF01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF01 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.139 | hwYDDEMSACMeterAqf01Current | AQF01 current | AQF01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF01 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.140 | hwYDDEMSACMeterAqf01ActivePower | AQF01 active power | AQF01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF01 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.141 | hwYDDEMSACMeterAqf01ActiveEnergy | AQF01 active energy | AQF01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF01 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.142 | hwYDDEMSACMeterAqf02Voltage | AQF02 voltage | AQF02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF02 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.143 | hwYDDEMSACMeterAqf02Current | AQF02 current | AQF02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF02 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.144 | hwYDDEMSACMeterAqf02ActivePower | AQF02 active power | AQF02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF02 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.145 | hwYDDEMSACMeterAqf02ActiveEnergy | AQF02 active energy | AQF02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF02 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.146 | hwYDDEMSACMeterAqf03Voltage | AQF03 voltage | AQF03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF03 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.147 | hwYDDEMSACMeterAqf03Current | AQF03 current | AQF03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF03 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.148 | hwYDDEMSACMeterAqf03ActivePower | AQF03 active power | AQF03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF03 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.149 | hwYDDEMSACMeterAqf03ActiveEnergy | AQF03 active energy | AQF03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF03 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.150 | hwYDDEMSACMeterAqf04Voltage | AQF04 voltage | AQF04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF04 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.151 | hwYDDEMSACMeterAqf04Current | AQF04 current | AQF04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF04 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.152 | hwYDDEMSACMeterAqf04ActivePower | AQF04 active power | AQF04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF04 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.153 | hwYDDEMSACMeterAqf04ActiveEnergy | AQF04 active energy | AQF04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF04 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.154 | hwYDDEMSACMeterAqf05Voltage | AQF05 voltage | AQF05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF05 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.155 | hwYDDEMSACMeterAqf05Current | AQF05 current | AQF05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF05 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.156 | hwYDDEMSACMeterAqf05ActivePower | AQF05 active power | AQF05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF05 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.157 | hwYDDEMSACMeterAqf05ActiveEnergy | AQF05 active energy | AQF05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF05 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.158 | hwYDDEMSACMeterAqf06Voltage | AQF06 voltage | AQF06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF06 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.159 | hwYDDEMSACMeterAqf06Current | AQF06 current | AQF06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF06 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.160 | hwYDDEMSACMeterAqf06ActivePower | AQF06 active power | AQF06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF06 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.161 | hwYDDEMSACMeterAqf06ActiveEnergy | AQF06 active energy | AQF06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF06 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.162 | hwYDDEMSACMeterAqf07Voltage | AQF07 voltage | AQF07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF07 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.163 | hwYDDEMSACMeterAqf07Current | AQF07 current | AQF07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF07 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.164 | hwYDDEMSACMeterAqf07ActivePower | AQF07 active power | AQF07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF07 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.165 | hwYDDEMSACMeterAqf07ActiveEnergy | AQF07 active energy | AQF07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF07 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.166 | hwYDDEMSACMeterAqf08Voltage | AQF08 voltage | AQF08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF08 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.167 | hwYDDEMSACMeterAqf08Current | AQF08 current | AQF08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF08 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.168 | hwYDDEMSACMeterAqf08ActivePower | AQF08 active power | AQF08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF08 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.169 | hwYDDEMSACMeterAqf08ActiveEnergy | AQF08 active energy | AQF08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF08 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.170 | hwYDDEMSACMeterAqf09Voltage | AQF09 voltage | AQF09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF09 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.171 | hwYDDEMSACMeterAqf09Current | AQF09 current | AQF09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF09 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.172 | hwYDDEMSACMeterAqf09ActivePower | AQF09 active power | AQF09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF09 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.173 | hwYDDEMSACMeterAqf09ActiveEnergy | AQF09 active energy | AQF09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF09 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.174 | hwYDDEMSACMeterAqf10Voltage | AQF10 voltage | AQF10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF10 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.175 | hwYDDEMSACMeterAqf10Current | AQF10 current | AQF10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF10 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.176 | hwYDDEMSACMeterAqf10ActivePower | AQF10 active power | AQF10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF10 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.177 | hwYDDEMSACMeterAqf10ActiveEnergy | AQF10 active energy | AQF10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF10 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.178 | hwYDDEMSACMeterAqf11Voltage | AQF11 voltage | AQF11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF11 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.179 | hwYDDEMSACMeterAqf11Current | AQF11 current | AQF11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF11 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.180 | hwYDDEMSACMeterAqf11ActivePower | AQF11 active power | AQF11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF11 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.181 | hwYDDEMSACMeterAqf11ActiveEnergy | AQF11 active energy | AQF11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF11 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.182 | hwYDDEMSACMeterAqf12Voltage | AQF12 voltage | AQF12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF12 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.183 | hwYDDEMSACMeterAqf12Current | AQF12 current | AQF12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF12 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.184 | hwYDDEMSACMeterAqf12ActivePower | AQF12 active power | AQF12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF12 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.185 | hwYDDEMSACMeterAqf12ActiveEnergy | AQF12 active energy | AQF12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF12 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.186 | hwYDDEMSACMeterAqf13Voltage | AQF13 voltage | AQF13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF13 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.187 | hwYDDEMSACMeterAqf13Current | AQF13 current | AQF13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF13 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.188 | hwYDDEMSACMeterAqf13ActivePower | AQF13 active power | AQF13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF13 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.189 | hwYDDEMSACMeterAqf13ActiveEnergy | AQF13 active energy | AQF13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF13 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.190 | hwYDDEMSACMeterAqf14Voltage | AQF14 voltage | AQF14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF14 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.191 | hwYDDEMSACMeterAqf14Current | AQF14 current | AQF14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF14 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.192 | hwYDDEMSACMeterAqf14ActivePower | AQF14 active power | AQF14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF14 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.193 | hwYDDEMSACMeterAqf14ActiveEnergy | AQF14 active energy | AQF14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF14 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.194 | hwYDDEMSACMeterAqf15Voltage | AQF15 voltage | AQF15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF15 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.195 | hwYDDEMSACMeterAqf15Current | AQF15 current | AQF15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF15 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.196 | hwYDDEMSACMeterAqf15ActivePower | AQF15 active power | AQF15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF15 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.197 | hwYDDEMSACMeterAqf15ActiveEnergy | AQF15 active energy | AQF15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF15 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.198 | hwYDDEMSACMeterBqf01Voltage | BQF01 voltage | BQF01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF01 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.199 | hwYDDEMSACMeterBqf01Current | BQF01 current | BQF01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF01 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.200 | hwYDDEMSACMeterBqf01ActivePower | BQF01 active power | BQF01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF01 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.201 | hwYDDEMSACMeterBqf01ActiveEnergy | BQF01 active energy | BQF01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF01 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.202 | hwYDDEMSACMeterBqf02Voltage | BQF02 voltage | BQF02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF02 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.203 | hwYDDEMSACMeterBqf02Current | BQF02 current | BQF02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF02 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.204 | hwYDDEMSACMeterBqf02ActivePower | BQF02 active power | BQF02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF02 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.205 | hwYDDEMSACMeterBqf02ActiveEnergy | BQF02 active energy | BQF02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF02 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.206 | hwYDDEMSACMeterBqf03Voltage | BQF03 voltage | BQF03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF03 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.207 | hwYDDEMSACMeterBqf03Current | BQF03 current | BQF03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF03 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.208 | hwYDDEMSACMeterBqf03ActivePower | BQF03 active power | BQF03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF03 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.209 | hwYDDEMSACMeterBqf03ActiveEnergy | BQF03 active energy | BQF03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF03 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.210 | hwYDDEMSACMeterBqf04Voltage | BQF04 voltage | BQF04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF04 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.211 | hwYDDEMSACMeterBqf04Current | BQF04 current | BQF04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF04 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.212 | hwYDDEMSACMeterBqf04ActivePower | BQF04 active power | BQF04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF04 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.213 | hwYDDEMSACMeterBqf04ActiveEnergy | BQF04 active energy | BQF04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF04 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.214 | hwYDDEMSACMeterBqf05Voltage | BQF05 voltage | BQF05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF05 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.215 | hwYDDEMSACMeterBqf05Current | BQF05 current | BQF05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF05 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.216 | hwYDDEMSACMeterBqf05ActivePower | BQF05 active power | BQF05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF05 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.217 | hwYDDEMSACMeterBqf05ActiveEnergy | BQF05 active energy | BQF05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF05 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.218 | hwYDDEMSACMeterBqf06Voltage | BQF06 voltage | BQF06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF06 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.219 | hwYDDEMSACMeterBqf06Current | BQF06 current | BQF06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF06 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.220 | hwYDDEMSACMeterBqf06ActivePower | BQF06 active power | BQF06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF06 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.221 | hwYDDEMSACMeterBqf06ActiveEnergy | BQF06 active energy | BQF06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF06 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.222 | hwYDDEMSACMeterBqf07Voltage | BQF07 voltage | BQF07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF07 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.223 | hwYDDEMSACMeterBqf07Current | BQF07 current | BQF07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF07 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.224 | hwYDDEMSACMeterBqf07ActivePower | BQF07 active power | BQF07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF07 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.225 | hwYDDEMSACMeterBqf07ActiveEnergy | BQF07 active energy | BQF07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF07 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.226 | hwYDDEMSACMeterBqf08Voltage | BQF08 voltage | BQF08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF08 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.227 | hwYDDEMSACMeterBqf08Current | BQF08 current | BQF08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF08 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.228 | hwYDDEMSACMeterBqf08ActivePower | BQF08 active power | BQF08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF08 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.229 | hwYDDEMSACMeterBqf08ActiveEnergy | BQF08 active energy | BQF08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF08 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.230 | hwYDDEMSACMeterBqf09Voltage | BQF09 voltage | BQF09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF09 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.231 | hwYDDEMSACMeterBqf09Current | BQF09 current | BQF09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF09 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.232 | hwYDDEMSACMeterBqf09ActivePower | BQF09 active power | BQF09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF09 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.233 | hwYDDEMSACMeterBqf09ActiveEnergy | BQF09 active energy | BQF09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF09 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.234 | hwYDDEMSACMeterBqf10Voltage | BQF10 voltage | BQF10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF10 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.235 | hwYDDEMSACMeterBqf10Current | BQF10 current | BQF10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF10 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.236 | hwYDDEMSACMeterBqf10ActivePower | BQF10 active power | BQF10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF10 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.237 | hwYDDEMSACMeterBqf10ActiveEnergy | BQF10 active energy | BQF10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF10 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.238 | hwYDDEMSACMeterBqf11Voltage | BQF11 voltage | BQF11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF11 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.239 | hwYDDEMSACMeterBqf11Current | BQF11 current | BQF11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF11 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.240 | hwYDDEMSACMeterBqf11ActivePower | BQF11 active power | BQF11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF11 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.241 | hwYDDEMSACMeterBqf11ActiveEnergy | BQF11 active energy | BQF11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF11 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.242 | hwYDDEMSACMeterBqf12Voltage | BQF12 voltage | BQF12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF12 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.243 | hwYDDEMSACMeterBqf12Current | BQF12 current | BQF12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF12 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.244 | hwYDDEMSACMeterBqf12ActivePower | BQF12 active power | BQF12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF12 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.245 | hwYDDEMSACMeterBqf12ActiveEnergy | BQF12 active energy | BQF12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF12 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.246 | hwYDDEMSACMeterBqf13Voltage | BQF13 voltage | BQF13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF13 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.247 | hwYDDEMSACMeterBqf13Current | BQF13 current | BQF13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF13 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.248 | hwYDDEMSACMeterBqf13ActivePower | BQF13 active power | BQF13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF13 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.249 | hwYDDEMSACMeterBqf13ActiveEnergy | BQF13 active energy | BQF13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF13 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.250 | hwYDDEMSACMeterBqf14Voltage | BQF14 voltage | BQF14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF14 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.251 | hwYDDEMSACMeterBqf14Current | BQF14 current | BQF14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF14 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.252 | hwYDDEMSACMeterBqf14ActivePower | BQF14 active power | BQF14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF14 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.253 | hwYDDEMSACMeterBqf14ActiveEnergy | BQF14 active energy | BQF14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF14 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.254 | hwYDDEMSACMeterBqf15Voltage | BQF15 voltage | BQF15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF15 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.255 | hwYDDEMSACMeterBqf15Current | BQF15 current | BQF15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF15 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.256 | hwYDDEMSACMeterBqf15ActivePower | BQF15 active power | BQF15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF15 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.257 | hwYDDEMSACMeterBqf15ActiveEnergy | BQF15 active energy | BQF15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF15 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.258 | hwYDDEMSACMeterCqf01Voltage | CQF01 voltage | CQF01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF01 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.259 | hwYDDEMSACMeterCqf01Current | CQF01 current | CQF01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF01 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.260 | hwYDDEMSACMeterCqf01ActivePower | CQF01 active power | CQF01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF01 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.261 | hwYDDEMSACMeterCqf01ActiveEnergy | CQF01 active energy | CQF01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF01 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.262 | hwYDDEMSACMeterCqf02Voltage | CQF02 voltage | CQF02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF02 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.263 | hwYDDEMSACMeterCqf02Current | CQF02 current | CQF02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF02 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.264 | hwYDDEMSACMeterCqf02ActivePower | CQF02 active power | CQF02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF02 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.265 | hwYDDEMSACMeterCqf02ActiveEnergy | CQF02 active energy | CQF02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF02 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.266 | hwYDDEMSACMeterCqf03Voltage | CQF03 voltage | CQF03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF03 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.267 | hwYDDEMSACMeterCqf03Current | CQF03 current | CQF03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF03 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.268 | hwYDDEMSACMeterCqf03ActivePower | CQF03 active power | CQF03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF03 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.269 | hwYDDEMSACMeterCqf03ActiveEnergy | CQF03 active energy | CQF03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF03 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.270 | hwYDDEMSACMeterCqf04Voltage | CQF04 voltage | CQF04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF04 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.271 | hwYDDEMSACMeterCqf04Current | CQF04 current | CQF04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF04 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.272 | hwYDDEMSACMeterCqf04ActivePower | CQF04 active power | CQF04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF04 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.273 | hwYDDEMSACMeterCqf04ActiveEnergy | CQF04 active energy | CQF04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF04 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.274 | hwYDDEMSACMeterCqf05Voltage | CQF05 voltage | CQF05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF05 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.275 | hwYDDEMSACMeterCqf05Current | CQF05 current | CQF05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF05 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.276 | hwYDDEMSACMeterCqf05ActivePower | CQF05 active power | CQF05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF05 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.277 | hwYDDEMSACMeterCqf05ActiveEnergy | CQF05 active energy | CQF05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF05 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.278 | hwYDDEMSACMeterCqf06Voltage | CQF06 voltage | CQF06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF06 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.279 | hwYDDEMSACMeterCqf06Current | CQF06 current | CQF06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF06 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.280 | hwYDDEMSACMeterCqf06ActivePower | CQF06 active power | CQF06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF06 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.281 | hwYDDEMSACMeterCqf06ActiveEnergy | CQF06 active energy | CQF06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF06 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.282 | hwYDDEMSACMeterCqf07Voltage | CQF07 voltage | CQF07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF07 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.283 | hwYDDEMSACMeterCqf07Current | CQF07 current | CQF07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF07 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.284 | hwYDDEMSACMeterCqf07ActivePower | CQF07 active power | CQF07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF07 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.285 | hwYDDEMSACMeterCqf07ActiveEnergy | CQF07 active energy | CQF07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF07 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.286 | hwYDDEMSACMeterCqf08Voltage | CQF08 voltage | CQF08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF08 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.287 | hwYDDEMSACMeterCqf08Current | CQF08 current | CQF08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF08 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.288 | hwYDDEMSACMeterCqf08ActivePower | CQF08 active power | CQF08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF08 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.289 | hwYDDEMSACMeterCqf08ActiveEnergy | CQF08 active energy | CQF08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF08 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.290 | hwYDDEMSACMeterCqf09Voltage | CQF09 voltage | CQF09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF09 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.291 | hwYDDEMSACMeterCqf09Current | CQF09 current | CQF09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF09 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.292 | hwYDDEMSACMeterCqf09ActivePower | CQF09 active power | CQF09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF09 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.293 | hwYDDEMSACMeterCqf09ActiveEnergy | CQF09 active energy | CQF09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF09 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.294 | hwYDDEMSACMeterCqf10Voltage | CQF10 voltage | CQF10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF10 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.295 | hwYDDEMSACMeterCqf10Current | CQF10 current | CQF10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF10 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.296 | hwYDDEMSACMeterCqf10ActivePower | CQF10 active power | CQF10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF10 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.297 | hwYDDEMSACMeterCqf10ActiveEnergy | CQF10 active energy | CQF10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF10 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.298 | hwYDDEMSACMeterCqf11Voltage | CQF11 voltage | CQF11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF11 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.300 | hwYDDEMSACMeterRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2 | hwYDDEMSACMeterRunningAndConfig2Table | / | / |  |  | / | / | The running table of YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.1 | hwYDDEMSACMeterRunningAndConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.2 | hwYDDEMSACMeterCqf11Current | CQF11 current | CQF11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF11 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.3 | hwYDDEMSACMeterCqf11ActivePower | CQF11 active power | CQF11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF11 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.4 | hwYDDEMSACMeterCqf11ActiveEnergy | CQF11 active energy | CQF11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF11 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.5 | hwYDDEMSACMeterCqf12Voltage | CQF12 voltage | CQF12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF12 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.6 | hwYDDEMSACMeterCqf12Current | CQF12 current | CQF12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF12 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.7 | hwYDDEMSACMeterCqf12ActivePower | CQF12 active power | CQF12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF12 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.8 | hwYDDEMSACMeterCqf12ActiveEnergy | CQF12 active energy | CQF12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF12 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.9 | hwYDDEMSACMeterCqf13Voltage | CQF13 voltage | CQF13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF13 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.10 | hwYDDEMSACMeterCqf13Current | CQF13 current | CQF13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF13 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.11 | hwYDDEMSACMeterCqf13ActivePower | CQF13 active power | CQF13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF13 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.12 | hwYDDEMSACMeterCqf13ActiveEnergy | CQF13 active energy | CQF13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF13 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.13 | hwYDDEMSACMeterCqf14Voltage | CQF14 voltage | CQF14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF14 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.14 | hwYDDEMSACMeterCqf14Current | CQF14 current | CQF14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF14 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.15 | hwYDDEMSACMeterCqf14ActivePower | CQF14 active power | CQF14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF14 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.16 | hwYDDEMSACMeterCqf14ActiveEnergy | CQF14 active energy | CQF14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF14 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.17 | hwYDDEMSACMeterCqf15Voltage | CQF15 voltage | CQF15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF15 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.18 | hwYDDEMSACMeterCqf15Current | CQF15 current | CQF15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF15 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.19 | hwYDDEMSACMeterCqf15ActivePower | CQF15 active power | CQF15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF15 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.20 | hwYDDEMSACMeterCqf15ActiveEnergy | CQF15 active energy | CQF15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF15 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.21 | hwYDDEMSACMeterCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the YD-DEMS AC Meter. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.22 | hwYDDEMSACMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.23 | hwYDDEMSACMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.24 | hwYDDEMSACMeterDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.300 | hwYDDEMSACMeterRunningAndConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of YD-DEMS AC Meter.

## YD-DEMS DC Meter
YD-DEMS DC Meter
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.2 | YDDEMSDCMeter | YD-DEMS DC Meter | YD-DEMS DC Meter | / | / | / | / | YD-DEMS DC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1 | hwYDDEMSDCMeterRunningandConfig1Table | / | / |  |  | / | / | The running table of YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.1 | hwYDDEMSDCMeterRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.2 | hwYDDEMSDCMeterVoltage | Voltage | 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.3 | hwYDDEMSDCMeterCurrent | Current | 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.4 | hwYDDEMSDCMeterPower | Power | 功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Power of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.5 | hwYDDEMSDCMeterCombinedElectricEnergy | Combined electric energy | 组合电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Combined electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.6 | hwYDDEMSDCMeterPositiveElectricEnergy | Positive electric energy | 正向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.7 | hwYDDEMSDCMeterNegativeEnergy | Negative energy | 反向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.8 | hwYDDEMSDCMeterVoltagePercentage | Voltage percentage | 电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage percentage of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.9 | hwYDDEMSDCMeterCurrentPercentage | Current percentage | 电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current percentage of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.10 | hwYDDEMSDCMeterPositiveInsulationResistance | Positive insulation resistance | 正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive insulation resistance of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.11 | hwYDDEMSDCMeterNegativeInsulationResistance | Negative insulation resistance | 负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative insulation resistance of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.12 | hwYDDEMSDCMeterBusForwardVoltage | Bus forward voltage | 母线正向电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Bus forward voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.13 | hwYDDEMSDCMeterBusNegativeVoltage | Bus negative voltage | 母线负向电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Bus negative voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.14 | hwYDDEMSDCMeterFu1Status | FU1 status | 熔丝1状态 | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | FU1 status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.15 | hwYDDEMSDCMeterFu2Status | FU2 status | 熔丝2状态 | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | FU2 status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.16 | hwYDDEMSDCMeterSpdStatus | SPD status | 防雷器状态 | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | SPD status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.17 | hwYDDEMSDCMeterQf01SwitchStatus | QF01 switch status | QF01开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF01 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.18 | hwYDDEMSDCMeterQf02SwitchStatus | QF02 switch status | QF02开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF02 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.19 | hwYDDEMSDCMeterQf03SwitchStatus | QF03 switch status | QF03开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF03 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.20 | hwYDDEMSDCMeterQf04SwitchStatus | QF04 switch status | QF04开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF04 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.21 | hwYDDEMSDCMeterQf05SwitchStatus | QF05 switch status | QF05开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF05 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.22 | hwYDDEMSDCMeterQf06SwitchStatus | QF06 switch status | QF06开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF06 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.23 | hwYDDEMSDCMeterQf07SwitchStatus | QF07 switch status | QF07开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF07 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.24 | hwYDDEMSDCMeterQf08SwitchStatus | QF08 switch status | QF08开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF08 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.25 | hwYDDEMSDCMeterQf09SwitchStatus | QF09 switch status | QF09开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF09 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.26 | hwYDDEMSDCMeterQf10SwitchStatus | QF10 switch status | QF10开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF10 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.27 | hwYDDEMSDCMeterQf11SwitchStatus | QF11 switch status | QF11开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF11 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.28 | hwYDDEMSDCMeterQf12SwitchStatus | QF12 switch status | QF12开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF12 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.29 | hwYDDEMSDCMeterQf13SwitchStatus | QF13 switch status | QF13开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF13 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.30 | hwYDDEMSDCMeterQf14SwitchStatus | QF14 switch status | QF14开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF14 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.31 | hwYDDEMSDCMeterQf15SwitchStatus | QF15 switch status | QF15开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF15 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.32 | hwYDDEMSDCMeterQf16SwitchStatus | QF16 switch status | QF16开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF16 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.33 | hwYDDEMSDCMeterQf17SwitchStatus | QF17 switch status | QF17开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF17 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.34 | hwYDDEMSDCMeterQf18SwitchStatus | QF18 switch status | QF18开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF18 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.35 | hwYDDEMSDCMeterQf19SwitchStatus | QF19 switch status | QF19开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF19 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.36 | hwYDDEMSDCMeterQf20SwitchStatus | QF20 switch status | QF20开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF20 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.37 | hwYDDEMSDCMeterQf21SwitchStatus | QF21 switch status | QF21开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF21 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.38 | hwYDDEMSDCMeterQf22SwitchStatus | QF22 switch status | QF22开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF22 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.39 | hwYDDEMSDCMeterQf23SwitchStatus | QF23 switch status | QF23开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF23 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.40 | hwYDDEMSDCMeterQf24SwitchStatus | QF24 switch status | QF24开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF24 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.41 | hwYDDEMSDCMeterQf25SwitchStatus | QF25 switch status | QF25开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF25 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.42 | hwYDDEMSDCMeterQf26SwitchStatus | QF26 switch status | QF26开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF26 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.43 | hwYDDEMSDCMeterQf27SwitchStatus | QF27 switch status | QF27开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF27 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.44 | hwYDDEMSDCMeterQf28SwitchStatus | QF28 switch status | QF28开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF28 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.45 | hwYDDEMSDCMeterQf29SwitchStatus | QF29 switch status | QF29开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF29 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.46 | hwYDDEMSDCMeterQf30SwitchStatus | QF30 switch status | QF30开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF30 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.47 | hwYDDEMSDCMeterQf31SwitchStatus | QF31 switch status | QF31开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF31 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.48 | hwYDDEMSDCMeterQf32SwitchStatus | QF32 switch status | QF32开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF32 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.49 | hwYDDEMSDCMeterQf33SwitchStatus | QF33 switch status | QF33开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF33 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.50 | hwYDDEMSDCMeterQf34SwitchStatus | QF34 switch status | QF34开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF34 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.51 | hwYDDEMSDCMeterQf35SwitchStatus | QF35 switch status | QF35开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF35 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.52 | hwYDDEMSDCMeterQf36SwitchStatus | QF36 switch status | QF36开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF36 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.53 | hwYDDEMSDCMeterQf37SwitchStatus | QF37 switch status | QF37开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF37 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.54 | hwYDDEMSDCMeterQf38SwitchStatus | QF38 switch status | QF38开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF38 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.55 | hwYDDEMSDCMeterQf39SwitchStatus | QF39 switch status | QF39开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF39 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.56 | hwYDDEMSDCMeterQf40SwitchStatus | QF40 switch status | QF40开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF40 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.57 | hwYDDEMSDCMeterQf41SwitchStatus | QF41 switch status | QF41开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF41 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.58 | hwYDDEMSDCMeterQf42SwitchStatus | QF42 switch status | QF42开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF42 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.59 | hwYDDEMSDCMeterQf43SwitchStatus | QF43 switch status | QF43开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF43 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.60 | hwYDDEMSDCMeterQf44SwitchStatus | QF44 switch status | QF44开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF44 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.61 | hwYDDEMSDCMeterQf45SwitchStatus | QF45 switch status | QF45开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF45 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.62 | hwYDDEMSDCMeterQf01Voltage | QF01 voltage | QF01电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF01 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.63 | hwYDDEMSDCMeterQf01Current | QF01 current | QF01电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF01 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.64 | hwYDDEMSDCMeterQf01ActivePower | QF01 active power | QF01有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF01 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.65 | hwYDDEMSDCMeterQf01ActiveElectricEnergy | QF01 active electric energy | QF01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.66 | hwYDDEMSDCMeterQf02Voltage | QF02 voltage | QF02电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF02 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.67 | hwYDDEMSDCMeterQf02Current | QF02 current | QF02电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF02 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.68 | hwYDDEMSDCMeterQf02ActivePower | QF02 active power | QF02有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF02 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.69 | hwYDDEMSDCMeterQf02ActiveElectricEnergy | QF02 active electric energy | QF02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF02 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.70 | hwYDDEMSDCMeterQf03Voltage | QF03 voltage | QF03电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF03 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.71 | hwYDDEMSDCMeterQf03Current | QF03 current | QF03电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF03 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.72 | hwYDDEMSDCMeterQf03ActivePower | QF03 active power | QF03有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF03 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.73 | hwYDDEMSDCMeterQf03ActiveElectricEnergy | QF03 active electric energy | QF03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF03 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.74 | hwYDDEMSDCMeterQf04Voltage | QF04 voltage | QF04电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF04 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.75 | hwYDDEMSDCMeterQf04Current | QF04 current | QF04电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF04 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.76 | hwYDDEMSDCMeterQf04ActivePower | QF04 active power | QF04有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF04 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.77 | hwYDDEMSDCMeterQf04ActiveElectricEnergy | QF04 active electric energy | QF04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF04 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.78 | hwYDDEMSDCMeterQf05Voltage | QF05 voltage | QF05电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF05 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.79 | hwYDDEMSDCMeterQf05Current | QF05 current | QF05电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF05 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.80 | hwYDDEMSDCMeterQf05ActivePower | QF05 active power | QF05有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF05 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.81 | hwYDDEMSDCMeterQf05ActiveElectricEnergy | QF05 active electric energy | QF05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF05 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.82 | hwYDDEMSDCMeterQf06Voltage | QF06 voltage | QF06电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF06 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.83 | hwYDDEMSDCMeterQf06Current | QF06 current | QF06电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF06 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.84 | hwYDDEMSDCMeterQf06ActivePower | QF06 active power | QF06有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF06 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.85 | hwYDDEMSDCMeterQf06ActiveElectricEnergy | QF06 active electric energy | QF06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF06 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.86 | hwYDDEMSDCMeterQf07Voltage | QF07 voltage | QF07电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF07 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.87 | hwYDDEMSDCMeterQf07Current | QF07 current | QF07电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF07 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.88 | hwYDDEMSDCMeterQf07ActivePower | QF07 active power | QF07有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF07 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.89 | hwYDDEMSDCMeterQf07ActiveElectricEnergy | QF07 active electric energy | QF07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF07 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.90 | hwYDDEMSDCMeterQf08Voltage | QF08 voltage | QF08电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF08 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.91 | hwYDDEMSDCMeterQf08Current | QF08 current | QF08电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF08 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.92 | hwYDDEMSDCMeterQf08ActivePower | QF08 active power | QF08有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF08 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.93 | hwYDDEMSDCMeterQf08ActiveElectricEnergy | QF08 active electric energy | QF08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF08 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.94 | hwYDDEMSDCMeterQf09Voltage | QF09 voltage | QF09电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF09 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.95 | hwYDDEMSDCMeterQf09Current | QF09 current | QF09电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF09 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.96 | hwYDDEMSDCMeterQf09ActivePower | QF09 active power | QF09有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF09 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.97 | hwYDDEMSDCMeterQf09ActiveElectricEnergy | QF09 active electric energy | QF09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF09 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.98 | hwYDDEMSDCMeterQf10Voltage | QF10 voltage | QF10电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF10 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.99 | hwYDDEMSDCMeterQf10Current | QF10 current | QF10电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF10 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.100 | hwYDDEMSDCMeterQf10ActivePower | QF10 active power | QF10有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF10 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.101 | hwYDDEMSDCMeterQf10ActiveElectricEnergy | QF10 active electric energy | QF10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF10 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.102 | hwYDDEMSDCMeterQf11Voltage | QF11 voltage | QF11电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF11 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.103 | hwYDDEMSDCMeterQf11Current | QF11 current | QF11电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF11 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.104 | hwYDDEMSDCMeterQf11ActivePower | QF11 active power | QF11有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF11 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.105 | hwYDDEMSDCMeterQf11ActiveElectricEnergy | QF11 active electric energy | QF11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF11 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.106 | hwYDDEMSDCMeterQf12Voltage | QF12 voltage | QF12电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF12 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.107 | hwYDDEMSDCMeterQf12Current | QF12 current | QF12电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF12 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.108 | hwYDDEMSDCMeterQf12ActivePower | QF12 active power | QF12有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF12 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.109 | hwYDDEMSDCMeterQf12ActiveElectricEnergy | QF12 active electric energy | QF12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF12 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.110 | hwYDDEMSDCMeterQf13Voltage | QF13 voltage | QF13电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF13 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.111 | hwYDDEMSDCMeterQf13Current | QF13 current | QF13电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF13 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.112 | hwYDDEMSDCMeterQf13ActivePower | QF13 active power | QF13有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF13 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.113 | hwYDDEMSDCMeterQf13ActiveElectricEnergy | QF13 active electric energy | QF13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF13 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.114 | hwYDDEMSDCMeterQf14Voltage | QF14 voltage | QF14电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF14 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.115 | hwYDDEMSDCMeterQf14Current | QF14 current | QF14电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF14 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.116 | hwYDDEMSDCMeterQf14ActivePower | QF14 active power | QF14有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF14 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.117 | hwYDDEMSDCMeterQf14ActiveElectricEnergy | QF14 active electric energy | QF14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF14 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.118 | hwYDDEMSDCMeterQf15Voltage | QF15 voltage | QF15电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF15 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.119 | hwYDDEMSDCMeterQf15Current | QF15 current | QF15电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF15 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.120 | hwYDDEMSDCMeterQf15ActivePower | QF15 active power | QF15有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF15 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.121 | hwYDDEMSDCMeterQf15ActiveElectricEnergy | QF15 active electric energy | QF15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF15 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.122 | hwYDDEMSDCMeterQf16Voltage | QF16 voltage | QF16电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF16 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.123 | hwYDDEMSDCMeterQf16Current | QF16 current | QF16电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF16 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.124 | hwYDDEMSDCMeterQf16ActivePower | QF16 active power | QF16有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF16 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.125 | hwYDDEMSDCMeterQf16ActiveElectricEnergy | QF16 active electric energy | QF16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF16 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.126 | hwYDDEMSDCMeterQf17Voltage | QF17 voltage | QF17电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF17 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.127 | hwYDDEMSDCMeterQf17Current | QF17 current | QF17电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF17 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.128 | hwYDDEMSDCMeterQf17ActivePower | QF17 active power | QF17有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF17 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.129 | hwYDDEMSDCMeterQf17ActiveElectricEnergy | QF17 active electric energy | QF17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF17 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.130 | hwYDDEMSDCMeterQf18Voltage | QF18 voltage | QF18电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF18 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.131 | hwYDDEMSDCMeterQf18Current | QF18 current | QF18电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF18 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.132 | hwYDDEMSDCMeterQf18ActivePower | QF18 active power | QF18有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF18 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.133 | hwYDDEMSDCMeterQf18ActiveElectricEnergy | QF18 active electric energy | QF18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF18 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.134 | hwYDDEMSDCMeterQf19Voltage | QF19 voltage | QF19电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF19 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.135 | hwYDDEMSDCMeterQf19Current | QF19 current | QF19电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF19 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.136 | hwYDDEMSDCMeterQf19ActivePower | QF19 active power | QF19有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF19 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.137 | hwYDDEMSDCMeterQf19ActiveElectricEnergy | QF19 active electric energy | QF19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF19 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.138 | hwYDDEMSDCMeterQf20Voltage | QF20 voltage | QF20电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF20 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.139 | hwYDDEMSDCMeterQf20Current | QF20 current | QF20电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF20 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.140 | hwYDDEMSDCMeterQf20ActivePower | QF20 active power | QF20有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF20 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.141 | hwYDDEMSDCMeterQf20ActiveElectricEnergy | QF20 active electric energy | QF20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF20 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.142 | hwYDDEMSDCMeterQf21Voltage | QF21 voltage | QF21电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF21 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.143 | hwYDDEMSDCMeterQf21Current | QF21 current | QF21电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF21 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.144 | hwYDDEMSDCMeterQf21ActivePower | QF21 active power | QF21有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF21 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.145 | hwYDDEMSDCMeterQf21ActiveElectricEnergy | QF21 active electric energy | QF21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF21 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.146 | hwYDDEMSDCMeterQf22Voltage | QF22 voltage | QF22电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF22 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.147 | hwYDDEMSDCMeterQf22Current | QF22 current | QF22电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF22 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.148 | hwYDDEMSDCMeterQf22ActivePower | QF22 active power | QF22有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF22 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.149 | hwYDDEMSDCMeterQf22ActiveElectricEnergy | QF22 active electric energy | QF22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF22 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.150 | hwYDDEMSDCMeterQf23Voltage | QF23 voltage | QF23电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF23 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.151 | hwYDDEMSDCMeterQf23Current | QF23 current | QF23电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF23 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.152 | hwYDDEMSDCMeterQf23ActivePower | QF23 active power | QF23有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF23 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.153 | hwYDDEMSDCMeterQf23ActiveElectricEnergy | QF23 active electric energy | QF23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF23 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.154 | hwYDDEMSDCMeterQf24Voltage | QF24 voltage | QF24电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF24 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.155 | hwYDDEMSDCMeterQf24Current | QF24 current | QF24电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF24 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.156 | hwYDDEMSDCMeterQf24ActivePower | QF24 active power | QF24有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF24 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.157 | hwYDDEMSDCMeterQf24ActiveElectricEnergy | QF24 active electric energy | QF24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF24 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.158 | hwYDDEMSDCMeterQf25Voltage | QF25 voltage | QF25电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF25 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.159 | hwYDDEMSDCMeterQf25Current | QF25 current | QF25电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF25 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.160 | hwYDDEMSDCMeterQf25ActivePower | QF25 active power | QF25有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF25 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.161 | hwYDDEMSDCMeterQf25ActiveElectricEnergy | QF25 active electric energy | QF25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF25 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.162 | hwYDDEMSDCMeterQf26Voltage | QF26 voltage | QF26电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF26 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.163 | hwYDDEMSDCMeterQf26Current | QF26 current | QF26电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF26 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.164 | hwYDDEMSDCMeterQf26ActivePower | QF26 active power | QF26有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF26 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.165 | hwYDDEMSDCMeterQf26ActiveElectricEnergy | QF26 active electric energy | QF26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF26 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.166 | hwYDDEMSDCMeterQf27Voltage | QF27 voltage | QF27电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF27 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.167 | hwYDDEMSDCMeterQf27Current | QF27 current | QF27电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF27 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.168 | hwYDDEMSDCMeterQf27ActivePower | QF27 active power | QF27有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF27 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.169 | hwYDDEMSDCMeterQf27ActiveElectricEnergy | QF27 active electric energy | QF27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF27 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.170 | hwYDDEMSDCMeterQf28Voltage | QF28 voltage | QF28电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF28 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.171 | hwYDDEMSDCMeterQf28Current | QF28 current | QF28电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF28 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.172 | hwYDDEMSDCMeterQf28ActivePower | QF28 active power | QF28有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF28 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.173 | hwYDDEMSDCMeterQf28ActiveElectricEnergy | QF28 active electric energy | QF28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF28 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.174 | hwYDDEMSDCMeterQf29Voltage | QF29 voltage | QF29电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF29 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.175 | hwYDDEMSDCMeterQf29Current | QF29 current | QF29电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF29 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.176 | hwYDDEMSDCMeterQf29ActivePower | QF29 active power | QF29有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF29 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.177 | hwYDDEMSDCMeterQf29ActiveElectricEnergy | QF29 active electric energy | QF29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF29 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.178 | hwYDDEMSDCMeterQf30Voltage | QF30 voltage | QF30电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF30 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.179 | hwYDDEMSDCMeterQf30Current | QF30 current | QF30电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF30 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.180 | hwYDDEMSDCMeterQf30ActivePower | QF30 active power | QF30有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF30 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.181 | hwYDDEMSDCMeterQf30ActiveElectricEnergy | QF30 active electric energy | QF30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF30 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.182 | hwYDDEMSDCMeterQf31Voltage | QF31 voltage | QF31电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF31 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.183 | hwYDDEMSDCMeterQf31Current | QF31 current | QF31电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF31 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.184 | hwYDDEMSDCMeterQf31ActivePower | QF31 active power | QF31有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF31 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.185 | hwYDDEMSDCMeterQf31ActiveElectricEnergy | QF31 active electric energy | QF31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF31 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.186 | hwYDDEMSDCMeterQf32Voltage | QF32 voltage | QF32电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF32 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.187 | hwYDDEMSDCMeterQf32Current | QF32 current | QF32电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF32 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.188 | hwYDDEMSDCMeterQf32ActivePower | QF32 active power | QF32有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF32 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.189 | hwYDDEMSDCMeterQf32ActiveElectricEnergy | QF32 active electric energy | QF32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF32 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.190 | hwYDDEMSDCMeterQf33Voltage | QF33 voltage | QF33电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF33 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.191 | hwYDDEMSDCMeterQf33Current | QF33 current | QF33电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF33 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.192 | hwYDDEMSDCMeterQf33ActivePower | QF33 active power | QF33有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF33 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.193 | hwYDDEMSDCMeterQf33ActiveElectricEnergy | QF33 active electric energy | QF33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF33 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.194 | hwYDDEMSDCMeterQf34Voltage | QF34 voltage | QF34电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF34 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.195 | hwYDDEMSDCMeterQf34Current | QF34 current | QF34电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF34 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.196 | hwYDDEMSDCMeterQf34ActivePower | QF34 active power | QF34有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF34 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.197 | hwYDDEMSDCMeterQf34ActiveElectricEnergy | QF34 active electric energy | QF34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF34 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.198 | hwYDDEMSDCMeterQf35Voltage | QF35 voltage | QF35电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF35 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.199 | hwYDDEMSDCMeterQf35Current | QF35 current | QF35电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF35 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.200 | hwYDDEMSDCMeterQf35ActivePower | QF35 active power | QF35有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF35 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.201 | hwYDDEMSDCMeterQf35ActiveElectricEnergy | QF35 active electric energy | QF35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF35 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.202 | hwYDDEMSDCMeterQf36Voltage | QF36 voltage | QF36电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF36 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.203 | hwYDDEMSDCMeterQf36Current | QF36 current | QF36电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF36 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.204 | hwYDDEMSDCMeterQf36ActivePower | QF36 active power | QF36有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF36 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.205 | hwYDDEMSDCMeterQf36ActiveElectricEnergy | QF36 active electric energy | QF36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF36 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.206 | hwYDDEMSDCMeterQf37Voltage | QF37 voltage | QF37电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF37 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.207 | hwYDDEMSDCMeterQf37Current | QF37 current | QF37电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF37 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.208 | hwYDDEMSDCMeterQf37ActivePower | QF37 active power | QF37有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF37 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.209 | hwYDDEMSDCMeterQf37ActiveElectricEnergy | QF37 active electric energy | QF37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF37 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.210 | hwYDDEMSDCMeterQf38Voltage | QF38 voltage | QF38电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF38 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.211 | hwYDDEMSDCMeterQf38Current | QF38 current | QF38电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF38 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.212 | hwYDDEMSDCMeterQf38ActivePower | QF38 active power | QF38有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF38 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.213 | hwYDDEMSDCMeterQf38ActiveElectricEnergy | QF38 active electric energy | QF38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF38 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.214 | hwYDDEMSDCMeterQf39Voltage | QF39 voltage | QF39电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF39 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.215 | hwYDDEMSDCMeterQf39Current | QF39 current | QF39电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF39 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.216 | hwYDDEMSDCMeterQf39ActivePower | QF39 active power | QF39有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF39 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.217 | hwYDDEMSDCMeterQf39ActiveElectricEnergy | QF39 active electric energy | QF39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF39 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.218 | hwYDDEMSDCMeterQf40Voltage | QF40 voltage | QF40电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF40 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.219 | hwYDDEMSDCMeterQf40Current | QF40 current | QF40电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF40 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.220 | hwYDDEMSDCMeterQf40ActivePower | QF40 active power | QF40有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF40 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.221 | hwYDDEMSDCMeterQf40ActiveElectricEnergy | QF40 active electric energy | QF40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF40 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.222 | hwYDDEMSDCMeterQf41Voltage | QF41 voltage | QF41电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF41 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.223 | hwYDDEMSDCMeterQf41Current | QF41 current | QF41电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF41 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.224 | hwYDDEMSDCMeterQf41ActivePower | QF41 active power | QF41有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF41 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.225 | hwYDDEMSDCMeterQf41ActiveElectricEnergy | QF41 active electric energy | QF41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF41 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.226 | hwYDDEMSDCMeterQf42Voltage | QF42 voltage | QF42电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF42 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.227 | hwYDDEMSDCMeterQf42Current | QF42 current | QF42电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF42 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.228 | hwYDDEMSDCMeterQf42ActivePower | QF42 active power | QF42有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF42 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.229 | hwYDDEMSDCMeterQf42ActiveElectricEnergy | QF42 active electric energy | QF42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF42 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.230 | hwYDDEMSDCMeterQf43Voltage | QF43 voltage | QF43电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF43 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.231 | hwYDDEMSDCMeterQf43Current | QF43 current | QF43电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF43 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.232 | hwYDDEMSDCMeterQf43ActivePower | QF43 active power | QF43有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF43 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.233 | hwYDDEMSDCMeterQf43ActiveElectricEnergy | QF43 active electric energy | QF43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF43 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.234 | hwYDDEMSDCMeterQf44Voltage | QF44 voltage | QF44电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF44 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.235 | hwYDDEMSDCMeterQf44Current | QF44 current | QF44电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF44 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.236 | hwYDDEMSDCMeterQf44ActivePower | QF44 active power | QF44有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF44 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.237 | hwYDDEMSDCMeterQf44ActiveElectricEnergy | QF44 active electric energy | QF44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF44 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.238 | hwYDDEMSDCMeterQf45Voltage | QF45 voltage | QF45电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF45 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.239 | hwYDDEMSDCMeterQf45Current | QF45 current | QF45电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF45 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.240 | hwYDDEMSDCMeterQf45ActivePower | QF45 active power | QF45有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF45 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.241 | hwYDDEMSDCMeterQf45ActiveElectricEnergy | QF45 active electric energy | QF45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF45 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.242 | hwYDDEMSDCMeterCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the YD-DEMS DC Meter. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.243 | hwYDDEMSDCMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.244 | hwYDDEMSDCMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.245 | hwYDDEMSDCMeterDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.300 | hwYDDEMSDCMeterRunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of YD-DEMS DC Meter.

## AC Meter-TellHow-qmc
交流电表-泰豪-qmc
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.4 | TELLHOWRAYBACMeter | AC Meter-TellHow-qmc | 交流电表-泰豪-qmc | / | / | / | / | TELLHOW-RAYB AC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1 | hwTELLHOW-RAYBACMeterRunning1Table | / | / |  |  | / | / | The running table of TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.1 | hwTELLHOW-RAYBACMeterRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.2 | hwTELLHOWRAYBACMeterIa | Ia | A相相电流 | 0-Read_Only | 只读 | 0..49999000 | 0..49999000 | Ia of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.3 | hwTELLHOWRAYBACMeterIb | Ib | B相相电流 | 0-Read_Only | 只读 | 0..49999000 | 0..49999000 | Ib of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.4 | hwTELLHOWRAYBACMeterIc | Ic | C相相电流 | 0-Read_Only | 只读 | 0..49999000 | 0..49999000 | Ic of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.5 | hwTELLHOWRAYBACMeterIAverage | I average | ABC三相电流平均值 | 0-Read_Only | 只读 | 0..49999000 | 0..49999000 | I average of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.6 | hwTELLHOWRAYBACMeterUan | Uan | A相相电压 | 0-Read_Only | 只读 | 0..220000000 | 0..220000000 | Uan of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.7 | hwTELLHOWRAYBACMeterUbn | Ubn | B相相电压 | 0-Read_Only | 只读 | 0..220000000 | 0..220000000 | Ubn of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.8 | hwTELLHOWRAYBACMeterUcn | Ucn | C相相电压 | 0-Read_Only | 只读 | 0..220000000 | 0..220000000 | Ucn of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.9 | hwTELLHOWRAYBACMeterUlnAverage | Uln average | ABC三相电压平均值 | 0-Read_Only | 只读 | 0..220000000 | 0..220000000 | Uln average of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.10 | hwTELLHOWRAYBACMeterUab | Uab | A相线电压 | 0-Read_Only | 只读 | 0..380000000 | 0..380000000 | Uab of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.11 | hwTELLHOWRAYBACMeterUbc | Ubc | B相线电压 | 0-Read_Only | 只读 | 0..380000000 | 0..380000000 | Ubc of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.12 | hwTELLHOWRAYBACMeterUca | Uca | C相线电压 | 0-Read_Only | 只读 | 0..380000000 | 0..380000000 | Uca of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.13 | hwTELLHOWRAYBACMeterUllAverage | Ull average | ABC三相线电压平均值 | 0-Read_Only | 只读 | 0..380000000 | 0..380000000 | Ull average of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.14 | hwTELLHOWRAYBACMeterPa | Pa | A相有功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Pa of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.15 | hwTELLHOWRAYBACMeterPb | Pb | B相有功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Pb of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.16 | hwTELLHOWRAYBACMeterPc | Pc | C相有功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Pc of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.17 | hwTELLHOWRAYBACMeterSigmaP | ∑P | ABC三相有功总功率 | 0-Read_Only | 只读 | 0..3300000 | 0..3300000 | SigmaP of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.18 | hwTELLHOWRAYBACMeterQa | Qa | A相无功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Qa of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.19 | hwTELLHOWRAYBACMeterQb | Qb | B相无功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Qb of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.20 | hwTELLHOWRAYBACMeterQc | Qc | C相无功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Qc of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.21 | hwTELLHOWRAYBACMeterSigmaQ | ∑Q | ABC三相无功总功率 | 0-Read_Only | 只读 | 0..3300000 | 0..3300000 | SigmaQ of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.22 | hwTELLHOWRAYBACMeterSa | Sa | A相视在功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Sa of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.23 | hwTELLHOWRAYBACMeterSb | Sb | B相视在功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Sb of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.24 | hwTELLHOWRAYBACMeterSc | Sc | C相视在功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Sc of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.25 | hwTELLHOWRAYBACMeterSigmaS | ∑S | ABC三相视在总功率 | 0-Read_Only | 只读 | 0..3300000 | 0..3300000 | SigmaS of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.26 | hwTELLHOWRAYBACMeterPfA | Pf a | A相功率因数 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Pf a of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.27 | hwTELLHOWRAYBACMeterPfB | Pf b | B相功率因数 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Pf b of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.28 | hwTELLHOWRAYBACMeterPfC | Pf c | C相功率因数 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Pf c of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.29 | hwTELLHOWRAYBACMeterPfAverage | Pf average | ABC三相平均功率因数 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Pf average of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.30 | hwTELLHOWRAYBACMeterFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Frequency of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.31 | hwTELLHOWRAYBACMeterCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the TELLHOW-RAYB AC Meter. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.32 | hwTELLHOWRAYBACMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.33 | hwTELLHOWRAYBACMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.34 | hwTELLHOWRAYBACMeterDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.300 | hwTELLHOW-RAYBACMeterRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of TELLHOW-RAYB AC Meter.

## Ac Meter-Yada-yd2060
交流电表-雅达-yd2060
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.5 | AcMeterYadayd2060 | Ac Meter-Yada-yd2060 | 交流电表-雅达-yd2060 | / | / | / | / | Ac Meter-Yada-yd2060 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1 | hwAcMeterYadayd2060RunningAndConfig1Table | / | / |  |  | / | / | The running table of Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.1 | hwAcMeterYadayd2060Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.2 | hwAcMeterYadayd2060Frequency | Frequency | 频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.3 | hwAcMeterYadayd2060AverageLineVoltage | Average line voltage | 平均线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average line voltage of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.4 | hwAcMeterYadayd2060LineVoltageUab | Line voltage UAB | 线电压UAB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage UAB of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.5 | hwAcMeterYadayd2060LineVoltageUbc | Line voltage UBC | 线电压UBC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage UBC of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.6 | hwAcMeterYadayd2060LineVoltageUca | Line voltage UCA | 线电压UCA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage UCA of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.7 | hwAcMeterYadayd2060AveragePhaseVoltage | Average phase voltage | 平均相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average phase voltage of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.8 | hwAcMeterYadayd2060PhaseVoltageA | Phase voltage A | 相电压A | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage A of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.9 | hwAcMeterYadayd2060PhaseVoltageB | Phase voltage B | 相电压B | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage B of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.10 | hwAcMeterYadayd2060PhaseVoltageC | Phase voltage C | 相电压C | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage C of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.11 | hwAcMeterYadayd2060PhaseAVoltagePhaseAngle | Phase A voltage phase angle | A相电压相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage phase angle of the device config table for the Ac Meter-Yada-yd2060.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.12 | hwAcMeterYadayd2060PhaseBVoltagePhaseAngle | Phase B voltage phase angle | B相电压相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B voltage phase angle of the device config table for the Ac Meter-Yada-yd2060.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.13 | hwAcMeterYadayd2060PhaseCVoltagePhaseAngle | Phase C voltage phase angle | C相电压相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C voltage phase angle of the device config table for the Ac Meter-Yada-yd2060.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.14 | hwAcMeterYadayd2060PhaseACurrentOfTheFirstRoute | Phase A current of the first route | 第1路A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.15 | hwAcMeterYadayd2060PhaseBCurrentOfTheFirstRoute | Phase B current of the first route | 第1路B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.16 | hwAcMeterYadayd2060PhaseCCurrentOfTheFirstRoute | Phase C current of the first route | 第1路C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.17 | hwAcMeterYadayd2060TotalActivePowerOfTheFirstRoute | Total active power of the first route | 第1路总有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total active power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.18 | hwAcMeterYadayd2060TotalReactivePowerOfTheFirstRoute | Total reactive power of the first route | 第1路总无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total reactive power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.19 | hwAcMeterYadayd2060TotalApparentPowerOfTheFirstRoute | Total apparent power of the first route | 第1路总视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total apparent power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.20 | hwAcMeterYadayd2060TotalPowerFactorOfTheFirstRoute | Total power factor of the first route | 第1路总功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total power factor of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.21 | hwAcMeterYadayd2060PhaseAActivePowerOfTheFirstRoute | Phase A active power of the first route | 第1路A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.22 | hwAcMeterYadayd2060PhaseBActivePowerOfTheFirstRoute | Phase B active power of the first route | 第1路B相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.23 | hwAcMeterYadayd2060PhaseCActivePowerOfTheFirstRoute | Phase C active power of the first route | 第1路C相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.24 | hwAcMeterYadayd2060PhaseAReactivePowerOfTheFirstRoute | Phase A reactive power of the first route | 第1路A相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A reactive power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.25 | hwAcMeterYadayd2060PhaseBReactivePowerOfTheFirstRoute | Phase B reactive power of the first route | 第1路B相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B reactive power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.26 | hwAcMeterYadayd2060PhaseCreactivePowerOfTheFirstRoute | Phase C reactive power of the first route | 第1路C相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase Creactive power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.27 | hwAcMeterYadayd2060PhaseAPowerFactorOfTheFirstRoute | Phase A power factor of the first route | 第1路A相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A power factor of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.28 | hwAcMeterYadayd2060PhaseBPowerFactorOfTheFirstRoute | Phase B power factor of the first route | 第1路B相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B power factor of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.29 | hwAcMeterYadayd2060PhaseCPowerFactorOfTheFirstRoute | Phase C power factor of the first route | 第1路C相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C power factor of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.30 | hwAcMeterYadayd2060TotalActiveEnergyOfTheFirstRoute | Total active energy of the first route | 第1路总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total active energy of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.31 | hwAcMeterYadayd2060PhaseAActiveEnergyOfTheFirstRoute | Phase A active energy of the first route | 第1路A相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active energy of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.32 | hwAcMeterYadayd2060PhaseBActiveEnergyOfTheFirstRoute | Phase B active energy of the first route | 第1路B相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active energy of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.33 | hwAcMeterYadayd2060PhaseCActiveEnergyOfTheFirstRoute | Phase C active energy of the first route | 第1路C相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active energy of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.34 | hwAcMeterYadayd2060CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Ac Meter-Yada-yd2060. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.35 | hwAcMeterYadayd2060PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.36 | hwAcMeterYadayd2060ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Ac Meter-Yada-yd2060.
| hwAcMeterYadayd2060Model | / | / | 0-Read_Only | 只读 | 0..8 | / | Model of the device config table for the Ac Meter-Yada-yd2060.
| hwAcMeterYadayd2060Version | / | / | 0-Read_Only | 只读 | 0..8 | / | Version of the device config table for the Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.39 | hwAcMeterYadayd2060DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.40 | hwAcMeterYadayd2060PhaseVoltage | Phase voltage | 相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.41 | hwAcMeterYadayd2060Current | Current | 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.42 | hwAcMeterYadayd2060ActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active power of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.43 | hwAcMeterYadayd2060ReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Reactive power of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.44 | hwAcMeterYadayd2060PowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Power factor of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.45 | hwAcMeterYadayd2060ActiveEnergy | Active energy | 有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active energy of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.46 | hwAcMeterYadayd2060InputMode | Input mode | 输入制式 | 1-Read_Write | 读写 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | Input mode of the device config table for the Ac Meter-Yada-yd2060. Value 1 single phase Value 2 three phase
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.47 | hwAcMeterYadayd2060ApparentPower | Apparent power | 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Apparent power of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.300 | hwAcMeterYadayd2060RunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Ac Meter-Yada-yd2060.

## UPS2000
UPS2000
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.1 | UPS2000GA | UPS2000 | UPS2000 | / | / | / | /
1.3.6.1.4.1.2011.6.178.1.1.5.1.1 | hwUPS2000GARunningAndConfig1Table | / | / |  |  | / | / | Running table of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.1 | hwUPS2000GARunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.2 | hwUPS2000GAEsn | ESN | ESN | 0-Read_Only | 只读 | 1..31 | 1..31 | ESN of the master device used for setting up a NetEco model. A string of characters.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.3 | hwUPS2000GADeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Name of the UPS system. A string of characters. Configurable.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.4 | hwUPS2000GAModel | UPS model | UPS机型 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | UPS model of the device config table for the UPS2000. Multiple:10.SigUnitInfo:K
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.5 | hwUPS2000GAPowerMode | Power status | 供电模式 | 0-Read_Only | 只读 | nopowersupply(1), bypassmode(2), mainsmode(3), batterymode(4), mainseco(5), batteryeco(6), unknown(255) | [均不供电=1]/[旁路供电=2]/[主路供电=3]/[电池供电=4]/[主路ECO=5]/[电池ECO=6]/[联合供电=7] | Device power supply mode. Enumeration type. Value 1 indicates no power supply. Value 2 indicates bypass mode. Value 3 indicates normal mode. Value 4 indicates battery mode. Value 5 indicates mains ECO mode. Value 6 indicates battery ECO mode.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.6 | hwUPS2000GAInputMode | Input mode | 输入制式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Device input mode. Value 1 indicates singlephase. Value 2 indicates threephase.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.7 | hwUPS2000GAOutputMode | Output mode | 输出制式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Device output mode. Value 1 indicates singlephase. Value 2 indicates threephase.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.8 | hwUPS2000GAInnerTemperature | Inside-UPS temperature | 机内温度 | 0-Read_Only | 只读 | -3276..3276 | -3276..3276 | Maximum temperature of the modules in the current device. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.9 | hwUPS2000GAStartupStatus | Startup status | 开机状态 | 0-Read_Only | 只读 | shutdown(1), starting(2), startupfailed(3), startupdone(4), unknown(255) | [关机=1]/[开机中=2]/[开机失败=3]/[开机完成=4] | Device Startup Status. Value 1 indicates shutdown. Value 2 indicates starting. Value 3 indicates startupfailed. Value 4 indicates startupdone.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.10 | hwUPS2000GAInputVoltage | Input voltage | 输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.11 | hwUPS2000GABypassVoltage | Bypass voltage | 旁路电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Bypass input voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.12 | hwUPS2000GAOutputVoltage | Output voltage | 输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack output voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.13 | hwUPS2000GAOutputCurrent | Output current | 输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack output current. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.14 | hwUPS2000GAOutputActivePower | Output active power | 输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack output active power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.15 | hwUPS2000GAOutputApparentPower | Output apparent power | 输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack output apparent power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.16 | hwUPS2000GALoadRatio | Load ratio | 负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Rack output load ratio. The value is accurate to one decimal place on the NetEco.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.17 | hwUPS2000GAPhaseAInputVoltage | Input phase voltage (A) | A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input voltage phase A. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.18 | hwUPS2000GAPhaseBInputVoltage | Input phase voltage (B) | B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input voltage phase B. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.19 | hwUPS2000GAPhaseCInputVoltage | Input phase voltage (C) | C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input voltage phase C. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.20 | hwUPS2000GAInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input frequency. The value is accurate to two decimal place on the NetEco. Multiple:10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.21 | hwUPS2000GAPhaseABypassVoltage | Bypass phase voltage (A) | A相旁路电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Bypass input voltage phase A. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.22 | hwUPS2000GAPhaseBBypassVoltage | Bypass phase voltage (B) | B相旁路电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Bypass input voltage phase B. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.23 | hwUPS2000GAPhaseCBypassVoltage | Bypass phase voltage (C) | C相旁路电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Bypass input voltage phase C. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.24 | hwUPS2000GABypassFrequency | Bypass frequency | 旁路频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Bypass input frequency. The value is accurate to two decimal place on the NetEco. Multiple:10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.25 | hwUPS2000GAPhaseAOutputVoltage | Output phase voltage (A) | A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase A output voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.26 | hwUPS2000GAPhaseBOutputVoltage | Output phase voltage (B) | B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase B output voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.27 | hwUPS2000GAPhaseCOutputVoltage | Output phase voltage (C) | C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase C output voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.28 | hwUPS2000GAPhaseAOutputCurrent | Output current (A) | A相输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase A output current. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.29 | hwUPS2000GAPhaseBOutputCurrent | Output current (B) | B相输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase B output current. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.30 | hwUPS2000GAPhaseCOutputCurrent | Output current (C) | C相输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase C output current. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.31 | hwUPS2000GAOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack output frequency. The value is accurate to two decimal place on the NetEco. Multiple:10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.32 | hwUPS2000GAPhaseAOutputActivePower | Output active power (A) | A相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output active power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.33 | hwUPS2000GAPhaseBOutputActivePower | Output active power (B) | B相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output active power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.34 | hwUPS2000GAPhaseCOutputActivePower | Output active power (C) | C相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output active power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.35 | hwUPS2000GAPhaseAOutputApparentPower | Output apparent power (A) | A相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output apparent power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.36 | hwUPS2000GAPhaseBOutputApparentPower | Output apparent power (B) | B相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output apparent power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.37 | hwUPS2000GAPhaseCOutputApparentPower | Output apparent power (C) | C相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output apparent power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.38 | hwUPS2000GAPhaseALoadRatio | Load ratio (A) | A相负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Rack phase A output load ratio. The value is accurate to one decimal place on the NetEco.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.39 | hwUPS2000GAPhaseBLoadRatio | Load ratio (B) | B相负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Rack phase B output load ratio. The value is accurate to one decimal place on the NetEco.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.40 | hwUPS2000GAPhaseCLoadRatio | Load ratio (C) | C相负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Rack phase C output load ratio. The value is accurate to one decimal place on the NetEco.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.41 | hwUPS2000GABatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery Voltage. It is a real-time analog parameter. Unit: V, and the value is accurate to one decimal place (.1).Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.42 | hwUPS2000GABatteryCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Battery Total Current. It is a real-time analog parameter. Unit: A, and the value is accurate to one decimal place (.1).Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.43 | hwUPS2000GABatteryStatus | Battery status | 电池状态 | 0-Read_Only | 只读 | notconnected(1), notchargingordischarging(2), hibernation(3), floatcharging(4), equalizedcharging(5), discharging(6), unknown(255) | [未接入=1]/[非充非放=2]/[休眠=3]/[浮充=4]/[均充=5]/[放电=6] | Battery status. Enumeration type. Value 1 indicates that no battery is connected. Value 2 indicates that the battery is not charging or discharging. Value 3 indicates hibernation. Value 4 indicates float charging. Value 5 indicates equalized charging. Value 6 indicates discharging.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.44 | hwUPS2000GABatteryRemainRatio | Remaining capacity | 电池剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery Capacity Left. Unit: %RH, and the value is an integer. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.45 | hwUPS2000GABatteryBackupTime | Battery backup time | 备电时间 | 0-Read_Only | 只读 | 0..2880 | 0..2880 | Battery Backup Time. Unit: Min, and the value is an integer. SigUnitInfo:min
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.46 | hwUPS2000GABatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Battery temperature.Unit:degC, and the value is accurate to one decimal place (.1). Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.47 | hwUPS2000GAParallelStatus | Parallel status | 并机状态 | 0-Read_Only | 只读 | single(1), parallel(2), unknown(255) | [单机在线=1]/[并机=2] | Device Parallel Status. Value 1 indicates single. Value 2 indicates parallel.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.48 | hwUPS2000GACommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Device communication status. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.49 | hwUPS2000GASlotNo | / | / | 0-Read_Only | 只读 | 0..6 | / | Device Slot No.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.50 | hwUPS2000GAPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..9 | 1..9 | Device Port No.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.51 | hwUPS2000GASoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | Device software version number. A string of characters.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.52 | hwUPS2000GAModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Device Modbus Address.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.53 | hwUPS2000GAMaintBreakerOn1 | / | / | 0-Read_Only | 只读 | 0..1 | / | UPS2000G Maintance Breaker On.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.54 | hwUPS2000GARedundancyNum | / | / | 0-Read_Only | 只读 | 0..3 | / | UPS2000G Redundancy Number.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.55 | hwUPS2000GAStartup | / | / | 1-Read_Write | 读写 | yes(1) | / | Startup the Device. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.56 | hwUPS2000GAShutdown | / | / | 1-Read_Write | 读写 | yes(1) | / | Shutdown the Device. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.100 | hwUPS2000GARunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of config table UPS2000-A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2 | hwUPS2000GAConfigTable | / | / |  |  | / | / | Running table of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.1 | hwUPS2000GAConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.2 | hwUPS2000GADischargeTestTimeInterval | Scheduled shallow discharge test interval | 定时浅放电测试间隔 | 1-Read_Write | 读写 | 30..90 | 30..90 | Discharge Test Time Interval of the device running table for the UPS2000. SigUnitInfo:days
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.3 | hwUPS2000GADischargeTestRatio | Discharge percentage | 浅放电百分比 | 1-Read_Write | 读写 | 10..50 | 10..50 | Discharge Test Ratio of the device running table for the UPS2000. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.4 | hwUPS2000GADischargeTestStart | Discharge test | 浅放电测试 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Discharge Test Start of the device running table for the UPS2000. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.5 | hwUPS2000GADischargeTestStop | Stop test | 结束测试 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Discharge Test Stop of the device running table for the UPS2000. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.6 | hwUPS2000GABatteryToEqualizedCharge | Battery conversion from manual charging to equalized charging | 电池手动转均充 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Battery To Equalized Charge of the device running table for the UPS2000. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.7 | hwUPS2000GABatteryToFloatCharge | Battery conversion from manual charging to floating charging | 电池手动转浮充 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Battery To Float Charge of the device running table for the UPS2000. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.8 | hwUPS2000GADischargeTestRemind | Scheduled shallow discharge test | 定时浅放电测试 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Discharge Test Remind of the device running table for the UPS2000. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.9 | hwUPS2000LiBattNumber | Li battery number | 锂电池数量 | 1-Read_Write | 读写 | 0..20 | 0..20 | Li battery number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.100 | hwUPS2000GAConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3 | hwUPS2000Running3Table | / | / |  |  | / | / | The running table of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.1 | hwUPS2000Running3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.2 | hwUPS2000FanLife | Fan life | 风扇寿命 | 0-Read_Only | 只读 | 0..100 | 0..100 | Fan life of the device config table for the UPS2000.SigUnitInfo:year.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.3 | hwUPS2000BusCapaLife | Bus Capa. Life | 母线电容寿命 | 0-Read_Only | 只读 | 0..120 | 0..120 | Bus Capa. Life of the device config table for the UPS2000.SigUnitInfo:year.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.4 | hwUPS2000BatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.5 | hwUPS2000BatterySoh | Battery SOH | 电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery SOH of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.6 | hwUPS2000LiBattery1WorkStatus | Li battery 1 work status | 锂电池1工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 1 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.7 | hwUPS2000LiBattery2WorkStatus | Li battery 2 work status | 锂电池2工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 2 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.8 | hwUPS2000LiBattery3WorkStatus | Li battery 3 work status | 锂电池3工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 3 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.9 | hwUPS2000LiBattery4WorkStatus | Li battery 4 work status | 锂电池4工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 4 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.10 | hwUPS2000LiBattery5WorkStatus | Li battery 5 work status | 锂电池5工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 5 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.11 | hwUPS2000LiBattery6WorkStatus | Li battery 6 work status | 锂电池6工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 6 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.12 | hwUPS2000LiBattery7WorkStatus | Li battery 7 work status | 锂电池7工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 7 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.13 | hwUPS2000LiBattery8WorkStatus | Li battery 8 work status | 锂电池8工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 8 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.14 | hwUPS2000LiBattery9WorkStatus | Li battery 9 work status | 锂电池9工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 9 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.15 | hwUPS2000LiBattery10WorkStatus | Li battery 10 work status | 锂电池10工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 10 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.16 | hwUPS2000LiBattery11WorkStatus | Li battery 11 work status | 锂电池11工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 11 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.17 | hwUPS2000LiBattery12WorkStatus | Li battery 12 work status | 锂电池12工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 12 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.18 | hwUPS2000LiBattery13WorkStatus | Li battery 13 work status | 锂电池13工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 13 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.19 | hwUPS2000LiBattery14WorkStatus | Li battery 14 work status | 锂电池14工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 14 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.20 | hwUPS2000LiBattery15WorkStatus | Li battery 15 work status | 锂电池15工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 15 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.21 | hwUPS2000LiBattery16WorkStatus | Li battery 16 work status | 锂电池16工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 16 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.22 | hwUPS2000LiBattery17WorkStatus | Li battery 17 work status | 锂电池17工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 17 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.23 | hwUPS2000LiBattery18WorkStatus | Li battery 18 work status | 锂电池18工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 18 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.24 | hwUPS2000LiBattery19WorkStatus | Li battery 19 work status | 锂电池19工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 19 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.25 | hwUPS2000LiBattery20WorkStatus | Li battery 20 work status | 锂电池20工作状态 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), malfunction(6), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5]/[故障=6] | Li battery 20 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby Value 6 indicate malfunction
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.26 | hwUPS2000LiBattery1BatteryVoltage | Li battery 1 battery voltage | 锂电池1电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.27 | hwUPS2000LiBattery1BatteryCurrent | Li battery 1 battery current | 锂电池1电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 1 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.28 | hwUPS2000LiBattery1CapacityLeft | Li battery 1 capacity left | 锂电池1剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 1 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.29 | hwUPS2000LiBattery1OutputPower | Li battery 1 output power | 锂电池1输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.30 | hwUPS2000LiBattery1OperatingMode | Li battery 1 operating mode | 锂电池1工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 1 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.31 | hwUPS2000LiBattery1BatteryCapacity | Li battery 1 battery capacity | 锂电池1电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.32 | hwUPS2000LiBattery1PackVoltage | Li battery 1 pack voltage | 锂电池1电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.33 | hwUPS2000LiBattery1BatterySoh | Li battery 1 battery soh | 锂电池1电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 1 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.34 | hwUPS2000LiBattery1CellNumber | Li battery 1 cell number | 锂电池1电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 1 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.35 | hwUPS2000LiBattery2BatteryVoltage | Li battery 2 battery voltage | 锂电池2电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.36 | hwUPS2000LiBattery2BatteryCurrent | Li battery 2 battery current | 锂电池2电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 2 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.37 | hwUPS2000LiBattery2CapacityLeft | Li battery 2 capacity left | 锂电池2剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 2 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.38 | hwUPS2000LiBattery2OutputPower | Li battery 2 output power | 锂电池2输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.39 | hwUPS2000LiBattery2OperatingMode | Li battery 2 operating mode | 锂电池2工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 2 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.40 | hwUPS2000LiBattery2BatteryCapacity | Li battery 2 battery capacity | 锂电池2电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.41 | hwUPS2000LiBattery2PackVoltage | Li battery 2 pack voltage | 锂电池2电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.42 | hwUPS2000LiBattery2BatterySoh | Li battery 2 battery soh | 锂电池2电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 2 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.43 | hwUPS2000LiBattery2CellNumber | Li battery 2 cell number | 锂电池2电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 2 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.44 | hwUPS2000LiBattery3BatteryVoltage | Li battery 3 battery voltage | 锂电池3电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.45 | hwUPS2000LiBattery3BatteryCurrent | Li battery 3 battery current | 锂电池3电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 3 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.46 | hwUPS2000LiBattery3CapacityLeft | Li battery 3 capacity left | 锂电池3剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 3 battery capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.47 | hwUPS2000LiBattery3OutputPower | Li battery 3 output power | 锂电池3输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.48 | hwUPS2000LiBattery3OperatingMode | Li battery 3 operating mode | 锂电池3工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 3 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.49 | hwUPS2000LiBattery3BatteryCapacity | Li battery 3 battery capacity | 锂电池3电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.50 | hwUPS2000LiBattery3PackVoltage | Li battery 3 pack voltage | 锂电池3电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.51 | hwUPS2000LiBattery3BatterySoh | Li battery 3 battery soh | 锂电池3电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 3 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.52 | hwUPS2000LiBattery3CellNumber | Li battery 3 cell number | 锂电池3电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 3 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.53 | hwUPS2000LiBattery4BatteryVoltage | Li battery 4 battery voltage | 锂电池4电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.54 | hwUPS2000LiBattery4BatteryCurrent | Li battery 4 battery current | 锂电池4电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 4 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.55 | hwUPS2000LiBattery4CapacityLeft | Li battery 4 capacity left | 锂电池4剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 4 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.56 | hwUPS2000LiBattery4OutputPower | Li battery 4 output power | 锂电池4输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.57 | hwUPS2000LiBattery4OperatingMode | Li battery 4 operating mode | 锂电池4工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 4 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.58 | hwUPS2000LiBattery4BatteryCapacity | Li battery 4 battery capacity | 锂电池4电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.59 | hwUPS2000LiBattery4PackVoltage | Li battery 4 pack voltage | 锂电池4电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.60 | hwUPS2000LiBattery4BatterySoh | Li battery 4 battery soh | 锂电池4电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 4 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.61 | hwUPS2000LiBattery4CellNumber | Li battery 4 cell number | 锂电池4电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 4 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.62 | hwUPS2000LiBattery5BatteryVoltage | Li battery 5 battery voltage | 锂电池5电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.63 | hwUPS2000LiBattery5BatteryCurrent | Li battery 5 battery current | 锂电池5电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 5 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.64 | hwUPS2000LiBattery5CapacityLeft | Li battery 5 capacity left | 锂电池5剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 5 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.65 | hwUPS2000LiBattery5OutputPower | Li battery 5 output power | 锂电池5输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.66 | hwUPS2000LiBattery5OperatingMode | Li battery 5 operating mode | 锂电池5工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 5 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.67 | hwUPS2000LiBattery5BatteryCapacity | Li battery 5 battery capacity | 锂电池5电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.68 | hwUPS2000LiBattery5PackVoltage | Li battery 5 pack voltage | 锂电池5电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.69 | hwUPS2000LiBattery5BatterySoh | Li battery 5 battery soh | 锂电池5电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 5 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.70 | hwUPS2000LiBattery5CellNumber | Li battery 5 cell number | 锂电池5电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 5 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.71 | hwUPS2000LiBattery6BatteryVoltage | Li battery 6 battery voltage | 锂电池6电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.72 | hwUPS2000LiBattery6BatteryCurrent | Li battery 6 battery current | 锂电池6电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 6 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.73 | hwUPS2000LiBattery6CapacityLeft | Li battery 6 capacity left | 锂电池6剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 6 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.74 | hwUPS2000LiBattery6OutputPower | Li battery 6 output power | 锂电池6输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.75 | hwUPS2000LiBattery6OperatingMode | Li battery 6 operating mode | 锂电池6工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 6 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.76 | hwUPS2000LiBattery6BatteryCapacity | Li battery 6 battery capacity | 锂电池6电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.77 | hwUPS2000LiBattery6PackVoltage | Li battery 6 pack voltage | 锂电池6电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.78 | hwUPS2000LiBattery6BatterySoh | Li battery 6 battery soh | 锂电池6电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 6 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.79 | hwUPS2000LiBattery6CellNumber | Li battery 6 cell number | 锂电池6电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 6 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.80 | hwUPS2000LiBattery7BatteryVoltage | Li battery 7 battery voltage | 锂电池7电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.81 | hwUPS2000LiBattery7BatteryCurrent | Li battery 7 battery current | 锂电池7电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 7 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.82 | hwUPS2000LiBattery7CapacityLeft | Li battery 7 capacity left | 锂电池7剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 7 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.83 | hwUPS2000LiBattery7OutputPower | Li battery 7 output power | 锂电池7输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.84 | hwUPS2000LiBattery7OperatingMode | Li battery 7 operating mode | 锂电池7工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 7 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.85 | hwUPS2000LiBattery7BatteryCapacity | Li battery 7 battery capacity | 锂电池7电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.86 | hwUPS2000LiBattery7PackVoltage | Li battery 7 pack voltage | 锂电池7电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.87 | hwUPS2000LiBattery7BatterySoh | Li battery 7 battery soh | 锂电池7电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 7 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.88 | hwUPS2000LiBattery7CellNumber | Li battery 7 cell number | 锂电池7电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 7 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.89 | hwUPS2000LiBattery8BatteryVoltage | Li battery 8 battery voltage | 锂电池8电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.90 | hwUPS2000LiBattery8BatteryCurrent | Li battery 8 battery current | 锂电池8电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 8 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.91 | hwUPS2000LiBattery8CapacityLeft | Li battery 8 capacity left | 锂电池8剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 8 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.92 | hwUPS2000LiBattery8OutputPower | Li battery 8 output power | 锂电池8输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.93 | hwUPS2000LiBattery8OperatingMode | Li battery 8 operating mode | 锂电池8工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 8 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.94 | hwUPS2000LiBattery8BatteryCapacity | Li battery 8 battery capacity | 锂电池8电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.95 | hwUPS2000LiBattery8PackVoltage | Li battery 8 pack voltage | 锂电池8电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.96 | hwUPS2000LiBattery8BatterySoh | Li battery 8 battery soh | 锂电池8电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 8 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.97 | hwUPS2000LiBattery8CellNumber | Li battery 8 cell number | 锂电池8电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 8 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.98 | hwUPS2000LiBattery9BatteryVoltage | Li battery 9 battery voltage | 锂电池9电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.99 | hwUPS2000LiBattery9BatteryCurrent | Li battery 9 battery current | 锂电池9电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 9 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.100 | hwUPS2000LiBattery9CapacityLeft | Li battery 9 capacity left | 锂电池9剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 9 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.101 | hwUPS2000LiBattery9OutputPower | Li battery 9 output power | 锂电池9输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.102 | hwUPS2000LiBattery9OperatingMode | Li battery 9 operating mode | 锂电池9工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 9 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.103 | hwUPS2000LiBattery9BatteryCapacity | Li battery 9 battery capacity | 锂电池9电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.104 | hwUPS2000LiBattery9PackVoltage | Li battery 9 pack voltage | 锂电池9电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.105 | hwUPS2000LiBattery9BatterySoh | Li battery 9 battery soh | 锂电池9电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 9 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.106 | hwUPS2000LiBattery9CellNumber | Li battery 9 cell number | 锂电池9电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 9 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.107 | hwUPS2000LiBattery10BatteryVoltage | Li battery 10 battery voltage | 锂电池10电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.108 | hwUPS2000LiBattery10BatteryCurrent | Li battery 10 battery current | 锂电池10电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 10 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.109 | hwUPS2000LiBattery10CapacityLeft | Li battery 10 capacity left | 锂电池10剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 10 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.110 | hwUPS2000LiBattery10OutputPower | Li battery 10 output power | 锂电池10输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.111 | hwUPS2000LiBattery10OperatingMode | Li battery 10 operating mode | 锂电池10工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 10 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.112 | hwUPS2000LiBattery10BatteryCapacity | Li battery 10 battery capacity | 锂电池10电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.113 | hwUPS2000LiBattery10PackVoltage | Li battery 10 pack voltage | 锂电池10电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.114 | hwUPS2000LiBattery10BatterySoh | Li battery 10 battery soh | 锂电池10电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 10 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.115 | hwUPS2000LiBattery10CellNumber | Li battery 10 cell number | 锂电池10电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 10 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.116 | hwUPS2000LiBattery11BatteryVoltage | Li battery 11 battery voltage | 锂电池11电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.117 | hwUPS2000LiBattery11BatteryCurrent | Li battery 11 battery current | 锂电池11电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 11 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.118 | hwUPS2000LiBattery11CapacityLeft | Li battery 11 capacity left | 锂电池11剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 11 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.119 | hwUPS2000LiBattery11OutputPower | Li battery 11 output power | 锂电池11输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.120 | hwUPS2000LiBattery11OperatingMode | Li battery 11 operating mode | 锂电池11工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 11 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.121 | hwUPS2000LiBattery11BatteryCapacity | Li battery 11 battery capacity | 锂电池11电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.122 | hwUPS2000LiBattery11PackVoltage | Li battery 11 pack voltage | 锂电池11电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.123 | hwUPS2000LiBattery11BatterySoh | Li battery 11 battery soh | 锂电池11电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 11 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.124 | hwUPS2000LiBattery11CellNumber | Li battery 11 cell number | 锂电池11电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 11 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.125 | hwUPS2000LiBattery12BatteryVoltage | Li battery 12 battery voltage | 锂电池12电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.126 | hwUPS2000LiBattery12BatteryCurrent | Li battery 12 battery current | 锂电池12电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 12 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.127 | hwUPS2000LiBattery12CapacityLeft | Li battery 12 capacity left | 锂电池12剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 12 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.128 | hwUPS2000LiBattery12OutputPower | Li battery 12 output power | 锂电池12输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.129 | hwUPS2000LiBattery12OperatingMode | Li battery 12 operating mode | 锂电池12工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 12 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.130 | hwUPS2000LiBattery12BatteryCapacity | Li battery 12 battery capacity | 锂电池12电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.131 | hwUPS2000LiBattery12PackVoltage | Li battery 12 pack voltage | 锂电池12电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.132 | hwUPS2000LiBattery12BatterySoh | Li battery 12 battery soh | 锂电池12电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 12 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.133 | hwUPS2000LiBattery12CellNumber | Li battery 12 cell number | 锂电池12电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 12 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.134 | hwUPS2000LiBattery13BatteryVoltage | Li battery 13 battery voltage | 锂电池13电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.135 | hwUPS2000LiBattery13BatteryCurrent | Li battery 13 battery current | 锂电池13电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 13 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.136 | hwUPS2000LiBattery13CapacityLeft | Li battery 13 capacity left | 锂电池13剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 13 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.137 | hwUPS2000LiBattery13OutputPower | Li battery 13 output power | 锂电池13输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.138 | hwUPS2000LiBattery13OperatingMode | Li battery 13 operating mode | 锂电池13工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 13 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.139 | hwUPS2000LiBattery13BatteryCapacity | Li battery 13 battery capacity | 锂电池13电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.140 | hwUPS2000LiBattery13PackVoltage | Li battery 13 pack voltage | 锂电池13电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.141 | hwUPS2000LiBattery13BatterySoh | Li battery 13 battery soh | 锂电池13电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 13 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.142 | hwUPS2000LiBattery13CellNumber | Li battery 13 cell number | 锂电池13电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 13 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.143 | hwUPS2000LiBattery14BatteryVoltage | Li battery 14 battery voltage | 锂电池14电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.144 | hwUPS2000LiBattery14BatteryCurrent | Li battery 14 battery current | 锂电池14电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 14 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.145 | hwUPS2000LiBattery14CapacityLeft | Li battery 14 capacity left | 锂电池14剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 14 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.146 | hwUPS2000LiBattery14OutputPower | Li battery 14 output power | 锂电池14输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.147 | hwUPS2000LiBattery14OperatingMode | Li battery 14 operating mode | 锂电池14工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 14 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.148 | hwUPS2000LiBattery14BatteryCapacity | Li battery 14 battery capacity | 锂电池14电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.149 | hwUPS2000LiBattery14PackVoltage | Li battery 14 pack voltage | 锂电池14电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.150 | hwUPS2000LiBattery14BatterySoh | Li battery 14 battery soh | 锂电池14电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 14 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.151 | hwUPS2000LiBattery14CellNumber | Li battery 14 cell number | 锂电池14电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 14 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.152 | hwUPS2000LiBattery15BatteryVoltage | Li battery 15 battery voltage | 锂电池15电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.153 | hwUPS2000LiBattery15BatteryCurrent | Li battery 15 battery current | 锂电池15电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 15 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.154 | hwUPS2000LiBattery15CapacityLeft | Li battery 15 capacity left | 锂电池15剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 15 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.155 | hwUPS2000LiBattery15OutputPower | Li battery 15 output power | 锂电池15输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.156 | hwUPS2000LiBattery15OperatingMode | Li battery 15 operating mode | 锂电池15工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 15 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.157 | hwUPS2000LiBattery15BatteryCapacity | Li battery 15 battery capacity | 锂电池15电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.158 | hwUPS2000LiBattery15PackVoltage | Li battery 15 pack voltage | 锂电池15电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.159 | hwUPS2000LiBattery15BatterySoh | Li battery 15 battery soh | 锂电池15电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 15 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.160 | hwUPS2000LiBattery15CellNumber | Li battery 15 cell number | 锂电池15电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 15 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.161 | hwUPS2000LiBattery16BatteryVoltage | Li battery 16 battery voltage | 锂电池16电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.162 | hwUPS2000LiBattery16BatteryCurrent | Li battery 16 battery current | 锂电池16电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 16 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.163 | hwUPS2000LiBattery16CapacityLeft | Li battery 16 capacity left | 锂电池16剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 16 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.164 | hwUPS2000LiBattery16OutputPower | Li battery 16 output power | 锂电池16输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.165 | hwUPS2000LiBattery16OperatingMode | Li battery 16 operating mode | 锂电池16工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 16 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.166 | hwUPS2000LiBattery16BatteryCapacity | Li battery 16 battery capacity | 锂电池16电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.167 | hwUPS2000LiBattery16PackVoltage | Li battery 16 pack voltage | 锂电池16电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.168 | hwUPS2000LiBattery16BatterySoh | Li battery 16 battery soh | 锂电池16电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 16 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.169 | hwUPS2000LiBattery16CellNumber | Li battery 16 cell number | 锂电池16电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 16 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.170 | hwUPS2000LiBattery17BatteryVoltage | Li battery 17 battery voltage | 锂电池17电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.171 | hwUPS2000LiBattery17BatteryCurrent | Li battery 17 battery current | 锂电池17电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 17 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.172 | hwUPS2000LiBattery17CapacityLeft | Li battery 17 capacity left | 锂电池17剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 17 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.173 | hwUPS2000LiBattery17OutputPower | Li battery 17 output power | 锂电池17输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.174 | hwUPS2000LiBattery17OperatingMode | Li battery 17 operating mode | 锂电池17工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 17 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.175 | hwUPS2000LiBattery17BatteryCapacity | Li battery 17 battery capacity | 锂电池17电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.176 | hwUPS2000LiBattery17PackVoltage | Li battery 17 pack voltage | 锂电池17电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.177 | hwUPS2000LiBattery17BatterySoh | Li battery 17 battery soh | 锂电池17电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 17 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.178 | hwUPS2000LiBattery17CellNumber | Li battery 17 cell number | 锂电池17电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 17 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.179 | hwUPS2000LiBattery18BatteryVoltage | Li battery 18 battery voltage | 锂电池18电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.180 | hwUPS2000LiBattery18BatteryCurrent | Li battery 18 battery current | 锂电池18电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 18 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.181 | hwUPS2000LiBattery18CapacityLeft | Li battery 18 capacity left | 锂电池18剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 18 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.182 | hwUPS2000LiBattery18OutputPower | Li battery 18 output power | 锂电池18输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.183 | hwUPS2000LiBattery18OperatingMode | Li battery 18 operating mode | 锂电池18工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 18 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.184 | hwUPS2000LiBattery18BatteryCapacity | Li battery 18 battery capacity | 锂电池18电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.185 | hwUPS2000LiBattery18PackVoltage | Li battery 18 pack voltage | 锂电池18电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.186 | hwUPS2000LiBattery18BatterySoh | Li battery 18 battery soh | 锂电池18电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 18 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.187 | hwUPS2000LiBattery18CellNumber | Li battery 18 cell number | 锂电池18电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 18 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.188 | hwUPS2000LiBattery19BatteryVoltage | Li battery 19 battery voltage | 锂电池19电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.189 | hwUPS2000LiBattery19BatteryCurrent | Li battery 19 battery current | 锂电池19电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 19 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.190 | hwUPS2000LiBattery19CapacityLeft | Li battery 19 capacity left | 锂电池19剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 19 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.191 | hwUPS2000LiBattery19OutputPower | Li battery 19 output power | 锂电池19输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.192 | hwUPS2000LiBattery19OperatingMode | Li battery 19 operating mode | 锂电池19工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 19 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.193 | hwUPS2000LiBattery19BatteryCapacity | Li battery 19 battery capacity | 锂电池19电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.194 | hwUPS2000LiBattery19PackVoltage | Li battery 19 pack voltage | 锂电池19电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.195 | hwUPS2000LiBattery19BatterySoh | Li battery 19 battery soh | 锂电池19电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 19 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.196 | hwUPS2000LiBattery19CellNumber | Li battery 19 cell number | 锂电池19电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 19 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.197 | hwUPS2000LiBattery20BatteryVoltage | Li battery 20 battery voltage | 锂电池20电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.198 | hwUPS2000LiBattery20BatteryCurrent | Li battery 20 battery current | 锂电池20电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 20 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.199 | hwUPS2000LiBattery20CapacityLeft | Li battery 20 capacity left | 锂电池20剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 20 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.200 | hwUPS2000LiBattery20OutputPower | Li battery 20 output power | 锂电池20输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.201 | hwUPS2000LiBattery20OperatingMode | Li battery 20 operating mode | 锂电池20工作模式 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 20 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.202 | hwUPS2000LiBattery20BatteryCapacity | Li battery 20 battery capacity | 锂电池20电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.203 | hwUPS2000LiBattery20PackVoltage | Li battery 20 pack voltage | 锂电池20电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.204 | hwUPS2000LiBattery20BatterySoh | Li battery 20 battery soh | 锂电池20电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 20 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.205 | hwUPS2000LiBattery20CellNumber | Li battery 20 cell number | 锂电池20电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 20 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.206 | hwUPS2000LiBattery1MaximumCellTemperature | Li battery 1 maximum cell temperature | 锂电池1电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 1 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.207 | hwUPS2000LiBattery1MinimumCellTemperature | Li battery 1 minimum cell temperature | 锂电池1电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 1 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.208 | hwUPS2000LiBattery1MaximumCellVoltage | Li battery 1 maximum cell voltage | 锂电池1电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.209 | hwUPS2000LiBattery1MinimumCellVoltage | Li battery 1 minimum cell voltage | 锂电池1电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.210 | hwUPS2000LiBattery2MaximumCellTemperature | Li battery 2 maximum cell temperature | 锂电池2电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 2 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.211 | hwUPS2000LiBattery2MinimumCellTemperature | Li battery 2 minimum cell temperature | 锂电池2电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 2 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.212 | hwUPS2000LiBattery2MaximumCellVoltage | Li battery 2 maximum cell voltage | 锂电池2电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.213 | hwUPS2000LiBattery2MinimumCellVoltage | Li battery 2 minimum cell voltage | 锂电池2电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.214 | hwUPS2000LiBattery3MaximumCellTemperature | Li battery 3 maximum cell temperature | 锂电池3电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 3 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.215 | hwUPS2000LiBattery3MinimumCellTemperature | Li battery 3 minimum cell temperature | 锂电池3电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 3 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.216 | hwUPS2000LiBattery3MaximumCellVoltage | Li battery 3 maximum cell voltage | 锂电池3电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.217 | hwUPS2000LiBattery3MinimumCellVoltage | Li battery 3 minimum cell voltage | 锂电池3电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.218 | hwUPS2000LiBattery4MaximumCellTemperature | Li battery 4 maximum cell temperature | 锂电池4电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 4 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.219 | hwUPS2000LiBattery4MinimumCellTemperature | Li battery 4 minimum cell temperature | 锂电池4电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 4 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.220 | hwUPS2000LiBattery4MaximumCellVoltage | Li battery 4 maximum cell voltage | 锂电池4电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.221 | hwUPS2000LiBattery4MinimumCellVoltage | Li battery 4 minimum cell voltage | 锂电池4电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.222 | hwUPS2000LiBattery5MaximumCellTemperature | Li battery 5 maximum cell temperature | 锂电池5电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 5 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.223 | hwUPS2000LiBattery5MinimumCellTemperature | Li battery 5 minimum cell temperature | 锂电池5电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 5 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.224 | hwUPS2000LiBattery5MaximumCellVoltage | Li battery 5 maximum cell voltage | 锂电池5电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.225 | hwUPS2000LiBattery5MinimumCellVoltage | Li battery 5 minimum cell voltage | 锂电池5电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.226 | hwUPS2000LiBattery6MaximumCellTemperature | Li battery 6 maximum cell temperature | 锂电池6电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 6 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.227 | hwUPS2000LiBattery6MinimumCellTemperature | Li battery 6 minimum cell temperature | 锂电池6电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 6 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.228 | hwUPS2000LiBattery6MaximumCellVoltage | Li battery 6 maximum cell voltage | 锂电池6电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.229 | hwUPS2000LiBattery6MinimumCellVoltage | Li battery 6 minimum cell voltage | 锂电池6电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.230 | hwUPS2000LiBattery7MaximumCellTemperature | Li battery 7 maximum cell temperature | 锂电池7电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 7 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.231 | hwUPS2000LiBattery7MinimumCellTemperature | Li battery 7 minimum cell temperature | 锂电池7电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 7 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.232 | hwUPS2000LiBattery7MaximumCellVoltage | Li battery 7 maximum cell voltage | 锂电池7电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.233 | hwUPS2000LiBattery7MinimumCellVoltage | Li battery 7 minimum cell voltage | 锂电池7电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.234 | hwUPS2000LiBattery8MaximumCellTemperature | Li battery 8 maximum cell temperature | 锂电池8电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 8 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.235 | hwUPS2000LiBattery8MinimumCellTemperature | Li battery 8 minimum cell temperature | 锂电池8电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 8 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.236 | hwUPS2000LiBattery8MaximumCellVoltage | Li battery 8 maximum cell voltage | 锂电池8电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.237 | hwUPS2000LiBattery8MinimumCellVoltage | Li battery 8 minimum cell voltage | 锂电池8电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.238 | hwUPS2000LiBattery9MaximumCellTemperature | Li battery 9 maximum cell temperature | 锂电池9电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 9 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.239 | hwUPS2000LiBattery9MinimumCellTemperature | Li battery 9 minimum cell temperature | 锂电池9电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 9 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.240 | hwUPS2000LiBattery9MaximumCellVoltage | Li battery 9 maximum cell voltage | 锂电池9电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.241 | hwUPS2000LiBattery9MinimumCellVoltage | Li battery 9 minimum cell voltage | 锂电池9电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.242 | hwUPS2000LiBattery10MaximumCellTemperature | Li battery 10 maximum cell temperature | 锂电池10电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 10 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.243 | hwUPS2000LiBattery10MinimumCellTemperature | Li battery 10 minimum cell temperature | 锂电池10电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 10 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.244 | hwUPS2000LiBattery10MaximumCellVoltage | Li battery 10 maximum cell voltage | 锂电池10电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.245 | hwUPS2000LiBattery10MinimumCellVoltage | Li battery 10 minimum cell voltage | 锂电池10电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.246 | hwUPS2000LiBattery11MaximumCellTemperature | Li battery 11 maximum cell temperature | 锂电池11电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 11 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.247 | hwUPS2000LiBattery11MinimumCellTemperature | Li battery 11 minimum cell temperature | 锂电池11电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 11 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.248 | hwUPS2000LiBattery11MaximumCellVoltage | Li battery 11 maximum cell voltage | 锂电池11电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.249 | hwUPS2000LiBattery11MinimumCellVoltage | Li battery 11 minimum cell voltage | 锂电池11电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.250 | hwUPS2000LiBattery12MaximumCellTemperature | Li battery 12 maximum cell temperature | 锂电池12电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 12 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.251 | hwUPS2000LiBattery12MinimumCellTemperature | Li battery 12 minimum cell temperature | 锂电池12电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 12 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.252 | hwUPS2000LiBattery12MaximumCellVoltage | Li battery 12 maximum cell voltage | 锂电池12电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.253 | hwUPS2000LiBattery12MinimumCellVoltage | Li battery 12 minimum cell voltage | 锂电池12电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.254 | hwUPS2000LiBattery13MaximumCellTemperature | Li battery 13 maximum cell temperature | 锂电池13电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 13 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.255 | hwUPS2000LiBattery13MinimumCellTemperature | Li battery 13 minimum cell temperature | 锂电池13电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 13 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.256 | hwUPS2000LiBattery13MaximumCellVoltage | Li battery 13 maximum cell voltage | 锂电池13电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.257 | hwUPS2000LiBattery13MinimumCellVoltage | Li battery 13 minimum cell voltage | 锂电池13电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.258 | hwUPS2000LiBattery14MaximumCellTemperature | Li battery 14 maximum cell temperature | 锂电池14电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 14 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.259 | hwUPS2000LiBattery14MinimumCellTemperature | Li battery 14 minimum cell temperature | 锂电池14电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 14 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.260 | hwUPS2000LiBattery14MaximumCellVoltage | Li battery 14 maximum cell voltage | 锂电池14电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.261 | hwUPS2000LiBattery14MinimumCellVoltage | Li battery 14 minimum cell voltage | 锂电池14电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.262 | hwUPS2000LiBattery15MaximumCellTemperature | Li battery 15 maximum cell temperature | 锂电池15电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 15 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.263 | hwUPS2000LiBattery15MinimumCellTemperature | Li battery 15 minimum cell temperature | 锂电池15电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 15 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.264 | hwUPS2000LiBattery15MaximumCellVoltage | Li battery 15 maximum cell voltage | 锂电池15电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.265 | hwUPS2000LiBattery15MinimumCellVoltage | Li battery 15 minimum cell voltage | 锂电池15电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.266 | hwUPS2000LiBattery16MaximumCellTemperature | Li battery 16 maximum cell temperature | 锂电池16电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 16 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.267 | hwUPS2000LiBattery16MinimumCellTemperature | Li battery 16 minimum cell temperature | 锂电池16电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 16 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.268 | hwUPS2000LiBattery16MaximumCellVoltage | Li battery 16 maximum cell voltage | 锂电池16电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.269 | hwUPS2000LiBattery16MinimumCellVoltage | Li battery 16 minimum cell voltage | 锂电池16电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.270 | hwUPS2000LiBattery17MaximumCellTemperature | Li battery 17 maximum cell temperature | 锂电池17电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 17 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.271 | hwUPS2000LiBattery17MinimumCellTemperature | Li battery 17 minimum cell temperature | 锂电池17电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 17 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.272 | hwUPS2000LiBattery17MaximumCellVoltage | Li battery 17 maximum cell voltage | 锂电池17电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.273 | hwUPS2000LiBattery17MinimumCellVoltage | Li battery 17 minimum cell voltage | 锂电池17电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.274 | hwUPS2000LiBattery18MaximumCellTemperature | Li battery 18 maximum cell temperature | 锂电池18电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 18 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.275 | hwUPS2000LiBattery18MinimumCellTemperature | Li battery 18 minimum cell temperature | 锂电池18电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 18 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.276 | hwUPS2000LiBattery18MaximumCellVoltage | Li battery 18 maximum cell voltage | 锂电池18电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.277 | hwUPS2000LiBattery18MinimumCellVoltage | Li battery 18 minimum cell voltage | 锂电池18电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.278 | hwUPS2000LiBattery19MaximumCellTemperature | Li battery 19 maximum cell temperature | 锂电池19电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 19 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.279 | hwUPS2000LiBattery19MinimumCellTemperature | Li battery 19 minimum cell temperature | 锂电池19电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 19 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.280 | hwUPS2000LiBattery19MaximumCellVoltage | Li battery 19 maximum cell voltage | 锂电池19电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.281 | hwUPS2000LiBattery19MinimumCellVoltage | Li battery 19 minimum cell voltage | 锂电池19电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.282 | hwUPS2000LiBattery20MaximumCellTemperature | Li battery 20 maximum cell temperature | 锂电池20电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 20 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.283 | hwUPS2000LiBattery20MinimumCellTemperature | Li battery 20 minimum cell temperature | 锂电池20电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 20 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.284 | hwUPS2000LiBattery20MaximumCellVoltage | Li battery 20 maximum cell voltage | 锂电池20电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.285 | hwUPS2000LiBattery20MinimumCellVoltage | Li battery 20 minimum cell voltage | 锂电池20电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.286 | hwUPS2000BatteryType | Battery type | 电池类型 | 0-Read_Only | 只读 | vrlabatt(1), lithiumbatt(2), unknown(255) | [铅酸电池=1]/[锂电池=2] | Battery type of the device config table for the UPS2000. Value 1 indicate vrla batt. Value 2 indicate lithium batt.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.287 | hwUPS2000MaximumCellTemperature | Maximum cell temperature | 电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.288 | hwUPS2000MinimumCellTemperature | Minimum cell temperature | 电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.289 | hwUPS2000MaximumCellVoltage | Maximum cell voltage | 电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.290 | hwUPS2000MinimumCellVoltage | Minimum cell voltage | 电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.291 | hwUPS2000InputCurrent | Input current | 输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.292 | hwUPS2000APhaseInputCurrent | Input phase current (A) | A相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | A phase input current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.293 | hwUPS2000BPhaseInputCurrent | Input phase current (B) | B相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | B phase input current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.294 | hwUPS2000CPhaseInputCurrent | Input phase current (C) | C相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | C phase input current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.295 | hwUPS2000LiBattery1PackCurrent | Li battery 1 pack current | 锂电池1电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 1 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.296 | hwUPS2000LiBattery2PackCurrent | Li battery 2 pack current | 锂电池2电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 2 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.297 | hwUPS2000LiBattery3PackCurrent | Li battery 3 pack current | 锂电池3电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 3 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.298 | hwUPS2000LiBattery4PackCurrent | Li battery 4 pack current | 锂电池4电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 4 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.299 | hwUPS2000LiBattery5PackCurrent | Li battery 5 pack current | 锂电池5电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 5 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.300 | hwUPS2000Running3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.10 | hwUPS2000GASupportedDeviceModel | / | / | 0-Read_Only | 只读 | / | / | The UPS2000 supports the following models: UPS2000G-A; UPS2000-H;
1.3.6.1.4.1.2011.6.178.1.1.5.1.4 | hwUPS2000RunningAndConfig4Table | / | / |  |  | / | / | The config table of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.1 | hwUPS2000RunningAndConfig4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.2 | hwUPS2000LiBattery6PackCurrent | Li battery 6 pack current | 锂电池6电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 6 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.3 | hwUPS2000LiBattery7PackCurrent | Li battery 7 pack current | 锂电池7电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 7 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.4 | hwUPS2000LiBattery8PackCurrent | Li battery 8 pack current | 锂电池8电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 8 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.5 | hwUPS2000LiBattery9PackCurrent | Li battery 9 pack current | 锂电池9电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 9 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.6 | hwUPS2000LiBattery10PackCurrent | Li battery 10 pack current | 锂电池10电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 10 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.7 | hwUPS2000LiBattery11PackCurrent | Li battery 11 pack current | 锂电池11电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 11 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.8 | hwUPS2000LiBattery12PackCurrent | Li battery 12 pack current | 锂电池12电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 12 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.9 | hwUPS2000LiBattery13PackCurrent | Li battery 13 pack current | 锂电池13电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 13 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.10 | hwUPS2000LiBattery14PackCurrent | Li battery 14 pack current | 锂电池14电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 14 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.11 | hwUPS2000LiBattery15PackCurrent | Li battery 15 pack current | 锂电池15电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 15 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.12 | hwUPS2000LiBattery16PackCurrent | Li battery 16 pack current | 锂电池16电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 16 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.13 | hwUPS2000LiBattery17PackCurrent | Li battery 17 pack current | 锂电池17电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 17 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.14 | hwUPS2000LiBattery18PackCurrent | Li battery 18 pack current | 锂电池18电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 18 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.15 | hwUPS2000LiBattery19PackCurrent | Li battery 19 pack current | 锂电池19电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 19 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.16 | hwUPS2000LiBattery20PackCurrent | Li battery 20 pack current | 锂电池20电芯包电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 20 pack current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.17 | hwUPS2000GroupCapacityTest | Group capacity test | 分组核对性容量测试 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Group capacity test of the device config table for the UPS2000. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.18 | hwUPS2000ScheduledGroupCapacityTest | Scheduled group capacity test | 定时分组核对性容量测试 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Scheduled group capacity test of the device config table for the UPS2000. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.19 | hwUPS2000ScheduledGroupCapacityTestInterval | Scheduled group capacity test interval | 定时分组核对性容量测试间隔 | 1-Read_Write | 读写 | 30..90 | 30..90 | Scheduled group capacity test interval of the device config table for the UPS2000.SigUnitInfo:days.
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.20 | hwUPS2000SingleUpsEco | Single UPS ECO | 单机ECO | 0-Read_Only | 只读 | disable(1), enabled(2), unknown(255) | [禁止=1]/[允许=2] | Single UPS ECO of the device config table for the UPS2000. Value 1 indicate disable Value 2 indicate enabled
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.21 | hwUPS2000CapacityTest | Capacity test | 核对性容量测试 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Capacity test of the device config table for the UPS2000. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.5.1.4.1.300 | hwUPS2000RunningAndConfig4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS2000.

## UPS5000
UPS5000
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.3 | UPS5000E | UPS5000 | UPS5000 | / | / | / | / | The UPS5000E Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1 | hwUPS5000ERunning1Table | / | / |  |  | / | / | The running and config table of UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.1 | hwUPS5000ERunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.2 | hwUPS5000ECommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Comm Status of the UPS5000E. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.3 | hwUPS5000EPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The Port No of the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.4 | hwUPS5000ESoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | The Software Version of the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.5 | hwUPS5000EModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Modbus Address of the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.6 | hwUPS5000EESN | ESN | ESN | 0-Read_Only | 只读 | 0..20 | 0..20 | The ESN of the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.7 | hwUPS5000ESystemCapacity | System capacity | 机型容量 | 0-Read_Only | 只读 | 20..3000 | 20..3000 | The SystemCapacity of the UPS5000E. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.8 | hwUPS5000EPowerMode | UPS power status | UPS供电状态 | 0-Read_Only | 只读 | noPowerSupplied(1), bypassMode(2), normalMode(3), batteryMode(4), sourceShareMode(5), mainsECOMode(6), batteryECOMode(7), unknown(255) | [均不供电=1]/[旁路供电=2]/[主路逆变供电=3]/[电池逆变供电=4]/[联合供电=5]/[市电ECO=6]/[电池ECO=7] | The Power Mode of the UPS5000E. Value 1 indicates noPowerSupplied. Value 2 indicates bypassMode. Value 3 indicates normalMode. Value 4 indicates batteryMode. Value 5 indicates sourceShareMode. Value 6 indicates Mains ECO mode. Value 7 indicates Battery ECO mode.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.9 | hwUPS5000ERunningStatus | UPS operating status | UPS运行状态 | 0-Read_Only | 只读 | single(1), parallel(2), singleECO(3), parallelECO(4), selfLoadMode(5), converterMode(6), unknown(255) | [单机=1]/[并机=2]/[单机ECO=3]/[并机ECO=4]/[自老化模式=5]/[变频器模式=6] | The Running Status of the UPS5000E. Value 1 indicates single. Value 2 indicates parallel. Value 3 indicates singleECO. Value 4 indicates parallelECO. Value 5 indicates self-loadMode. Value 6 indicates converterMode.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.10 | hwUPS5000EBatteryStatus | Battery operating status | 电池运行状态 | 0-Read_Only | 只读 | notConnected(1), nonChargingNonDischarge(2), hibernation(3), floatCharging(4), equalizedCharging(5), discharging(6), unknown(255) | [未接入=1]/[非充非放=2]/[休眠=3]/[浮充=4]/[均充=5]/[放电=6] | The Battery Status of the UPS5000E. Value 1 indicates notConnected. Value 2 indicates Non-charging Non-discharge. Value 3 indicates hibernation. Value 4 indicates floatCharging. Value 5 indicates equalizedCharging. Value 6 indicates discharging.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.11 | hwUPS5000EPhAInputVolt | Phase A input voltage | A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Ph A Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.12 | hwUPS5000EPhBInputVolt | Phase B input voltage | B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Ph B Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.13 | hwUPS5000EPhCInputVolt | Phase C input voltage | C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Ph C Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.14 | hwUPS5000EABInputLineVoltage | AB input line voltage | AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The AB Input Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.15 | hwUPS5000EBCInputLineVoltage | BC input line voltage | BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The BC Input Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.16 | hwUPS5000ECAInputLineVoltage | CA input line voltage | CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The CA Input Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.17 | hwUPS5000EPhAInputCur | Phase A input current | A相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Ph A Input Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.18 | hwUPS5000EPhBInputCur | Phase B input current | B相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Ph B Input Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.19 | hwUPS5000EPhCInputCur | Phase C input current | C相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Ph C Input Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.20 | hwUPS5000EInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Input Frequency of the UPS5000E. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.21 | hwUPS5000EPhaseAInputPowerFactor | Phase A input power factor | A相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Phase A Input Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.22 | hwUPS5000EPhaseBInputPowerFactor | Phase B input power factor | B相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Phase B Input Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.23 | hwUPS5000EPhaseCInputPowerFactor | Phase C input power factor | C相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Phase C Input Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.26 | hwUPS5000EBPMPhAInputVolt | BPM ph. A input volt. | A相旁路输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The BPM Ph A Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.27 | hwUPS5000EBPMPhBInputVolt | BPM ph. B input volt. | B相旁路输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The BPM Ph B Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.28 | hwUPS5000EBPMPhCInputVolt | BPM ph. C input volt. | C相旁路输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The BPM Ph C Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.29 | hwUPS5000EBPMABLineVoltage | BPM AB line voltage | 旁路AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The BPM AB Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.30 | hwUPS5000EBPMBCLineVoltage | BPM BC line voltage | 旁路BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The BPM BC Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.31 | hwUPS5000EBPMCALineVoltage | BPM CA line voltage | 旁路CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The BPM CA Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.32 | hwUPS5000EBPMInputFrequency | BPM input frequency | 旁路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The BPM Input Frequency of the UPS5000E. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.33 | hwUPS5000EAmbientTemperature | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The Ambient Temperature of the UPS5000E. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.34 | hwUPS5000EAmbientHumid | Ambient humidity | 环境湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Ambient Humid of the UPS5000E. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.35 | hwUPS5000ERackPhAOutputVolt | Ph. A output volt. | A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Rack Ph A Output Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.36 | hwUPS5000ERackPhBOutputVolt | Ph. B output volt. | B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Rack Ph B Output Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.37 | hwUPS5000ERackPhCOutputVolt | Ph. C output volt. | C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Rack Ph C Output Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.38 | hwUPS5000ERackABOutputLineVolt | Rack AB output line voltage | 机架AB输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The Rack AB Output Line Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.39 | hwUPS5000ERackBCOutputLineVolt | Rack BC output line voltage | 机架BC输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The Rack BC Output Line Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.40 | hwUPS5000ERackCAOutputLineVolt | Rack CA output line voltage | 机架CA输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The Rack CA Output Line Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.41 | hwUPS5000ERackPhAOutputCur | Ph. A output cur. | A相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Rack Ph A Output Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.42 | hwUPS5000ERackPhBOutputCur | Ph. B output cur. | B相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Rack Ph B Output Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.43 | hwUPS5000ERackPhCOutputCur | Ph. C output cur. | C相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Rack Ph C Output Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.44 | hwUPS5000ERackOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Rack Output Frequency of the UPS5000E. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.45 | hwUPS5000ERackPhAOutputActivePower | Ph. A output active power | A相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph A Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.46 | hwUPS5000ERackPhBOutputActivePower | Ph. B output active power | B相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph B Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.47 | hwUPS5000ERackPhCOutputActivePower | Ph. C output active power | C相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph C Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.48 | hwUPS5000ERackPhAOutputAppearancePower | Ph. A output apparent power | A相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph A Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.49 | hwUPS5000ERackPhBOutputAppearancePower | Ph. B output apparent power | B相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph B Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.50 | hwUPS5000ERackPhCOutputAppearancePower | Ph. C output apparent power | C相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph C Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.51 | hwUPS5000ERackPhAOutputReactivePower | Rack phase A output reactive power | 机架A相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph A Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.52 | hwUPS5000ERackPhBOutputReactivePower | Rack phase B output reactive power | 机架B相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph B Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.53 | hwUPS5000ERackPhCOutputReactivePower | Rack phase C output reactive power | 机架C相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph C Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.54 | hwUPS5000ERackPhAOutputPowerFactor | Ph. A output power factor | A相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Rack Ph A Output Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.55 | hwUPS5000ERackPhBOutputPowerFactor | Ph. B output power factor | B相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Rack Ph B Output Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.56 | hwUPS5000ERackPhCOutputPowerFactor | Ph. C output power factor | C相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Rack Ph C Output Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.57 | hwUPS5000ERackPhAOutputloadRatio | Ph. A output load ratio | A相输出负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The Rack Ph A Output load Ratio of the UPS5000E. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.58 | hwUPS5000ERackPhBOutputloadRatio | Ph. B output load ratio | B相输出负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The Rack Ph B Output load Ratio of the UPS5000E. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.59 | hwUPS5000ERackPhCOutputloadRatio | Ph. C output load ratio | C相输出负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The Rack Ph C Output load Ratio of the UPS5000E. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.60 | hwUPS5000ERackPhAOutputCrestRatio | Rack phase A output curr. crest ratio | 机架A相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Rack Ph A Output Crest Ratio of the UPS5000E. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.61 | hwUPS5000ERackPhBOutputCrestRatio | Rack phase B output curr. crest ratio | 机架B相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Rack Ph B Output Crest Ratio of the UPS5000E. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.62 | hwUPS5000ERackPhCOutputCrestRatio | Rack phase C output curr. crest ratio | 机架C相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Rack Ph C Output Crest Ratio of the UPS5000E. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.63 | hwUPS5000ESysPhAOutputActivePower | System phase A output active power | 系统A相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph A Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.64 | hwUPS5000ESysPhBOutputActivePower | System phase B output active power | 系统B相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph B Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.65 | hwUPS5000ESysPhCOutputActivePower | System phase C output active power | 系统C相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph C Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.66 | hwUPS5000ESysPhAOutputAppearancePower | System phase A output apparent power | 系统A相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph A Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.67 | hwUPS5000ESysPhBOutputAppearancePower | System phase B output apparent power | 系统B相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph B Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.68 | hwUPS5000ESysPhCOutputAppearancePower | System phase C output apparent power | 系统C相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph C Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.69 | hwUPS5000ESysPhAOutputReactivePower | System phase A output reactive power | 系统A相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph A Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.70 | hwUPS5000ESysPhBOutputReactivePower | System phase B output reactive power | 系统B相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph B Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.71 | hwUPS5000ESysPhCOutputReactivePower | System phase C output reactive power | 系统C相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph C Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.72 | hwUPS5000EPosBatteryVoltage | Positive battery voltage | 正组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Pos Battery Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.73 | hwUPS5000ENegBatteryVoltage | Negative battery voltage | 负组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Neg Battery Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.74 | hwUPS5000EPosBatteryCurrent | Positive battery current | 正组电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | The Pos Battery Current of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.75 | hwUPS5000ENegBatteryCurrent | Negative battery current | 负组电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | The Neg Battery Current of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.76 | hwUPS5000EBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -200..800 | -200..800 | The Battery Temperature of the UPS5000E. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.77 | hwUPS5000EBackupTime | Backup time | 电池备电时间 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | The Backup Time of the UPS5000E. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.78 | hwUPS5000EBatteryRemainingCapacity | Battery remaining capacity | 电池剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Battery Remaining capacity of the UPS5000E. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.79 | hwUPS5000EDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The name of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.80 | hwUPS5000EBackupTimeNew | Battery backup time | 电池备电时间 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Backup time of the device config table for the UPS5000E.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.81 | hwUPS5000EMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.100 | hwUPS5000ERunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2 | hwUPS5000ERunning2Table | / | / |  |  | / | / | The running and config table of UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.1 | hwUPS5000ERunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.2 | hwUPS5000EElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | The elabel of the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.3 | hwUPS5000EOnlinemodulenumber | Number of online modules | 在线模块个数 | 0-Read_Only | 只读 | 0..20 | 0..20 | The Online module number of UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.4 | hwUPS5000EModuleonlinestatus | Module online status | 模块在位状态 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Module online status of UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.5 | hwUPS5000EEnergyflow1 | Energy flow diagram 1 | 能量流图1 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow 1: value 1 indicates hollow. value 2 indicates solid. value 3 indicates right flow. value 4 indicates none.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.6 | hwUPS5000EEnergyflow2 | Energy flow diagram 2 | 能量流图2 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow 2: value 1 indicates hollow. value 2 indicates solid. value 3 indicates right flow. value 4 indicates none.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.7 | hwUPS5000EEnergyflow3 | Energy flow diagram 3 | 能量流图3 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow 3: value 1 indicates hollow. value 2 indicates solid. value 3 indicates right flow. value 4 indicates none.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.8 | hwUPS5000EEnergyflow4 | Energy flow diagram 4 | 能量流图4 | 0-Read_Only | 只读 | hollow(1), solid(2), downwardflow(3), upwardflow(4), unknown(255) | [空心=1]/[实心=2]/[向下流动=3]/[向上流动=4] | Energy flow 4: value 1 indicates hollow. value 2 indicates solid. value 3 indicates downward flow. value 4 indicates upward flow.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.9 | hwUPS5000EEnergyflow5 | Energy flow diagram 5 | 能量流图5 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow 5: value 1 indicates hollow. value 2 indicates solid. value 3 indicates right flow. value 4 indicates none.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.10 | hwUPS5000EEnergyflow6 | Energy flow diagram 6 | 能量流图6 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow 6: value 1 indicates hollow. value 2 indicates solid. value 3 indicates right flow. value 4 indicates none.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.11 | hwUPS5000EEnergyflow7 | Energy flow diagram 7 | 能量流图7 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow 7: value 1 indicates hollow. value 2 indicates solid. value 3 indicates right flow. value 4 indicates none.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.12 | hwUPS5000EEnergyflow8 | Energy flow diagram 8 | 能量流图8 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow 8: value 1 indicates hollow. value 2 indicates solid. value 3 indicates right flow. value 4 indicates none.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.13 | hwUPS5000ECoolingPower | Rated cooling capacity (cooling power) | 额定的制冷容量（制冷功率） | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Cooling Power status of UPS5000E. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.14 | hwUPS5000EPositivebusvoltage | Positive bus voltage | 正母线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Positive bus voltage of UPS5000E.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.15 | hwUPS5000ENegativebusvoltage | Negative bus voltage | 负母线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Negative bus voltage of UPS5000E.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.16 | hwUPS5000EBatterySOH | Battery SOH | 电池SOH | 0-Read_Only | 只读 | good(1), maintain(2), abnormal(3), unknown(255) | [良好=1]/[需维护=2]/[异常=3] | Battery SOH of the device config table for the UPS5000E. Value 1 indicate good Value 2 indicate maintain Value 3 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.17 | hwUPS5000EZeroSequenceCurrent | Zero sequence current | 零序电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Zero Sequence Current of UPS5000E.Multiple 10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.18 | hwUPS5000EModuleTemperature | Module temperature | 模块温度 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The Module Temperature of UPS5000E.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.19 | hwUPS5000EBatteryvoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The Battery voltage of UPS5000E.Multiple 10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.20 | hwUPS5000EBatterycurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | The Battery current of UPS5000E.Multiple 10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.100 | hwUPS5000ERunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3 | hwUPS5000ERunning3Table | / | / |  |  | / | / | The running and config table of UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.1 | hwUPS5000ERunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the UPS5000E.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.3 | hwUPS5000EBpmPhaseAInputCurrent | BPM phase A input current | 旁路A相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase A input current of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.4 | hwUPS5000EBpmPhaseBInputCurrent | BPM phase B input current | 旁路B相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase B input current of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.5 | hwUPS5000EBpmPhaseCInputCurrent | BPM phase C input current | 旁路C相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase C input current of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.6 | hwUPS5000EBatteryType | Battery type | 电池类型 | 0-Read_Only | 只读 | vrla(1), lithiumbattery(2), unknown(255) | [铅酸电池=1]/[锂电电池=2] | Battery type of the device config table for the UPS5000E. Value 1 indicate vrla Value 2 indicate lithium battery
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.7 | hwUPS5000EVoltageLevel | Voltage level | 电压等级 | 0-Read_Only | 只读 | twoHundred(1), twoHundredAndEight(2), twoHundredAndTwenty(3), threeHundredAndEighty(4), fourHundred(5), fourHundredAndFifteen(6), fourHundredAndEighty(7), sixHundred(8), sixHundredAndNinety(9), threeHundredAndSixty(10), twoHundredAndThirty(11), fourHundredAndTwenty(12), twoHundredAndTen(13), unknown(255) | [200=1]/[208=2]/[220=3]/[380=4]/[400=5]/[415=6]/[480=7]/[600=8]/[690=9]/[360=10]/[230=11]/[420=12]/[210=13] | Voltage level of the device config table for the UPS5000. Value 1 indicate 200 Value 2 indicate 208 Value 3 indicate 220 Value 4 indicate 380 Value 5 indicate 400 Value 6 indicate 415 Value 7 indicate 480 Value 8 indicate 600 Value 9 indicate 690 Value 10 indicate 360 Value 11 indicate 230 Value 12 indicate 420 Value 13 indicate 210SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.8 | hwUPS5000ESystemOutputFrequency | System output frequency | 系统输出频率 | 0-Read_Only | 只读 | fifty(1), sixty(2), unknown(255) | [50=1]/[60=2] | System output frequency of the device config table for the UPS5000. Value 1 indicate 50 Value 2 indicate 60SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.9 | hwUPS5000EBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 5..9999 | 5..9999 | Battery capacity of the device config table for the UPS5000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.10 | hwUPS5000EWorkMode | Work mode | 工作模式 | 0-Read_Only | 只读 | normalmode(1), eco(2), selfloadmode(3), convertermode(4), unknown(255) | [正常模式=1]/[ECO=2]/[自老化模式=3]/[变频器模式=4] | Work mode of the device config table for the UPS5000. Value 1 indicate normal mode Value 2 indicate eco Value 3 indicate self-load mode Value 4 indicate converter mode
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.11 | hwUPS5000ESchedShallowDisTest | Sched. shallow dis. test | 定时浅放电测试 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Sched. shallow dis. test of the device config table for the UPS5000. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.12 | hwUPS5000ESchedShallowDisTestTime | Sched. shallow dis. test time | 定时浅放电测试时间段 | 1-Read_Write | 读写 | zeroToSixHourly(1), sixToTwelveHourly(2), twelveToEighteenHourly(3), eighteenToTwentyfourHourly(4), unknown(255) | [00:00~06:00=1]/[06:00~12:00=2]/[12:00~18:00=3]/[18:00~24:00=4] | Sched. shallow dis. test time of the device config table for the UPS5000. Value 1 indicate 00:00~06:00 Value 2 indicate 06:00~12:00 Value 3 indicate 12:00~18:00 Value 4 indicate 18:00~24:00
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.13 | hwUPS5000ESchedShallowDisTestInterval | Sched. shallow dis. test interval | 定时浅放电测试间隔 | 1-Read_Write | 读写 | 30..90 | 30..90 | Sched. shallow dis. test interval of the device config table for the UPS5000.SigUnitInfo:days.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.14 | hwUPS5000EShallowDisTestDisRatio | Shallow dis. test dis. ratio | 浅放电测试放电百分比 | 1-Read_Write | 读写 | 10..50 | 10..50 | Shallow dis. test dis. ratio of the device config table for the UPS5000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.15 | hwUPS5000ESmartParallelSleepMode | Smart parallel sleep mode | 智能并机休眠模式 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Smart parallel sleep mode of the device config table for the UPS5000. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.16 | hwUPS5000EPowerGridModuleEnable | Power grid module enable | 电网调频模块使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Power grid module enable of the device config table for the UPS5000E. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.17 | hwUPS5000EFfrMode | FFR mode | FFR模式 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | FFR mode of the device config table for the UPS5000E. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.18 | hwUPS5000EFfrFrequencyThresholdForAction | FFR frequency threshold for action | FFR频率动作点 | 1-Read_Write | 读写 | 4940..5990 | 4940..5990 | FFR frequency threshold for action of the device config table for the UPS5000E.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.19 | hwUPS5000EFfrDuration | FFR duration | FFR持续时间 | 1-Read_Write | 读写 | 50..36000 | 50..36000 | FFR duration of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.20 | hwUPS5000EMaximumBatteryPowerSupplyRatioInFfrMode | Maximum battery power supply ratio in FFR mode | FFR模式最大电池供电百分比 | 1-Read_Write | 读写 | 30..100 | 30..100 | Maximum battery power supply ratio in FFR mode of the device config table for the UPS5000E.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.21 | hwUPS5000ENormalBackupTimeReservedForFfrMode | Normal backup time reserved for FFR mode | FFR模式预留正常备电时间 | 1-Read_Write | 读写 | 5..600 | 5..600 | Normal backup time reserved for FFR mode of the device config table for the UPS5000E.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.22 | hwUPS5000EBatteryInitialSocForFfrMode | Battery initial SOC for FFR mode | 进入FFR模式的电池初始SOC | 1-Read_Write | 读写 | 40..100 | 40..100 | Battery initial SOC for FFR mode of the device config table for the UPS5000E.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.23 | hwUPS5000EFfrMaximumFullActivationTime | FFR Maximum full activation time | FFR最大响应时间 | 1-Read_Write | 读写 | 7..50 | 7..50 | FFR Maximum full activation time of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.24 | hwUPS5000ESocThresholdForTheBatteryToExitFfrMode | SOC threshold for the battery to exit FFR mode | 退出FFR模式的电池SOC | 1-Read_Write | 读写 | 30..90 | 30..90 | SOC threshold for the battery to exit FFR mode of the device config table for the UPS5000E.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.25 | hwUPS5000EBatterySOHPercentage | Battery SOH | 电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery SOH Percentage of the device config table for the UPS5000E.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.26 | hwUPS5000ERackOutputTotalElectricityEnergy | Rack output total electricity energy | 机架输出总电能 | 0-Read_Only | 只读 | 0..429496720 | 0..429496720 | Rack output total electricity energy of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.100 | hwUPS5000ERunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase UPS5000E.

## iBOX
iBOX
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.4 | iBOX | iBOX | iBOX | / | / | / | / | The iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1 | hwiBOXRunning1Table | / | / |  |  | / | / | The running table 1 of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.1 | hwiBOXRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.2 | hwiBOXCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device for the iBOX: Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.3 | hwiBOXEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 1..28 | 1..28 | the ESN. of iBOX Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.4 | hwiBOXSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | SoftWareVersion of the device for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.5 | hwiBOXHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | hardWareVersion of the device for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.6 | hwiBOXRFSoftwareVersion | RF software version | RF软件版本 | 0-Read_Only | 只读 | 1..16 | 1..16 | RF SoftWareVersion of the device for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.7 | hwiBOXBatteryVoltage | Single string voltage | 单组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BatteryVoltage of the device for the iBOX. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.8 | hwiBOXSOC | Single string SOC | 单组电池SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | SOC of the device for the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.9 | hwiBOXSOH | Single string SOH | 单组电池SOH | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.10 | hwiBOXBatteryCurrent | Single string current | 单组电池电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Battery current of the iBOX. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.11 | hwiBOXIbatVoltage1 | Single battery 1 voltage | 单节电池1电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 1 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.12 | hwiBOXIbatVoltage2 | Single battery 2 voltage | 单节电池2电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 2 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.13 | hwiBOXIbatVoltage3 | Single battery 3 voltage | 单节电池3电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 3 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.14 | hwiBOXIbatVoltage4 | Single battery 4 voltage | 单节电池4电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 4 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.15 | hwiBOXIbatVoltage5 | Single battery 5 voltage | 单节电池5电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 5 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.16 | hwiBOXIbatVoltage6 | Single battery 6 voltage | 单节电池6电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 6 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.17 | hwiBOXIbatVoltage7 | Single battery 7 voltage | 单节电池7电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 7 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.18 | hwiBOXIbatVoltage8 | Single battery 8 voltage | 单节电池8电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 8 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.19 | hwiBOXIbatVoltage9 | Single battery 9 voltage | 单节电池9电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 9 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.20 | hwiBOXIbatVoltage10 | Single battery 10 voltage | 单节电池10电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 10 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.21 | hwiBOXIbatVoltage11 | Single battery 11 voltage | 单节电池11电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 11 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.22 | hwiBOXIbatVoltage12 | Single battery 12 voltage | 单节电池12电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 12 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.23 | hwiBOXIbatVoltage13 | Single battery 13 voltage | 单节电池13电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 13 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.24 | hwiBOXIbatVoltage14 | Single battery 14 voltage | 单节电池14电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 14 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.25 | hwiBOXIbatVoltage15 | Single battery 15 voltage | 单节电池15电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 15 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.26 | hwiBOXIbatVoltage16 | Single battery 16 voltage | 单节电池16电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 16 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.27 | hwiBOXIbatVoltage17 | Single battery 17 voltage | 单节电池17电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 17 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.28 | hwiBOXIbatVoltage18 | Single battery 18 voltage | 单节电池18电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 18 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.29 | hwiBOXIbatVoltage19 | Single battery 19 voltage | 单节电池19电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 19 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.30 | hwiBOXIbatVoltage20 | Single battery 20 voltage | 单节电池20电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 20 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.31 | hwiBOXIbatVoltage21 | Single battery 21 voltage | 单节电池21电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 21 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.32 | hwiBOXIbatVoltage22 | Single battery 22 voltage | 单节电池22电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 22 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.33 | hwiBOXIbatVoltage23 | Single battery 23 voltage | 单节电池23电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 23 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.34 | hwiBOXIbatVoltage24 | Single battery 24 voltage | 单节电池24电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 24 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.35 | hwiBOXIbatVoltage25 | Single battery 25 voltage | 单节电池25电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 25 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.36 | hwiBOXIbatVoltage26 | Single battery 26 voltage | 单节电池26电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 26 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.37 | hwiBOXIbatVoltage27 | Single battery 27 voltage | 单节电池27电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 27 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.38 | hwiBOXIbatVoltage28 | Single battery 28 voltage | 单节电池28电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 28 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.39 | hwiBOXIbatVoltage29 | Single battery 29 voltage | 单节电池29电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 29 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.40 | hwiBOXIbatVoltage30 | Single battery 30 voltage | 单节电池30电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 30 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.41 | hwiBOXIbatVoltage31 | Single battery 31 voltage | 单节电池31电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 31 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.42 | hwiBOXIbatVoltage32 | Single battery 32 voltage | 单节电池32电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 32 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.43 | hwiBOXIbatVoltage33 | Single battery 33 voltage | 单节电池33电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 33 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.44 | hwiBOXIbatVoltage34 | Single battery 34 voltage | 单节电池34电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 34 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.45 | hwiBOXIbatVoltage35 | Single battery 35 voltage | 单节电池35电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 35 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.46 | hwiBOXIbatVoltage36 | Single battery 36 voltage | 单节电池36电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 36 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.47 | hwiBOXIbatVoltage37 | Single battery 37 voltage | 单节电池37电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 37 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.48 | hwiBOXIbatVoltage38 | Single battery 38 voltage | 单节电池38电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 38 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.49 | hwiBOXIbatVoltage39 | Single battery 39 voltage | 单节电池39电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 39 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.50 | hwiBOXIbatVoltage40 | Single battery 40 voltage | 单节电池40电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 40 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.51 | hwiBOXIbatRes1 | Single battery 1 resistance | 单节电池1内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 1 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.52 | hwiBOXIbatRes2 | Single battery 2 resistance | 单节电池2内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 2 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.53 | hwiBOXIbatRes3 | Single battery 3 resistance | 单节电池3内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 3 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.54 | hwiBOXIbatRes4 | Single battery 4 resistance | 单节电池4内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 4 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.55 | hwiBOXIbatRes5 | Single battery 5 resistance | 单节电池5内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 5 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.56 | hwiBOXIbatRes6 | Single battery 6 resistance | 单节电池6内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 6 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.57 | hwiBOXIbatRes7 | Single battery 7 resistance | 单节电池7内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 7 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.58 | hwiBOXIbatRes8 | Single battery 8 resistance | 单节电池8内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 8 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.59 | hwiBOXIbatRes9 | Single battery 9 resistance | 单节电池9内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 9 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.60 | hwiBOXIbatRes10 | Single battery 10 resistance | 单节电池10内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 10 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.61 | hwiBOXIbatRes11 | Single battery 11 resistance | 单节电池11内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 11 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.62 | hwiBOXIbatRes12 | Single battery 12 resistance | 单节电池12内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 12 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.63 | hwiBOXIbatRes13 | Single battery 13 resistance | 单节电池13内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 13 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.64 | hwiBOXIbatRes14 | Single battery 14 resistance | 单节电池14内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 14 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.65 | hwiBOXIbatRes15 | Single battery 15 resistance | 单节电池15内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 15 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.66 | hwiBOXIbatRes16 | Single battery 16 resistance | 单节电池16内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 16 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.67 | hwiBOXIbatRes17 | Single battery 17 resistance | 单节电池17内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 17 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.68 | hwiBOXIbatRes18 | Single battery 18 resistance | 单节电池18内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 18 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.69 | hwiBOXIbatRes19 | Single battery 19 resistance | 单节电池19内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 19 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.70 | hwiBOXIbatRes20 | Single battery 20 resistance | 单节电池20内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 20 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.71 | hwiBOXIbatRes21 | Single battery 21 resistance | 单节电池21内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 21 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.72 | hwiBOXIbatRes22 | Single battery 22 resistance | 单节电池22内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 22 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.73 | hwiBOXIbatRes23 | Single battery 23 resistance | 单节电池23内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 23 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.74 | hwiBOXIbatRes24 | Single battery 24 resistance | 单节电池24内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 24 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.75 | hwiBOXIbatRes25 | Single battery 25 resistance | 单节电池25内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 25 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.76 | hwiBOXIbatRes26 | Single battery 26 resistance | 单节电池26内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 26 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.77 | hwiBOXIbatRes27 | Single battery 27 resistance | 单节电池27内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 27 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.78 | hwiBOXIbatRes28 | Single battery 28 resistance | 单节电池28内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 28 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.79 | hwiBOXIbatRes29 | Single battery 29 resistance | 单节电池29内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 29 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.80 | hwiBOXIbatRes30 | Single battery 30 resistance | 单节电池30内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 30 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.81 | hwiBOXIbatRes31 | Single battery 31 resistance | 单节电池31内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 31 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.82 | hwiBOXIbatRes32 | Single battery 32 resistance | 单节电池32内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 32 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.83 | hwiBOXIbatRes33 | Single battery 33 resistance | 单节电池33内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 33 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.84 | hwiBOXIbatRes34 | Single battery 34 resistance | 单节电池34内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 34 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.85 | hwiBOXIbatRes35 | Single battery 35 resistance | 单节电池35内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 35 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.86 | hwiBOXIbatRes36 | Single battery 36 resistance | 单节电池36内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 36 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.87 | hwiBOXIbatRes37 | Single battery 37 resistance | 单节电池37内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 37 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.88 | hwiBOXIbatRes38 | Single battery 38 resistance | 单节电池38内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 38 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.89 | hwiBOXIbatRes39 | Single battery 39 resistance | 单节电池39内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 39 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.90 | hwiBOXIbatRes40 | Single battery 40 resistance | 单节电池40内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 40 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.100 | hwiBOXRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.2 | hwiBOXRunning2Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.1 | hwiBOXRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 2 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.2 | hwiBOXIbatSOH1 | Single battery 1 SOH | 单节电池1SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH1 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.3 | hwiBOXIbatSOH2 | Single battery 2 SOH | 单节电池2SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH2 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.4 | hwiBOXIbatSOH3 | Single battery 3 SOH | 单节电池3SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH3 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.5 | hwiBOXIbatSOH4 | Single battery 4 SOH | 单节电池4SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH4 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.6 | hwiBOXIbatSOH5 | Single battery 5 SOH | 单节电池5SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH5 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.7 | hwiBOXIbatSOH6 | Single battery 6 SOH | 单节电池6SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH6 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.8 | hwiBOXIbatSOH7 | Single battery 7 SOH | 单节电池7SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH7 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.9 | hwiBOXIbatSOH8 | Single battery 8 SOH | 单节电池8SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH8 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.10 | hwiBOXIbatSOH9 | Single battery 9 SOH | 单节电池9SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH9 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.11 | hwiBOXIbatSOH10 | Single battery 10 SOH | 单节电池10SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH10 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.12 | hwiBOXIbatSOH11 | Single battery 11 SOH | 单节电池11SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH11 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.13 | hwiBOXIbatSOH12 | Single battery 12 SOH | 单节电池12SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH12 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.14 | hwiBOXIbatSOH13 | Single battery 13 SOH | 单节电池13SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH13 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.15 | hwiBOXIbatSOH14 | Single battery 14 SOH | 单节电池14SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH14 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.16 | hwiBOXIbatSOH15 | Single battery 15 SOH | 单节电池15SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH15 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.17 | hwiBOXIbatSOH16 | Single battery 16 SOH | 单节电池16SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH16 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.18 | hwiBOXIbatSOH17 | Single battery 17 SOH | 单节电池17SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH17 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.19 | hwiBOXIbatSOH18 | Single battery 18 SOH | 单节电池18SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH18 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.20 | hwiBOXIbatSOH19 | Single battery 19 SOH | 单节电池19SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH19 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.21 | hwiBOXIbatSOH20 | Single battery 20 SOH | 单节电池20SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH20 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.22 | hwiBOXIbatSOH21 | Single battery 21 SOH | 单节电池21SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH21 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.23 | hwiBOXIbatSOH22 | Single battery 22 SOH | 单节电池22SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH22 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.24 | hwiBOXIbatSOH23 | Single battery 23 SOH | 单节电池23SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH23 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.25 | hwiBOXIbatSOH24 | Single battery 24 SOH | 单节电池24SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH24 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.26 | hwiBOXIbatSOH25 | Single battery 25 SOH | 单节电池25SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH25 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.27 | hwiBOXIbatSOH26 | Single battery 26 SOH | 单节电池26SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH26 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.28 | hwiBOXIbatSOH27 | Single battery 27 SOH | 单节电池27SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH27 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.29 | hwiBOXIbatSOH28 | Single battery 28 SOH | 单节电池28SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH28 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.30 | hwiBOXIbatSOH29 | Single battery 29 SOH | 单节电池29SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH29 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.31 | hwiBOXIbatSOH30 | Single battery 30 SOH | 单节电池30SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH30 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.32 | hwiBOXIbatSOH31 | Single battery 31 SOH | 单节电池31SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH31 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.33 | hwiBOXIbatSOH32 | Single battery 32 SOH | 单节电池32SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH32 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.34 | hwiBOXIbatSOH33 | Single battery 33 SOH | 单节电池33SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH33 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.35 | hwiBOXIbatSOH34 | Single battery 34 SOH | 单节电池34SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH34 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.36 | hwiBOXIbatSOH35 | Single battery 35 SOH | 单节电池35SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH35 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.37 | hwiBOXIbatSOH36 | Single battery 36 SOH | 单节电池36SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH36 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.38 | hwiBOXIbatSOH37 | Single battery 37 SOH | 单节电池37SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH37 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.39 | hwiBOXIbatSOH38 | Single battery 38 SOH | 单节电池38SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH38 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.40 | hwiBOXIbatSOH39 | Single battery 39 SOH | 单节电池39SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH39 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.41 | hwiBOXIbatSOH40 | Single battery 40 SOH | 单节电池40SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH40 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.42 | hwiBOXIbatSOC1 | Single battery 1 SOC | 单节电池1SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC1 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.43 | hwiBOXIbatSOC2 | Single battery 2 SOC | 单节电池2SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC2 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.44 | hwiBOXIbatSOC3 | Single battery 3 SOC | 单节电池3SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC3 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.45 | hwiBOXIbatSOC4 | Single battery 4 SOC | 单节电池4SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC4 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.46 | hwiBOXIbatSOC5 | Single battery 5 SOC | 单节电池5SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC5 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.47 | hwiBOXIbatSOC6 | Single battery 6 SOC | 单节电池6SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC6 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.48 | hwiBOXIbatSOC7 | Single battery 7 SOC | 单节电池7SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC7 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.49 | hwiBOXIbatSOC8 | Single battery 8 SOC | 单节电池8SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC8 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.50 | hwiBOXIbatSOC9 | Single battery 9 SOC | 单节电池9SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC9 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.51 | hwiBOXIbatSOC10 | Single battery 10 SOC | 单节电池10SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC10 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.52 | hwiBOXIbatSOC11 | Single battery 11 SOC | 单节电池11SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC11 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.53 | hwiBOXIbatSOC12 | Single battery 12 SOC | 单节电池12SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC12 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.54 | hwiBOXIbatSOC13 | Single battery 13 SOC | 单节电池13SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC13 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.55 | hwiBOXIbatSOC14 | Single battery 14 SOC | 单节电池14SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC14 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.56 | hwiBOXIbatSOC15 | Single battery 15 SOC | 单节电池15SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC15 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.57 | hwiBOXIbatSOC16 | Single battery 16 SOC | 单节电池16SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC16 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.58 | hwiBOXIbatSOC17 | Single battery 17 SOC | 单节电池17SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC17 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.59 | hwiBOXIbatSOC18 | Single battery 18 SOC | 单节电池18SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC18 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.60 | hwiBOXIbatSOC19 | Single battery 19 SOC | 单节电池19SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC19 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.61 | hwiBOXIbatSOC20 | Single battery 20 SOC | 单节电池20SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC20 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.62 | hwiBOXIbatSOC21 | Single battery 21 SOC | 单节电池21SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC21 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.63 | hwiBOXIbatSOC22 | Single battery 22 SOC | 单节电池22SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC22 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.64 | hwiBOXIbatSOC23 | Single battery 23 SOC | 单节电池23SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC23 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.65 | hwiBOXIbatSOC24 | Single battery 24 SOC | 单节电池24SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC24 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.66 | hwiBOXIbatSOC25 | Single battery 25 SOC | 单节电池25SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC25 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.67 | hwiBOXIbatSOC26 | Single battery 26 SOC | 单节电池26SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC26 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.68 | hwiBOXIbatSOC27 | Single battery 27 SOC | 单节电池27SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC27 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.69 | hwiBOXIbatSOC28 | Single battery 28 SOC | 单节电池28SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC28 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.70 | hwiBOXIbatSOC29 | Single battery 29 SOC | 单节电池29SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC29 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.71 | hwiBOXIbatSOC30 | Single battery 30 SOC | 单节电池30SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC30 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.72 | hwiBOXIbatSOC31 | Single battery 31 SOC | 单节电池31SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC31 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.73 | hwiBOXIbatSOC32 | Single battery 32 SOC | 单节电池32SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC32 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.74 | hwiBOXIbatSOC33 | Single battery 33 SOC | 单节电池33SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC33 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.75 | hwiBOXIbatSOC34 | Single battery 34 SOC | 单节电池34SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC34 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.76 | hwiBOXIbatSOC35 | Single battery 35 SOC | 单节电池35SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC35 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.77 | hwiBOXIbatSOC36 | Single battery 36 SOC | 单节电池36SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC36 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.78 | hwiBOXIbatSOC37 | Single battery 37 SOC | 单节电池37SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC37 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.79 | hwiBOXIbatSOC38 | Single battery 38 SOC | 单节电池38SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC38 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.80 | hwiBOXIbatSOC39 | Single battery 39 SOC | 单节电池39SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC39 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.81 | hwiBOXIbatSOC40 | Single battery 40 SOC | 单节电池40SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC40 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.100 | hwiBOXRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3 | hwiBOXRunning3Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.1 | hwiBOXRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 3 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.2 | hwiBOXIbatCurrent1 | Single battery 1 current | 单节电池1电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 1 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.3 | hwiBOXIbatCurrent2 | Single battery 2 current | 单节电池2电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 2 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.4 | hwiBOXIbatCurrent3 | Single battery 3 current | 单节电池3电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 3 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.5 | hwiBOXIbatCurrent4 | Single battery 4 current | 单节电池4电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 4 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.6 | hwiBOXIbatCurrent5 | Single battery 5 current | 单节电池5电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 5 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.7 | hwiBOXIbatCurrent6 | Single battery 6 current | 单节电池6电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 6 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.8 | hwiBOXIbatCurrent7 | Single battery 7 current | 单节电池7电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 7 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.9 | hwiBOXIbatCurrent8 | Single battery 8 current | 单节电池8电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 8 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.10 | hwiBOXIbatCurrent9 | Single battery 9 current | 单节电池9电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 9 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.11 | hwiBOXIbatCurrent10 | Single battery 10 current | 单节电池10电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 10 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.12 | hwiBOXIbatCurrent11 | Single battery 11 current | 单节电池11电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 11 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.13 | hwiBOXIbatCurrent12 | Single battery 12 current | 单节电池12电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 12 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.14 | hwiBOXIbatCurrent13 | Single battery 13 current | 单节电池13电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 13 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.15 | hwiBOXIbatCurrent14 | Single battery 14 current | 单节电池14电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 14 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.16 | hwiBOXIbatCurrent15 | Single battery 15 current | 单节电池15电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 15 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.17 | hwiBOXIbatCurrent16 | Single battery 16 current | 单节电池16电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 16 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.18 | hwiBOXIbatCurrent17 | Single battery 17 current | 单节电池17电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 17 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.19 | hwiBOXIbatCurrent18 | Single battery 18 current | 单节电池18电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 18 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.20 | hwiBOXIbatCurrent19 | Single battery 19 current | 单节电池19电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 19 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.21 | hwiBOXIbatCurrent20 | Single battery 20 current | 单节电池20电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 20 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.22 | hwiBOXIbatCurrent21 | Single battery 21 current | 单节电池21电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 21 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.23 | hwiBOXIbatCurrent22 | Single battery 22 current | 单节电池22电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 22 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.24 | hwiBOXIbatCurrent23 | Single battery 23 current | 单节电池23电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 23 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.25 | hwiBOXIbatCurrent24 | Single battery 24 current | 单节电池24电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 24 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.26 | hwiBOXIbatCurrent25 | Single battery 25 current | 单节电池25电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 25 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.27 | hwiBOXIbatCurrent26 | Single battery 26 current | 单节电池26电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 26 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.28 | hwiBOXIbatCurrent27 | Single battery 27 current | 单节电池27电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 27 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.29 | hwiBOXIbatCurrent28 | Single battery 28 current | 单节电池28电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 28 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.30 | hwiBOXIbatCurrent29 | Single battery 29 current | 单节电池29电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 29 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.31 | hwiBOXIbatCurrent30 | Single battery 30 current | 单节电池30电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 30 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.32 | hwiBOXIbatCurrent31 | Single battery 31 current | 单节电池31电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 31 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.33 | hwiBOXIbatCurrent32 | Single battery 32 current | 单节电池32电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 32 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.34 | hwiBOXIbatCurrent33 | Single battery 33 current | 单节电池33电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 33 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.35 | hwiBOXIbatCurrent34 | Single battery 34 current | 单节电池34电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 34 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.36 | hwiBOXIbatCurrent35 | Single battery 35 current | 单节电池35电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 35 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.37 | hwiBOXIbatCurrent36 | Single battery 36 current | 单节电池36电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 36 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.38 | hwiBOXIbatCurrent37 | Single battery 37 current | 单节电池37电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 37 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.39 | hwiBOXIbatCurrent38 | Single battery 38 current | 单节电池38电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 38 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.40 | hwiBOXIbatCurrent39 | Single battery 39 current | 单节电池39电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 39 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.41 | hwiBOXIbatCurrent40 | Single battery 40 current | 单节电池40电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 40 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.42 | hwiBOXIbatSOHStatus1 | Single battery 1 SOH status | 单节电池1SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.43 | hwiBOXIbatSOHStatus2 | Single battery 2 SOH status | 单节电池2SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.44 | hwiBOXIbatSOHStatus3 | Single battery 3 SOH status | 单节电池3SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.45 | hwiBOXIbatSOHStatus4 | Single battery 4 SOH status | 单节电池4SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.46 | hwiBOXIbatSOHStatus5 | Single battery 5 SOH status | 单节电池5SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.47 | hwiBOXIbatSOHStatus6 | Single battery 6 SOH status | 单节电池6SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.48 | hwiBOXIbatSOHStatus7 | Single battery 7 SOH status | 单节电池7SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.49 | hwiBOXIbatSOHStatus8 | Single battery 8 SOH status | 单节电池8SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.50 | hwiBOXIbatSOHStatus9 | Single battery 9 SOH status | 单节电池9SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.51 | hwiBOXIbatSOHStatus10 | Single battery 10 SOH status | 单节电池10SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.52 | hwiBOXIbatSOHStatus11 | Single battery 11 SOH status | 单节电池11SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.53 | hwiBOXIbatSOHStatus12 | Single battery 12 SOH status | 单节电池12SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.54 | hwiBOXIbatSOHStatus13 | Single battery 13 SOH status | 单节电池13SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.55 | hwiBOXIbatSOHStatus14 | Single battery 14 SOH status | 单节电池14SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.56 | hwiBOXIbatSOHStatus15 | Single battery 15 SOH status | 单节电池15SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.57 | hwiBOXIbatSOHStatus16 | Single battery 16 SOH status | 单节电池16SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.58 | hwiBOXIbatSOHStatus17 | Single battery 17 SOH status | 单节电池17SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.59 | hwiBOXIbatSOHStatus18 | Single battery 18 SOH status | 单节电池18SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.60 | hwiBOXIbatSOHStatus19 | Single battery 19 SOH status | 单节电池19SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.61 | hwiBOXIbatSOHStatus20 | Single battery 20 SOH status | 单节电池20SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.62 | hwiBOXIbatSOHStatus21 | Single battery 21 SOH status | 单节电池21SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.63 | hwiBOXIbatSOHStatus22 | Single battery 22 SOH status | 单节电池22SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.64 | hwiBOXIbatSOHStatus23 | Single battery 23 SOH status | 单节电池23SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.65 | hwiBOXIbatSOHStatus24 | Single battery 24 SOH status | 单节电池24SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.66 | hwiBOXIbatSOHStatus25 | Single battery 25 SOH status | 单节电池25SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.67 | hwiBOXIbatSOHStatus26 | Single battery 26 SOH status | 单节电池26SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.68 | hwiBOXIbatSOHStatus27 | Single battery 27 SOH status | 单节电池27SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.69 | hwiBOXIbatSOHStatus28 | Single battery 28 SOH status | 单节电池28SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.70 | hwiBOXIbatSOHStatus29 | Single battery 29 SOH status | 单节电池29SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.71 | hwiBOXIbatSOHStatus30 | Single battery 30 SOH status | 单节电池30SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.72 | hwiBOXIbatSOHStatus31 | Single battery 31 SOH status | 单节电池31SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.73 | hwiBOXIbatSOHStatus32 | Single battery 32 SOH status | 单节电池32SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.74 | hwiBOXIbatSOHStatus33 | Single battery 33 SOH status | 单节电池33SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.75 | hwiBOXIbatSOHStatus34 | Single battery 34 SOH status | 单节电池34SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.76 | hwiBOXIbatSOHStatus35 | Single battery 35 SOH status | 单节电池35SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.77 | hwiBOXIbatSOHStatus36 | Single battery 36 SOH status | 单节电池36SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.78 | hwiBOXIbatSOHStatus37 | Single battery 37 SOH status | 单节电池37SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.79 | hwiBOXIbatSOHStatus38 | Single battery 38 SOH status | 单节电池38SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.80 | hwiBOXIbatSOHStatus39 | Single battery 39 SOH status | 单节电池39SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.81 | hwiBOXIbatSOHStatus40 | Single battery 40 SOH status | 单节电池40SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.100 | hwiBOXRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4 | hwiBOXRunning4Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.1 | hwiBOXRunning4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 4 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.2 | hwiBOXIbatPoleTemp1 | Single battery 1 pole temperature | 单节电池1极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 1 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.3 | hwiBOXIbatPoleTemp2 | Single battery 2 pole temperature | 单节电池2极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 2 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.4 | hwiBOXIbatPoleTemp3 | Single battery 3 pole temperature | 单节电池3极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 3 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.5 | hwiBOXIbatPoleTemp4 | Single battery 4 pole temperature | 单节电池4极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 4 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.6 | hwiBOXIbatPoleTemp5 | Single battery 5 pole temperature | 单节电池5极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 5 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.7 | hwiBOXIbatPoleTemp6 | Single battery 6 pole temperature | 单节电池6极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 6 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.8 | hwiBOXIbatPoleTemp7 | Single battery 7 pole temperature | 单节电池7极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 7 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.9 | hwiBOXIbatPoleTemp8 | Single battery 8 pole temperature | 单节电池8极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 8 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.10 | hwiBOXIbatPoleTemp9 | Single battery 9 pole temperature | 单节电池9极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 9 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.11 | hwiBOXIbatPoleTemp10 | Single battery 10 pole temperature | 单节电池10极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 10 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.12 | hwiBOXIbatPoleTemp11 | Single battery 11 pole temperature | 单节电池11极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 11 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.13 | hwiBOXIbatPoleTemp12 | Single battery 12 pole temperature | 单节电池12极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 12 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.14 | hwiBOXIbatPoleTemp13 | Single battery 13 pole temperature | 单节电池13极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 13 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.15 | hwiBOXIbatPoleTemp14 | Single battery 14 pole temperature | 单节电池14极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 14 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.16 | hwiBOXIbatPoleTemp15 | Single battery 15 pole temperature | 单节电池15极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 15 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.17 | hwiBOXIbatPoleTemp16 | Single battery 16 pole temperature | 单节电池16极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 16 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.18 | hwiBOXIbatPoleTemp17 | Single battery 17 pole temperature | 单节电池17极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 17 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.19 | hwiBOXIbatPoleTemp18 | Single battery 18 pole temperature | 单节电池18极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 18 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.20 | hwiBOXIbatPoleTemp19 | Single battery 19 pole temperature | 单节电池19极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 19 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.21 | hwiBOXIbatPoleTemp20 | Single battery 20 pole temperature | 单节电池20极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 20 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.22 | hwiBOXIbatPoleTemp21 | Single battery 21 pole temperature | 单节电池21极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 21 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.23 | hwiBOXIbatPoleTemp22 | Single battery 22 pole temperature | 单节电池22极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 22 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.24 | hwiBOXIbatPoleTemp23 | Single battery 23 pole temperature | 单节电池23极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 23 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.25 | hwiBOXIbatPoleTemp24 | Single battery 24 pole temperature | 单节电池24极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 24 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.26 | hwiBOXIbatPoleTemp25 | Single battery 25 pole temperature | 单节电池25极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 25 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.27 | hwiBOXIbatPoleTemp26 | Single battery 26 pole temperature | 单节电池26极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 26 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.28 | hwiBOXIbatPoleTemp27 | Single battery 27 pole temperature | 单节电池27极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 27 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.29 | hwiBOXIbatPoleTemp28 | Single battery 28 pole temperature | 单节电池28极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 28 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.30 | hwiBOXIbatPoleTemp29 | Single battery 29 pole temperature | 单节电池29极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 29 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.31 | hwiBOXIbatPoleTemp30 | Single battery 30 pole temperature | 单节电池30极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 30 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.32 | hwiBOXIbatPoleTemp31 | Single battery 31 pole temperature | 单节电池31极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 31 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.33 | hwiBOXIbatPoleTemp32 | Single battery 32 pole temperature | 单节电池32极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 32 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.34 | hwiBOXIbatPoleTemp33 | Single battery 33 pole temperature | 单节电池33极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 33 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.35 | hwiBOXIbatPoleTemp34 | Single battery 34 pole temperature | 单节电池34极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 34 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.36 | hwiBOXIbatPoleTemp35 | Single battery 35 pole temperature | 单节电池35极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 35 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.37 | hwiBOXIbatPoleTemp36 | Single battery 36 pole temperature | 单节电池36极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 36 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.38 | hwiBOXIbatPoleTemp37 | Single battery 37 pole temperature | 单节电池37极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 37 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.39 | hwiBOXIbatPoleTemp38 | Single battery 38 pole temperature | 单节电池38极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 38 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.40 | hwiBOXIbatPoleTemp39 | Single battery 39 pole temperature | 单节电池39极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 39 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.41 | hwiBOXIbatPoleTemp40 | Single battery 40 pole temperature | 单节电池40极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 40 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.100 | hwiBOXRunning4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5 | hwiBOXRunning5Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.1 | hwiBOXRunning5Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 5 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.2 | hwiBOXIbatVoltage41 | Single battery 41 voltage | 单节电池41电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 41 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.3 | hwiBOXIbatVoltage42 | Single battery 42 voltage | 单节电池42电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 42 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.4 | hwiBOXIbatVoltage43 | Single battery 43 voltage | 单节电池43电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 43 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.5 | hwiBOXIbatVoltage44 | Single battery 44 voltage | 单节电池44电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 44 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.6 | hwiBOXIbatVoltage45 | Single battery 45 voltage | 单节电池45电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 45 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.7 | hwiBOXIbatVoltage46 | Single battery 46 voltage | 单节电池46电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 46 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.8 | hwiBOXIbatRes41 | Single battery 41 resistance | 单节电池41内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 41 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.9 | hwiBOXIbatRes42 | Single battery 42 resistance | 单节电池42内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 42 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.10 | hwiBOXIbatRes43 | Single battery 43 resistance | 单节电池43内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 43 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.11 | hwiBOXIbatRes44 | Single battery 44 resistance | 单节电池44内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 44 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.12 | hwiBOXIbatRes45 | Single battery 45 resistance | 单节电池45内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 45 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.13 | hwiBOXIbatRes46 | Single battery 46 resistance | 单节电池46内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 46 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.14 | hwiBOXIbatPoleTemp41 | Single battery 41 pole temperature | 单节电池41极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 41 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.15 | hwiBOXIbatPoleTemp42 | Single battery 42 pole temperature | 单节电池42极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 42 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.16 | hwiBOXIbatPoleTemp43 | Single battery 43 pole temperature | 单节电池43极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 43 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.17 | hwiBOXIbatPoleTemp44 | Single battery 44 pole temperature | 单节电池44极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 44 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.18 | hwiBOXIbatPoleTemp45 | Single battery 45 pole temperature | 单节电池45极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 45 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.19 | hwiBOXIbatPoleTemp46 | Single battery 46 pole temperature | 单节电池46极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 46 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.20 | hwiBOXIbatSOH41 | Single battery 41 SOH | 单节电池41SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH41 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.21 | hwiBOXIbatSOH42 | Single battery 42 SOH | 单节电池42SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH42 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.22 | hwiBOXIbatSOH43 | Single battery 43 SOH | 单节电池43SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH43 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.23 | hwiBOXIbatSOH44 | Single battery 44 SOH | 单节电池44SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH44 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.24 | hwiBOXIbatSOH45 | Single battery 45 SOH | 单节电池45SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH45 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.25 | hwiBOXIbatSOH46 | Single battery 46 SOH | 单节电池46SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH46 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.26 | hwiBOXIbatSOC41 | Single battery 41 SOC | 单节电池41SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC41 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.27 | hwiBOXIbatSOC42 | Single battery 42 SOC | 单节电池42SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC42 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.28 | hwiBOXIbatSOC43 | Single battery 43 SOC | 单节电池43SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC43 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.29 | hwiBOXIbatSOC44 | Single battery 44 SOC | 单节电池44SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC44 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.30 | hwiBOXIbatSOC45 | Single battery 45 SOC | 单节电池45SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC45 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.31 | hwiBOXIbatSOC46 | Single battery 46 SOC | 单节电池46SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC46 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.32 | hwiBOXIbatCurrent41 | Single battery 41 current | 单节电池41电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 41 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.33 | hwiBOXIbatCurrent42 | Single battery 42 current | 单节电池42电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 42 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.34 | hwiBOXIbatCurrent43 | Single battery 43 current | 单节电池43电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 43 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.35 | hwiBOXIbatCurrent44 | Single battery 44 current | 单节电池44电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 44 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.36 | hwiBOXIbatCurrent45 | Single battery 45 current | 单节电池45电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 45 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.37 | hwiBOXIbatCurrent46 | Single battery 46 current | 单节电池46电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 46 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.38 | hwiBOXIbatSOHStatus41 | Single battery 41 SOH status | 单节电池41SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.39 | hwiBOXIbatSOHStatus42 | Single battery 42 SOH status | 单节电池42SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.40 | hwiBOXIbatSOHStatus43 | Single battery 43 SOH status | 单节电池43SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.41 | hwiBOXIbatSOHStatus44 | Single battery 44 SOH status | 单节电池44SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.42 | hwiBOXIbatSOHStatus45 | Single battery 45 SOH status | 单节电池45SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.43 | hwiBOXIbatSOHStatus46 | Single battery 46 SOH status | 单节电池46SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.100 | hwiBOXRunning5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6 | hwiBOXConfig1Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.1 | hwiBOXConfig1Index | / | / | 1-Read_Write | 读写 | / | / | Index of the device running table 2 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.2 | hwiBOXSetIbatNum | iBOX single battery quantity | iBOX单节电池数量 | 1-Read_Write | 读写 | 0..46 | 0..46 | The iBOX Set Ibat Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.3 | hwiBOXBattInstallTime | Battery installation time | 电池安装时间 | 1-Read_Write | 读写 | 946684800..2145830400 | 946684800..2145830400 | The iBOX Batt Install Time of iBOX. The time is accumulated from 00:00:00 on January 1,1970. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.4 | hwiBOXSingleBattCap | Single battery capacity | 单节电池容量 | 1-Read_Write | 读写 | 5..10000 | 5..10000 | The Single battery capacity of iBOX. SigUnitInfo:Ah
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.5 | hwiBOXCurrGatSource | Current source | 电流获取源 | 1-Read_Write | 读写 | host(1), zeroToFiftyAhalleffectsensor(2), zeroToOneHundredAhalleffectsensor(3), zeroToTwoHundredAhalleffectsensor(4), zeroToFiveHundredAhalleffectsensor(5), zeroToSixHundredAhalleffectsensor(6), zeroToOneThousandAhalleffectsensor(7), zeroToOneThousandandFiveHundredAhalleffectsensor(8), zeroToTwoThousandandAhalleffectsensor(9), unknown(255) | [上位机=1]/[0-50A 档霍尔=2]/[0-100A 档霍尔=3]/[0-200A 档霍尔=4]/[0-500A 档霍尔=5]/[0-600A 档霍尔=6]/[0-1000A 档霍尔=7]/[0-1500A 档霍尔=8]/[0-2000A 档霍尔=9] | The iBOX Curr Gat Source of iBOX. Value 1 indicates host. Value 2 indicates 0-50a hall effect sensor. Value 3 indicates 0-100a hall effect sensor. Value 4 indicates 0-200a hall effect sensor. Value 5 indicates 0-500a hall effect sensor. Value 6 indicates 0-600a hall effect sensor. Value 7 indicates 0-1000a hall effect sensor. Value 8 indicates 0-1500a hall effect sensor. Value 9 indicates 0-2000a hall effect sensor.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.6 | hwiBOXBattGroupNum | Number of iBOX battery strings | iBOX电池组数 | 1-Read_Write | 读写 | 1..4 | 1..4 | The iBOX Batt Group Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.7 | hwiBOXSingleBattGroupBattNum | Single string battery quantity | 单电池组电池个数 | 1-Read_Write | 读写 | 0..300 | 0..300 | The iBOX Single Batt Group Batt Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.8 | hwiBOXBattGroupIndex | Battery string number | 电池组号 | 1-Read_Write | 读写 | 1..4 | 1..4 | The iBOX Batt Group Index of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.9 | hwiBOXBattGroupStartBIMNum | Battery string start iBAT number | 电池组起始iBAT编号 | 1-Read_Write | 读写 | 1..300 | 1..300 | The iBOX Batt Group Start BIM Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.10 | hwiBOXBattGroupEndBIMNum | Battery string end iBAT number | 电池组结束iBAT编号 | 1-Read_Write | 读写 | 1..300 | 1..300 | The iBOX Batt Group End BIM Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.11 | hwiBOXBattAbnormalBCBTrip | BCB tripping upon battery abnormal | 电池异常BCB脱扣 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [使能=1]/[禁止=2] | The iBOX Batt Abnormal BCB Trip of iBOX. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.12 | hwiBOXBattGrpCurrAbnPoint | Single string current deviation alarm threshold | 单组电流偏差告警阈值 | 1-Read_Write | 读写 | 5..50 | 5..50 | The iBOX Batt Grp Curr Abn Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.13 | hwiBOXBattGrpCurrSohPoint | Single string SOH deviation alarm threshold | 单组SOH偏差告警阈值 | 1-Read_Write | 读写 | 30..100 | 30..100 | The iBOX Batt Grp Curr Soh Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.14 | hwiBOXIbatChargeVoltPoint | Battery charging voltage bias threshold | 单节电池浮充电压偏差告警阈值 | 1-Read_Write | 读写 | 5..30 | 5..30 | The iBOX Ibat Charge Volt Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.15 | hwiBOXIbatDischargeVoltPoint | Single battery discharging voltage deviation alarm threshold | 单节电池放电电压偏差告警阈值 | 1-Read_Write | 读写 | 10..30 | 10..30 | The iBOX Ibat Discharge Volt Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.16 | hwiBOXIbatTempOvPoint | Battery overtemperature bias threshold | 单节电池高温偏差告警阈值 | 1-Read_Write | 读写 | 10..50 | 10..50 | The iBOX Ibat Temp Over Point of iBOX. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.17 | hwiBOXIbatTerminalTempPoint | Battery terminal overtemperature threshold | 单节电池端子温度高温告警阈值 | 1-Read_Write | 读写 | 50..80 | 50..80 | The iBOX Ibat Terminal Temp Point of iBOX. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.18 | hwiBOXChargrCurrOverPoint | Single string charging overcurrent threshold | 单组充电过流阈值 | 1-Read_Write | 读写 | 15..100 | 15..100 | The iBOX Chargr Curr Over Point of iBOX.Multiple:100. SigUnitInfo:CA
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.19 | hwiBOXIbatSleepVoltExcepPoint | Single battery hibernation voltage abnormal deviation threshold | 单节电池休眠电压异常偏差阈值 | 1-Read_Write | 读写 | 5..30 | 5..30 | The iBOX Ibat Sleep Volt Excep Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.20 | hwiBOXFatherUPSEquipId | Parent UPS id in iBOX | iBOX中记录的父设备UPS设备ID | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | The iBOX Father UPS EquipId of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.21 | hwiBOXParentDeviceDevId | Parent battery cabinet id in iBOX | iBOX中记录的父设备电池柜设备ID | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | The Parent Device DevId of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.22 | hwiBOXFaultClear | Clear faults | 故障清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | The iBOX Fault Clear of iBOX. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.23 | hwiBOXDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device Name of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.24 | hwiBOXBatteryFileSyncNo | Battery file sync number | 放电曲线文件上报同步号 | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | The Battery File Sync No of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.100 | hwiBOXConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7 | hwiBOXRunning6Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.1 | hwiBOXRunning6Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 6 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.2 | hwiBOXIbatCommState1 | Single battery 1 communication status | 单节电池1通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.3 | hwiBOXIbatCommState2 | Single battery 2 communication status | 单节电池2通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.4 | hwiBOXIbatCommState3 | Single battery 3 communication status | 单节电池3通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.5 | hwiBOXIbatCommState4 | Single battery 4 communication status | 单节电池4通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.6 | hwiBOXIbatCommState5 | Single battery 5 communication status | 单节电池5通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.7 | hwiBOXIbatCommState6 | Single battery 6 communication status | 单节电池6通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.8 | hwiBOXIbatCommState7 | Single battery 7 communication status | 单节电池7通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.9 | hwiBOXIbatCommState8 | Single battery 8 communication status | 单节电池8通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.10 | hwiBOXIbatCommState9 | Single battery 9 communication status | 单节电池9通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.11 | hwiBOXIbatCommState10 | Single battery 10 communication status | 单节电池10通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.12 | hwiBOXIbatCommState11 | Single battery 11 communication status | 单节电池11通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.13 | hwiBOXIbatCommState12 | Single battery 12 communication status | 单节电池12通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.14 | hwiBOXIbatCommState13 | Single battery 13 communication status | 单节电池13通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.15 | hwiBOXIbatCommState14 | Single battery 14 communication status | 单节电池14通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.16 | hwiBOXIbatCommState15 | Single battery 15 communication status | 单节电池15通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.17 | hwiBOXIbatCommState16 | Single battery 16 communication status | 单节电池16通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.18 | hwiBOXIbatCommState17 | Single battery 17 communication status | 单节电池17通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.19 | hwiBOXIbatCommState18 | Single battery 18 communication status | 单节电池18通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.20 | hwiBOXIbatCommState19 | Single battery 19 communication status | 单节电池19通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.21 | hwiBOXIbatCommState20 | Single battery 20 communication status | 单节电池20通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.22 | hwiBOXIbatCommState21 | Single battery 21 communication status | 单节电池21通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.23 | hwiBOXIbatCommState22 | Single battery 22 communication status | 单节电池22通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.24 | hwiBOXIbatCommState23 | Single battery 23 communication status | 单节电池23通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.25 | hwiBOXIbatCommState24 | Single battery 24 communication status | 单节电池24通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.26 | hwiBOXIbatCommState25 | Single battery 25 communication status | 单节电池25通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.27 | hwiBOXIbatCommState26 | Single battery 26 communication status | 单节电池26通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.28 | hwiBOXIbatCommState27 | Single battery 27 communication status | 单节电池27通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.29 | hwiBOXIbatCommState28 | Single battery 28 communication status | 单节电池28通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.30 | hwiBOXIbatCommState29 | Single battery 29 communication status | 单节电池29通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.31 | hwiBOXIbatCommState30 | Single battery 30 communication status | 单节电池30通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.32 | hwiBOXIbatCommState31 | Single battery 31 communication status | 单节电池31通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.33 | hwiBOXIbatCommState32 | Single battery 32 communication status | 单节电池32通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.34 | hwiBOXIbatCommState33 | Single battery 33 communication status | 单节电池33通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.35 | hwiBOXIbatCommState34 | Single battery 34 communication status | 单节电池34通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.36 | hwiBOXIbatCommState35 | Single battery 35 communication status | 单节电池35通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.37 | hwiBOXIbatCommState36 | Single battery 36 communication status | 单节电池36通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.38 | hwiBOXIbatCommState37 | Single battery 37 communication status | 单节电池37通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.39 | hwiBOXIbatCommState38 | Single battery 38 communication status | 单节电池38通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.40 | hwiBOXIbatCommState39 | Single battery 39 communication status | 单节电池39通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.41 | hwiBOXIbatCommState40 | Single battery 40 communication status | 单节电池40通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.42 | hwiBOXIbatCommState41 | Single battery 41 communication status | 单节电池41通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.43 | hwiBOXIbatCommState42 | Single battery 42 communication status | 单节电池42通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.44 | hwiBOXIbatCommState43 | Single battery 43 communication status | 单节电池43通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.45 | hwiBOXIbatCommState44 | Single battery 44 communication status | 单节电池44通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.46 | hwiBOXIbatCommState45 | Single battery 45 communication status | 单节电池45通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.47 | hwiBOXIbatCommState46 | Single battery 46 communication status | 单节电池46通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.48 | hwiBOXSinglestringSOH | Single string SOH | 单组电池SOH百分比 | 0-Read_Only | 只读 | 0..100 | 0..100 | stringSOH of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.49 | hwiBOXSingleStringTemperature | Single string temperature | 单组电池温度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Temperature of Single string.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.100 | hwiBOXRunning6RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.

## Integrated UPS Cabinet
一体化UPS柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.5 | IntegratedUPS | Integrated UPS Cabinet | 一体化UPS柜 | / | / | / | / | The IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1 | hwIntegratedUPSRunning1Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.1 | hwIntegratedUPSRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.2 | hwIntegratedUPSCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Comm State. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.3 | hwIntegratedUPSMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.4 | hwIntegratedUPSInputTotalValidEnergy | Total active electricity energy of UPS input | UPS输入总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Input Total Valid Energy of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.5 | hwIntegratedUPSItInputTotalValidEnergy | Total active electricity energy of IT load input | IT负载输入总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | It Input Total Valid Energy of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.6 | hwIntegratedUPSAirConditionerLoadInputTotalValidEnergy | Total active electricity energy of A/C load input | 空调负载输入总有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Air Conditioner Load Input Total Valid Energy of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.7 | hwIntegratedUPSIP | UPS IP | UPS IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IP of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.8 | hwIntegratedUPSEquipELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | Equip ELabel of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.9 | hwIntegratedUPSEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | Equip ESN of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.10 | hwIntegratedUPSMonitorVersion | Monitoring software version | 监控软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Monitor Version of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.11 | hwIntegratedUPSPowerVersion | Power software version | 功率软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Power Version of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.12 | hwIntegratedUPSInputAPhaseVolt | Ph. A input volt. | A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.13 | hwIntegratedUPSInputBPhaseVolt | Ph. B input volt. | B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input B Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.14 | hwIntegratedUPSInputCPhaseVolt | Ph. C input volt. | C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input C Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.15 | hwIntegratedUPSInputAPhaseCurr | Ph. A input cur. | A相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Input A Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.16 | hwIntegratedUPSInputBPhaseCurr | Ph. B input cur. | B相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Input B Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.17 | hwIntegratedUPSInputCPhaseCurr | Ph. C input cur. | C相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Input C Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.18 | hwIntegratedUPSInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.19 | hwIntegratedUPSInputAPowerFactor | Ph. A input power factor | A相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Input A Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.20 | hwIntegratedUPSInputBPowerFactor | Ph. B input power factor | B相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Input B Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.21 | hwIntegratedUPSInputCPowerFactor | Ph. C input power factor | C相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Input C Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.22 | hwIntegratedUPSInputBypassAVolt | BPM ph. A input volt. | 旁路A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Bypass A Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.23 | hwIntegratedUPSInputBypassBVolt | BPM ph. B input volt. | 旁路B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Bypass B Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.24 | hwIntegratedUPSInputBypassCVolt | BPM ph. C input volt. | 旁路C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Bypass C Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.25 | hwIntegratedUPSInputBypassFrequency | BPM input frequency | 旁路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Bypass Frequency of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.26 | hwIntegratedUPSEnvTemp | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Env Temp of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.27 | hwIntegratedUPSOutputAPhaseVolt | Ph. A output voltage | A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Output A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.28 | hwIntegratedUPSOutputBPhaseVolt | Ph. B output voltage | B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Output B Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.29 | hwIntegratedUPSOutputCPhaseVolt | Ph. C output voltage | C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Output C Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.30 | hwIntegratedUPSOutputAPhaseCurr | Ph. A output current | A相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Output A Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.31 | hwIntegratedUPSOutputBPhaseCurr | Ph. B output current | B相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Output B Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.32 | hwIntegratedUPSOutputCPhaseCurr | Ph. C output current | C相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Output C Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.33 | hwIntegratedUPSOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Output Frequency of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.34 | hwIntegratedUPSOutputAPowerFactor | Ph. A output power factor | A相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Output A Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.35 | hwIntegratedUPSOutputBPowerFactor | Ph. B output power factor | B相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Output B Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.36 | hwIntegratedUPSOutputCPowerFactor | Ph. C output power factor | C相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Output C Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.37 | hwIntegratedUPSOutputALoadFactor | Ph. A output load ratio | A相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Output A Load Factor of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.38 | hwIntegratedUPSOutputBLoadFactor | Ph. B output load ratio | B相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Output B Load Factor of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.39 | hwIntegratedUPSOutputCLoadFactor | Ph. C output load ratio | C相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Output C Load Factor of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.40 | hwIntegratedUPSOutputAValidPower | Ph. A output active power | A相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output A Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.41 | hwIntegratedUPSOutputBValidPower | Ph. B output active power | B相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output B Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.42 | hwIntegratedUPSOutputCValidPower | Ph. C output active power | C相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output C Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.43 | hwIntegratedUPSOutputAApparentPower | Ph. A output appearance power | A相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output A Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.44 | hwIntegratedUPSOutputBApparentPower | Ph. B output appearance power | B相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output B Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.45 | hwIntegratedUPSOutputCApparentPower | Ph. C output appearance power | C相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output C Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.46 | hwIntegratedUPSBattVolt | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Batt Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.47 | hwIntegratedUPSBattCurr | Battery current | 电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | Batt Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.48 | hwIntegratedUPSBattTemp | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -200..800 | -200..800 | Batt Temp of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.49 | hwIntegratedUPSBattBackupTime | Backup time | 备电时间 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Batt Backup Time of the device config table for the IntegratedUPSCabinet. SigUnitInfo:min
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.50 | hwIntegratedUPSSupplyPowerStatus | Power supply status | 供电状态 | 0-Read_Only | 只读 | nopowersupplied(1), bypassmode(2), mainsinvertermode(3), batteryinvertermode(4), sourceSharemode(5), unknown(255) | [均不供电=1]/[旁路供电=2]/[主路逆变供电=3]/[电池逆变供电=4]/[联合供电=5] | Supply Power Status. Value 1 indicates No power supplied. Value 2 indicates Bypass mode. Value 3 indicates Mains inverter mode. Value 4 indicates Battery inverter mode. Value 5 indicates source-share mode.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.51 | hwIntegratedUPSRunStatus | UPS running status | UPS运行状态 | 0-Read_Only | 只读 | single(1), parallel(2), singleeco(3), paralleleco(4), selfLoadmode(5), convertermode(6), unknown(255) | [单机=1]/[并机=2]/[单机ECO=3]/[并机ECO=4]/[自老化模式=5]/[变频器模式=6] | Run Status. Value 1 indicates Single. Value 2 indicates Parallel. Value 3 indicates Single eco. Value 4 indicates Parallel eco. Value 5 indicates self-load mode. Value 6 indicates Converter mode.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.52 | hwIntegratedUPSBattRunStatus | Battery running status | 电池运行状态 | 0-Read_Only | 只读 | notconnected(1), connected(2), hibernation(3), floatcharging(4), equalizedcharging(5), discharging(6), charging(7), unknown(255) | [未接入=1]/[非充非放=2]/[休眠=3]/[浮充=4]/[均充=5]/[放电=6]/[充电=7] | Batt Run Status. Value 1 indicates Notconnected. Value 2 indicates Connected. Value 3 indicates Hibernation. Value 4 indicates Float charging. Value 5 indicates Equalized charging. Value 6 indicates Discharging. Value 7 indicates Charging.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.53 | hwIntegratedUPSHandAutoState | Manual automatic status | 手动自动状态 | 0-Read_Only | 只读 | automatic(1), manual(2), unknown(255) | [自动=1]/[手动=2]/[测试程序=3]/[待机=4] | Hand Auto State. Value 1 indicates Automatic. Value 2 indicates Manual.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.54 | hwIntegratedUPSUseOrnotAlternator | Use generator | 是否使用发电机 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Use Ornot Alternator. Value 1 indicates NO. Value 2 indicates YES.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.55 | hwIntegratedUPSDerailLn1State | LN1 switch status | LN1 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Derail Ln1 State. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.56 | hwIntegratedUPSDerailLn2State | LN2 switch status | LN2 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Derail Ln2 State. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.57 | hwIntegratedUPSMainL1InputPhaseVolt | Input L1 phase voltage | L1输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L1 Input Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.58 | hwIntegratedUPSMainL2InputPhaseVolt | Input L2 phase voltage | L2输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L2 Input Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.59 | hwIntegratedUPSMainL3InputPhaseVolt | Input L3 phase voltage | L3输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L3 Input Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.60 | hwIntegratedUPSMainL1L2InputLineVolt | Input L1-L2 line voltage | L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L1L2 Input Line Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.61 | hwIntegratedUPSMainL2L3InputLineVolt | Input L2-L3 line voltage | L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L2L3 Input Line Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.62 | hwIntegratedUPSMainL3L1InputLineVolt | Input L3-L1 line voltage | L3-L1输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L3L1 Input Line Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.63 | hwIntegratedUPSMainL1InputCurr | Input L1 current | L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main L1 Input Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.64 | hwIntegratedUPSMainL2InputCurr | Input L2 current | L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main L2 Input Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.65 | hwIntegratedUPSMainL3InputCurr | Input L3 current | L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main L3 Input Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.66 | hwIntegratedUPSMainInputFrequency | Mains input frequency | 主路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main Input frequency of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.67 | hwIntegratedUPSMainL1InputValidPower | Input L1 active power | L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L1 Input Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.68 | hwIntegratedUPSMainL2InputValidPower | Input L2 active power | L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L2 Input Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.69 | hwIntegratedUPSMainL3InputValidPower | Input L3 active power | L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L3 Input Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.70 | hwIntegratedUPSMainL1InputApparentPower | Input L1 appearance power | L1输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L1 Input Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.71 | hwIntegratedUPSMainL2InputApparentPower | Input L2 appearance power | L2输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L2 Input Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.72 | hwIntegratedUPSMainL3InputApparentPower | Input L3 appearance power | L3输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L3 Input Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.73 | hwIntegratedUPSMainL1InputInValidPower | Input L1 reactive power | L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L1 Input Invalid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.74 | hwIntegratedUPSMainL2InputInValidPower | Input L2 reactive power | L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L2 Input Invalid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.75 | hwIntegratedUPSMainL3InputInValidPower | Input L3 reactive power | L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L3 Input Invalid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.76 | hwIntegratedUPSMainL1InputPowerFactor | Input L1 power factor | L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main L1 Input Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.77 | hwIntegratedUPSMainL2InputPowerFactor | Input L2 power factor | L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main L2 Input Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.78 | hwIntegratedUPSMainL3InputPowerFactor | Input L3 power factor | L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main L3 Input Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.79 | hwIntegratedUPSMainInputValidEnergy | Input L1 active energy | 输入有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Main Input Valid Energy of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.80 | hwIntegratedUPSMainL1InputLoadfactor | Input L1 power load rate | L1输入电源带载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main L1 Input Load Factor of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.81 | hwIntegratedUPSMainL2InputLoadfactor | Input L2 power load rate | L2输入电源带载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main L2 Input Load Factor of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.82 | hwIntegratedUPSMainL3InputLoadfactor | Input L3 power load rate | L3输入电源带载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main L3 Input Load Factor of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.83 | hwIntegratedUPSMainL1CurrHarmonic | L1 THDi | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L1 Curr Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.84 | hwIntegratedUPSMainL2CurrHarmonic | L2 THDi | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L2 Curr Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.85 | hwIntegratedUPSMainL3CurrHarmonic | L3 THDi | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L3 Curr Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.86 | hwIntegratedUPSMainL1VoltHarmonic | L1 THDu | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L1 Volt Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.87 | hwIntegratedUPSMainL2VoltHarmonic | L2 THDu | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L2 Volt Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.88 | hwIntegratedUPSMainL3VoltHarmonic | L3 THDu | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L3 Volt Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.89 | hwIntegratedUPSMainInputTotalValidPower | Total input active power | 总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main Input Total Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.90 | hwIntegratedUPSMainInputTotalApparentPower | Total input apparent power | 总输入视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main Input Total Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.91 | hwIntegratedUPSMainInputTotalInvalidPower | Total input reactive power | 总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main Input Total Invalid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.92 | hwIntegratedUPSOutputBarUTemp | UPS output bar U temperature | UPS输出铜排U温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Output Temp U of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.93 | hwIntegratedUPSOutputBarVTemp | UPS output bar V temperature | UPS输出铜排V温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Output Temp V of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.94 | hwIntegratedUPSMainIntputTemp | Mains input bar L3 temperature | 主路输入铜排L3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main Intput Temp of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.100 | hwIntegratedUPSRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.2 | hwIntegratedUPSRunning2Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.1 | hwIntegratedUPSRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.2 | hwIntegratedUPSModule1BusCapLife | Bus capacitor life (module 1) | 母线电容寿命 (模块1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module1 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.3 | hwIntegratedUPSModule2BusCapLife | Bus capacitor life (module 2) | 母线电容寿命 (模块2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module2 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.4 | hwIntegratedUPSModule3BusCapLife | Bus capacitor life (module 3) | 母线电容寿命 (模块3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module3 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.5 | hwIntegratedUPSModule4BusCapLife | Bus capacitor life (module 4) | 母线电容寿命 (模块4) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module4 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.6 | hwIntegratedUPSModule5BusCapLife | Bus capacitor life (module 5) | 母线电容寿命 (模块5) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module5 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.7 | hwIntegratedUPSModule6BusCapLife | Bus capacitor life (module 6) | 母线电容寿命 (模块6) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module6 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.8 | hwIntegratedUPSModule7BusCapLife | Bus capacitor life (module 7) | 母线电容寿命 (模块7) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module7 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.9 | hwIntegratedUPSModule8BusCapLife | Bus capacitor life (module 8) | 母线电容寿命 (模块8) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module8 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.10 | hwIntegratedUPSModule9BusCapLife | Bus capacitor life (module 9) | 母线电容寿命 (模块9) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module9 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.11 | hwIntegratedUPSModule10BusCapLife | Bus capacitor life (module 10) | 母线电容寿命 (模块10) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module10 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.12 | hwIntegratedUPSModule11BusCapLife | Bus capacitor life (module 11) | 母线电容寿命 (模块11) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module11 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.13 | hwIntegratedUPSModule12BusCapLife | Bus capacitor life (module 12) | 母线电容寿命 (模块12) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module12 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.14 | hwIntegratedUPSModule13BusCapLife | Bus capacitor life (module 13) | 母线电容寿命 (模块13) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module13 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.15 | hwIntegratedUPSModule14BusCapLife | Bus capacitor life (module 14) | 母线电容寿命 (模块14) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module14 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.16 | hwIntegratedUPSModule15BusCapLife | Bus capacitor life (module 15) | 母线电容寿命 (模块15) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module15 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.17 | hwIntegratedUPSModule16BusCapLife | Bus capacitor life (module 16) | 母线电容寿命 (模块16) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module16 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.18 | hwIntegratedUPSModule17BusCapLife | Bus capacitor life (module 17) | 母线电容寿命 (模块17) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module17 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.19 | hwIntegratedUPSModule18BusCapLife | Bus capacitor life (module 18) | 母线电容寿命 (模块18) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module18 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.20 | hwIntegratedUPSModule19BusCapLife | Bus capacitor life (module 19) | 母线电容寿命 (模块19) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module19 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.21 | hwIntegratedUPSModule20BusCapLife | Bus capacitor life (module 20) | 母线电容寿命 (模块20) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module20 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.100 | hwIntegratedUPSRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3 | hwIntegratedUPSRunning3Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.1 | hwIntegratedUPSRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.2 | hwIntegratedUPSIT1ValidPower1 | 1QF1 power(L1) | 1QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.3 | hwIntegratedUPSIT1ValidPower2 | 1QF2 power(L2) | 1QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.4 | hwIntegratedUPSIT1ValidPower3 | 1QF3 power(L3) | 1QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.5 | hwIntegratedUPSIT1ValidPower4 | 1QF4 power(L1) | 1QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.6 | hwIntegratedUPSIT1ValidPower5 | 1QF5 power(L2) | 1QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.7 | hwIntegratedUPSIT1ValidPower6 | 1QF6 power(L3) | 1QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.8 | hwIntegratedUPSIT1ValidPower7 | 1QF7 power(L1) | 1QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.9 | hwIntegratedUPSIT1ValidPower8 | 1QF8 power(L2) | 1QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.10 | hwIntegratedUPSIT1ValidPower9 | 1QF9 power(L3) | 1QF9 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.11 | hwIntegratedUPSIT1ValidPower10 | 1QF10 power(L1) | 1QF10 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.12 | hwIntegratedUPSIT1ValidPower11 | 1QF11 power(L2) | 1QF11 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.13 | hwIntegratedUPSIT1ValidPower12 | 1QF12 power(L3) | 1QF12 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.14 | hwIntegratedUPSIT1ValidPower13 | 1QF13 power(L1) | 1QF13 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.15 | hwIntegratedUPSIT1ValidPower14 | 1QF14 power(L2) | 1QF14 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.16 | hwIntegratedUPSIT1ValidPower15 | 1QF15 power(L3) | 1QF15 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.17 | hwIntegratedUPSIT1ValidPower16 | 1QF16 power(L1) | 1QF16 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.18 | hwIntegratedUPSIT1ValidPower17 | 1QF17 power(L2) | 1QF17 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.19 | hwIntegratedUPSIT1ValidPower18 | 1QF18 power(L3) | 1QF18 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.20 | hwIntegratedUPSIT1ValidPower19 | 1QF19 power(L1) | 1QF19 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.21 | hwIntegratedUPSIT1ValidPower20 | 1QF20 power(L2) | 1QF20 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.22 | hwIntegratedUPSIT1ValidPower21 | 1QF21 power(L3) | 1QF21 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.23 | hwIntegratedUPSIT1ValidPower22 | 1QF22 power(L1) | 1QF22 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.24 | hwIntegratedUPSIT1ValidPower23 | 1QF23 power(L2) | 1QF23 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.25 | hwIntegratedUPSIT1ValidPower24 | 1QF24 power(L3) | 1QF24 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.26 | hwIntegratedUPSIT1ValidEnergy1 | 1QF1 electricity energy(L1) | 1QF1 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.27 | hwIntegratedUPSIT1ValidEnergy2 | 1QF2 electricity energy(L2) | 1QF2 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.28 | hwIntegratedUPSIT1ValidEnergy3 | 1QF3 electricity energy(L3) | 1QF3 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.29 | hwIntegratedUPSIT1ValidEnergy4 | 1QF4 electricity energy(L1) | 1QF4 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.30 | hwIntegratedUPSIT1ValidEnergy5 | 1QF5 electricity energy(L2) | 1QF5 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.31 | hwIntegratedUPSIT1ValidEnergy6 | 1QF6 electricity energy(L3) | 1QF6 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.32 | hwIntegratedUPSIT1ValidEnergy7 | 1QF7 electricity energy(L1) | 1QF7 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.33 | hwIntegratedUPSIT1ValidEnergy8 | 1QF8 electricity energy(L2) | 1QF8 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.34 | hwIntegratedUPSIT1ValidEnergy9 | 1QF9 electricity energy(L3) | 1QF9 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.35 | hwIntegratedUPSIT1ValidEnergy10 | 1QF10 electricity energy(L1) | 1QF10 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.36 | hwIntegratedUPSIT1ValidEnergy11 | 1QF11 electricity energy(L2) | 1QF11 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.37 | hwIntegratedUPSIT1ValidEnergy12 | 1QF12 electricity energy(L3) | 1QF12 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.38 | hwIntegratedUPSIT1ValidEnergy13 | 1QF13 electricity energy(L1) | 1QF13 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.39 | hwIntegratedUPSIT1ValidEnergy14 | 1QF14 electricity energy(L2) | 1QF14 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.40 | hwIntegratedUPSIT1ValidEnergy15 | 1QF15 electricity energy(L3) | 1QF15 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.41 | hwIntegratedUPSIT1ValidEnergy16 | 1QF16 electricity energy(L1) | 1QF16 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.42 | hwIntegratedUPSIT1ValidEnergy17 | 1QF17 electricity energy(L2) | 1QF17 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.43 | hwIntegratedUPSIT1ValidEnergy18 | 1QF18 electricity energy(L3) | 1QF18 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.44 | hwIntegratedUPSIT1ValidEnergy19 | 1QF19 electricity energy(L1) | 1QF19 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.45 | hwIntegratedUPSIT1ValidEnergy20 | 1QF20 electricity energy(L2) | 1QF20 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.46 | hwIntegratedUPSIT1ValidEnergy21 | 1QF21 electricity energy(L3) | 1QF21 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.47 | hwIntegratedUPSIT1ValidEnergy22 | 1QF22 electricity energy(L1) | 1QF22 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.48 | hwIntegratedUPSIT1ValidEnergy23 | 1QF23 electricity energy(L2) | 1QF23 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.49 | hwIntegratedUPSIT1ValidEnergy24 | 1QF24 electricity energy(L3) | 1QF24 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.50 | hwIntegratedUPSIT1ValidTemp1 | 1QF1 temperature(L1) | 1QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.51 | hwIntegratedUPSIT1ValidTemp2 | 1QF2 temperature(L2) | 1QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.52 | hwIntegratedUPSIT1ValidTemp3 | 1QF3 temperature(L3) | 1QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.53 | hwIntegratedUPSIT1ValidTemp4 | 1QF4 temperature(L1) | 1QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.54 | hwIntegratedUPSIT1ValidTemp5 | 1QF5 temperature(L2) | 1QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.55 | hwIntegratedUPSIT1ValidTemp6 | 1QF6 temperature(L3) | 1QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.56 | hwIntegratedUPSIT1ValidTemp7 | 1QF7 temperature(L1) | 1QF7 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.57 | hwIntegratedUPSIT1ValidTemp8 | 1QF8 temperature(L2) | 1QF8 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.58 | hwIntegratedUPSIT1ValidTemp9 | 1QF9 temperature(L3) | 1QF9 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.59 | hwIntegratedUPSIT1ValidTemp10 | 1QF10 temperature(L1) | 1QF10 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.60 | hwIntegratedUPSIT1ValidTemp11 | 1QF11 temperature(L2) | 1QF11 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.61 | hwIntegratedUPSIT1ValidTemp12 | 1QF12 temperature(L3) | 1QF12 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.62 | hwIntegratedUPSIT1ValidTemp13 | 1QF13 temperature(L1) | 1QF13 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.63 | hwIntegratedUPSIT1ValidTemp14 | 1QF14 temperature(L2) | 1QF14 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.64 | hwIntegratedUPSIT1ValidTemp15 | 1QF15 temperature(L3) | 1QF15 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.65 | hwIntegratedUPSIT1ValidTemp16 | 1QF16 temperature(L1) | 1QF16 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.66 | hwIntegratedUPSIT1ValidTemp17 | 1QF17 temperature(L2) | 1QF17 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.67 | hwIntegratedUPSIT1ValidTemp18 | 1QF18 temperature(L3) | 1QF18 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.68 | hwIntegratedUPSIT1ValidTemp19 | 1QF19 temperature(L1) | 1QF19 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.69 | hwIntegratedUPSIT1ValidTemp20 | 1QF20 temperature(L2) | 1QF20 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.70 | hwIntegratedUPSIT1ValidTemp21 | 1QF21 temperature(L3) | 1QF21 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.71 | hwIntegratedUPSIT1ValidTemp22 | 1QF22 temperature(L1) | 1QF22 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.72 | hwIntegratedUPSIT1ValidTemp23 | 1QF23 temperature(L2) | 1QF23 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.73 | hwIntegratedUPSIT1ValidTemp24 | 1QF24 temperature(L3) | 1QF24 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.100 | hwIntegratedUPSRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4 | hwIntegratedUPSRunning4Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.1 | hwIntegratedUPSRunning4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.2 | hwIntegratedUPSIT2ValidPower1 | 2QF1 power(L1) | 2QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.3 | hwIntegratedUPSIT2ValidPower2 | 2QF2 power(L2) | 2QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.4 | hwIntegratedUPSIT2ValidPower3 | 2QF3 power(L3) | 2QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.5 | hwIntegratedUPSIT2ValidPower4 | 2QF4 power(L1) | 2QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.6 | hwIntegratedUPSIT2ValidPower5 | 2QF5 power(L2) | 2QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.7 | hwIntegratedUPSIT2ValidPower6 | 2QF6 power(L3) | 2QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.8 | hwIntegratedUPSIT2ValidPower7 | 2QF7 power(L1) | 2QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.9 | hwIntegratedUPSIT2ValidPower8 | 2QF8 power(L2) | 2QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.10 | hwIntegratedUPSIT2ValidPower9 | 2QF9 power(L3) | 2QF9 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.11 | hwIntegratedUPSIT2ValidPower10 | 2QF10 power(L1) | 2QF10 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.12 | hwIntegratedUPSIT2ValidPower11 | 2QF11 power(L2) | 2QF11 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.13 | hwIntegratedUPSIT2ValidPower12 | 2QF12 power(L3) | 2QF12 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.14 | hwIntegratedUPSIT2ValidPower13 | 2QF13 power(L1) | 2QF13 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.15 | hwIntegratedUPSIT2ValidPower14 | 2QF14 power(L2) | 2QF14 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.16 | hwIntegratedUPSIT2ValidPower15 | 2QF15 power(L3) | 2QF15 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.17 | hwIntegratedUPSIT2ValidPower16 | 2QF16 power(L1) | 2QF16 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.18 | hwIntegratedUPSIT2ValidPower17 | 2QF17 power(L2) | 2QF17 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.19 | hwIntegratedUPSIT2ValidPower18 | 2QF18 power(L3) | 2QF18 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.20 | hwIntegratedUPSIT2ValidPower19 | 2QF19 power(L1) | 2QF19 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.21 | hwIntegratedUPSIT2ValidPower20 | 2QF20 power(L2) | 2QF20 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.22 | hwIntegratedUPSIT2ValidPower21 | 2QF21 power(L3) | 2QF21 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.23 | hwIntegratedUPSIT2ValidPower22 | 2QF22 power(L1) | 2QF22 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.24 | hwIntegratedUPSIT2ValidPower23 | 2QF23 power(L2) | 2QF23 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.25 | hwIntegratedUPSIT2ValidPower24 | 2QF24 power(L3) | 2QF24 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.26 | hwIntegratedUPSIT2ValidEnergy1 | 2QF1 electricity energy(L1) | 2QF1 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.27 | hwIntegratedUPSIT2ValidEnergy2 | 2QF2 electricity energy(L2) | 2QF2 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.28 | hwIntegratedUPSIT2ValidEnergy3 | 2QF3 electricity energy(L3) | 2QF3 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.29 | hwIntegratedUPSIT2ValidEnergy4 | 2QF4 electricity energy(L1) | 2QF4 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.30 | hwIntegratedUPSIT2ValidEnergy5 | 2QF5 electricity energy(L2) | 2QF5 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.31 | hwIntegratedUPSIT2ValidEnergy6 | 2QF6 electricity energy(L3) | 2QF6 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.32 | hwIntegratedUPSIT2ValidEnergy7 | 2QF7 electricity energy(L1) | 2QF7 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.33 | hwIntegratedUPSIT2ValidEnergy8 | 2QF8 electricity energy(L2) | 2QF8 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.34 | hwIntegratedUPSIT2ValidEnergy9 | 2QF9 electricity energy(L3) | 2QF9 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.35 | hwIntegratedUPSIT2ValidEnergy10 | 2QF10 electricity energy(L1) | 2QF10 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.36 | hwIntegratedUPSIT2ValidEnergy11 | 2QF11 electricity energy(L2) | 2QF11 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.37 | hwIntegratedUPSIT2ValidEnergy12 | 2QF12 electricity energy(L3) | 2QF12 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.38 | hwIntegratedUPSIT2ValidEnergy13 | 2QF13 electricity energy(L1) | 2QF13 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.39 | hwIntegratedUPSIT2ValidEnergy14 | 2QF14 electricity energy(L2) | 2QF14 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.40 | hwIntegratedUPSIT2ValidEnergy15 | 2QF15 electricity energy(L3) | 2QF15 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.41 | hwIntegratedUPSIT2ValidEnergy16 | 2QF16 electricity energy(L1) | 2QF16 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.42 | hwIntegratedUPSIT2ValidEnergy17 | 2QF17 electricity energy(L2) | 2QF17 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.43 | hwIntegratedUPSIT2ValidEnergy18 | 2QF18 electricity energy(L3) | 2QF18 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.44 | hwIntegratedUPSIT2ValidEnergy19 | 2QF19 electricity energy(L1) | 2QF19 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.45 | hwIntegratedUPSIT2ValidEnergy20 | 2QF20 electricity energy(L2) | 2QF20 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.46 | hwIntegratedUPSIT2ValidEnergy21 | 2QF21 electricity energy(L3) | 2QF21 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.47 | hwIntegratedUPSIT2ValidEnergy22 | 2QF22 electricity energy(L1) | 2QF22 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.48 | hwIntegratedUPSIT2ValidEnergy23 | 2QF23 electricity energy(L2) | 2QF23 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.49 | hwIntegratedUPSIT2ValidEnergy24 | 2QF24 electricity energy(L3) | 2QF24 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.50 | hwIntegratedUPSIT2ValidTemp1 | 2QF1 temperature(L1) | 2QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.51 | hwIntegratedUPSIT2ValidTemp2 | 2QF2 temperature(L2) | 2QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.52 | hwIntegratedUPSIT2ValidTemp3 | 2QF3 temperature(L3) | 2QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.53 | hwIntegratedUPSIT2ValidTemp4 | 2QF4 temperature(L1) | 2QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.54 | hwIntegratedUPSIT2ValidTemp5 | 2QF5 temperature(L2) | 2QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.55 | hwIntegratedUPSIT2ValidTemp6 | 2QF6 temperature(L3) | 2QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.56 | hwIntegratedUPSIT2ValidTemp7 | 2QF7 temperature(L1) | 2QF7 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.57 | hwIntegratedUPSIT2ValidTemp8 | 2QF8 temperature(L2) | 2QF8 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.58 | hwIntegratedUPSIT2ValidTemp9 | 2QF9 temperature(L3) | 2QF9 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.59 | hwIntegratedUPSIT2ValidTemp10 | 2QF10 temperature(L1) | 2QF10 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.60 | hwIntegratedUPSIT2ValidTemp11 | 2QF11 temperature(L2) | 2QF11 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.61 | hwIntegratedUPSIT2ValidTemp12 | 2QF12 temperature(L3) | 2QF12 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.62 | hwIntegratedUPSIT2ValidTemp13 | 2QF13 temperature(L1) | 2QF13 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.63 | hwIntegratedUPSIT2ValidTemp14 | 2QF14 temperature(L2) | 2QF14 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.64 | hwIntegratedUPSIT2ValidTemp15 | 2QF15 temperature(L3) | 2QF15 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.65 | hwIntegratedUPSIT2ValidTemp16 | 2QF16 temperature(L1) | 2QF16 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.66 | hwIntegratedUPSIT2ValidTemp17 | 2QF17 temperature(L2) | 2QF17 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.67 | hwIntegratedUPSIT2ValidTemp18 | 2QF18 temperature(L3) | 2QF18 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.68 | hwIntegratedUPSIT2ValidTemp19 | 2QF19 temperature(L1) | 2QF19 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.69 | hwIntegratedUPSIT2ValidTemp20 | 2QF20 temperature(L2) | 2QF20 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.70 | hwIntegratedUPSIT2ValidTemp21 | 2QF21 temperature(L3) | 2QF21 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.71 | hwIntegratedUPSIT2ValidTemp22 | 2QF22 temperature(L1) | 2QF22 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.72 | hwIntegratedUPSIT2ValidTemp23 | 2QF23 temperature(L2) | 2QF23 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.73 | hwIntegratedUPSIT2ValidTemp24 | 2QF24 temperature(L3) | 2QF24 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.100 | hwIntegratedUPSRunning4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5 | hwIntegratedUPSRunning5Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.1 | hwIntegratedUPSRunning5Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.2 | hwIntegratedUPS3QF1Power | 3QF1 power(L1) | 3QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.3 | hwIntegratedUPS3QF2Power | 3QF1 power(L2) | 3QF1 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.4 | hwIntegratedUPS3QF3Power | 3QF1 power(L3) | 3QF1 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.5 | hwIntegratedUPS3QF4Power | 3QF2 power(L1) | 3QF2 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.6 | hwIntegratedUPS3QF5Power | 3QF2 power(L2) | 3QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.7 | hwIntegratedUPS3QF6Power | 3QF2 power(L3) | 3QF2 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.8 | hwIntegratedUPS3QF7Power | 3QF3 power(L1) | 3QF3 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.9 | hwIntegratedUPS3QF8Power | 3QF3 power(L2) | 3QF3 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.10 | hwIntegratedUPS3QF9Power | 3QF3 power(L3) | 3QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.11 | hwIntegratedUPS3QF10Power | 3QF4 power(L1) | 3QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.12 | hwIntegratedUPS3QF11Power | 3QF4 power(L2) | 3QF4 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.13 | hwIntegratedUPS3QF12Power | 3QF4 power(L3) | 3QF4 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.14 | hwIntegratedUPS3QF13Power | 3QF5 power(L1) | 3QF5 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.15 | hwIntegratedUPS3QF14Power | 3QF5 power(L2) | 3QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.16 | hwIntegratedUPS3QF15Power | 3QF5 power(L3) | 3QF5 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.17 | hwIntegratedUPS3QF16Power | 3QF6 power(L1) | 3QF6 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.18 | hwIntegratedUPS3QF17Power | 3QF6 power(L2) | 3QF6 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.19 | hwIntegratedUPS3QF18Power | 3QF6 power(L3) | 3QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.20 | hwIntegratedUPS3QF19Power | 3QF7 power(L1) | 3QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.21 | hwIntegratedUPS3QF20Power | 3QF7 power(L2) | 3QF7 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.22 | hwIntegratedUPS3QF21Power | 3QF7 power(L3) | 3QF7 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.23 | hwIntegratedUPS3QF22Power | 3QF8 power(L1) | 3QF8 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.24 | hwIntegratedUPS3QF23Power | 3QF8 power(L2) | 3QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.25 | hwIntegratedUPS3QF24Power | 3QF8 power(L3) | 3QF8 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.26 | hwIntegratedUPS3QF1ElectricityEnergy | 3QF1 electricity energy(L1) | 3QF1 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.27 | hwIntegratedUPS3QF2ElectricityEnergy | 3QF1 electricity energy(L2) | 3QF1 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.28 | hwIntegratedUPS3QF3ElectricityEnergy | 3QF1 electricity energy(L3) | 3QF1 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.29 | hwIntegratedUPS3QF4ElectricityEnergy | 3QF2 electricity energy(L1) | 3QF2 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.30 | hwIntegratedUPS3QF5ElectricityEnergy | 3QF2 electricity energy(L2) | 3QF2 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.31 | hwIntegratedUPS3QF6ElectricityEnergy | 3QF2 electricity energy(L3) | 3QF2 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.32 | hwIntegratedUPS3QF7ElectricityEnergy | 3QF3 electricity energy(L1) | 3QF3 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.33 | hwIntegratedUPS3QF8ElectricityEnergy | 3QF3 electricity energy(L2) | 3QF3 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.34 | hwIntegratedUPS3QF9ElectricityEnergy | 3QF3 electricity energy(L3) | 3QF3 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.35 | hwIntegratedUPS3QF10ElectricityEnergy | 3QF4 electricity energy(L1) | 3QF4 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.36 | hwIntegratedUPS3QF11ElectricityEnergy | 3QF4 electricity energy(L2) | 3QF4 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.37 | hwIntegratedUPS3QF12ElectricityEnergy | 3QF4 electricity energy(L3) | 3QF4 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.38 | hwIntegratedUPS3QF13ElectricityEnergy | 3QF5 electricity energy(L1) | 3QF5 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.39 | hwIntegratedUPS3QF14ElectricityEnergy | 3QF5 electricity energy(L2) | 3QF5 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.40 | hwIntegratedUPS3QF15ElectricityEnergy | 3QF5 electricity energy(L3) | 3QF5 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.41 | hwIntegratedUPS3QF16ElectricityEnergy | 3QF6 electricity energy(L1) | 3QF6 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.42 | hwIntegratedUPS3QF17ElectricityEnergy | 3QF6 electricity energy(L2) | 3QF6 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.43 | hwIntegratedUPS3QF18ElectricityEnergy | 3QF6 electricity energy(L3) | 3QF6 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.44 | hwIntegratedUPS3QF19ElectricityEnergy | 3QF7 electricity energy(L1) | 3QF7 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.45 | hwIntegratedUPS3QF20ElectricityEnergy | 3QF7 electricity energy(L2) | 3QF7 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.46 | hwIntegratedUPS3QF21ElectricityEnergy | 3QF7 electricity energy(L3) | 3QF7 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.47 | hwIntegratedUPS3QF22ElectricityEnergy | 3QF8 electricity energy(L1) | 3QF8 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.48 | hwIntegratedUPS3QF23ElectricityEnergy | 3QF8 electricity energy(L2) | 3QF8 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.49 | hwIntegratedUPS3QF24ElectricityEnergy | 3QF8 electricity energy(L3) | 3QF8 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.50 | hwIntegratedUPS3QF1Temperature | 3QF1 temperature(L1) | 3QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.51 | hwIntegratedUPS3QF2Temperature | 3QF1 temperature(L2) | 3QF1 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.52 | hwIntegratedUPS3QF3Temperature | 3QF1 temperature(L3) | 3QF1 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.53 | hwIntegratedUPS3QF4Temperature | 3QF2 temperature(L1) | 3QF2 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.54 | hwIntegratedUPS3QF5Temperature | 3QF2 temperature(L2) | 3QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.55 | hwIntegratedUPS3QF6Temperature | 3QF2 temperature(L3) | 3QF2 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.56 | hwIntegratedUPS3QF7Temperature | 3QF3 temperature(L1) | 3QF3 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.57 | hwIntegratedUPS3QF8Temperature | 3QF3 temperature(L2) | 3QF3 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.58 | hwIntegratedUPS3QF9Temperature | 3QF3 temperature(L3) | 3QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.59 | hwIntegratedUPS3QF10Temperature | 3QF4 temperature(L1) | 3QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.60 | hwIntegratedUPS3QF11Temperature | 3QF4 temperature(L2) | 3QF4 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.61 | hwIntegratedUPS3QF12Temperature | 3QF4 temperature(L3) | 3QF4 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.62 | hwIntegratedUPS3QF13Temperature | 3QF5 temperature(L1) | 3QF5 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.63 | hwIntegratedUPS3QF14Temperature | 3QF5 temperature(L2) | 3QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.64 | hwIntegratedUPS3QF15Temperature | 3QF5 temperature(L3) | 3QF5 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.65 | hwIntegratedUPS3QF16Temperature | 3QF6 temperature(L1) | 3QF6 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.66 | hwIntegratedUPS3QF17Temperature | 3QF6 temperature(L2) | 3QF6 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.67 | hwIntegratedUPS3QF18Temperature | 3QF6 temperature(L3) | 3QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.68 | hwIntegratedUPS3QF19Temperature | 3QF7 temperature(L1) | 3QF7 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.69 | hwIntegratedUPS3QF20Temperature | 3QF7 temperature(L2) | 3QF7 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.70 | hwIntegratedUPS3QF21Temperature | 3QF7 temperature(L3) | 3QF7 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.71 | hwIntegratedUPS3QF22Temperature | 3QF8 temperature(L1) | 3QF8 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.72 | hwIntegratedUPS3QF23Temperature | 3QF8 temperature(L2) | 3QF8 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.73 | hwIntegratedUPS3QF24Temperature | 3QF8 temperature(L3) | 3QF8 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.100 | hwIntegratedUPSRunning5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6 | hwIntegratedUPSConfigTable | / | / |  |  | / | / | The configtable of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6.1.1 | hwIntegratedUPSConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6.1.2 | hwIntegratedUPSFatherEquippduID | UPS related PDU device ID | UPS中记录的父设备配电柜的设备ID | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | Father Equippdu ID of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6.1.3 | hwIntegratedUPSDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6.1.100 | hwIntegratedUPSConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7 | hwIntegratedUPSRunning6Table | / | / |  |  | / | / | The running and config table of Intergrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.1 | hwIntegratedUPSRunning6Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table of Intergrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.2 | hwIntegratedUPSAIRValidPower1 | 3QF1 power(L1) | 3QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF1 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.3 | hwIntegratedUPSAIRValidPower2 | 3QF1 power(L2) | 3QF1 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF2 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.4 | hwIntegratedUPSAIRValidPower3 | 3QF1 power(L3) | 3QF1 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF3 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.5 | hwIntegratedUPSAIRValidPower4 | 3QF2 power(L1) | 3QF2 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF4 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.6 | hwIntegratedUPSAIRValidPower5 | 3QF2 power(L2) | 3QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF5 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.7 | hwIntegratedUPSAIRValidPower6 | 3QF2 power(L3) | 3QF2 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF6 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.8 | hwIntegratedUPSAIRValidPower7 | 3QF3 power(L1) | 3QF3 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF7 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.9 | hwIntegratedUPSAIRValidPower8 | 3QF3 power(L2) | 3QF3 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF8 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.10 | hwIntegratedUPSAIRValidPower9 | 3QF3 power(L3) | 3QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF9 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.11 | hwIntegratedUPSAIRValidPower10 | 3QF4 power(L1) | 3QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF10 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.12 | hwIntegratedUPSAIRValidPower11 | 3QF4 power(L2) | 3QF4 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF11 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.13 | hwIntegratedUPSAIRValidPower12 | 3QF4 power(L3) | 3QF4 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF12 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.14 | hwIntegratedUPSAIRValidPower13 | 3QF5 power(L1) | 3QF5 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF13 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.15 | hwIntegratedUPSAIRValidPower14 | 3QF5 power(L2) | 3QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF14 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.16 | hwIntegratedUPSAIRValidPower15 | 3QF5 power(L3) | 3QF5 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF15 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.17 | hwIntegratedUPSAIRValidPower16 | 3QF6 power(L1) | 3QF6 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF16 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.18 | hwIntegratedUPSAIRValidPower17 | 3QF6 power(L2) | 3QF6 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF17 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.19 | hwIntegratedUPSAIRValidPower18 | 3QF6 power(L3) | 3QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF18 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.20 | hwIntegratedUPSAIRValidPower19 | 3QF7 power(L1) | 3QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF19 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.21 | hwIntegratedUPSAIRValidPower20 | 3QF7 power(L2) | 3QF7 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF20 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.22 | hwIntegratedUPSAIRValidPower21 | 3QF7 power(L3) | 3QF7 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF21 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.23 | hwIntegratedUPSAIRValidPower22 | 3QF8 power(L1) | 3QF8 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF22 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.24 | hwIntegratedUPSAIRValidPower23 | 3QF8 power(L2) | 3QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF23 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.25 | hwIntegratedUPSAIRValidPower24 | 3QF8 power(L3) | 3QF8 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF24 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.26 | hwIntegratedUPSAIRValidEnergy1 | 3QF1 electricity energy(L1) | 3QF1 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF1 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.27 | hwIntegratedUPSAIRValidEnergy2 | 3QF1 electricity energy(L2) | 3QF1 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF2 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.28 | hwIntegratedUPSAIRValidEnergy3 | 3QF1 electricity energy(L3) | 3QF1 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF3 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.29 | hwIntegratedUPSAIRValidEnergy4 | 3QF2 electricity energy(L1) | 3QF2 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF4 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.30 | hwIntegratedUPSAIRValidEnergy5 | 3QF2 electricity energy(L2) | 3QF2 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF5 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.31 | hwIntegratedUPSAIRValidEnergy6 | 3QF2 electricity energy(L3) | 3QF2 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF6 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.32 | hwIntegratedUPSAIRValidEnergy7 | 3QF3 electricity energy(L1) | 3QF3 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF7 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.33 | hwIntegratedUPSAIRValidEnergy8 | 3QF3 electricity energy(L2) | 3QF3 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF8 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.34 | hwIntegratedUPSAIRValidEnergy9 | 3QF3 electricity energy(L3) | 3QF3 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF9 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.35 | hwIntegratedUPSAIRValidEnergy10 | 3QF4 electricity energy(L1) | 3QF4 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF10 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.36 | hwIntegratedUPSAIRValidEnergy11 | 3QF4 electricity energy(L2) | 3QF4 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF11 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.37 | hwIntegratedUPSAIRValidEnergy12 | 3QF4 electricity energy(L3) | 3QF4 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF12 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.38 | hwIntegratedUPSAIRValidEnergy13 | 3QF5 electricity energy(L1) | 3QF5 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF13 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.39 | hwIntegratedUPSAIRValidEnergy14 | 3QF5 electricity energy(L2) | 3QF5 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF14 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.40 | hwIntegratedUPSAIRValidEnergy15 | 3QF5 electricity energy(L3) | 3QF5 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF15 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.41 | hwIntegratedUPSAIRValidEnergy16 | 3QF6 electricity energy(L1) | 3QF6 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF16 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.42 | hwIntegratedUPSAIRValidEnergy17 | 3QF6 electricity energy(L2) | 3QF6 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF17 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.43 | hwIntegratedUPSAIRValidEnergy18 | 3QF6 electricity energy(L3) | 3QF6 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF18 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.44 | hwIntegratedUPSAIRValidEnergy19 | 3QF7 electricity energy(L1) | 3QF7 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF19 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.45 | hwIntegratedUPSAIRValidEnergy20 | 3QF7 electricity energy(L2) | 3QF7 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF20 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.46 | hwIntegratedUPSAIRValidEnergy21 | 3QF7 electricity energy(L3) | 3QF7 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF21 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.47 | hwIntegratedUPSAIRValidEnergy22 | 3QF8 electricity energy(L1) | 3QF8 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF22 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.48 | hwIntegratedUPSAIRValidEnergy23 | 3QF8 electricity energy(L2) | 3QF8 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF23 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.49 | hwIntegratedUPSAIRValidEnergy24 | 3QF8 electricity energy(L3) | 3QF8 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF24 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.50 | hwIntegratedUPSAIRValidTemp1 | 3QF1 temperature(L1) | 3QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF1 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.51 | hwIntegratedUPSAIRValidTemp2 | 3QF1 temperature(L2) | 3QF1 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF2 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.52 | hwIntegratedUPSAIRValidTemp3 | 3QF1 temperature(L3) | 3QF1 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF3 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.53 | hwIntegratedUPSAIRValidTemp4 | 3QF2 temperature(L1) | 3QF2 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF4 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.54 | hwIntegratedUPSAIRValidTemp5 | 3QF2 temperature(L2) | 3QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF5 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.55 | hwIntegratedUPSAIRValidTemp6 | 3QF2 temperature(L3) | 3QF2 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF6 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.56 | hwIntegratedUPSAIRValidTemp7 | 3QF3 temperature(L1) | 3QF3 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF7 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.57 | hwIntegratedUPSAIRValidTemp8 | 3QF3 temperature(L2) | 3QF3 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF8 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.58 | hwIntegratedUPSAIRValidTemp9 | 3QF3 temperature(L3) | 3QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF9 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.59 | hwIntegratedUPSAIRValidTemp10 | 3QF4 temperature(L1) | 3QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF10 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.60 | hwIntegratedUPSAIRValidTemp11 | 3QF4 temperature(L2) | 3QF4 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF11 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.61 | hwIntegratedUPSAIRValidTemp12 | 3QF4 temperature(L3) | 3QF4 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF12 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.62 | hwIntegratedUPSAIRValidTemp13 | 3QF5 temperature(L1) | 3QF5 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF13 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.63 | hwIntegratedUPSAIRValidTemp14 | 3QF5 temperature(L2) | 3QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF14 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.64 | hwIntegratedUPSAIRValidTemp15 | 3QF5 temperature(L3) | 3QF5 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF15 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.65 | hwIntegratedUPSAIRValidTemp16 | 3QF6 temperature(L1) | 3QF6 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF16 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.66 | hwIntegratedUPSAIRValidTemp17 | 3QF6 temperature(L2) | 3QF6 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF17 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.67 | hwIntegratedUPSAIRValidTemp18 | 3QF6 temperature(L3) | 3QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF18 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.68 | hwIntegratedUPSAIRValidTemp19 | 3QF7 temperature(L1) | 3QF7 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF19 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.69 | hwIntegratedUPSAIRValidTemp20 | 3QF7 temperature(L2) | 3QF7 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF20 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.70 | hwIntegratedUPSAIRValidTemp21 | 3QF7 temperature(L3) | 3QF7 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF21 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.71 | hwIntegratedUPSAIRValidTemp22 | 3QF8 temperature(L1) | 3QF8 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF22 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.72 | hwIntegratedUPSAIRValidTemp23 | 3QF8 temperature(L2) | 3QF8 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF23 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.73 | hwIntegratedUPSAIRValidTemp24 | 3QF8 temperature(L3) | 3QF8 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF24 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.100 | hwIntegratedUPSRunning6RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8 | hwIntegratedUPSRunning7Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.1 | hwIntegratedUPSRunning7Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.2 | hwIntegratedUPSIT1Current1 | 1QF1 current(L1) | 1QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.3 | hwIntegratedUPSIT1Current2 | 1QF2 current(L2) | 1QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.4 | hwIntegratedUPSIT1Current3 | 1QF3 current(L3) | 1QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.5 | hwIntegratedUPSIT1Current4 | 1QF4 current(L1) | 1QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.6 | hwIntegratedUPSIT1Current5 | 1QF5 current(L2) | 1QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.7 | hwIntegratedUPSIT1Current6 | 1QF6 current(L3) | 1QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.8 | hwIntegratedUPSIT1Current7 | 1QF7 current(L1) | 1QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.9 | hwIntegratedUPSIT1Current8 | 1QF8 current(L2) | 1QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.10 | hwIntegratedUPSIT1Current9 | 1QF9 current(L3) | 1QF9 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.11 | hwIntegratedUPSIT1Current10 | 1QF10 current(L1) | 1QF10 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.12 | hwIntegratedUPSIT1Current11 | 1QF11 current(L2) | 1QF11 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.13 | hwIntegratedUPSIT1Current12 | 1QF12 current(L3) | 1QF12 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.14 | hwIntegratedUPSIT1Current13 | 1QF13 current(L1) | 1QF13 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.15 | hwIntegratedUPSIT1Current14 | 1QF14 current(L2) | 1QF14 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.16 | hwIntegratedUPSIT1Current15 | 1QF15 current(L3) | 1QF15 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.17 | hwIntegratedUPSIT1Current16 | 1QF16 current(L1) | 1QF16 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.18 | hwIntegratedUPSIT1Current17 | 1QF17 current(L2) | 1QF17 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.19 | hwIntegratedUPSIT1Current18 | 1QF18 current(L3) | 1QF18 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.20 | hwIntegratedUPSIT1Current19 | 1QF19 current(L1) | 1QF19 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.21 | hwIntegratedUPSIT1Current20 | 1QF20 current(L2) | 1QF20 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.22 | hwIntegratedUPSIT1Current21 | 1QF21 current(L3) | 1QF21 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.23 | hwIntegratedUPSIT1Current22 | 1QF22 current(L1) | 1QF22 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.24 | hwIntegratedUPSIT1Current23 | 1QF23 current(L2) | 1QF23 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.25 | hwIntegratedUPSIT1Current24 | 1QF24 current(L3) | 1QF24 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.26 | hwIntegratedUPSIT1LoadFactor1 | 1QF1 load factor(L1) | 1QF1 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 1 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.27 | hwIntegratedUPSIT1LoadFactor2 | 1QF2 load factor(L2) | 1QF2 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 2 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.28 | hwIntegratedUPSIT1LoadFactor3 | 1QF3 load factor(L3) | 1QF3 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 3 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.29 | hwIntegratedUPSIT1LoadFactor4 | 1QF4 load factor(L1) | 1QF4 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 4 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.30 | hwIntegratedUPSIT1LoadFactor5 | 1QF5 load factor(L2) | 1QF5 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 5 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.31 | hwIntegratedUPSIT1LoadFactor6 | 1QF6 load factor(L3) | 1QF6 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 6 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.32 | hwIntegratedUPSIT1LoadFactor7 | 1QF7 load factor(L1) | 1QF7 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 7 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.33 | hwIntegratedUPSIT1LoadFactor8 | 1QF8 load factor(L2) | 1QF8 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 8 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.34 | hwIntegratedUPSIT1LoadFactor9 | 1QF9 load factor(L3) | 1QF9 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 9 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.35 | hwIntegratedUPSIT1LoadFactor10 | 1QF10 load factor(L1) | 1QF10 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 10 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.36 | hwIntegratedUPSIT1LoadFactor11 | 1QF11 load factor(L2) | 1QF11 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 11 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.37 | hwIntegratedUPSIT1LoadFactor12 | 1QF12 load factor(L3) | 1QF12 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 12 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.38 | hwIntegratedUPSIT1LoadFactor13 | 1QF13 load factor(L1) | 1QF13 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 13 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.39 | hwIntegratedUPSIT1LoadFactor14 | 1QF14 load factor(L2) | 1QF14 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 14 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.40 | hwIntegratedUPSIT1LoadFactor15 | 1QF15 load factor(L3) | 1QF15 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 15 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.41 | hwIntegratedUPSIT1LoadFactor16 | 1QF16 load factor(L1) | 1QF16 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 16 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.42 | hwIntegratedUPSIT1LoadFactor17 | 1QF17 load factor(L2) | 1QF17 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 17 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.43 | hwIntegratedUPSIT1LoadFactor18 | 1QF18 load factor(L3) | 1QF18 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 18 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.44 | hwIntegratedUPSIT1LoadFactor19 | 1QF19 load factor(L1) | 1QF19 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 19 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.45 | hwIntegratedUPSIT1LoadFactor20 | 1QF20 load factor(L2) | 1QF20 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 20 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.46 | hwIntegratedUPSIT1LoadFactor21 | 1QF21 load factor(L3) | 1QF21 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 21 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.47 | hwIntegratedUPSIT1LoadFactor22 | 1QF22 load factor(L1) | 1QF22 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 22 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.48 | hwIntegratedUPSIT1LoadFactor23 | 1QF23 load factor(L2) | 1QF23 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 23 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.49 | hwIntegratedUPSIT1LoadFactor24 | 1QF24 load factor(L3) | 1QF24 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 24 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.50 | hwIntegratedUPSIT1SwitchStatus1 | 1QF1 switch status(L1) | 1QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 1 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.51 | hwIntegratedUPSIT1SwitchStatus2 | 1QF2 switch status(L2) | 1QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 2 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.52 | hwIntegratedUPSIT1SwitchStatus3 | 1QF3 switch status(L3) | 1QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 3 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.53 | hwIntegratedUPSIT1SwitchStatus4 | 1QF4 switch status(L1) | 1QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 4 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.54 | hwIntegratedUPSIT1SwitchStatus5 | 1QF5 switch status(L2) | 1QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 5 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.55 | hwIntegratedUPSIT1SwitchStatus6 | 1QF6 switch status(L3) | 1QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 6 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.56 | hwIntegratedUPSIT1SwitchStatus7 | 1QF7 switch status(L1) | 1QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 7 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.57 | hwIntegratedUPSIT1SwitchStatus8 | 1QF8 switch status(L2) | 1QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 8 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.58 | hwIntegratedUPSIT1SwitchStatus9 | 1QF9 switch status(L3) | 1QF9 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 9 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.59 | hwIntegratedUPSIT1SwitchStatus10 | 1QF10 switch status(L1) | 1QF10 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 10 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.60 | hwIntegratedUPSIT1SwitchStatus11 | 1QF11 switch status(L2) | 1QF11 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 11 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.61 | hwIntegratedUPSIT1SwitchStatus12 | 1QF12 switch status(L3) | 1QF12 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 12 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.62 | hwIntegratedUPSIT1SwitchStatus13 | 1QF13 switch status(L1) | 1QF13 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 13 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.63 | hwIntegratedUPSIT1SwitchStatus14 | 1QF14 switch status(L2) | 1QF14 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 14 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.64 | hwIntegratedUPSIT1SwitchStatus15 | 1QF15 switch status(L3) | 1QF15 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 15 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.65 | hwIntegratedUPSIT1SwitchStatus16 | 1QF16 switch status(L1) | 1QF16 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 16 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.66 | hwIntegratedUPSIT1SwitchStatus17 | 1QF17 switch status(L2) | 1QF17 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 17 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.67 | hwIntegratedUPSIT1SwitchStatus18 | 1QF18 switch status(L3) | 1QF18 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 18 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.68 | hwIntegratedUPSIT1SwitchStatus19 | 1QF19 switch status(L1) | 1QF19 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 19 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.69 | hwIntegratedUPSIT1SwitchStatus20 | 1QF20 switch status(L2) | 1QF20 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 20 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.70 | hwIntegratedUPSIT1SwitchStatus21 | 1QF21 switch status(L3) | 1QF21 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 21 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.71 | hwIntegratedUPSIT1SwitchStatus22 | 1QF22 switch status(L1) | 1QF22 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 22 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.72 | hwIntegratedUPSIT1SwitchStatus23 | 1QF23 switch status(L2) | 1QF23 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 23 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.73 | hwIntegratedUPSIT1SwitchStatus24 | 1QF24 switch status(L3) | 1QF24 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 24 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.100 | hwIntegratedUPSRunning7RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9 | hwIntegratedUPSRunning8Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.1 | hwIntegratedUPSRunning8Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.2 | hwIntegratedUPSIT2Current1 | 2QF1 current(L1) | 2QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.3 | hwIntegratedUPSIT2Current2 | 2QF2 current(L2) | 2QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.4 | hwIntegratedUPSIT2Current3 | 2QF3 current(L3) | 2QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.5 | hwIntegratedUPSIT2Current4 | 2QF4 current(L1) | 2QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.6 | hwIntegratedUPSIT2Current5 | 2QF5 current(L2) | 2QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.7 | hwIntegratedUPSIT2Current6 | 2QF6 current(L3) | 2QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.8 | hwIntegratedUPSIT2Current7 | 2QF7 current(L1) | 2QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.9 | hwIntegratedUPSIT2Current8 | 2QF8 current(L2) | 2QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.10 | hwIntegratedUPSIT2Current9 | 2QF9 current(L3) | 2QF9 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.11 | hwIntegratedUPSIT2Current10 | 2QF10 current(L1) | 2QF10 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.12 | hwIntegratedUPSIT2Current11 | 2QF11 current(L2) | 2QF11 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.13 | hwIntegratedUPSIT2Current12 | 2QF12 current(L3) | 2QF12 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.14 | hwIntegratedUPSIT2Current13 | 2QF13 current(L1) | 2QF13 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.15 | hwIntegratedUPSIT2Current14 | 2QF14 current(L2) | 2QF14 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.16 | hwIntegratedUPSIT2Current15 | 2QF15 current(L3) | 2QF15 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.17 | hwIntegratedUPSIT2Current16 | 2QF16 current(L1) | 2QF16 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.18 | hwIntegratedUPSIT2Current17 | 2QF17 current(L2) | 2QF17 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.19 | hwIntegratedUPSIT2Current18 | 2QF18 current(L3) | 2QF18 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.20 | hwIntegratedUPSIT2Current19 | 2QF19 current(L1) | 2QF19 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.21 | hwIntegratedUPSIT2Current20 | 2QF20 current(L2) | 2QF20 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.22 | hwIntegratedUPSIT2Current21 | 2QF21 current(L3) | 2QF21 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.23 | hwIntegratedUPSIT2Current22 | 2QF22 current(L1) | 2QF22 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.24 | hwIntegratedUPSIT2Current23 | 2QF23 current(L2) | 2QF23 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.25 | hwIntegratedUPSIT2Current24 | 2QF24 current(L3) | 2QF24 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.26 | hwIntegratedUPSIT2LoadFactor1 | 2QF1 load factor(L1) | 2QF1 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 1 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.27 | hwIntegratedUPSIT2LoadFactor2 | 2QF2 load factor(L2) | 2QF2 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 2 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.28 | hwIntegratedUPSIT2LoadFactor3 | 2QF3 load factor(L3) | 2QF3 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 3 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.29 | hwIntegratedUPSIT2LoadFactor4 | 2QF4 load factor(L1) | 2QF4 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 4 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.30 | hwIntegratedUPSIT2LoadFactor5 | 2QF5 load factor(L2) | 2QF5 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 5 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.31 | hwIntegratedUPSIT2LoadFactor6 | 2QF6 load factor(L3) | 2QF6 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 6 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.32 | hwIntegratedUPSIT2LoadFactor7 | 2QF7 load factor(L1) | 2QF7 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 7 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.33 | hwIntegratedUPSIT2LoadFactor8 | 2QF8 load factor(L2) | 2QF8 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 8 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.34 | hwIntegratedUPSIT2LoadFactor9 | 2QF9 load factor(L3) | 2QF9 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 9 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.35 | hwIntegratedUPSIT2LoadFactor10 | 2QF10 load factor(L1) | 2QF10 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 10 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.36 | hwIntegratedUPSIT2LoadFactor11 | 2QF11 load factor(L2) | 2QF11 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 11 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.37 | hwIntegratedUPSIT2LoadFactor12 | 2QF12 load factor(L3) | 2QF12 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 12 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.38 | hwIntegratedUPSIT2LoadFactor13 | 2QF13 load factor(L1) | 2QF13 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 13 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.39 | hwIntegratedUPSIT2LoadFactor14 | 2QF14 load factor(L2) | 2QF14 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 14 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.40 | hwIntegratedUPSIT2LoadFactor15 | 2QF15 load factor(L3) | 2QF15 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 15 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.41 | hwIntegratedUPSIT2LoadFactor16 | 2QF16 load factor(L1) | 2QF16 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 16 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.42 | hwIntegratedUPSIT2LoadFactor17 | 2QF17 load factor(L2) | 2QF17 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 17 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.43 | hwIntegratedUPSIT2LoadFactor18 | 2QF18 load factor(L3) | 2QF18 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 18 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.44 | hwIntegratedUPSIT2LoadFactor19 | 2QF19 load factor(L1) | 2QF19 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 19 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.45 | hwIntegratedUPSIT2LoadFactor20 | 2QF20 load factor(L2) | 2QF20 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 20 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.46 | hwIntegratedUPSIT2LoadFactor21 | 2QF21 load factor(L3) | 2QF21 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 21 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.47 | hwIntegratedUPSIT2LoadFactor22 | 2QF22 load factor(L1) | 2QF22 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 22 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.48 | hwIntegratedUPSIT2LoadFactor23 | 2QF23 load factor(L2) | 2QF23 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 23 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.49 | hwIntegratedUPSIT2LoadFactor24 | 2QF24 load factor(L3) | 2QF24 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 24 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.50 | hwIntegratedUPSIT2SwitchStatus1 | 2QF1 switch status(L1) | 2QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 1 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.51 | hwIntegratedUPSIT2SwitchStatus2 | 2QF2 switch status(L2) | 2QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 2 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.52 | hwIntegratedUPSIT2SwitchStatus3 | 2QF3 switch status(L3) | 2QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 3 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.53 | hwIntegratedUPSIT2SwitchStatus4 | 2QF4 switch status(L1) | 2QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 4 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.54 | hwIntegratedUPSIT2SwitchStatus5 | 2QF5 switch status(L2) | 2QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 5 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.55 | hwIntegratedUPSIT2SwitchStatus6 | 2QF6 switch status(L3) | 2QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 6 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.56 | hwIntegratedUPSIT2SwitchStatus7 | 2QF7 switch status(L1) | 2QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 7 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.57 | hwIntegratedUPSIT2SwitchStatus8 | 2QF8 switch status(L2) | 2QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 8 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.58 | hwIntegratedUPSIT2SwitchStatus9 | 2QF9 switch status(L3) | 2QF9 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 9 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.59 | hwIntegratedUPSIT2SwitchStatus10 | 2QF10 switch status(L1) | 2QF10 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 10 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.60 | hwIntegratedUPSIT2SwitchStatus11 | 2QF11 switch status(L2) | 2QF11 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 11 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.61 | hwIntegratedUPSIT2SwitchStatus12 | 2QF12 switch status(L3) | 2QF12 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 12 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.62 | hwIntegratedUPSIT2SwitchStatus13 | 2QF13 switch status(L1) | 2QF13 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 13 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.63 | hwIntegratedUPSIT2SwitchStatus14 | 2QF14 switch status(L2) | 2QF14 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 14 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.64 | hwIntegratedUPSIT2SwitchStatus15 | 2QF15 switch status(L3) | 2QF15 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 15 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.65 | hwIntegratedUPSIT2SwitchStatus16 | 2QF16 switch status(L1) | 2QF16 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 16 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.66 | hwIntegratedUPSIT2SwitchStatus17 | 2QF17 switch status(L2) | 2QF17 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 17 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.67 | hwIntegratedUPSIT2SwitchStatus18 | 2QF18 switch status(L3) | 2QF18 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 18 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.68 | hwIntegratedUPSIT2SwitchStatus19 | 2QF19 switch status(L1) | 2QF19 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 19 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.69 | hwIntegratedUPSIT2SwitchStatus20 | 2QF20 switch status(L2) | 2QF20 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 20 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.70 | hwIntegratedUPSIT2SwitchStatus21 | 2QF21 switch status(L3) | 2QF21 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 21 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.71 | hwIntegratedUPSIT2SwitchStatus22 | 2QF22 switch status(L1) | 2QF22 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 22 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.72 | hwIntegratedUPSIT2SwitchStatus23 | 2QF23 switch status(L2) | 2QF23 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 23 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.73 | hwIntegratedUPSIT2SwitchStatus24 | 2QF24 switch status(L3) | 2QF24 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 24 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.100 | hwIntegratedUPSRunning8RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10 | hwIntegratedUPSRunning9Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.1 | hwIntegratedUPSRunning9Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.2 | hwIntegratedUPSAIRCurrent1 | 3QF1 current(L1) | 3QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.3 | hwIntegratedUPSAIRCurrent2 | 3QF1 current(L2) | 3QF1 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.4 | hwIntegratedUPSAIRCurrent3 | 3QF1 current(L3) | 3QF1 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.5 | hwIntegratedUPSAIRCurrent4 | 3QF2 current(L1) | 3QF2 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.6 | hwIntegratedUPSAIRCurrent5 | 3QF2 current(L2) | 3QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.7 | hwIntegratedUPSAIRCurrent6 | 3QF2 current(L3) | 3QF2 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.8 | hwIntegratedUPSAIRCurrent7 | 3QF3 current(L1) | 3QF3 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.9 | hwIntegratedUPSAIRCurrent8 | 3QF3 current(L2) | 3QF3 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.10 | hwIntegratedUPSAIRCurrent9 | 3QF3 current(L3) | 3QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.11 | hwIntegratedUPSAIRCurrent10 | 3QF4 current(L1) | 3QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.12 | hwIntegratedUPSAIRCurrent11 | 3QF4 current(L2) | 3QF4 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.13 | hwIntegratedUPSAIRCurrent12 | 3QF4 current(L3) | 3QF4 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.14 | hwIntegratedUPSAIRCurrent13 | 3QF5 current(L1) | 3QF5 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.15 | hwIntegratedUPSAIRCurrent14 | 3QF5 current(L2) | 3QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.16 | hwIntegratedUPSAIRCurrent15 | 3QF5 current(L3) | 3QF5 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.17 | hwIntegratedUPSAIRCurrent16 | 3QF6 current(L1) | 3QF6 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.18 | hwIntegratedUPSAIRCurrent17 | 3QF6 current(L2) | 3QF6 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.19 | hwIntegratedUPSAIRCurrent18 | 3QF6 current(L3) | 3QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.20 | hwIntegratedUPSAIRCurrent19 | 3QF7 current(L1) | 3QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.21 | hwIntegratedUPSAIRCurrent20 | 3QF7 current(L2) | 3QF7 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.22 | hwIntegratedUPSAIRCurrent21 | 3QF7 current(L3) | 3QF7 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.23 | hwIntegratedUPSAIRCurrent22 | 3QF8 current(L1) | 3QF8 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.24 | hwIntegratedUPSAIRCurrent23 | 3QF8 current(L2) | 3QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.25 | hwIntegratedUPSAIRCurrent24 | 3QF8 current(L3) | 3QF8 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.26 | hwIntegratedUPSAIRLoadFactor1 | 3QF1 load factor(L1) | 3QF1 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 1 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.27 | hwIntegratedUPSAIRLoadFactor2 | 3QF1 load factor(L2) | 3QF1 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 2 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.28 | hwIntegratedUPSAIRLoadFactor3 | 3QF1 load factor(L3) | 3QF1 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 3 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.29 | hwIntegratedUPSAIRLoadFactor4 | 3QF2 load factor(L1) | 3QF2 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 4 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.30 | hwIntegratedUPSAIRLoadFactor5 | 3QF2 load factor(L2) | 3QF2 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 5 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.31 | hwIntegratedUPSAIRLoadFactor6 | 3QF2 load factor(L3) | 3QF2 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 6 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.32 | hwIntegratedUPSAIRLoadFactor7 | 3QF3 load factor(L1) | 3QF3 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 7 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.33 | hwIntegratedUPSAIRLoadFactor8 | 3QF3 load factor(L2) | 3QF3 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 8 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.34 | hwIntegratedUPSAIRLoadFactor9 | 3QF3 load factor(L3) | 3QF3 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 9 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.35 | hwIntegratedUPSAIRLoadFactor10 | 3QF4 load factor(L1) | 3QF4 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 10 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.36 | hwIntegratedUPSAIRLoadFactor11 | 3QF4 load factor(L2) | 3QF4 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 11 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.37 | hwIntegratedUPSAIRLoadFactor12 | 3QF4 load factor(L3) | 3QF4 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 12 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.38 | hwIntegratedUPSAIRLoadFactor13 | 3QF5 load factor(L1) | 3QF5 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 13 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.39 | hwIntegratedUPSAIRLoadFactor14 | 3QF5 load factor(L2) | 3QF5 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 14 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.40 | hwIntegratedUPSAIRLoadFactor15 | 3QF5 load factor(L3) | 3QF5 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 15 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.41 | hwIntegratedUPSAIRLoadFactor16 | 3QF6 load factor(L1) | 3QF6 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 16 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.42 | hwIntegratedUPSAIRLoadFactor17 | 3QF6 load factor(L2) | 3QF6 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 17 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.43 | hwIntegratedUPSAIRLoadFactor18 | 3QF6 load factor(L3) | 3QF6 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 18 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.44 | hwIntegratedUPSAIRLoadFactor19 | 3QF7 load factor(L1) | 3QF7 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 19 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.45 | hwIntegratedUPSAIRLoadFactor20 | 3QF7 load factor(L2) | 3QF7 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 20 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.46 | hwIntegratedUPSAIRLoadFactor21 | 3QF7 load factor(L3) | 3QF7 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 21 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.47 | hwIntegratedUPSAIRLoadFactor22 | 3QF8 load factor(L1) | 3QF8 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 22 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.48 | hwIntegratedUPSAIRLoadFactor23 | 3QF8 load factor(L2) | 3QF8 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 23 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.49 | hwIntegratedUPSAIRLoadFactor24 | 3QF8 load factor(L3) | 3QF8 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 24 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.50 | hwIntegratedUPSAIRSwitchStatus1 | 3QF1 switch status(L1) | 3QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 1 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.51 | hwIntegratedUPSAIRSwitchStatus2 | 3QF1 switch status(L2) | 3QF1 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 2 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.52 | hwIntegratedUPSAIRSwitchStatus3 | 3QF1 switch status(L3) | 3QF1 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 3 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.53 | hwIntegratedUPSAIRSwitchStatus4 | 3QF2 switch status(L1) | 3QF2 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 4 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.54 | hwIntegratedUPSAIRSwitchStatus5 | 3QF2 switch status(L2) | 3QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 5 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.55 | hwIntegratedUPSAIRSwitchStatus6 | 3QF2 switch status(L3) | 3QF2 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 6 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.56 | hwIntegratedUPSAIRSwitchStatus7 | 3QF3 switch status(L1) | 3QF3 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 7 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.57 | hwIntegratedUPSAIRSwitchStatus8 | 3QF3 switch status(L2) | 3QF3 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 8 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.58 | hwIntegratedUPSAIRSwitchStatus9 | 3QF3 switch status(L3) | 3QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 9 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.59 | hwIntegratedUPSAIRSwitchStatus10 | 3QF4 switch status(L1) | 3QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 10 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.60 | hwIntegratedUPSAIRSwitchStatus11 | 3QF4 switch status(L2) | 3QF4 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 11 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.61 | hwIntegratedUPSAIRSwitchStatus12 | 3QF4 switch status(L3) | 3QF4 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 12 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.62 | hwIntegratedUPSAIRSwitchStatus13 | 3QF5 switch status(L1) | 3QF5 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 13 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.63 | hwIntegratedUPSAIRSwitchStatus14 | 3QF5 switch status(L2) | 3QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 14 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.64 | hwIntegratedUPSAIRSwitchStatus15 | 3QF5 switch status(L3) | 3QF5 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 15 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.65 | hwIntegratedUPSAIRSwitchStatus16 | 3QF6 switch status(L1) | 3QF6 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 16 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.66 | hwIntegratedUPSAIRSwitchStatus17 | 3QF6 switch status(L2) | 3QF6 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 17 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.67 | hwIntegratedUPSAIRSwitchStatus18 | 3QF6 switch status(L3) | 3QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 18 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.68 | hwIntegratedUPSAIRSwitchStatus19 | 3QF7 switch status(L1) | 3QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 19 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.69 | hwIntegratedUPSAIRSwitchStatus20 | 3QF7 switch status(L2) | 3QF7 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 20 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.70 | hwIntegratedUPSAIRSwitchStatus21 | 3QF7 switch status(L3) | 3QF7 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 21 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.71 | hwIntegratedUPSAIRSwitchStatus22 | 3QF8 switch status(L1) | 3QF8 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 22 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.72 | hwIntegratedUPSAIRSwitchStatus23 | 3QF8 switch status(L2) | 3QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 23 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.73 | hwIntegratedUPSAIRSwitchStatus24 | 3QF8 switch status(L3) | 3QF8 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 24 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.100 | hwIntegratedUPSRunning9RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11 | hwIntegratedUPSRunning10Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.1 | hwIntegratedUPSRunning10Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.2 | hwIntegratedUPSATS1inputL1phasevoltage | LN1 A phase voltage | LN1 A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.3 | hwIntegratedUPSATS1inputL2phasevoltage | LN1 B phase voltage | LN1 B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.4 | hwIntegratedUPSATS1inputL3phasevoltage | LN1 C phase voltage | LN1 C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.5 | hwIntegratedUPSATS1inputL1L2phasevoltage | LN1 AB line voltage | LN1 AB线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.6 | hwIntegratedUPSATS1inputL2L3phasevoltage | LN1 BC line voltage | LN1 BC线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.7 | hwIntegratedUPSATS1inputL3L1phasevoltage | LN1 CA line voltage | LN1 CA线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.8 | hwIntegratedUPSATS2inputL1phasevoltage | LN2 A phase voltage | LN2 A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.9 | hwIntegratedUPSATS2inputL2phasevoltage | LN2 B phase voltage | LN2 B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.10 | hwIntegratedUPSATS2inputL3phasevoltage | LN2 C phase voltage | LN2 C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.11 | hwIntegratedUPSATS2inputL1L2phasevoltage | LN2 AB line voltage | LN2 AB线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.12 | hwIntegratedUPSATS2inputL2L3phasevoltage | LN2 BC line voltage | LN2 BC线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.13 | hwIntegratedUPSATS2inputL3L1phasevoltage | LN2 CA line voltage | LN2 CA线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.14 | hwIntegratedUPSATS1InputFrequency | LN1 frequency | LN1 频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.15 | hwIntegratedUPSATS2InputFrequency | LN2 frequency | LN2 频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.16 | hwIntegratedUPSManualAutomaticStatus | Manual/Automatic | 手动/自动 | 0-Read_Only | 只读 | automatic(1), manual(2), unknown(255) | [自动=1]/[手动=2] | Manual Automatic Status. Value 1 indicates Automatic. Value 2 indicates Manual.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.17 | hwIntegratedUPSATS1Status | LN1 switch status | LN1 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | ATS1 Status. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.18 | hwIntegratedUPSATS2Status | LN2 switch status | LN2 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | ATS2 Status. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.19 | hwIntegratedUPSBatterySOH | Battery SOH | 电池SOH | 0-Read_Only | 只读 | good(1), maintain(2), abnormal(3), unknown(255) | [良好=1]/[需维护=2]/[异常=3] | Battery SOH of the device config table for the IntegratedUPSCabinet. Value 1 indicate good Value 2 indicate maintain Value 3 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.100 | hwIntegratedUPSRunning10RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.12 | hwIntegratedUPSRunning11Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.1 | hwIntegratedUPSRunning11Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.2 | hwIntegratedUPSATSLN1inputL1phasevoltage | LN1 A phase voltage | LN1 A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.3 | hwIntegratedUPSATSLN1inputL2phasevoltage | LN1 B phase voltage | LN1 B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.4 | hwIntegratedUPSATSLN1inputL3phasevoltage | LN1 C phase voltage | LN1 C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.5 | hwIntegratedUPSATSLN1inputL1L2phasevoltage | LN1 AB line voltage | LN1 AB线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.6 | hwIntegratedUPSATSLN1inputL2L3phasevoltage | LN1 BC line voltage | LN1 BC线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.7 | hwIntegratedUPSATSLN1inputL3L1phasevoltage | LN1 CA line voltage | LN1 CA线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.8 | hwIntegratedUPSATSLN2inputL1phasevoltage | LN2 A phase voltage | LN2 A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.9 | hwIntegratedUPSATSLN2inputL2phasevoltage | LN2 B phase voltage | LN2 B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.10 | hwIntegratedUPSATSLN2inputL3phasevoltage | LN2 C phase voltage | LN2 C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.11 | hwIntegratedUPSATSLN2inputL1L2phasevoltage | LN2 AB line voltage | LN2 AB线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.12 | hwIntegratedUPSATSLN2inputL2L3phasevoltage | LN2 BC line voltage | LN2 BC线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.13 | hwIntegratedUPSATSLN2inputL3L1phasevoltage | LN2 CA line voltage | LN2 CA线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.14 | hwIntegratedUPSATSLN1InputFrequency | LN1 frequency | LN1 频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.15 | hwIntegratedUPSATSLN2InputFrequency | LN2 frequency | LN2 频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.100 | hwIntegratedUPSRunning11RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13 | hwIntegratedUPSRunning12Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.1 | hwIntegratedUPSRunning12Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.2 | hwIntegratedUPSSystemCapacity | System capacity | 整机机型容量 | 0-Read_Only | 只读 | 20..2000 | 20..2000 | System capacity of the device config table for the Integrated UPS Cabinet.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.3 | hwIntegratedUPSAbInputLineVolt | AB input line volt. | AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | AB input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.4 | hwIntegratedUPSBcInputLineVolt | BC input line volt. | BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BC input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.5 | hwIntegratedUPSCaInputLineVolt | CA input line volt. | CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | CA input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.6 | hwIntegratedUPSBpmAbInputLineVolt | BPM AB input line volt. | 旁路AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM AB input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.7 | hwIntegratedUPSBpmBcInputLineVolt | BPM BC input line volt. | 旁路BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM BC input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.8 | hwIntegratedUPSBpmCaInputLineVolt | BPM CA input line volt. | 旁路CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM CA input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.9 | hwIntegratedUPSEnvironHumidity | Ambient humidity | 环境湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Environ Humidity of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.10 | hwIntegratedUPSBpmPhAInputCur | BPM ph. A input cur. | A相旁路输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM ph. A input cur. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.11 | hwIntegratedUPSBpmPhBInputCur | BPM ph. B input cur. | B相旁路输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM ph. B input cur. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.12 | hwIntegratedUPSBpmPhCInputCur | BPM ph. C input cur. | C相旁路输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM ph. C input cur. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.13 | hwIntegratedUPSRackAbOutLineVolt | Rack AB Out Line Volt. | 机架AB输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack AB Out Line Volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.14 | hwIntegratedUPSRackBcOutLineVolt | Rack BC Out Line Volt. | 机架BC输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack BC Out Line Volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.15 | hwIntegratedUPSRackCaOutLineVolt | Rack CA Out Line Volt. | 机架CA输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack CA Out Line Volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.16 | hwIntegratedUPSRackPhAOutputCurrCrestRatio | Rack ph. A output Curr. Crest ratio | 机架A相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack ph. A output Curr. Crest ratio of the device config table for the Integrated UPS Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.17 | hwIntegratedUPSRackPhBOutputCurrCrestRatio | Rack ph. B output Curr. Crest ratio | 机架B相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack ph. B output Curr. Crest ratio of the device config table for the Integrated UPS Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.18 | hwIntegratedUPSRackPhCOutputCurrCrestRatio | Rack ph. C output Curr. Crest ratio | 机架C相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack ph. C output Curr. Crest ratio of the device config table for the Integrated UPS Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.19 | hwIntegratedUPSSystemPhAOutputActivePower | System ph. A output active power | 系统A相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. A output active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.20 | hwIntegratedUPSSystemPhBOutputActivePower | System ph. B output active power | 系统B相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. B output active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.21 | hwIntegratedUPSSystemPhCOutputActivePower | System ph. C output active power | 系统C相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. C output active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.22 | hwIntegratedUPSSystemPhAOutputApparentPower | System ph. A output apparent power | 系统A相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. A output apparent power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.23 | hwIntegratedUPSSystemPhBOutputApparentPower | System ph. B output apparent power | 系统B相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. B output apparent power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.24 | hwIntegratedUPSSystemPhCOutputApparentPower | System ph. C output apparent power | 系统C相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. C output apparent power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.101 | hwIntegratedUPSRunning12RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14 | hwIntegratedUPSRunning13Table | / | / |  |  | / | / | The running table of Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.1 | hwIntegratedUPSRunning13Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.2 | hwIntegratedUPSTotalActiveEnergyOfIt2BranchOutput | Total active energy of IT2 branch output | IT2支路输出总有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Total active energy of IT2 branch output of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.3 | hwIntegratedUPSTotalActiveEnergyOfIt1BranchOutput | Total active energy of IT1 branch output | IT1支路输出总有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Total active energy of IT1 branch output of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.4 | hwIntegratedUPSTotalActiveEnergyOfLighting | Total active energy of lighting | 照明总有功电能 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total active energy of lighting of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.5 | hwIntegratedUPSBatteryRemainingCapacity | Battery remaining capacity | 电池剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery remaining capacity of the device config table for the Integrated UPS Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.6 | hwIntegratedUPSIsAtsSwitch | Is ATS switch | 是否为ATS配电开关 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Is ATS switch of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.7 | hwIntegratedUPSAirconNumber | Aircon number | 空调支路数目 | 0-Read_Only | 只读 | 0..24 | 0..24 | Aircon number of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.8 | hwIntegratedUPSIt2CabinetNumber | IT2 cabinet number | IT支路2数目 | 0-Read_Only | 只读 | 0..24 | 0..24 | IT2 cabinet number of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.9 | hwIntegratedUPSIt1CabinetNumber | IT1 cabinet number | IT支路1数目 | 0-Read_Only | 只读 | 0..24 | 0..24 | IT1 cabinet number of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.10 | hwIntegratedUPSBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 5..9999 | 5..9999 | Battery capacity of the device config table for the Integrated UPS Cabinet.SigUnitInfo:AH.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.11 | hwIntegratedUPSBatteryType | Battery type | 电池类型 | 0-Read_Only | 只读 | leadacidbattery(1), lithiumbattery(2), unknown(255) | [铅酸电池=1]/[锂电池=2] | Battery type of the device config table for the Integrated UPS Cabinet. Value 1 indicate lead-acid battery Value 2 indicate lithium battery
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.12 | hwIntegratedUPSUpsWorkMode | UPS work mode | UPS工作模式 | 0-Read_Only | 只读 | normalmode(1), eco(2), selfloadmode(3), convertermode(4), unknown(255) | [正常模式=1]/[ECO=2]/[自老化模式=3]/[变频器模式=4] | UPS work mode of the device config table for the Integrated UPS Cabinet. Value 1 indicate normal mode Value 2 indicate eco Value 3 indicate self-load mode Value 4 indicate converter mode
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.13 | hwIntegratedUPSCabinetVoltageLevel | Voltage level | 电压等级 | 0-Read_Only | 只读 | twoHundred(1), twoHundredAndEight(2), twoHundredAndTwenty(3), threeHundredAndEighty(4), fourHundred(5), fourHundredAndFifteen(6), fourHundredAndEighty(7), sixHundred(8), sixHundredAndNinety(9), threeHundredAndSixty(10), twoHundredAndThirty(11), fourHundredAndTwenty(12), twoHundredAndTen(13), unknown(255) | [200=1]/[208=2]/[220=3]/[380=4]/[400=5]/[415=6]/[480=7]/[600=8]/[690=9]/[360=10]/[230=11]/[420=12]/[210=13] | Voltage level of the device config table for the Integrated UPS Cabinet. Value 1 indicate 200 Value 2 indicate 208 Value 3 indicate 220 Value 4 indicate 380 Value 5 indicate 400 Value 6 indicate 415 Value 7 indicate 480 Value 8 indicate 600 Value 9 indicate 690 Value 10 indicate 360 Value 11 indicate 230 Value 12 indicate 420 Value 13 indicate 210SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.14 | hwIntegratedUPSCabinetSystemOutputFrequency | System output frequency | 系统输出频率 | 0-Read_Only | 只读 | fifty(1), sixty(2), unknown(255) | [50=1]/[60=2] | System output frequency of the device config table for the Integrated UPS Cabinet. Value 1 indicate 50 Value 2 indicate 60SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.15 | hwIntegratedUPSCabinetSchedShallowDisTest | Sched. shallow dis. test | 定时浅放电测试 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Sched. shallow dis. test of the device config table for the Integrated UPS Cabinet. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.16 | hwIntegratedUPSCabinetSchedShallowDisTestTime | Sched. shallow dis. test time | 定时浅放电测试时间段 | 1-Read_Write | 读写 | zeroToSixHourly(1), sixToTwelveHourly(2), twelveToEighteenHourly(3), eighteenToTwentyfourHourly(4), unknown(255) | [00:00~06:00=1]/[06:00~12:00=2]/[12:00~18:00=3]/[18:00~24:00=4] | Sched. shallow dis. test time of the device config table for the Integrated UPS Cabinet. Value 1 indicate 00:00~06:00 Value 2 indicate 06:00~12:00 Value 3 indicate 12:00~18:00 Value 4 indicate 18:00~24:00
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.17 | hwIntegratedUPSCabinetSchedShallowDisTestInterval | Sched. shallow dis. test interval | 定时浅放电测试间隔 | 1-Read_Write | 读写 | 30..90 | 30..90 | Sched. shallow dis. test interval of the device config table for the Integrated UPS Cabinet.SigUnitInfo:days.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.18 | hwIntegratedUPSCabinetShallowDisTestDisRatio | Shallow dis. test dis. ratio | 浅放电测试放电百分比 | 1-Read_Write | 读写 | 10..50 | 10..50 | Shallow dis. test dis. ratio of the device config table for the Integrated UPS Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.19 | hwIntegratedUPSCabinetSmartParallelSleepMode | Smart parallel sleep mode | 智能并机休眠模式 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Smart parallel sleep mode of the device config table for the Integrated UPS Cabinet. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.20 | hwIntegratedUPSBatterySOHPercentage | Battery SOH | 电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery SOH Percentage of the device config table for the Integrated UPS Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.22 | hwIntegratedUPSCabinetBpmInputL1PhaseVoltage | BPM input L1 phase voltage | 旁路L1输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM input L1 phase voltage of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.23 | hwIntegratedUPSCabinetBpmInputL2PhaseVoltage | BPM input L2 phase voltage | 旁路L2输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM input L2 phase voltage of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.24 | hwIntegratedUPSCabinetBpmInputL3PhaseVoltage | BPM input L3 phase voltage | 旁路L3输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM input L3 phase voltage of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.25 | hwIntegratedUPSCabinetBpmInputL1L2LineVoltage | BPM input L1-L2 line voltage | 旁路L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM input L1-L2 line voltage of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.26 | hwIntegratedUPSCabinetBpmInputL2L3LineVoltage | BPM input L2-L3 line voltage | 旁路L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM input L2-L3 line voltage of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.27 | hwIntegratedUPSCabinetBpmInputL3L1LineVoltage | BPM input L3-L1 line voltage | 旁路L3-L1输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM input L3-L1line voltage of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.28 | hwIntegratedUPSCabinetBpmInputL1Current | BPM input L1 current | 旁路L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | BPM input L1 current of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.29 | hwIntegratedUPSCabinetBpmInputL2Current | BPM input L2 current | 旁路L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | BPM input L2 current of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.30 | hwIntegratedUPSCabinetBpmInputL3Current | BPM input L3 current | 旁路L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | BPM input L3 current of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.31 | hwIntegratedUPSCabinetBpmMainsInputFrequency | BPM mains input frequency | 旁路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM mains input frequency of the device config table for the Integrated UPS Cabinet.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.32 | hwIntegratedUPSCabinetBpmInputL1ActivePower | BPM input L1 active power | 旁路L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L1 active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.33 | hwIntegratedUPSCabinetBpmInputL2ActivePower | BPM input L2 active power | 旁路L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L2 active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.34 | hwIntegratedUPSCabinetBpmInputL3ActivePower | BPM input L3 active power | 旁路L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L3 active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.35 | hwIntegratedUPSCabinetBpmInputL1AppearancePower | BPM input L1 appearance power | 旁路L1输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L1 appearance power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.36 | hwIntegratedUPSCabinetBpmInputL2AppearancePower | BPM input L2 appearance power | 旁路L2输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L2 appearance power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.37 | hwIntegratedUPSCabinetBpmInputL3AppearancePower | BPM input L3 appearance power | 旁路L3输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L3 appearance power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.38 | hwIntegratedUPSCabinetBpmInputL1ReactivePower | BPM input L1 reactive power | 旁路L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L1 reactive power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.39 | hwIntegratedUPSCabinetBpmInputL2ReactivePower | BPM input L2 reactive power | 旁路L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L2 reactive power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.40 | hwIntegratedUPSCabinetBpmInputL3ReactivePower | BPM input L3 reactive power | 旁路L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | BPM input L3 reactive power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.41 | hwIntegratedUPSCabinetBpmInputL1PowerFactor | BPM input L1 power factor | 旁路L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM input L1 power factor of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.42 | hwIntegratedUPSCabinetBpmInputL2PowerFactor | BPM input L2 power factor | 旁路L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM input L2 power factor of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.43 | hwIntegratedUPSCabinetBpmInputL3PowerFactor | BPM input L3 power factor | 旁路L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM input L3 power factor of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.44 | hwIntegratedUPSCabinetBpmInputL1PowerLoadRate | BPM input L1 power load rate | 旁路L1输入电源负载率 | 0-Read_Only | 只读 | 0..500 | 0..500 | BPM input L1 power load rate of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.45 | hwIntegratedUPSCabinetBpmInputL2PowerLoadRate | BPM input L2 power load rate | 旁路L2输入电源负载率 | 0-Read_Only | 只读 | 0..500 | 0..500 | BPM input L2 power load rate of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.46 | hwIntegratedUPSCabinetBpmInputL3PowerLoadRate | BPM input L3 power load rate | 旁路L3输入电源负载率 | 0-Read_Only | 只读 | 0..500 | 0..500 | BPM input L3 power load rate of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.47 | hwIntegratedUPSCabinetBpmL1Thdu | BPM L1 THDu | 旁路L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM L1 THDu of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.48 | hwIntegratedUPSCabinetBpmL2Thdu | BPM L2 THDu | 旁路L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM L2 THDu of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.49 | hwIntegratedUPSCabinetBpmL3Thdu | BPM L3 THDu | 旁路L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM L3 THDu of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.50 | hwIntegratedUPSCabinetBpmL1Thdi | BPM L1 THDi | 旁路L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM L1 THDi of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.51 | hwIntegratedUPSCabinetBpmL2Thdi | BPM L2 THDi | 旁路L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM L2 THDi of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.52 | hwIntegratedUPSCabinetBpmL3Thdi | BPM L3 THDi | 旁路L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM L3 THDi of the device config table for the Integrated UPS Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.53 | hwIntegratedUPSCabinetBpmTotalInputActivePower | BPM total input active power | 旁路总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | BPM total input active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.54 | hwIntegratedUPSCabinetBpmTotalInputApparentPower | BPM total input apparent power | 旁路总输入视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | BPM total input apparent power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.55 | hwIntegratedUPSCabinetBpmTotalInputReactivePower | BPM total input reactive power | 旁路总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | BPM total input reactive power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.56 | hwIntegratedUPSCabinetBpmInputActiveElectricityEnergy | BPM input active electricity energy | 旁路输入有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | BPM input active electricity energy of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.57 | hwIntegratedUPSCabinetUpsOutputBarPhaseWTemperature | UPS output bar phase W temp. | UPS输出铜排W相温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | UPS output bar phase W temperature of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.58 | hwIntegratedUPSCabinetUpsOutputBarPhaseNTemperature | UPS output bar phase N temp. | UPS输出铜排N相温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | UPS output bar phase N temperature of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.59 | hwIntegratedUPSCabinetUpsOutputCopperBarAmbientTemperature | UPS output copper bar ambient temperature | UPS输出铜排环境温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | UPS output copper bar ambient temperature of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.60 | hwIntegratedUPSCabinetBattNCopperBarTemp | Batt N copper bar temp | 电池N铜牌温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt N copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.61 | hwIntegratedUPSCabinetMainsInputACopperBarTemp | Mains input A copper bar temp | 主路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input A copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.62 | hwIntegratedUPSCabinetMainsInputBCopperBarTemp | Mains input B copper bar temp | 主路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input B copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.63 | hwIntegratedUPSCabinetMainsInputCCopperBarTemp | Mains input C copper bar temp | 主路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input C copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.64 | hwIntegratedUPSCabinetMainsInputNCopperBarTemp | Mains input N copper bar temp | 主路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input N copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.65 | hwIntegratedUPSCabinetMainsInputAmbientTemp | Mains input ambient temp | 主路输入环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input ambient temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.66 | hwIntegratedUPSCabinetOutputACopperBarTemp | Output A copper bar temp | 输出A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output A copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.67 | hwIntegratedUPSCabinetOutputBCopperBarTemp | Output B copper bar temp | 输出B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output B copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.68 | hwIntegratedUPSCabinetOutputCCopperBarTemp | Output C copper bar temp | 输出C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output C copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.69 | hwIntegratedUPSCabinetOutputNCopperBarTemp | Output N copper bar temp | 输出N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output N copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.70 | hwIntegratedUPSCabinetOutputAmbientTemp | Output ambient temp | 输出环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output ambient temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.71 | hwIntegratedUPSCabinetBypassInputACopperBarTemp | Bypass input A copper bar temp | 旁路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input A copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.72 | hwIntegratedUPSCabinetBypassInputBCopperBarTemp | Bypass input B copper bar temp | 旁路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input B copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.73 | hwIntegratedUPSCabinetBypassInputCCopperBarTemp | Bypass input C copper bar temp | 旁路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input C copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.74 | hwIntegratedUPSCabinetBypassInputNCopperBarTemp | Bypass input N copper bar temp | 旁路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input N copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.75 | hwIntegratedUPSCabinetBypassInputAmbientTemp | Bypass input ambient temp | 旁路输入环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input ambient temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.76 | hwIntegratedUPSCabinetBattPositCopperBarTemp | Batt+ copper bar temp | 电池正铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt posit copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.77 | hwIntegratedUPSCabinetBattNegativeCopperBarTemp | Batt– copper bar temp | 电池负铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt negative copper bar temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.78 | hwIntegratedUPSCabinetBattCopperBarAmbientTemp | Batt copper bar ambient temp | 电池铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt copper bar ambient temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.79 | hwIntegratedUPSCabinetOutputSwitchTemp | Output switch temp | 输出开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output switch temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.80 | hwIntegratedUPSCabinetBypassInputSwitchTemp | Bypass input switch temp | 旁路输入开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input switch temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.81 | hwIntegratedUPSCabinetMainsInputSwitchTemp | Mains input switch temp | 主路输入开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input switch temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.82 | hwIntegratedUPSCabinetMaintenanceBypassSwitchTemp | Maintenance bypass switch temp | 维修旁路开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Maintenance bypass switch temp of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.83 | hwIntegratedUPSCabinetMainTotalInputActivePower | Mains total input active power | 主路总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main total input active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.84 | hwIntegratedUPSCabinetMainTotalInputApparentPower | Mains total input apparent power | 主路总输入视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main total input apparent power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.85 | hwIntegratedUPSCabinetMainTotalInputReactivePower | Mains total input reactive power | 主路总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main total input reactive power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.86 | hwIntegratedUPSBpmInputAPowerFactor | BPM ph. A input power factor | 旁路A相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM Input A Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.87 | hwIntegratedUPSBpmInputBPowerFactor | BPM ph. B input power factor | 旁路B相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM Input B Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.88 | hwIntegratedUPSBpmInputCPowerFactor | BPM ph. C input power factor | 旁路C相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | BPM Input C Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.300 | hwIntegratedUPSRunning13RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Integrated UPS Cabinet.

## Lithium Battery
锂电池
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.132.1 | LithiumBattery | Lithium Battery | 锂电池 | / | / | / | / | Lithium Battery Equipment.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1 | hwLithiumBatteryRunningAndConfig1Table | / | / |  |  | / | / | The running table of Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.1 | hwLithiumBatteryRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.2 | hwLithiumBatterySampBatteryPackVoltage | Pack voltage | 电芯包电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Pack voltage of the device config table for the Lithium Battery.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.3 | hwLithiumBatterySampBatteryPackCurrent | Pack current | 电芯包电流 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Pack current of the device config table for the Lithium Battery.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.4 | hwLithiumBatterySampBackupTime | Backup time | 备电时间 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Backup time of the device config table for the Lithium Battery.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.5 | hwLithiumBatterySampBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery voltage of the device config table for the Lithium Battery.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.6 | hwLithiumBatterySampBatteryCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Battery current of the device config table for the Lithium Battery.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.7 | hwLithiumBatterySampRunningStatus | Running status | 运行状态 | 0-Read_Only | 只读 | invalid(1), running(2), hibernating(3), offline(4), standby(5), faulty(6), charging(7), discharging(8), unknown(255) | [无效=1]/[运行=2]/[休眠=3]/[离线=4]/[待机=5]/[故障=6]/[充电=7]/[放电=8] | Running status of the device config table for the Lithium Battery. Value 1 indicate invalid Value 2 indicate running Value 3 indicate hibernating Value 4 indicate offline Value 5 indicate standby Value 6 indicate faulty Value 7 indicate charging Value 8 indicate discharging
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.8 | hwLithiumBatterySampBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Battery capacity of the device config table for the Lithium Battery.Multiple:10.SigUnitInfo:AH.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.9 | hwLithiumBatterySampSoc | SOC | SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | SOC of the device config table for the Lithium Battery.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.10 | hwLithiumBatterySampSoh | SOH | SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | SOH of the device config table for the Lithium Battery.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.11 | hwLithiumBatterySampChargeorDischargePower | Charge/Discharge power | 充放电功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Charge/Discharge power of the device config table for the Lithium Battery.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.12 | hwLithiumBatterySampHighestCellTemperature | Highest cell temperature | 电芯最高温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Highest cell temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.13 | hwLithiumBatterySampLowestCellTemperature | Lowest cell temperature | 电芯最低温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Lowest cell temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.14 | hwLithiumBatterySampHighestCellVoltage | Highest cell voltage | 电芯最高电压 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Highest cell voltage of the device config table for the Lithium Battery.SigUnitInfo:mV.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.15 | hwLithiumBatterySampLowestCellVoltage | Lowest cell voltage | 电芯最低电压 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lowest cell voltage of the device config table for the Lithium Battery.SigUnitInfo:mV.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.16 | hwLithiumBatterySampCell1Voltage | Cell 1 voltage | 电芯1电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 1 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.17 | hwLithiumBatterySampCell2Voltage | Cell 2 voltage | 电芯2电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 2 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.18 | hwLithiumBatterySampCell3Voltage | Cell 3 voltage | 电芯3电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 3 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.19 | hwLithiumBatterySampCell4Voltage | Cell 4 voltage | 电芯4电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 4 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.20 | hwLithiumBatterySampCell5Voltage | Cell 5 voltage | 电芯5电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 5 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.21 | hwLithiumBatterySampCell6Voltage | Cell 6 voltage | 电芯6电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 6 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.22 | hwLithiumBatterySampCell7Voltage | Cell 7 voltage | 电芯7电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 7 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.23 | hwLithiumBatterySampCell8Voltage | Cell 8 voltage | 电芯8电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 8 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.24 | hwLithiumBatterySampCell9Voltage | Cell 9 voltage | 电芯9电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 9 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.25 | hwLithiumBatterySampCell10Voltage | Cell 10 voltage | 电芯10电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 10 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.26 | hwLithiumBatterySampCell11Voltage | Cell 11 voltage | 电芯11电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 11 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.27 | hwLithiumBatterySampCell12Voltage | Cell 12 voltage | 电芯12电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 12 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.28 | hwLithiumBatterySampCell13Voltage | Cell 13 voltage | 电芯13电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 13 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.29 | hwLithiumBatterySampCell14Voltage | Cell 14 voltage | 电芯14电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 14 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.30 | hwLithiumBatterySampCell15Voltage | Cell 15 voltage | 电芯15电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 15 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.31 | hwLithiumBatterySampCell16Voltage | Cell 16 voltage | 电芯16电压 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Cell 16 voltage of the device config table for the Lithium Battery.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.32 | hwLithiumBatterySampCell1Temperature | Cell 1 temperature | 电芯1温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 1 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.33 | hwLithiumBatterySampCell2Temperature | Cell 2 temperature | 电芯2温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 2 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.34 | hwLithiumBatterySampCell3Temperature | Cell 3 temperature | 电芯3温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 3 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.35 | hwLithiumBatterySampCell4Temperature | Cell 4 temperature | 电芯4温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 4 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.36 | hwLithiumBatterySampCell5Temperature | Cell 5 temperature | 电芯5温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 5 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.37 | hwLithiumBatterySampCell6Temperature | Cell 6 temperature | 电芯6温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 6 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.38 | hwLithiumBatterySampCell7Temperature | Cell 7 temperature | 电芯7温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 7 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.39 | hwLithiumBatterySampCell8Temperature | Cell 8 temperature | 电芯8温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 8 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.40 | hwLithiumBatterySampCell9Temperature | Cell 9 temperature | 电芯9温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 9 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.41 | hwLithiumBatterySampCell10Temperature | Cell 10 temperature | 电芯10温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 10 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.42 | hwLithiumBatterySampCell11Temperature | Cell 11 temperature | 电芯11温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 11 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.43 | hwLithiumBatterySampCell12Temperature | Cell 12 temperature | 电芯12温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 12 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.44 | hwLithiumBatterySampCell13Temperature | Cell 13 temperature | 电芯13温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 13 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.45 | hwLithiumBatterySampCell14Temperature | Cell 14 temperature | 电芯14温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 14 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.46 | hwLithiumBatterySampCell15Temperature | Cell 15 temperature | 电芯15温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 15 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.47 | hwLithiumBatterySampCell16Temperature | Cell 16 temperature | 电芯16温度 | 0-Read_Only | 只读 | -32767..32767 | -32767..32767 | Cell 16 temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.48 | hwLithiumBatterySampCopperBarPosTemperature | Copper bar (+) temperature | 铜牌正极温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Copper bar positive temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.49 | hwLithiumBatterySampCopperBarNegTemperature | Copper bar (–) temperature | 铜牌负极温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Copper bar negatives temperature of the device config table for the Lithium Battery.Multiple:100.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.50 | hwLithiumBatterySampBatteryInstallTime | Battery install time | 电池安装时间 | 0-Read_Only | 只读 |  |  | Battery install time of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.51 | hwLithiumBatterySampCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Lithium Battery. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.52 | hwLithiumBatterySampPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.53 | hwLithiumBatterySampModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.54 | hwLithiumBatterySampEsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.55 | hwLithiumBatterySampSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..30 | 0..30 | Software version of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.56 | hwLithiumBatterySampPowerSoftwareVersion | Power software version | 功率软件版本 | 0-Read_Only | 只读 | 0..30 | 0..30 | Power software version of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.57 | hwLithiumBatterySampELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.58 | hwLithiumBatterySampWifiSoftwareVersion | WiFi software version | WiFi软件版本 | 0-Read_Only | 只读 | 0..30 | 0..30 | Wifi software version of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.59 | hwLithiumBatterySetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Lithium Battery.
1.3.6.1.4.1.2011.6.178.1.1.132.1.1.1.300 | hwLithiumBatteryRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Lithium Battery.

## Smart MCCB
智能塑壳断路器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.15 | SmartMCCB | Smart MCCB | 智能塑壳断路器 | / | / | / | / | Smart MCCB Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1 | hwSmartMCCBRunningAndConfig1Table | / | / |  |  | / | / | The running table of Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.1 | hwSmartMCCBRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.2 | hwSmartMCCBL1PhaseVoltage | L1 phase voltage | L1相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 phase voltage of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.3 | hwSmartMCCBL1InputCopperBarTemperature | L1 input copper bar temperature | L1输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.4 | hwSmartMCCBCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Smart MCCB. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.5 | hwSmartMCCBPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.6 | hwSmartMCCBModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.7 | hwSmartMCCBL2PhaseVoltage | L2 phase voltage | L2相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 phase voltage of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.8 | hwSmartMCCBL3PhaseVoltage | L3 phase voltage | L3相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 phase voltage of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.9 | hwSmartMCCBL1L2LineVoltage | L1-L2 line voltage | L1-L2线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1-L2 line voltage of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.10 | hwSmartMCCBL2L3LineVoltage | L2-L3 line voltage | L2-L3线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2-L3 line voltage of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.11 | hwSmartMCCBL3L1LineVoltage | L3-L1 line voltage | L3-L1线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3-L1 line voltage of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.12 | hwSmartMCCBL1Current | L1 current | L1相电流 | 0-Read_Only | 只读 | 0..200000000 | 0..200000000 | L1 current of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.13 | hwSmartMCCBL2Current | L2 current | L2相电流 | 0-Read_Only | 只读 | 0..200000000 | 0..200000000 | L2 current of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.14 | hwSmartMCCBL3Current | L3 current | L3相电流 | 0-Read_Only | 只读 | 0..200000000 | 0..200000000 | L3 current of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.15 | hwSmartMCCBNCurrent | N current | N线电流 | 0-Read_Only | 只读 | 0..200000000 | 0..200000000 | N current of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.16 | hwSmartMCCBFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Frequency of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.17 | hwSmartMCCBL1ActivePower | L1 active power | L1有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 active power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.18 | hwSmartMCCBL2ActivePower | L2 active power | L2有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 active power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.19 | hwSmartMCCBL3ActivePower | L3 active power | L3有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 active power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.20 | hwSmartMCCBL1AppearancePower | L1 appearance power | L1视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 appearance power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.21 | hwSmartMCCBL2AppearancePower | L2 appearance power | L2视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 appearance power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.22 | hwSmartMCCBL3AppearancePower | L3 appearance power | L3视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 appearance power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.23 | hwSmartMCCBL1ReactivePower | L1 reactive power | L1无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 reactive power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.24 | hwSmartMCCBL2ReactivePower | L2 reactive power | L2无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 reactive power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.25 | hwSmartMCCBL3ReactivePower | L3 reactive power | L3无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 reactive power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.26 | hwSmartMCCBL1PowerFactor | L1 power factor | L1功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L1 power factor of the device config table for the Smart MCCB.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.27 | hwSmartMCCBL2PowerFactor | L2 power factor | L2功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L2 power factor of the device config table for the Smart MCCB.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.28 | hwSmartMCCBL3PowerFactor | L3 power factor | L3功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L3 power factor of the device config table for the Smart MCCB.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.29 | hwSmartMCCBTotalActiveEnergy | Total active energy | 总有功电能 | 0-Read_Only | 只读 | 0..200000000 | 0..200000000 | Total active energy of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.30 | hwSmartMCCBL1LoadRatio | L1 load ratio | L1负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L1 load ratio of the device config table for the Smart MCCB.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.31 | hwSmartMCCBL2LoadRatio | L2 load ratio | L2负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L2 load ratio of the device config table for the Smart MCCB.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.32 | hwSmartMCCBL3LoadRatio | L3 load ratio | L3负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L3 load ratio of the device config table for the Smart MCCB.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.33 | hwSmartMCCBL1ThdU | L1 THD-u | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-u of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.34 | hwSmartMCCBL2ThdU | L2 THD-u | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-u of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.35 | hwSmartMCCBL3ThdU | L3 THD-u | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-u of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.36 | hwSmartMCCBL1ThdI | L1 THD-i | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-i of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.37 | hwSmartMCCBL2ThdI | L2 THD-i | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-i of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.38 | hwSmartMCCBL3ThdI | L3 THD-i | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-i of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.39 | hwSmartMCCBTotalOutputActivePower | Total output active power | 总输出有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output active power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.40 | hwSmartMCCBTotalOutputAppearancePower | Total output appearance power | 总输出视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output appearance power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.41 | hwSmartMCCBTotalOutputReactivePower | Total output reactive power | 总输出无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output reactive power of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.42 | hwSmartMCCBL2InputCopperBarTemperature | L2 input copper bar temperature | L2输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.43 | hwSmartMCCBL3InputCopperBarTemperature | L3 input copper bar temperature | L3输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.44 | hwSmartMCCBL1OutputCopperBarTemperature | L1 output copper bar temperature | L1输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.45 | hwSmartMCCBL2OutputCopperBarTemperature | L2 output copper bar temperature | L2输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.46 | hwSmartMCCBL3OutputCopperBarTemperature | L3 output copper bar temperature | L3输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.47 | hwSmartMCCBCopperBarEnvironmentTemperature | Copper bar environment temperature | 铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Copper bar environment temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.48 | hwSmartMCCBL1OutputJointCopperBarTemperature | L1 output joint copper bar temperature | L1输出连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output joint copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.49 | hwSmartMCCBL2OutputJointCopperBarTemperature | L2 output joint copper bar temperature | L2输出连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output joint copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.50 | hwSmartMCCBL3OutputJointCopperBarTemperature | L3 output joint copper bar temperature | L3输出连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output joint copper bar temperature of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.51 | hwSmartMCCBSwitchStatus | Switch status | 开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [断开=1]/[闭合=2] | Switch status of the device config table for the Smart MCCB. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.52 | hwSmartMCCBTrippingStatus | Tripping status | 脱扣状态 | 0-Read_Only | 只读 | normal(1), tripping(2), unknown(255) | [正常=1]/[脱扣=2] | Tripping status of the device config table for the Smart MCCB. Value 1 indicate normal Value 2 indicate tripping
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.53 | hwSmartMCCBRunningIndicatorStatus | Running indicator status | 运行灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Running indicator status of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.54 | hwSmartMCCBAlarmIndicatorStatus | Alarm indicator status | 告警灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Alarm indicator status of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.55 | hwSmartMCCBAcInputSwitchIndicator | AC input switch indicator | AC输入开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC input switch indicator of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.56 | hwSmartMCCBAcOutputSwitchIndicator | AC output switch indicator | AC输出开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC output switch indicator of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.57 | hwSmartMCCBAbrasion | Abrasion | 磨损程度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Abrasion of the device config table for the Smart MCCB.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.58 | hwSmartMCCBTotalReactiveEnergy | Total reactive energy | 总无功电能 | 0-Read_Only | 只读 | 0..429496729 | 0..429496729 | Total reactive energy of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.59 | hwSmartMCCBOperations | Operations | 操作次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Operations of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.60 | hwSmartMCCBCircuitBreakerNumber | Circuit breaker number | 断路器序列号 | 0-Read_Only | 只读 | 0..16 | 0..16 | Circuit breaker number of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.61 | hwSmartMCCBCircuitBreakerName | Circuit breaker name | 断路器名称 | 0-Read_Only | 只读 | 0..16 | 0..16 | Circuit breaker name of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.62 | hwSmartMCCBTrippingRecordStorage | Tripping record storage | 脱扣记录储存 | 0-Read_Only | 只读 | 0..16 | 0..16 | Tripping record storage of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.63 | hwSmartMCCBDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Smart MCCB.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.64 | hwSmartMCCBRatedCurrent | Rated current | 额定电流设置 | 1-Read_Write | 读写 | 63..6300 | 63..6300 | Rated current of the device config table for the Smart MCCB.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.65 | hwSmartMCCBCircuitBreakerBusBarPhaseSequence | Circuit breaker bus bar phase sequence | 开关铜排相序 | 1-Read_Write | 读写 | undefined(1), positiveSequence(2), negativeSequence(3), unknown(255) | [未定义=1]/[正序=2]/[反序=3] | Circuit breaker bus bar phase sequence of the device config table for the Smart MCCB. Value 1 indicate undefined Value 2 indicate positive sequence Value 3 indicate negative sequence
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.66 | hwSmartMCCBRatedFrequency | Rated frequency | 额定频率 | 1-Read_Write | 读写 | 45..65 | 45..65 | Rated frequency of the device config table for the Smart MCCB.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.67 | hwSmartMCCBRatedVoltage | Rated voltage | 额定电压设置 | 1-Read_Write | 读写 | 100..480 | 100..480 | Rated voltage of the device config table for the Smart MCCB.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.68 | hwSmartMCCBProtectionMode | Protection mode | 保护模式 | 1-Read_Write | 读写 | bothSAndIAreDisabled(1), sIsEnabledAndIIsDisabled(2), sIsDisabledAndIIsEnabled(3), bothSAndIAreEnabled(4), unknown(255) | [S和I都不使能=1]/[S使能和I不使能=2]/[S不使能和I使能=3]/[S和I都使能=4] | Protection mode of the device config table for the Smart MCCB. Value 1 indicate bothSAndIAreDisabled Value 2 indicate sIsEnabledAndIIsDisabled Value 3 indicate sIsDisabledAndIIsEnabled Value 4 indicate bothSAndIAreEnabled
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.69 | hwSmartMCCBLongTimeDelayProtectionCurrentCoefficient | Long time delay protection current coefficient | 长延时保护电流系数 | 1-Read_Write | 读写 | 400..1000 | 400..1000 | Long time delay protection current coefficient of the device config table for the Smart MCCB.Multiple:1000.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.70 | hwSmartMCCBLongTimeDelayProtectionTime | Long time delay protection time | 长延时保护时间 | 1-Read_Write | 读写 | 300..4800 | 300..4800 | Long time delay protection time of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.71 | hwSmartMCCBShortTimeDelayProtectionCurrentCoefficient | Short time delay protection current coefficient | 短延时保护电流系数 | 1-Read_Write | 读写 | 60..1000 | 60..1000 | Short time delay protection current coefficient of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.72 | hwSmartMCCBShortTimeDelayProtectionTime | Short time delay protection time | 短延时保护时间 | 1-Read_Write | 读写 | 5..50 | 5..50 | Short time delay protection time of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.73 | hwSmartMCCBInstantaneousProtectionCurrent | Instantaneous protection current | 瞬时保护电流系数 | 1-Read_Write | 读写 | 150..1000 | 150..1000 | Instantaneous protection current of the device config table for the Smart MCCB.Multiple:100.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.74 | hwSmartMCCBElectricEnergyReset | Electric energy reset | 电能清除 | 1-Read_Write | 读写 | yes(1) | [是=1] | Electric energy reset of the device config table for the Smart MCCB. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.75 | hwSmartMCCBWearDegreeReset | Wear degree reset | 磨损程度清除 | 1-Read_Write | 读写 | yes(1) | [是=1] | Wear degree reset of the device config table for the Smart MCCB. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.76 | hwSmartMCCBTrippingRecordReset | Tripping record reset | 脱扣记录清除 | 1-Read_Write | 读写 | yes(1) | [是=1] | Tripping record reset of the device config table for the Smart MCCB. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.77 | hwSmartMCCBOpenPhaseThreshold | Open phase threshold | 缺相告警阈值 | 1-Read_Write | 读写 | 0..60 | 0..60 | Open phase threshold of the device config table for the Smart MCCB.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.78 | hwSmartMCCBHarmonicAlarm | Harmonic alarm | 谐波告警 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Harmonic alarm of the device config table for the Smart MCCB. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.79 | hwSmartMCCBVoltageHarmonicAlarmThreshold | Voltage harmonic alarm threshold | 电压谐波告警阈值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Voltage harmonic alarm threshold of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.80 | hwSmartMCCBCurrentHarmonicAlarmThreshold | Current harmonic alarm threshold | 电流谐波告警阈值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Current harmonic alarm threshold of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.81 | hwSmartMCCBOvervoltageThreshold | Overvoltage threshold | 过压告警阈值 | 1-Read_Write | 读写 | 1050..1300 | 1050..1300 | Overvoltage threshold of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.82 | hwSmartMCCBOvervoltageAcknowledgeTime | Overvoltage acknowledge time | 过压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overvoltage acknowledge time of the device config table for the Smart MCCB.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.83 | hwSmartMCCBUndervoltageThreshold | Undervoltage threshold | 欠压告警阈值 | 1-Read_Write | 读写 | 750..950 | 750..950 | Undervoltage threshold of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.84 | hwSmartMCCBUndervoltageAcknowledgeTime | Undervoltage acknowledge time | 欠压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Undervoltage acknowledge time of the device config table for the Smart MCCB.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.85 | hwSmartMCCBOverloadThreshold | Overload threshold | 负载过载阈值 | 1-Read_Write | 读写 | 100..120 | 100..120 | Overload threshold of the device config table for the Smart MCCB.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.86 | hwSmartMCCBOverloadAcknowledgeTime | Overload acknowledge time | 负载过载确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overload acknowledge time of the device config table for the Smart MCCB.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.87 | hwSmartMCCBOverfrequencyThreshold | Overfrequency threshold | 频率越限阈值 | 1-Read_Write | 读写 | 10..100 | 10..100 | Overfrequency threshold of the device config table for the Smart MCCB.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.88 | hwSmartMCCBOverfrequencyAcknowledgeTime | Overfrequency acknowledge time | 频率越限确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overfrequency acknowledge time of the device config table for the Smart MCCB.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.89 | hwSmartMCCBThreePhaseLoadImbalance | Three-phase load imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..50 | 0..50 | Three-phase load imbalance of the device config table for the Smart MCCB.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.90 | hwSmartMCCBOvercurrentThreshold | Overcurrent threshold | 电流高阈值 | 1-Read_Write | 读写 | 40..100 | 40..100 | Overcurrent threshold of the device config table for the Smart MCCB.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.91 | hwSmartMCCBUndercurrentThreshold | Undercurrent threshold | 电流低阈值 | 1-Read_Write | 读写 | 30..80 | 30..80 | Undercurrent threshold of the device config table for the Smart MCCB.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.15.1.1.300 | hwSmartMCCBRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Smart MCCB.

## YD-DEMS-VD2 DC Meter
YD-DEMS-VD2 直流电表
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.6 | YDDEMSVD2DCMeter | YD-DEMS-VD2 DC Meter | YD-DEMS-VD2 直流电表 | / | / | / | / | YD-DEMS-VD2 DC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1 | hwYDDEMSVD2DCMeterrRunningandConfig1Table | / | / |  |  | / | / | The running table of YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.1 | hwYDDEMSVD2DCMeterrRunningandConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.2 | hwYDDEMSVD2DCMeterInletCircuit1Voltage | Inlet circuit 1-voltage | 第1进线回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.3 | hwYDDEMSVD2DCMeterInletCircuit1Current | Inlet circuit 1-current | 第1进线回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.4 | hwYDDEMSVD2DCMeterInletCircuit1Power | Inlet circuit 1-power | 第1进线回路-功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-power of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.5 | hwYDDEMSVD2DCMeterInletCircuit1CombinedEnergy | Inlet circuit 1-combined energy | 第1进线回路-组合电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-combined energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.6 | hwYDDEMSVD2DCMeterInletCircuit1PositiveEnergy | Inlet circuit 1-positive energy | 第1进线回路-正向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-positive energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.7 | hwYDDEMSVD2DCMeterInletCircuit1NegativeEnergy | Inlet circuit 1-negative energy | 第1进线回路-反向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-negative energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.8 | hwYDDEMSVD2DCMeterInletCircuit1PowerRequired | Inlet circuit 1-power required | 第1进线回路-功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-power required of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.9 | hwYDDEMSVD2DCMeterInletCircuit1CurrentRequired | Inlet circuit 1-current required | 第1进线回路-电能需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-current required of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.10 | hwYDDEMSVD2DCMeterInletCircuit1VoltagePercentage | Inlet circuit 1-voltage percentage | 第1进线回路-电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-voltage percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.11 | hwYDDEMSVD2DCMeterInletCircuit1CurrentPercentage | Inlet circuit 1-current percentage | 第1进线回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.12 | hwYDDEMSVD2DCMeterInletCircuit1PositiveInsulationResistance | Inlet circuit 1-positive insulation resistance | 第1进线回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.13 | hwYDDEMSVD2DCMeterInletCircuit1NegativeInsulationResistance | Inlet circuit 1-negative insulation resistance | 第1进线回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.14 | hwYDDEMSVD2DCMeterInletCircuit1Temperature1 | Inlet circuit 1-temperature 1 | 第1进线回路-温度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-temperature 1 of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.15 | hwYDDEMSVD2DCMeterInletCircuit1Temperature2 | Inlet circuit 1-temperature 2 | 第1进线回路-温度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 1-temperature 2 of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.16 | hwYDDEMSVD2DCMeterInletCircuit2Voltage | Inlet circuit 2-voltage | 第2进线回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.17 | hwYDDEMSVD2DCMeterInletCircuit2Current | Inlet circuit 2-current | 第2进线回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.18 | hwYDDEMSVD2DCMeterInletCircuit2Power | Inlet circuit 2-power | 第2进线回路-功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-power of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.19 | hwYDDEMSVD2DCMeterInletCircuit2CombinedEnergy | Inlet circuit 2-combined energy | 第2进线回路-组合电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-combined energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.20 | hwYDDEMSVD2DCMeterInletCircuit2PositiveEnergy | Inlet circuit 2-positive energy | 第2进线回路-正向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-positive energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.21 | hwYDDEMSVD2DCMeterInletCircuit2NegativeEnergy | Inlet circuit 2-negative energy | 第2进线回路-反向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-negative energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.22 | hwYDDEMSVD2DCMeterInletCircuit2PowerRequired | Inlet circuit 2-power required | 第2进线回路-功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-power required of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.23 | hwYDDEMSVD2DCMeterInletCircuit2CurrentRequired | Inlet circuit 2-current required | 第2进线回路-电能需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-current required of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.24 | hwYDDEMSVD2DCMeterInletCircuit2VoltagePercentage | Inlet circuit 2-voltage percentage | 第2进线回路-电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-voltage percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.25 | hwYDDEMSVD2DCMeterInletCircuit2CurrentPercentage | Inlet circuit 2-current percentage | 第2进线回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.26 | hwYDDEMSVD2DCMeterInletCircuit2PositiveInsulationResistance | Inlet circuit 2-positive insulation resistance | 第2进线回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.27 | hwYDDEMSVD2DCMeterInletCircuit2NegativeInsulationResistance | Inlet circuit 2-negative insulation resistance | 第2进线回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.28 | hwYDDEMSVD2DCMeterInletCircuit2Temperature1 | Inlet circuit 2-temperature 1 | 第2进线回路-温度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-temperature 1 of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.29 | hwYDDEMSVD2DCMeterInletCircuit2Temperature2 | Inlet circuit 2-temperature 2 | 第2进线回路-温度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet circuit 2-temperature 2 of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.30 | hwYDDEMSVD2DCMeterMainCircuit1PrimarySwitchOf | Main circuit 1-primary switch OF | 第1主路主开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 1-primary switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.31 | hwYDDEMSVD2DCMeterMainCircuit1PrimarySwitchSd | Main circuit 1-primary switch SD | 第1主路主开关SD | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 1-primary switch SD of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.32 | hwYDDEMSVD2DCMeterMainCircuit1SpdSwitch | Main circuit 1-SPD switch | 第1主路防雷器开关 | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 1-SPD switch of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.33 | hwYDDEMSVD2DCMeterMainCircuit1SpdSwitchStatus | Main circuit 1-SPD switch status | 第1主路防雷状态 | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 1-SPD switch status of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.34 | hwYDDEMSVD2DCMeterMainCircuit1StandbySwitchStatus | Main circuit 1-standby switch status | 第1主路备用开关状态 | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 1-standby switch status of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.35 | hwYDDEMSVD2DCMeterMainCircuit1StandbySwitchSd | Main circuit 1-standby switch SD | 第1主路备用开关SD | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 1-standby switch SD of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.36 | hwYDDEMSVD2DCMeterMainCircuit2PrimarySwitchOf | Main circuit 2-primary switch OF | 第2主路主开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 2-primary switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.37 | hwYDDEMSVD2DCMeterMainCircuit2PrimarySwitchSd | Main circuit 2-primary switch SD | 第2主路主开关SD | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 2-primary switch SD of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.38 | hwYDDEMSVD2DCMeterMainCircuit2SpdSwitch | Main circuit 2-SPD switch | 第2主路防雷器开关 | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 2-SPD switch of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.39 | hwYDDEMSVD2DCMeterMainCircuit2SpdSwitchStatus | Main circuit 2-SPD switch status | 第2主路防雷状态 | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 2-SPD switch status of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.40 | hwYDDEMSVD2DCMeterMainCircuit2StandbySwitchStatus | Main circuit 2-standby switch status | 第2主路备用开关状态 | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 2-standby switch status of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.41 | hwYDDEMSVD2DCMeterMainCircuit2StandbySwitchSd | Main circuit 2-standby switch SD | 第2主路备用开关SD | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Main circuit 2-standby switch SD of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.42 | hwYDDEMSVD2DCMeterDo1Status | DO1 status | DO1状态 | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | DO1 status of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.43 | hwYDDEMSVD2DCMeterDo2Status | DO2 status | DO2状态 | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | DO2 status of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.44 | hwYDDEMSVD2DCMeterSystemRuntime | System runtime | 系统运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | System runtime of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.45 | hwYDDEMSVD2DCMeterBranch1SwitchOf | Branch 1 switch OF | 支路01开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 1 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.46 | hwYDDEMSVD2DCMeterBranch2SwitchOf | Branch 2 switch OF | 支路02开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 2 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.47 | hwYDDEMSVD2DCMeterBranch3SwitchOf | Branch 3 switch OF | 支路03开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 3 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.48 | hwYDDEMSVD2DCMeterBranch4SwitchOf | Branch 4 switch OF | 支路04开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 4 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.49 | hwYDDEMSVD2DCMeterBranch5SwitchOf | Branch 5 switch OF | 支路05开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 5 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.50 | hwYDDEMSVD2DCMeterBranch6SwitchOf | Branch 6 switch OF | 支路06开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 6 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.51 | hwYDDEMSVD2DCMeterBranch7SwitchOf | Branch 7 switch OF | 支路07开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 7 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.52 | hwYDDEMSVD2DCMeterBranch8SwitchOf | Branch 8 switch OF | 支路08开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 8 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.53 | hwYDDEMSVD2DCMeterBranch9SwitchOf | Branch 9 switch OF | 支路09开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 9 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.54 | hwYDDEMSVD2DCMeterBranch10SwitchOf | Branch 10 switch OF | 支路10开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 10 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.55 | hwYDDEMSVD2DCMeterBranch11SwitchOf | Branch 11 switch OF | 支路11开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 11 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.56 | hwYDDEMSVD2DCMeterBranch12SwitchOf | Branch 12 switch OF | 支路12开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 12 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.57 | hwYDDEMSVD2DCMeterBranch13SwitchOf | Branch 13 switch OF | 支路13开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 13 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.58 | hwYDDEMSVD2DCMeterBranch14SwitchOf | Branch 14 switch OF | 支路14开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 14 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.59 | hwYDDEMSVD2DCMeterBranch15SwitchOf | Branch 15 switch OF | 支路15开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 15 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.60 | hwYDDEMSVD2DCMeterBranch16SwitchOf | Branch 16 switch OF | 支路16开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 16 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.61 | hwYDDEMSVD2DCMeterBranch17SwitchOf | Branch 17 switch OF | 支路17开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 17 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.62 | hwYDDEMSVD2DCMeterBranch18SwitchOf | Branch 18 switch OF | 支路18开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 18 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.63 | hwYDDEMSVD2DCMeterBranch19SwitchOf | Branch 19 switch OF | 支路19开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 19 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.64 | hwYDDEMSVD2DCMeterBranch20SwitchOf | Branch 20 switch OF | 支路20开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 20 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.65 | hwYDDEMSVD2DCMeterBranch21SwitchOf | Branch 21 switch OF | 支路21开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 21 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.66 | hwYDDEMSVD2DCMeterBranch22SwitchOf | Branch 22 switch OF | 支路22开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 22 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.67 | hwYDDEMSVD2DCMeterBranch23SwitchOf | Branch 23 switch OF | 支路23开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 23 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.68 | hwYDDEMSVD2DCMeterBranch24SwitchOf | Branch 24 switch OF | 支路24开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 24 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.69 | hwYDDEMSVD2DCMeterBranch25SwitchOf | Branch 25 switch OF | 支路25开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 25 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.70 | hwYDDEMSVD2DCMeterBranch26SwitchOf | Branch 26 switch OF | 支路26开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 26 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.71 | hwYDDEMSVD2DCMeterBranch27SwitchOf | Branch 27 switch OF | 支路27开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 27 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.72 | hwYDDEMSVD2DCMeterBranch28SwitchOf | Branch 28 switch OF | 支路28开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 28 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.73 | hwYDDEMSVD2DCMeterBranch29SwitchOf | Branch 29 switch OF | 支路29开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 29 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.74 | hwYDDEMSVD2DCMeterBranch30SwitchOf | Branch 30 switch OF | 支路30开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 30 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.75 | hwYDDEMSVD2DCMeterBranch31SwitchOf | Branch 31 switch OF | 支路31开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 31 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.76 | hwYDDEMSVD2DCMeterBranch32SwitchOf | Branch 32 switch OF | 支路32开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 32 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.77 | hwYDDEMSVD2DCMeterBranch33SwitchOf | Branch 33 switch OF | 支路33开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 33 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.78 | hwYDDEMSVD2DCMeterBranch34SwitchOf | Branch 34 switch OF | 支路34开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 34 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.79 | hwYDDEMSVD2DCMeterBranch35SwitchOf | Branch 35 switch OF | 支路35开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 35 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.80 | hwYDDEMSVD2DCMeterBranch36SwitchOf | Branch 36 switch OF | 支路36开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 36 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.81 | hwYDDEMSVD2DCMeterBranch37SwitchOf | Branch 37 switch OF | 支路37开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 37 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.82 | hwYDDEMSVD2DCMeterBranch38SwitchOf | Branch 38 switch OF | 支路38开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 38 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.83 | hwYDDEMSVD2DCMeterBranch39SwitchOf | Branch 39 switch OF | 支路39开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 39 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.84 | hwYDDEMSVD2DCMeterBranch40SwitchOf | Branch 40 switch OF | 支路40开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 40 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.85 | hwYDDEMSVD2DCMeterBranch41SwitchOf | Branch 41 switch OF | 支路41开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 41 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.86 | hwYDDEMSVD2DCMeterBranch42SwitchOf | Branch 42 switch OF | 支路42开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 42 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.87 | hwYDDEMSVD2DCMeterBranch43SwitchOf | Branch 43 switch OF | 支路43开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 43 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.88 | hwYDDEMSVD2DCMeterBranch44SwitchOf | Branch 44 switch OF | 支路44开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 44 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.89 | hwYDDEMSVD2DCMeterBranch45SwitchOf | Branch 45 switch OF | 支路45开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 45 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.90 | hwYDDEMSVD2DCMeterBranch46SwitchOf | Branch 46 switch OF | 支路46开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 46 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.91 | hwYDDEMSVD2DCMeterBranch47SwitchOf | Branch 47 switch OF | 支路47开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 47 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.92 | hwYDDEMSVD2DCMeterBranch48SwitchOf | Branch 48 switch OF | 支路48开关OF | 0-Read_Only | 只读 | switchoff(1), switchon(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 48 switch OF of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate switchoff Value 2 indicate switchon
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.93 | hwYDDEMSVD2DCMeterFeederCircuit1Voltage | Feeder circuit 1-voltage | 第1路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 1-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.94 | hwYDDEMSVD2DCMeterFeederCircuit1Current | Feeder circuit 1-current | 第1路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 1-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.95 | hwYDDEMSVD2DCMeterFeederCircuit1CurrentPercentage | Feeder circuit 1-current percentage | 第1路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 1-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.96 | hwYDDEMSVD2DCMeterFeederCircuit1Power | Feeder circuit 1-power | 第1路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 1-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.97 | hwYDDEMSVD2DCMeterFeederCircuit1Energy | Feeder circuit 1-energy | 第1路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 1-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.98 | hwYDDEMSVD2DCMeterFeederCircuit1PositiveInsulationResistance | Feeder circuit 1-positive insulation resistance | 第1路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 1-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.99 | hwYDDEMSVD2DCMeterFeederCircuit1NegativeInsulationResistance | Feeder circuit 1-negative insulation resistance | 第1路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 1-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.100 | hwYDDEMSVD2DCMeterFeederCircuit2Voltage | Feeder circuit 2-voltage | 第2路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 2-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.101 | hwYDDEMSVD2DCMeterFeederCircuit2Current | Feeder circuit 2-current | 第2路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 2-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.102 | hwYDDEMSVD2DCMeterFeederCircuit2CurrentPercentage | Feeder circuit 2-current percentage | 第2路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 2-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.103 | hwYDDEMSVD2DCMeterFeederCircuit2Power | Feeder circuit 2-power | 第2路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 2-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.104 | hwYDDEMSVD2DCMeterFeederCircuit2Energy | Feeder circuit 2-energy | 第2路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 2-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.105 | hwYDDEMSVD2DCMeterFeederCircuit2PositiveInsulationResistance | Feeder circuit 2-positive insulation resistance | 第2路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 2-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.106 | hwYDDEMSVD2DCMeterFeederCircuit2NegativeInsulationResistance | Feeder circuit 2-negative insulation resistance | 第2路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 2-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.107 | hwYDDEMSVD2DCMeterFeederCircuit3Voltage | Feeder circuit 3-voltage | 第3路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 3-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.108 | hwYDDEMSVD2DCMeterFeederCircuit3Current | Feeder circuit 3-current | 第3路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 3-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.109 | hwYDDEMSVD2DCMeterFeederCircuit3CurrentPercentage | Feeder circuit 3-current percentage | 第3路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 3-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.110 | hwYDDEMSVD2DCMeterFeederCircuit3Power | Feeder circuit 3-power | 第3路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 3-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.111 | hwYDDEMSVD2DCMeterFeederCircuit3Energy | Feeder circuit 3-energy | 第3路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 3-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.112 | hwYDDEMSVD2DCMeterFeederCircuit3PositiveInsulationResistance | Feeder circuit 3-positive insulation resistance | 第3路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 3-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.113 | hwYDDEMSVD2DCMeterFeederCircuit3NegativeInsulationResistance | Feeder circuit 3-negative insulation resistance | 第3路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 3-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.114 | hwYDDEMSVD2DCMeterFeederCircuit4Voltage | Feeder circuit 4-voltage | 第4路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 4-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.115 | hwYDDEMSVD2DCMeterFeederCircuit4Current | Feeder circuit 4-current | 第4路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 4-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.116 | hwYDDEMSVD2DCMeterFeederCircuit4CurrentPercentage | Feeder circuit 4-current percentage | 第4路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 4-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.117 | hwYDDEMSVD2DCMeterFeederCircuit4Power | Feeder circuit 4-power | 第4路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 4-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.118 | hwYDDEMSVD2DCMeterFeederCircuit4Energy | Feeder circuit 4-energy | 第4路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 4-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.119 | hwYDDEMSVD2DCMeterFeederCircuit4PositiveInsulationResistance | Feeder circuit 4-positive insulation resistance | 第4路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 4-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.120 | hwYDDEMSVD2DCMeterFeederCircuit4NegativeInsulationResistance | Feeder circuit 4-negative insulation resistance | 第4路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 4-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.121 | hwYDDEMSVD2DCMeterFeederCircuit5Voltage | Feeder circuit 5-voltage | 第5路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 5-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.122 | hwYDDEMSVD2DCMeterFeederCircuit5Current | Feeder circuit 5-current | 第5路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 5-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.123 | hwYDDEMSVD2DCMeterFeederCircuit5CurrentPercentage | Feeder circuit 5-current percentage | 第5路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 5-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.124 | hwYDDEMSVD2DCMeterFeederCircuit5Power | Feeder circuit 5-power | 第5路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 5-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.125 | hwYDDEMSVD2DCMeterFeederCircuit5Energy | Feeder circuit 5-energy | 第5路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 5-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.126 | hwYDDEMSVD2DCMeterFeederCircuit5PositiveInsulationResistance | Feeder circuit 5-positive insulation resistance | 第5路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 5-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.127 | hwYDDEMSVD2DCMeterFeederCircuit5NegativeInsulationResistance | Feeder circuit 5-negative insulation resistance | 第5路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 5-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.128 | hwYDDEMSVD2DCMeterFeederCircuit6Voltage | Feeder circuit 6-voltage | 第6路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 6-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.129 | hwYDDEMSVD2DCMeterFeederCircuit6Current | Feeder circuit 6-current | 第6路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 6-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.130 | hwYDDEMSVD2DCMeterFeederCircuit6CurrentPercentage | Feeder circuit 6-current percentage | 第6路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 6-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.131 | hwYDDEMSVD2DCMeterFeederCircuit6Power | Feeder circuit 6-power | 第6路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 6-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.132 | hwYDDEMSVD2DCMeterFeederCircuit6Energy | Feeder circuit 6-energy | 第6路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 6-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.133 | hwYDDEMSVD2DCMeterFeederCircuit6PositiveInsulationResistance | Feeder circuit 6-positive insulation resistance | 第6路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 6-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.134 | hwYDDEMSVD2DCMeterFeederCircuit6NegativeInsulationResistance | Feeder circuit 6-negative insulation resistance | 第6路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 6-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.135 | hwYDDEMSVD2DCMeterFeederCircuit7Voltage | Feeder circuit 7-voltage | 第7路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 7-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.136 | hwYDDEMSVD2DCMeterFeederCircuit7Current | Feeder circuit 7-current | 第7路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 7-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.137 | hwYDDEMSVD2DCMeterFeederCircuit7CurrentPercentage | Feeder circuit 7-current percentage | 第7路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 7-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.138 | hwYDDEMSVD2DCMeterFeederCircuit7Power | Feeder circuit 7-power | 第7路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 7-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.139 | hwYDDEMSVD2DCMeterFeederCircuit7Energy | Feeder circuit 7-energy | 第7路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 7-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.140 | hwYDDEMSVD2DCMeterFeederCircuit7PositiveInsulationResistance | Feeder circuit 7-positive insulation resistance | 第7路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 7-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.141 | hwYDDEMSVD2DCMeterFeederCircuit7NegativeInsulationResistance | Feeder circuit 7-negative insulation resistance | 第7路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 7-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.142 | hwYDDEMSVD2DCMeterFeederCircuit8Voltage | Feeder circuit 8-voltage | 第8路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 8-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.143 | hwYDDEMSVD2DCMeterFeederCircuit8Current | Feeder circuit 8-current | 第8路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 8-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.144 | hwYDDEMSVD2DCMeterFeederCircuit8CurrentPercentage | Feeder circuit 8-current percentage | 第8路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 8-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.145 | hwYDDEMSVD2DCMeterFeederCircuit8Power | Feeder circuit 8-power | 第8路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 8-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.146 | hwYDDEMSVD2DCMeterFeederCircuit8Energy | Feeder circuit 8-energy | 第8路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 8-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.147 | hwYDDEMSVD2DCMeterFeederCircuit8PositiveInsulationResistance | Feeder circuit 8-positive insulation resistance | 第8路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 8-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.148 | hwYDDEMSVD2DCMeterFeederCircuit8NegativeInsulationResistance | Feeder circuit 8-negative insulation resistance | 第8路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 8-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.149 | hwYDDEMSVD2DCMeterFeederCircuit9Voltage | Feeder circuit 9-voltage | 第9路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 9-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.150 | hwYDDEMSVD2DCMeterFeederCircuit9Current | Feeder circuit 9-current | 第9路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 9-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.151 | hwYDDEMSVD2DCMeterFeederCircuit9CurrentPercentage | Feeder circuit 9-current percentage | 第9路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 9-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.152 | hwYDDEMSVD2DCMeterFeederCircuit9Power | Feeder circuit 9-power | 第9路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 9-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.153 | hwYDDEMSVD2DCMeterFeederCircuit9Energy | Feeder circuit 9-energy | 第9路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 9-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.154 | hwYDDEMSVD2DCMeterFeederCircuit9PositiveInsulationResistance | Feeder circuit 9-positive insulation resistance | 第9路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 9-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.155 | hwYDDEMSVD2DCMeterFeederCircuit9NegativeInsulationResistance | Feeder circuit 9-negative insulation resistance | 第9路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 9-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.156 | hwYDDEMSVD2DCMeterFeederCircuit10Voltage | Feeder circuit 10-voltage | 第10路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 10-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.157 | hwYDDEMSVD2DCMeterFeederCircuit10Current | Feeder circuit 10-current | 第10路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 10-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.158 | hwYDDEMSVD2DCMeterFeederCircuit10CurrentPercentage | Feeder circuit 10-current percentage | 第10路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 10-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.159 | hwYDDEMSVD2DCMeterFeederCircuit10Power | Feeder circuit 10-power | 第10路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 10-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.160 | hwYDDEMSVD2DCMeterFeederCircuit10Energy | Feeder circuit 10-energy | 第10路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 10-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.161 | hwYDDEMSVD2DCMeterFeederCircuit10PositiveInsulationResistance | Feeder circuit 10-positive insulation resistance | 第10路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 10-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.162 | hwYDDEMSVD2DCMeterFeederCircuit10NegativeInsulationResistance | Feeder circuit 10-negative insulation resistance | 第10路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 10-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.163 | hwYDDEMSVD2DCMeterFeederCircuit11Voltage | Feeder circuit 11-voltage | 第11路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 11-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.164 | hwYDDEMSVD2DCMeterFeederCircuit11Current | Feeder circuit 11-current | 第11路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 11-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.165 | hwYDDEMSVD2DCMeterFeederCircuit11CurrentPercentage | Feeder circuit 11-current percentage | 第11路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 11-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.166 | hwYDDEMSVD2DCMeterFeederCircuit11Power | Feeder circuit 11-power | 第11路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 11-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.167 | hwYDDEMSVD2DCMeterFeederCircuit11Energy | Feeder circuit 11-energy | 第11路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 11-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.168 | hwYDDEMSVD2DCMeterFeederCircuit11PositiveInsulationResistance | Feeder circuit 11-positive insulation resistance | 第11路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 11-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.169 | hwYDDEMSVD2DCMeterFeederCircuit11NegativeInsulationResistance | Feeder circuit 11-negative insulation resistance | 第11路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 11-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.170 | hwYDDEMSVD2DCMeterFeederCircuit12Voltage | Feeder circuit 12-voltage | 第12路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 12-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.171 | hwYDDEMSVD2DCMeterFeederCircuit12Current | Feeder circuit 12-current | 第12路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 12-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.172 | hwYDDEMSVD2DCMeterFeederCircuit12CurrentPercentage | Feeder circuit 12-current percentage | 第12路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 12-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.173 | hwYDDEMSVD2DCMeterFeederCircuit12Power | Feeder circuit 12-power | 第12路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 12-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.174 | hwYDDEMSVD2DCMeterFeederCircuit12Energy | Feeder circuit 12-energy | 第12路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 12-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.175 | hwYDDEMSVD2DCMeterFeederCircuit12PositiveInsulationResistance | Feeder circuit 12-positive insulation resistance | 第12路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 12-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.176 | hwYDDEMSVD2DCMeterFeederCircuit12NegativeInsulationResistance | Feeder circuit 12-negative insulation resistance | 第12路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 12-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.177 | hwYDDEMSVD2DCMeterFeederCircuit13Voltage | Feeder circuit 13-voltage | 第13路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 13-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.178 | hwYDDEMSVD2DCMeterFeederCircuit13Current | Feeder circuit 13-current | 第13路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 13-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.179 | hwYDDEMSVD2DCMeterFeederCircuit13CurrentPercentage | Feeder circuit 13-current percentage | 第13路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 13-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.180 | hwYDDEMSVD2DCMeterFeederCircuit13Power | Feeder circuit 13-power | 第13路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 13-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.181 | hwYDDEMSVD2DCMeterFeederCircuit13Energy | Feeder circuit 13-energy | 第13路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 13-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.182 | hwYDDEMSVD2DCMeterFeederCircuit13PositiveInsulationResistance | Feeder circuit 13-positive insulation resistance | 第13路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 13-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.183 | hwYDDEMSVD2DCMeterFeederCircuit13NegativeInsulationResistance | Feeder circuit 13-negative insulation resistance | 第13路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 13-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.184 | hwYDDEMSVD2DCMeterFeederCircuit14Voltage | Feeder circuit 14-voltage | 第14路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 14-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.185 | hwYDDEMSVD2DCMeterFeederCircuit14Current | Feeder circuit 14-current | 第14路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 14-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.186 | hwYDDEMSVD2DCMeterFeederCircuit14CurrentPercentage | Feeder circuit 14-current percentage | 第14路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 14-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.187 | hwYDDEMSVD2DCMeterFeederCircuit14Power | Feeder circuit 14-power | 第14路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 14-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.188 | hwYDDEMSVD2DCMeterFeederCircuit14Energy | Feeder circuit 14-energy | 第14路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 14-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.189 | hwYDDEMSVD2DCMeterFeederCircuit14PositiveInsulationResistance | Feeder circuit 14-positive insulation resistance | 第14路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 14-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.190 | hwYDDEMSVD2DCMeterFeederCircuit14NegativeInsulationResistance | Feeder circuit 14-negative insulation resistance | 第14路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 14-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.191 | hwYDDEMSVD2DCMeterFeederCircuit15Voltage | Feeder circuit 15-voltage | 第15路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 15-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.192 | hwYDDEMSVD2DCMeterFeederCircuit15Current | Feeder circuit 15-current | 第15路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 15-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.193 | hwYDDEMSVD2DCMeterFeederCircuit15CurrentPercentage | Feeder circuit 15-current percentage | 第15路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 15-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.194 | hwYDDEMSVD2DCMeterFeederCircuit15Power | Feeder circuit 15-power | 第15路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 15-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.195 | hwYDDEMSVD2DCMeterFeederCircuit15Energy | Feeder circuit 15-energy | 第15路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 15-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.196 | hwYDDEMSVD2DCMeterFeederCircuit15PositiveInsulationResistance | Feeder circuit 15-positive insulation resistance | 第15路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 15-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.197 | hwYDDEMSVD2DCMeterFeederCircuit15NegativeInsulationResistance | Feeder circuit 15-negative insulation resistance | 第15路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 15-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.198 | hwYDDEMSVD2DCMeterFeederCircuit16Voltage | Feeder circuit 16-voltage | 第16路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 16-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.199 | hwYDDEMSVD2DCMeterFeederCircuit16Current | Feeder circuit 16-current | 第16路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 16-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.200 | hwYDDEMSVD2DCMeterFeederCircuit16CurrentPercentage | Feeder circuit 16-current percentage | 第16路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 16-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.201 | hwYDDEMSVD2DCMeterFeederCircuit16Power | Feeder circuit 16-power | 第16路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 16-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.202 | hwYDDEMSVD2DCMeterFeederCircuit16Energy | Feeder circuit 16-energy | 第16路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 16-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.203 | hwYDDEMSVD2DCMeterFeederCircuit16PositiveInsulationResistance | Feeder circuit 16-positive insulation resistance | 第16路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 16-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.204 | hwYDDEMSVD2DCMeterFeederCircuit16NegativeInsulationResistance | Feeder circuit 16-negative insulation resistance | 第16路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 16-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.205 | hwYDDEMSVD2DCMeterFeederCircuit17Voltage | Feeder circuit 17-voltage | 第17路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 17-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.206 | hwYDDEMSVD2DCMeterFeederCircuit17Current | Feeder circuit 17-current | 第17路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 17-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.207 | hwYDDEMSVD2DCMeterFeederCircuit17CurrentPercentage | Feeder circuit 17-current percentage | 第17路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 17-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.208 | hwYDDEMSVD2DCMeterFeederCircuit17Power | Feeder circuit 17-power | 第17路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 17-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.209 | hwYDDEMSVD2DCMeterFeederCircuit17Energy | Feeder circuit 17-energy | 第17路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 17-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.210 | hwYDDEMSVD2DCMeterFeederCircuit17PositiveInsulationResistance | Feeder circuit 17-positive insulation resistance | 第17路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 17-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.211 | hwYDDEMSVD2DCMeterFeederCircuit17NegativeInsulationResistance | Feeder circuit 17-negative insulation resistance | 第17路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 17-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.212 | hwYDDEMSVD2DCMeterFeederCircuit18Voltage | Feeder circuit 18-voltage | 第18路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 18-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.213 | hwYDDEMSVD2DCMeterFeederCircuit18Current | Feeder circuit 18-current | 第18路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 18-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.214 | hwYDDEMSVD2DCMeterFeederCircuit18CurrentPercentage | Feeder circuit 18-current percentage | 第18路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 18-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.215 | hwYDDEMSVD2DCMeterFeederCircuit18Power | Feeder circuit 18-power | 第18路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 18-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.216 | hwYDDEMSVD2DCMeterFeederCircuit18Energy | Feeder circuit 18-energy | 第18路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 18-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.217 | hwYDDEMSVD2DCMeterFeederCircuit18PositiveInsulationResistance | Feeder circuit 18-positive insulation resistance | 第18路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 18-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.218 | hwYDDEMSVD2DCMeterFeederCircuit18NegativeInsulationResistance | Feeder circuit 18-negative insulation resistance | 第18路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 18-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.219 | hwYDDEMSVD2DCMeterFeederCircuit19Voltage | Feeder circuit 19-voltage | 第19路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 19-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.220 | hwYDDEMSVD2DCMeterFeederCircuit19Current | Feeder circuit 19-current | 第19路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 19-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.221 | hwYDDEMSVD2DCMeterFeederCircuit19CurrentPercentage | Feeder circuit 19-current percentage | 第19路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 19-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.222 | hwYDDEMSVD2DCMeterFeederCircuit19Power | Feeder circuit 19-power | 第19路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 19-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.223 | hwYDDEMSVD2DCMeterFeederCircuit19Energy | Feeder circuit 19-energy | 第19路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 19-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.224 | hwYDDEMSVD2DCMeterFeederCircuit19PositiveInsulationResistance | Feeder circuit 19-positive insulation resistance | 第19路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 19-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.225 | hwYDDEMSVD2DCMeterFeederCircuit19NegativeInsulationResistance | Feeder circuit 19-negative insulation resistance | 第19路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 19-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.226 | hwYDDEMSVD2DCMeterFeederCircuit20Voltage | Feeder circuit 20-voltage | 第20路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 20-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.227 | hwYDDEMSVD2DCMeterFeederCircuit20Current | Feeder circuit 20-current | 第20路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 20-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.228 | hwYDDEMSVD2DCMeterFeederCircuit20CurrentPercentage | Feeder circuit 20-current percentage | 第20路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 20-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.229 | hwYDDEMSVD2DCMeterFeederCircuit20Power | Feeder circuit 20-power | 第20路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 20-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.230 | hwYDDEMSVD2DCMeterFeederCircuit20Energy | Feeder circuit 20-energy | 第20路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 20-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.231 | hwYDDEMSVD2DCMeterFeederCircuit20PositiveInsulationResistance | Feeder circuit 20-positive insulation resistance | 第20路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 20-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.232 | hwYDDEMSVD2DCMeterFeederCircuit20NegativeInsulationResistance | Feeder circuit 20-negative insulation resistance | 第20路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 20-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.233 | hwYDDEMSVD2DCMeterFeederCircuit21Voltage | Feeder circuit 21-voltage | 第21路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 21-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.234 | hwYDDEMSVD2DCMeterFeederCircuit21Current | Feeder circuit 21-current | 第21路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 21-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.235 | hwYDDEMSVD2DCMeterFeederCircuit21CurrentPercentage | Feeder circuit 21-current percentage | 第21路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 21-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.236 | hwYDDEMSVD2DCMeterFeederCircuit21Power | Feeder circuit 21-power | 第21路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 21-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.237 | hwYDDEMSVD2DCMeterFeederCircuit21Energy | Feeder circuit 21-energy | 第21路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 21-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.238 | hwYDDEMSVD2DCMeterFeederCircuit21PositiveInsulationResistance | Feeder circuit 21-positive insulation resistance | 第21路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 21-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.239 | hwYDDEMSVD2DCMeterFeederCircuit21NegativeInsulationResistance | Feeder circuit 21-negative insulation resistance | 第21路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 21-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.240 | hwYDDEMSVD2DCMeterFeederCircuit22Voltage | Feeder circuit 22-voltage | 第22路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 22-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.241 | hwYDDEMSVD2DCMeterFeederCircuit22Current | Feeder circuit 22-current | 第22路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 22-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.242 | hwYDDEMSVD2DCMeterFeederCircuit22CurrentPercentage | Feeder circuit 22-current percentage | 第22路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 22-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.243 | hwYDDEMSVD2DCMeterFeederCircuit22Power | Feeder circuit 22-power | 第22路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 22-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.244 | hwYDDEMSVD2DCMeterFeederCircuit22Energy | Feeder circuit 22-energy | 第22路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 22-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.245 | hwYDDEMSVD2DCMeterFeederCircuit22PositiveInsulationResistance | Feeder circuit 22-positive insulation resistance | 第22路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 22-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.246 | hwYDDEMSVD2DCMeterFeederCircuit22NegativeInsulationResistance | Feeder circuit 22-negative insulation resistance | 第22路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 22-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.247 | hwYDDEMSVD2DCMeterFeederCircuit23Voltage | Feeder circuit 23-voltage | 第23路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 23-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.248 | hwYDDEMSVD2DCMeterFeederCircuit23Current | Feeder circuit 23-current | 第23路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 23-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.249 | hwYDDEMSVD2DCMeterFeederCircuit23CurrentPercentage | Feeder circuit 23-current percentage | 第23路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 23-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.250 | hwYDDEMSVD2DCMeterFeederCircuit23Power | Feeder circuit 23-power | 第23路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 23-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.251 | hwYDDEMSVD2DCMeterFeederCircuit23Energy | Feeder circuit 23-energy | 第23路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 23-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.252 | hwYDDEMSVD2DCMeterFeederCircuit23PositiveInsulationResistance | Feeder circuit 23-positive insulation resistance | 第23路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 23-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.253 | hwYDDEMSVD2DCMeterFeederCircuit23NegativeInsulationResistance | Feeder circuit 23-negative insulation resistance | 第23路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 23-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.254 | hwYDDEMSVD2DCMeterFeederCircuit24Voltage | Feeder circuit 24-voltage | 第24路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 24-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.255 | hwYDDEMSVD2DCMeterFeederCircuit24Current | Feeder circuit 24-current | 第24路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 24-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.256 | hwYDDEMSVD2DCMeterFeederCircuit24CurrentPercentage | Feeder circuit 24-current percentage | 第24路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 24-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.257 | hwYDDEMSVD2DCMeterFeederCircuit24Power | Feeder circuit 24-power | 第24路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 24-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.258 | hwYDDEMSVD2DCMeterFeederCircuit24Energy | Feeder circuit 24-energy | 第24路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 24-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.259 | hwYDDEMSVD2DCMeterFeederCircuit24PositiveInsulationResistance | Feeder circuit 24-positive insulation resistance | 第24路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 24-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.260 | hwYDDEMSVD2DCMeterFeederCircuit24NegativeInsulationResistance | Feeder circuit 24-negative insulation resistance | 第24路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 24-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.261 | hwYDDEMSVD2DCMeterFeederCircuit25Voltage | Feeder circuit 25-voltage | 第25路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 25-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.262 | hwYDDEMSVD2DCMeterFeederCircuit25Current | Feeder circuit 25-current | 第25路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 25-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.263 | hwYDDEMSVD2DCMeterFeederCircuit25CurrentPercentage | Feeder circuit 25-current percentage | 第25路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 25-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.264 | hwYDDEMSVD2DCMeterFeederCircuit25Power | Feeder circuit 25-power | 第25路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 25-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.265 | hwYDDEMSVD2DCMeterFeederCircuit25Energy | Feeder circuit 25-energy | 第25路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 25-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.266 | hwYDDEMSVD2DCMeterFeederCircuit25PositiveInsulationResistance | Feeder circuit 25-positive insulation resistance | 第25路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 25-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.267 | hwYDDEMSVD2DCMeterFeederCircuit25NegativeInsulationResistance | Feeder circuit 25-negative insulation resistance | 第25路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 25-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.268 | hwYDDEMSVD2DCMeterFeederCircuit26Voltage | Feeder circuit 26-voltage | 第26路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 26-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.269 | hwYDDEMSVD2DCMeterFeederCircuit26Current | Feeder circuit 26-current | 第26路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 26-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.270 | hwYDDEMSVD2DCMeterFeederCircuit26CurrentPercentage | Feeder circuit 26-current percentage | 第26路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 26-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.271 | hwYDDEMSVD2DCMeterFeederCircuit26Power | Feeder circuit 26-power | 第26路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 26-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.272 | hwYDDEMSVD2DCMeterFeederCircuit26Energy | Feeder circuit 26-energy | 第26路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 26-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.273 | hwYDDEMSVD2DCMeterFeederCircuit26PositiveInsulationResistance | Feeder circuit 26-positive insulation resistance | 第26路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 26-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.274 | hwYDDEMSVD2DCMeterFeederCircuit26NegativeInsulationResistance | Feeder circuit 26-negative insulation resistance | 第26路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 26-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.275 | hwYDDEMSVD2DCMeterFeederCircuit27Voltage | Feeder circuit 27-voltage | 第27路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 27-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.276 | hwYDDEMSVD2DCMeterFeederCircuit27Current | Feeder circuit 27-current | 第27路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 27-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.277 | hwYDDEMSVD2DCMeterFeederCircuit27CurrentPercentage | Feeder circuit 27-current percentage | 第27路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 27-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.278 | hwYDDEMSVD2DCMeterFeederCircuit27Power | Feeder circuit 27-power | 第27路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 27-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.279 | hwYDDEMSVD2DCMeterFeederCircuit27Energy | Feeder circuit 27-energy | 第27路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 27-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.280 | hwYDDEMSVD2DCMeterFeederCircuit27PositiveInsulationResistance | Feeder circuit 27-positive insulation resistance | 第27路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 27-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.281 | hwYDDEMSVD2DCMeterFeederCircuit27NegativeInsulationResistance | Feeder circuit 27-negative insulation resistance | 第27路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 27-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.282 | hwYDDEMSVD2DCMeterFeederCircuit28Voltage | Feeder circuit 28-voltage | 第28路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 28-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.283 | hwYDDEMSVD2DCMeterFeederCircuit28Current | Feeder circuit 28-current | 第28路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 28-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.284 | hwYDDEMSVD2DCMeterFeederCircuit28CurrentPercentage | Feeder circuit 28-current percentage | 第28路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 28-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.285 | hwYDDEMSVD2DCMeterFeederCircuit28Power | Feeder circuit 28-power | 第28路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 28-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.286 | hwYDDEMSVD2DCMeterFeederCircuit28Energy | Feeder circuit 28-energy | 第28路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 28-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.287 | hwYDDEMSVD2DCMeterFeederCircuit28PositiveInsulationResistance | Feeder circuit 28-positive insulation resistance | 第28路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 28-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.288 | hwYDDEMSVD2DCMeterFeederCircuit28NegativeInsulationResistance | Feeder circuit 28-negative insulation resistance | 第28路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 28-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.289 | hwYDDEMSVD2DCMeterFeederCircuit29Voltage | Feeder circuit 29-voltage | 第29路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 29-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.290 | hwYDDEMSVD2DCMeterFeederCircuit29Current | Feeder circuit 29-current | 第29路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 29-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.291 | hwYDDEMSVD2DCMeterFeederCircuit29CurrentPercentage | Feeder circuit 29-current percentage | 第29路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 29-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.292 | hwYDDEMSVD2DCMeterFeederCircuit29Power | Feeder circuit 29-power | 第29路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 29-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.293 | hwYDDEMSVD2DCMeterFeederCircuit29Energy | Feeder circuit 29-energy | 第29路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 29-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.294 | hwYDDEMSVD2DCMeterFeederCircuit29PositiveInsulationResistance | Feeder circuit 29-positive insulation resistance | 第29路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 29-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.295 | hwYDDEMSVD2DCMeterFeederCircuit29NegativeInsulationResistance | Feeder circuit 29-negative insulation resistance | 第29路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 29-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.296 | hwYDDEMSVD2DCMeterFeederCircuit30Voltage | Feeder circuit 30-voltage | 第30路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 30-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.297 | hwYDDEMSVD2DCMeterFeederCircuit30Current | Feeder circuit 30-current | 第30路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 30-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.298 | hwYDDEMSVD2DCMeterFeederCircuit30CurrentPercentage | Feeder circuit 30-current percentage | 第30路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 30-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.299 | hwYDDEMSVD2DCMeterFeederCircuit30Power | Feeder circuit 30-power | 第30路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 30-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.1.1.300 | hwYDDEMSVD2DCMeterrRunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2 | hwYDDEMSVD2DCMeterrRunningandConfig2Table | / | / |  |  | / | / | The running table of YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.1 | hwYDDEMSVD2DCMeterrRunningandConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.2 | hwYDDEMSVD2DCMeterFeederCircuit30Energy | Feeder circuit 30-energy | 第30路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 30-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.3 | hwYDDEMSVD2DCMeterFeederCircuit30PositiveInsulationResistance | Feeder circuit 30-positive insulation resistance | 第30路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 30-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.4 | hwYDDEMSVD2DCMeterFeederCircuit30NegativeInsulationResistance | Feeder circuit 30-negative insulation resistance | 第30路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 30-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.5 | hwYDDEMSVD2DCMeterFeederCircuit31Voltage | Feeder circuit 31-voltage | 第31路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 31-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.6 | hwYDDEMSVD2DCMeterFeederCircuit31Current | Feeder circuit 31-current | 第31路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 31-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.7 | hwYDDEMSVD2DCMeterFeederCircuit31CurrentPercentage | Feeder circuit 31-current percentage | 第31路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 31-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.8 | hwYDDEMSVD2DCMeterFeederCircuit31Power | Feeder circuit 31-power | 第31路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 31-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.9 | hwYDDEMSVD2DCMeterFeederCircuit31Energy | Feeder circuit 31-energy | 第31路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 31-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.10 | hwYDDEMSVD2DCMeterFeederCircuit31PositiveInsulationResistance | Feeder circuit 31-positive insulation resistance | 第31路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 31-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.11 | hwYDDEMSVD2DCMeterFeederCircuit31NegativeInsulationResistance | Feeder circuit 31-negative insulation resistance | 第31路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 31-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.12 | hwYDDEMSVD2DCMeterFeederCircuit32Voltage | Feeder circuit 32-voltage | 第32路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 32-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.13 | hwYDDEMSVD2DCMeterFeederCircuit32Current | Feeder circuit 32-current | 第32路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 32-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.14 | hwYDDEMSVD2DCMeterFeederCircuit32CurrentPercentage | Feeder circuit 32-current percentage | 第32路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 32-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.15 | hwYDDEMSVD2DCMeterFeederCircuit32Power | Feeder circuit 32-power | 第32路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 32-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.16 | hwYDDEMSVD2DCMeterFeederCircuit32Energy | Feeder circuit 32-energy | 第32路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 32-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.17 | hwYDDEMSVD2DCMeterFeederCircuit32PositiveInsulationResistance | Feeder circuit 32-positive insulation resistance | 第32路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 32-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.18 | hwYDDEMSVD2DCMeterFeederCircuit32NegativeInsulationResistance | Feeder circuit 32-negative insulation resistance | 第32路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 32-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.19 | hwYDDEMSVD2DCMeterFeederCircuit33Voltage | Feeder circuit 33-voltage | 第33路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 33-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.20 | hwYDDEMSVD2DCMeterFeederCircuit33Current | Feeder circuit 33-current | 第33路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 33-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.21 | hwYDDEMSVD2DCMeterFeederCircuit33CurrentPercentage | Feeder circuit 33-current percentage | 第33路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 33-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.22 | hwYDDEMSVD2DCMeterFeederCircuit33Power | Feeder circuit 33-power | 第33路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 33-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.23 | hwYDDEMSVD2DCMeterFeederCircuit33Energy | Feeder circuit 33-energy | 第33路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 33-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.24 | hwYDDEMSVD2DCMeterFeederCircuit33PositiveInsulationResistance | Feeder circuit 33-positive insulation resistance | 第33路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 33-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.25 | hwYDDEMSVD2DCMeterFeederCircuit33NegativeInsulationResistance | Feeder circuit 33-negative insulation resistance | 第33路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 33-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.26 | hwYDDEMSVD2DCMeterFeederCircuit34Voltage | Feeder circuit 34-voltage | 第34路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 34-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.27 | hwYDDEMSVD2DCMeterFeederCircuit34Current | Feeder circuit 34-current | 第34路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 34-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.28 | hwYDDEMSVD2DCMeterFeederCircuit34CurrentPercentage | Feeder circuit 34-current percentage | 第34路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 34-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.29 | hwYDDEMSVD2DCMeterFeederCircuit34Power | Feeder circuit 34-power | 第34路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 34-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.30 | hwYDDEMSVD2DCMeterFeederCircuit34Energy | Feeder circuit 34-energy | 第34路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 34-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.31 | hwYDDEMSVD2DCMeterFeederCircuit34PositiveInsulationResistance | Feeder circuit 34-positive insulation resistance | 第34路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 34-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.32 | hwYDDEMSVD2DCMeterFeederCircuit34NegativeInsulationResistance | Feeder circuit 34-negative insulation resistance | 第34路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 34-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.33 | hwYDDEMSVD2DCMeterFeederCircuit35Voltage | Feeder circuit 35-voltage | 第35路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 35-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.34 | hwYDDEMSVD2DCMeterFeederCircuit35Current | Feeder circuit 35-current | 第35路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 35-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.35 | hwYDDEMSVD2DCMeterFeederCircuit35CurrentPercentage | Feeder circuit 35-current percentage | 第35路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 35-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.36 | hwYDDEMSVD2DCMeterFeederCircuit35Power | Feeder circuit 35-power | 第35路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 35-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.37 | hwYDDEMSVD2DCMeterFeederCircuit35Energy | Feeder circuit 35-energy | 第35路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 35-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.38 | hwYDDEMSVD2DCMeterFeederCircuit35PositiveInsulationResistance | Feeder circuit 35-positive insulation resistance | 第35路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 35-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.39 | hwYDDEMSVD2DCMeterFeederCircuit35NegativeInsulationResistance | Feeder circuit 35-negative insulation resistance | 第35路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 35-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.40 | hwYDDEMSVD2DCMeterFeederCircuit36Voltage | Feeder circuit 36-voltage | 第36路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 36-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.41 | hwYDDEMSVD2DCMeterFeederCircuit36Current | Feeder circuit 36-current | 第36路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 36-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.42 | hwYDDEMSVD2DCMeterFeederCircuit36CurrentPercentage | Feeder circuit 36-current percentage | 第36路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 36-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.43 | hwYDDEMSVD2DCMeterFeederCircuit36Power | Feeder circuit 36-power | 第36路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 36-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.44 | hwYDDEMSVD2DCMeterFeederCircuit36Energy | Feeder circuit 36-energy | 第36路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 36-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.45 | hwYDDEMSVD2DCMeterFeederCircuit36PositiveInsulationResistance | Feeder circuit 36-positive insulation resistance | 第36路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 36-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.46 | hwYDDEMSVD2DCMeterFeederCircuit36NegativeInsulationResistance | Feeder circuit 36-negative insulation resistance | 第36路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 36-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.47 | hwYDDEMSVD2DCMeterFeederCircuit37Voltage | Feeder circuit 37-voltage | 第37路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 37-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.48 | hwYDDEMSVD2DCMeterFeederCircuit37Current | Feeder circuit 37-current | 第37路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 37-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.49 | hwYDDEMSVD2DCMeterFeederCircuit37CurrentPercentage | Feeder circuit 37-current percentage | 第37路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 37-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.50 | hwYDDEMSVD2DCMeterFeederCircuit37Power | Feeder circuit 37-power | 第37路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 37-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.51 | hwYDDEMSVD2DCMeterFeederCircuit37Energy | Feeder circuit 37-energy | 第37路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 37-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.52 | hwYDDEMSVD2DCMeterFeederCircuit37PositiveInsulationResistance | Feeder circuit 37-positive insulation resistance | 第37路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 37-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.53 | hwYDDEMSVD2DCMeterFeederCircuit37NegativeInsulationResistance | Feeder circuit 37-negative insulation resistance | 第37路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 37-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.54 | hwYDDEMSVD2DCMeterFeederCircuit38Voltage | Feeder circuit 38-voltage | 第38路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 38-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.55 | hwYDDEMSVD2DCMeterFeederCircuit38Current | Feeder circuit 38-current | 第38路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 38-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.56 | hwYDDEMSVD2DCMeterFeederCircuit38CurrentPercentage | Feeder circuit 38-current percentage | 第38路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 38-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.57 | hwYDDEMSVD2DCMeterFeederCircuit38Power | Feeder circuit 38-power | 第38路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 38-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.58 | hwYDDEMSVD2DCMeterFeederCircuit38Energy | Feeder circuit 38-energy | 第38路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 38-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.59 | hwYDDEMSVD2DCMeterFeederCircuit38PositiveInsulationResistance | Feeder circuit 38-positive insulation resistance | 第38路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 38-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.60 | hwYDDEMSVD2DCMeterFeederCircuit38NegativeInsulationResistance | Feeder circuit 38-negative insulation resistance | 第38路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 38-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.61 | hwYDDEMSVD2DCMeterFeederCircuit39Voltage | Feeder circuit 39-voltage | 第39路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 39-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.62 | hwYDDEMSVD2DCMeterFeederCircuit39Current | Feeder circuit 39-current | 第39路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 39-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.63 | hwYDDEMSVD2DCMeterFeederCircuit39CurrentPercentage | Feeder circuit 39-current percentage | 第39路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 39-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.64 | hwYDDEMSVD2DCMeterFeederCircuit39Power | Feeder circuit 39-power | 第39路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 39-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.65 | hwYDDEMSVD2DCMeterFeederCircuit39Energy | Feeder circuit 39-energy | 第39路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 39-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.66 | hwYDDEMSVD2DCMeterFeederCircuit39PositiveInsulationResistance | Feeder circuit 39-positive insulation resistance | 第39路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 39-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.67 | hwYDDEMSVD2DCMeterFeederCircuit39NegativeInsulationResistance | Feeder circuit 39-negative insulation resistance | 第39路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 39-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.68 | hwYDDEMSVD2DCMeterFeederCircuit40Voltage | Feeder circuit 40-voltage | 第40路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 40-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.69 | hwYDDEMSVD2DCMeterFeederCircuit40Current | Feeder circuit 40-current | 第40路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 40-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.70 | hwYDDEMSVD2DCMeterFeederCircuit40CurrentPercentage | Feeder circuit 40-current percentage | 第40路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 40-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.71 | hwYDDEMSVD2DCMeterFeederCircuit40Power | Feeder circuit 40-power | 第40路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 40-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.72 | hwYDDEMSVD2DCMeterFeederCircuit40Energy | Feeder circuit 40-energy | 第40路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 40-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.73 | hwYDDEMSVD2DCMeterFeederCircuit40PositiveInsulationResistance | Feeder circuit 40-positive insulation resistance | 第40路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 40-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.74 | hwYDDEMSVD2DCMeterFeederCircuit40NegativeInsulationResistance | Feeder circuit 40-negative insulation resistance | 第40路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 40-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.75 | hwYDDEMSVD2DCMeterFeederCircuit41Voltage | Feeder circuit 41-voltage | 第41路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 41-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.76 | hwYDDEMSVD2DCMeterFeederCircuit41Current | Feeder circuit 41-current | 第41路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 41-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.77 | hwYDDEMSVD2DCMeterFeederCircuit41CurrentPercentage | Feeder circuit 41-current percentage | 第41路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 41-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.78 | hwYDDEMSVD2DCMeterFeederCircuit41Power | Feeder circuit 41-power | 第41路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 41-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.79 | hwYDDEMSVD2DCMeterFeederCircuit41Energy | Feeder circuit 41-energy | 第41路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 41-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.80 | hwYDDEMSVD2DCMeterFeederCircuit41PositiveInsulationResistance | Feeder circuit 41-positive insulation resistance | 第41路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 41-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.81 | hwYDDEMSVD2DCMeterFeederCircuit41NegativeInsulationResistance | Feeder circuit 41-negative insulation resistance | 第41路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 41-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.82 | hwYDDEMSVD2DCMeterFeederCircuit42Voltage | Feeder circuit 42-voltage | 第42路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 42-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.83 | hwYDDEMSVD2DCMeterFeederCircuit42Current | Feeder circuit 42-current | 第42路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 42-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.84 | hwYDDEMSVD2DCMeterFeederCircuit42CurrentPercentage | Feeder circuit 42-current percentage | 第42路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 42-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.85 | hwYDDEMSVD2DCMeterFeederCircuit42Power | Feeder circuit 42-power | 第42路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 42-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.86 | hwYDDEMSVD2DCMeterFeederCircuit42Energy | Feeder circuit 42-energy | 第42路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 42-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.87 | hwYDDEMSVD2DCMeterFeederCircuit42PositiveInsulationResistance | Feeder circuit 42-positive insulation resistance | 第42路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 42-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.88 | hwYDDEMSVD2DCMeterFeederCircuit42NegativeInsulationResistance | Feeder circuit 42-negative insulation resistance | 第42路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 42-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.89 | hwYDDEMSVD2DCMeterFeederCircuit43Voltage | Feeder circuit 43-voltage | 第43路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 43-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.90 | hwYDDEMSVD2DCMeterFeederCircuit43Current | Feeder circuit 43-current | 第43路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 43-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.91 | hwYDDEMSVD2DCMeterFeederCircuit43CurrentPercentage | Feeder circuit 43-current percentage | 第43路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 43-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.92 | hwYDDEMSVD2DCMeterFeederCircuit43Power | Feeder circuit 43-power | 第43路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 43-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.93 | hwYDDEMSVD2DCMeterFeederCircuit43Energy | Feeder circuit 43-energy | 第43路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 43-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.94 | hwYDDEMSVD2DCMeterFeederCircuit43PositiveInsulationResistance | Feeder circuit 43-positive insulation resistance | 第43路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 43-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.95 | hwYDDEMSVD2DCMeterFeederCircuit43NegativeInsulationResistance | Feeder circuit 43-negative insulation resistance | 第43路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 43-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.96 | hwYDDEMSVD2DCMeterFeederCircuit44Voltage | Feeder circuit 44-voltage | 第44路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 44-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.97 | hwYDDEMSVD2DCMeterFeederCircuit44Current | Feeder circuit 44-current | 第44路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 44-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.98 | hwYDDEMSVD2DCMeterFeederCircuit44CurrentPercentage | Feeder circuit 44-current percentage | 第44路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 44-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.99 | hwYDDEMSVD2DCMeterFeederCircuit44Power | Feeder circuit 44-power | 第44路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 44-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.100 | hwYDDEMSVD2DCMeterFeederCircuit44Energy | Feeder circuit 44-energy | 第44路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 44-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.101 | hwYDDEMSVD2DCMeterFeederCircuit44PositiveInsulationResistance | Feeder circuit 44-positive insulation resistance | 第44路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 44-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.102 | hwYDDEMSVD2DCMeterFeederCircuit44NegativeInsulationResistance | Feeder circuit 44-negative insulation resistance | 第44路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 44-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.103 | hwYDDEMSVD2DCMeterFeederCircuit45Voltage | Feeder circuit 45-voltage | 第45路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 45-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.104 | hwYDDEMSVD2DCMeterFeederCircuit45Current | Feeder circuit 45-current | 第45路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 45-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.105 | hwYDDEMSVD2DCMeterFeederCircuit45CurrentPercentage | Feeder circuit 45-current percentage | 第45路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 45-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.106 | hwYDDEMSVD2DCMeterFeederCircuit45Power | Feeder circuit 45-power | 第45路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 45-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.107 | hwYDDEMSVD2DCMeterFeederCircuit45Energy | Feeder circuit 45-energy | 第45路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 45-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.108 | hwYDDEMSVD2DCMeterFeederCircuit45PositiveInsulationResistance | Feeder circuit 45-positive insulation resistance | 第45路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 45-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.109 | hwYDDEMSVD2DCMeterFeederCircuit45NegativeInsulationResistance | Feeder circuit 45-negative insulation resistance | 第45路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 45-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.110 | hwYDDEMSVD2DCMeterFeederCircuit46Voltage | Feeder circuit 46-voltage | 第46路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 46-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.111 | hwYDDEMSVD2DCMeterFeederCircuit46Current | Feeder circuit 46-current | 第46路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 46-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.112 | hwYDDEMSVD2DCMeterFeederCircuit46CurrentPercentage | Feeder circuit 46-current percentage | 第46路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 46-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.113 | hwYDDEMSVD2DCMeterFeederCircuit46Power | Feeder circuit 46-power | 第46路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 46-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.114 | hwYDDEMSVD2DCMeterFeederCircuit46Energy | Feeder circuit 46-energy | 第46路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 46-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.115 | hwYDDEMSVD2DCMeterFeederCircuit46PositiveInsulationResistance | Feeder circuit 46-positive insulation resistance | 第46路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 46-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.116 | hwYDDEMSVD2DCMeterFeederCircuit46NegativeInsulationResistance | Feeder circuit 46-negative insulation resistance | 第46路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 46-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.117 | hwYDDEMSVD2DCMeterFeederCircuit47Voltage | Feeder circuit 47-voltage | 第47路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 47-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.118 | hwYDDEMSVD2DCMeterFeederCircuit47Current | Feeder circuit 47-current | 第47路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 47-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.119 | hwYDDEMSVD2DCMeterFeederCircuit47CurrentPercentage | Feeder circuit 47-current percentage | 第47路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 47-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.120 | hwYDDEMSVD2DCMeterFeederCircuit47Power | Feeder circuit 47-power | 第47路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 47-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.121 | hwYDDEMSVD2DCMeterFeederCircuit47Energy | Feeder circuit 47-energy | 第47路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 47-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.122 | hwYDDEMSVD2DCMeterFeederCircuit47PositiveInsulationResistance | Feeder circuit 47-positive insulation resistance | 第47路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 47-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.123 | hwYDDEMSVD2DCMeterFeederCircuit47NegativeInsulationResistance | Feeder circuit 47-negative insulation resistance | 第47路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 47-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.124 | hwYDDEMSVD2DCMeterFeederCircuit48Voltage | Feeder circuit 48-voltage | 第48路馈出回路-电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 48-voltage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.125 | hwYDDEMSVD2DCMeterFeederCircuit48Current | Feeder circuit 48-current | 第48路馈出回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 48-current of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.126 | hwYDDEMSVD2DCMeterFeederCircuit48CurrentPercentage | Feeder circuit 48-current percentage | 第48路馈出回路-电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 48-current percentage of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.127 | hwYDDEMSVD2DCMeterFeederCircuit48Power | Feeder circuit 48-power | 第48路馈出回路-功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Feeder circuit 48-power of the device config table for the YD-DEMS-VD2 DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.128 | hwYDDEMSVD2DCMeterFeederCircuit48Energy | Feeder circuit 48-energy | 第48路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 48-energy of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.129 | hwYDDEMSVD2DCMeterFeederCircuit48PositiveInsulationResistance | Feeder circuit 48-positive insulation resistance | 第48路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 48-positive insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.130 | hwYDDEMSVD2DCMeterFeederCircuit48NegativeInsulationResistance | Feeder circuit 48-negative insulation resistance | 第48路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Feeder circuit 48-negative insulation resistance of the device config table for the YD-DEMS-VD2 DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.131 | hwYDDEMSVD2DCMeterCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the YD-DEMS-VD2 DC Meter. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.132 | hwYDDEMSVD2DCMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.133 | hwYDDEMSVD2DCMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.134 | hwYDDEMSVD2DCMeterDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.135 | hwYDDEMSVD2DCMeterTotalBranchNumber | Total branch number | 总支路数 | 1-Read_Write | 读写 | 1..48 | 1..48 | Total branch number of the device config table for the YD-DEMS-VD2 DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.6.2.1.300 | hwYDDEMSVD2DCMeterRunningandConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of YD-DEMS-VD2 DC Meter.

## PDU2000-MH-3PH
PDU2000-MH-3PH
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.20 | PDU2000MH3PH | PDU2000-MH-3PH | PDU2000-MH-3PH | / | / | / | / | PDU2000-MH-3PH Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1 | hwPDU2000MH3PHRunningandConfig1Table | / | / |  |  | / | / | The running table of PDU2000-MH-3PH.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.1 | hwPDU2000MH3PHRunningandConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU2000-MH-3PH.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.2 | hwPDU2000MH3PHVoltageValue | Voltage value | 电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | Voltage value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.3 | hwPDU2000MH3PHHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the PDU2000-MH-3PH.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.4 | hwPDU2000MH3PHSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the PDU2000-MH-3PH.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.5 | hwPDU2000MH3PHRatedVoltage | Rated voltage | 额定电压 | 0-Read_Only | 只读 | 220..380 | 220..380 | Rated voltage of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.6 | hwPDU2000MH3PHRatedCurrent | Rated current | 额定电流 | 0-Read_Only | 只读 | 16..32 | 16..32 | Rated current of the device config table for the PDU2000-MH-3PH.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.7 | hwPDU2000MH3PHRatedFrequency | Rated frequency | 额定频率 | 0-Read_Only | 只读 | 0..50 | 0..50 | Rated frequency of the device config table for the PDU2000-MH-3PH.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.8 | hwPDU2000MH3PHCurrentValue | Current value | 电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.9 | hwPDU2000MH3PHActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Active power of the device config table for the PDU2000-MH-3PH.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.10 | hwPDU2000MH3PHReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Reactive power of the device config table for the PDU2000-MH-3PH.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.11 | hwPDU2000MH3PHPowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of the device config table for the PDU2000-MH-3PH.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.12 | hwPDU2000MH3PHTotalPowerEnergyValue | Total power energy value | 有功电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Total power energy value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.13 | hwPDU2000MH3PHFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 4500..6500 | 4500..6500 | Frequency of the device config table for the PDU2000-MH-3PH.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.14 | hwPDU2000MH3PHL1VoltageValue | L1 voltage value | L1相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L1 voltage value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.15 | hwPDU2000MH3PHL2VoltageValue | L2 voltage value | L2相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L2 voltage value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.16 | hwPDU2000MH3PHL3VoltageValue | L3 voltage value | L3相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L3 voltage value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.17 | hwPDU2000MH3PHL1CurrentValue | L1 current value | L1相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L1 current value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.18 | hwPDU2000MH3PHL2CurrentValue | L2 current value | L2相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L2 current value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.19 | hwPDU2000MH3PHL3CurrentValue | L3 current value | L3相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L3 current value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.20 | hwPDU2000MH3PHL1ActivePower | L1 active power | L1相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 active power of the device config table for the PDU2000-MH-3PH.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.21 | hwPDU2000MH3PHL2ActivePower | L2 active power | L2相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 active power of the device config table for the PDU2000-MH-3PH.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.22 | hwPDU2000MH3PHL3ActivePower | L3 active power | L3相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 active power of the device config table for the PDU2000-MH-3PH.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.23 | hwPDU2000MH3PHL1ReactivePower | L1 reactive power | L1相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 reactive power of the device config table for the PDU2000-MH-3PH.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.24 | hwPDU2000MH3PHL2ReactivePower | L2 reactive power | L2相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 reactive power of the device config table for the PDU2000-MH-3PH.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.25 | hwPDU2000MH3PHL3ReactivePower | L3 reactive power | L3相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 reactive power of the device config table for the PDU2000-MH-3PH.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.26 | hwPDU2000MH3PHL1PowerFactor | L1 power factor | L1相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L1 power factor of the device config table for the PDU2000-MH-3PH.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.27 | hwPDU2000MH3PHL2PowerFactor | L2 power factor | L2相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L2 power factor of the device config table for the PDU2000-MH-3PH.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.28 | hwPDU2000MH3PHL3PowerFactor | L3 power factor | L3相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L3 power factor of the device config table for the PDU2000-MH-3PH.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.29 | hwPDU2000MH3PHCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the PDU2000-MH-3PH. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.30 | hwPDU2000MH3PHPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the PDU2000-MH-3PH.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.31 | hwPDU2000MH3PHModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the PDU2000-MH-3PH.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.32 | hwPDU2000MH3PHInputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Input mode of the device config table for the PDU2000-MH-3PH. Value 1 indicate singlephase Value 2 indicate threephase
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.33 | hwPDU2000MH3PHDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the PDU2000-MH-3PH.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.34 | hwPDU2000MH3PHParentDeviceId | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Parent device ID of the device config table for the PDU2000-MH-3PH.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.35 | hwPDU2000MH3PHCurrentUpperLimitAlarmSetValue | Current upper limit alarm set value | 电流上限告警设定值 | 1-Read_Write | 读写 | 0..324 | 0..324 | Current upper limit alarm set value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.36 | hwPDU2000MH3PHCurrentDownLimitAlarmSetValue | Current down limit alarm set value | 电流下限告警设定值 | 1-Read_Write | 读写 | 0..324 | 0..324 | Current down limit alarm set value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.37 | hwPDU2000MH3PHBuzzerSwitch | Buzzer switch | 蜂鸣器开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Buzzer switch of the device config table for the PDU2000-MH-3PH. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.38 | hwPDU2000MH3PHAlarmDryContactSwitch | Alarm dry-contact switch | 报警干接点开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Alarm dry-contact switch of the device config table for the PDU2000-MH-3PH. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.39 | hwPDU2000MH3PHL1CurrentUpperLimitAlarmSetValue | L1 current upper limit alarm set value | L1相电流上限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | L1 current upper limit alarm set value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.40 | hwPDU2000MH3PHL2CurrentUpperLimitAlarmSetValue | L2 current upper limit alarm set value | L2相电流上限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | L2 current upper limit alarm set value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.41 | hwPDU2000MH3PHL3CurrentUpperLimitAlarmSetValue | L3 current upper limit alarm set value | L3相电流上限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | L3 current upper limit alarm set value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.42 | hwPDU2000MH3PHL1CurrentDownLimitAlarmSetValue | L1 current down limit alarm set value | L1相电流下限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | L1 current down limit alarm set value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.43 | hwPDU2000MH3PHL2CurrentDownLimitAlarmSetValue | L2 current down limit alarm set value | L2相电流下限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | L2 current down limit alarm set value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.44 | hwPDU2000MH3PHL3CurrentDownLimitAlarmSetValue | L3 current down limit alarm set value | L3相电流下限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | L3 current down limit alarm set value of the device config table for the PDU2000-MH-3PH.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.45 | hwPDU2000MH3PHL1VoltageUpperLimitAlarmSetValue | L1 voltage upper limit alarm set value | L1相电压上限告警设定值 | 1-Read_Write | 读写 | 0..240 | 0..240 | L1 voltage upper limit alarm set value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.46 | hwPDU2000MH3PHL2VoltageUpperLimitAlarmSetValue | L2 voltage upper limit alarm set value | L2相电压上限告警设定值 | 1-Read_Write | 读写 | 0..240 | 0..240 | L2 voltage upper limit alarm set value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.47 | hwPDU2000MH3PHL3VoltageUpperLimitAlarmSetValue | L3 voltage upper limit alarm set value | L3相电压上限告警设定值 | 1-Read_Write | 读写 | 0..240 | 0..240 | L3 voltage upper limit alarm set value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.48 | hwPDU2000MH3PHL1VoltageDownLimitAlarmSetValue | L1 voltage down limit alarm set value | L1相电压下限告警设定值 | 1-Read_Write | 读写 | 0..240 | 0..240 | L1 voltage down limit alarm set value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.49 | hwPDU2000MH3PHL2VoltageDownLimitAlarmSetValue | L2 voltage down limit alarm set value | L2相电压下限告警设定值 | 1-Read_Write | 读写 | 0..240 | 0..240 | L2 voltage down limit alarm set value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.50 | hwPDU2000MH3PHL3VoltageDownLimitAlarmSetValue | L3 voltage down limit alarm set value | L3相电压下限告警设定值 | 1-Read_Write | 读写 | 0..240 | 0..240 | L3 voltage down limit alarm set value of the device config table for the PDU2000-MH-3PH.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.20.1.1.300 | hwPDU2000MH3PHRunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PDU2000-MH-3PH.

## IEC-EHU260
IEC-EHU260
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.16 | IECEHU260 | IEC-EHU260 | IEC-EHU260 | / | / | / | / | IECEHU260 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1 | hwIECEHU260RunningAndConfig1Table | / | / |  |  | / | / | The running and config table of IECEHU260
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.1 | hwIECEHU260RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the IECEHU260
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.2 | hwIECEHU260ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the IECEHU260.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.3 | hwIECEHU260PortNo | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running and config table for the IECEHU260.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.4 | hwIECEHU260CommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the IECEHU260.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.5 | hwIECEHU260NumberOfCriticalAlarms | Number of critical alarms | 紧急告警数量 | 0-Read_Only | 只读 | / | / | NumberOfCriticalAlarms of the device running and config table for the IECEHU260.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.6 | hwIECEHU260NumberOfMajorAlarms | Number of major alarms | 重要告警数量 | 0-Read_Only | 只读 | / | / | NumberOfMajorAlarms of the device running and config table for the IECEHU260.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.7 | hwIECEHU260NumberOfMinorAlarms | Number of minor alarms | 次要告警数量 | 0-Read_Only | 只读 | / | / | NumberOfMinorAlarms of the device running and config table for the IECEHU260.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.8 | hwIECEHU260NumberOfWarningAlarms | Number of warning alarms | 提示告警数量 | 0-Read_Only | 只读 | / | / | NumberOfWarningAlarms of the device running and config table for the IECEHU260.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.9 | hwIECEHU260TotalDeviceUptime | Total device uptime | 设备总运行时间 | 0-Read_Only | 只读 | / | / | Total Device Uptime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.10 | hwIECEHU260IndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | / | / | IndoorFan1TotalRuntime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.11 | hwIECEHU260IndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | / | / | IndoorFan2TotalRuntime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.12 | hwIECEHU260IndoorFan3TotalRuntime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | / | / | IndoorFan3TotalRuntime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.13 | hwIECEHU260IndoorFan4TotalRuntime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | / | / | IndoorFan4TotalRuntime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.14 | hwIECEHU260SystemTotalPowerConsumption | System total power consumption | 机组累计耗电量 | 0-Read_Only | 只读 | / | / | SystemTotalPowerConsumption of the device running and config table for the IECEHU260. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.15 | hwIECEHU260ExhaustFan1TotalRuntime | Exhaust fan 1 total runtime | 排风机1累计运行时间 | 0-Read_Only | 只读 | / | / | ExhaustFan1TotalRuntime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.16 | hwIECEHU260ExhaustFan2TotalRuntime | Exhaust fan 2 total runtime | 排风机2累计运行时间 | 0-Read_Only | 只读 | / | / | ExhaustFan2TotalRuntime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.17 | hwIECEHU260ExhaustFan3TotalRuntime | Exhaust fan 3 total runtime | 排风机3累计运行时间 | 0-Read_Only | 只读 | / | / | ExhaustFan3TotalRuntime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.18 | hwIECEHU260ExhaustFan4TotalRuntime | Exhaust fan 4 total runtime | 排风机4累计运行时间 | 0-Read_Only | 只读 | / | / | ExhaustFan4TotalRuntime of the device running and config table for the IECEHU260. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.19 | hwIECEHU260OnOrOffStatusOfSystem | On or Off status of system | 机组开关机状态 | 0-Read_Only | 只读 | off(1),on(2),unknown(255) | [1=关机][2=开机] | OnOrOffStatusOfSystem of the device running and config table for the IECEHU260. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.20 | hwIECEHU260CoolingOutput | Cooling output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | CoolingOutput of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.21 | hwIECEHU260IndoorFanOutput | Indoor fan output | 室内风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | IndoorFanOutput of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.22 | hwIECEHU260RealTimeCoolingPower | Real time cooling power | 实时制冷功率 | 0-Read_Only | 只读 | / | / | Real-Time Cooling Power of the device running and config table for the IECEHU260. Multiple:100. SigUnitInfo:Btu/h.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.23 | hwIECEHU260CoolingMode | Cooling mode | 制冷模式 | 0-Read_Only | 只读 | off(1),dryMode(2),wetMode(3),auxiliaryCoolingMode(4),dryModeAndAuxiliaryCoolingMode(5),wetModeAndAuxiliaryCoolingMode(6),unknown(255) | [1=关闭][2=干模式][3=湿模式][4=辅冷模式][5=干模式+辅冷模式][6=湿模式+辅冷模式] | CoolingMode of the device running and config table for the IECEHU260. Value1 indicate Off Value2 indicate Dry mode Value3 indicate Wet mode Value4 indicate Auxiliary cooling mode Value5 indicate Dry mode and auxiliary cooling mode Value6 indicate Wet mode and auxiliary cooling mode
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.24 | hwIECEHU260PowerFrequency | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | PowerFrequency of the device running and config table for the IECEHU260. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.25 | hwIECEHU260ABLineVoltage | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | ABLineVoltage of the device running and config table for the IECEHU260. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.26 | hwIECEHU260BCLineVoltage | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | BCLineVoltage of the device running and config table for the IECEHU260. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.27 | hwIECEHU260CALineVoltage | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | CALineVoltage of the device running and config table for the IECEHU260. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.28 | hwIECEHU260SystemTotalPower | System total power | 机组总功率 | 0-Read_Only | 只读 | 0..400 | 0..400 | SystemTotalPower of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.29 | hwIECEHU260PhaseACurrent | Phase A current | 系统电源A相电流 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | PhaseACurrent of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.30 | hwIECEHU260PhaseBCurrent | Phase B current | 系统电源B相电流 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | PhaseBCurrent of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.31 | hwIECEHU260PhaseCCurrent | Phase C current | 系统电源C相电流 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | PhaseCCurrent of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.32 | hwIECEHU260PrimaryPowerSupplyStatus | Primary power supply status | 主路供电状态 | 0-Read_Only | 只读 | withOutLoad(1),withLoad(2),unknown(255) | [1=未带载][2=带载] | PrimaryPowerSupplyStatus of the device running and config table for the IECEHU260. Value1 indicate With out load Value2 indicate With load
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.33 | hwIECEHU260TemperatureAndHumidityControlType | Temperature and humidity control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnAir(1),supplyAir(2),coldAisle(3),hotAisle(4),unknown(255) | [1=回风][2=送风][3=冷通道][4=热通道] | TemperatureAndHumidityControlType of the device running and config table for the IECEHU260. Value1 indicate Return air Value2 indicate Supply air Value3 indicate Cold aisle Value4 indicate Hot aisle
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.34 | hwIECEHU260CurrentTemperature | Current temperature | 当前温度 | 0-Read_Only | 只读 | -50..150 | -50..150 | CurrentTemperature of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.35 | hwIECEHU260CurrentHumidity | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | CurrentHumidity of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.36 | hwIECEHU260AverageSupplyAirTemperature | Average supply air temperature | 送风平均温度 | 0-Read_Only | 只读 | -50..150 | -50..150 | AverageSupplyAirTemperature of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.37 | hwIECEHU260AverageReturnAirTemperature | Average return air temperature | 回风平均温度 | 0-Read_Only | 只读 | -50..150 | -50..150 | AverageReturnAirTemperature of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.38 | hwIECEHU260AverageColdAisleTemperature | Average cold aisle temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -50..150 | -50..150 | AverageColdAisleTemperature of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.39 | hwIECEHU260AverageHotAisleTemperature | Average hot aisle temperature | 热通道平均温度 | 0-Read_Only | 只读 | -50..150 | -50..150 | AverageHotAisleTemperature of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.40 | hwIECEHU260AverageSupplyAirHumidity | Average supply air humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | AverageSupplyAirHumidity of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.41 | hwIECEHU260AverageReturnAirHumidity | Average return air humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | AverageReturnAirHumidity of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.42 | hwIECEHU260AverageColdAisleHumidity | Average cold aisle humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | AverageColdAisleHumidity of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.43 | hwIECEHU260AverageHotAisleHumidity | Average hot aisle humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | AverageHotAisleHumidity of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.44 | hwIECEHU260AverageOutdoorIntakeAirTemperature | Average outdoor intake air temperature | 室外侧进风平均温度 | 0-Read_Only | 只读 | -50..150 | -50..150 | AverageOutdoorIntakeAirTemperature of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.45 | hwIECEHU260AverageOutdoorIntakeAirHumidity | Average outdoor intake air humidity | 室外侧进风平均湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | AverageOutdoorIntakeAirHumidity of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.46 | hwIECEHU260Compressor1RunningStatus | Compressor 1 running status | 压缩机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Compressor1RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.47 | hwIECEHU260Compressor2RunningStatus | Compressor 2 running status | 压缩机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Compressor2RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.48 | hwIECEHU260IndoorFan1RunningStatus | Indoor fan 1 running status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | IndoorFan1RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.49 | hwIECEHU260IndoorFan2RunningStatus | Indoor fan 2 running status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | IndoorFan2RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.50 | hwIECEHU260IndoorFan3RunningStatus | Indoor fan 3 running status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | IndoorFan3RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.51 | hwIECEHU260IndoorFan4RunningStatus | Indoor fan 4 running status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | IndoorFan4RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.52 | hwIECEHU260IndoorFan1ControlStatus | Indoor fan 1 control status | 室内风机1控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | IndoorFan1ControlStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.53 | hwIECEHU260IndoorFan2ControlStatus | Indoor fan 2 control status | 室内风机2控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | IndoorFan2ControlStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.54 | hwIECEHU260IndoorFan3ControlStatus | Indoor fan 3 control status | 室内风机3控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | IndoorFan3ControlStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.55 | hwIECEHU260IndoorFan4ControlStatus | Indoor fan 4 control status | 室内风机4控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | IndoorFan4ControlStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.56 | hwIECEHU260SpraySystemRunningStatus | Spray system running status | 喷淋系统运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | SpraySystemRunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.57 | hwIECEHU260LiquidLevelStatus | Liquid level status | 液位状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | LiquidLevelStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.58 | hwIECEHU260SprayPump1RunningStatus | Spray pump 1 running status | 喷淋水泵1运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | SprayPump1RunningStatus of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.59 | hwIECEHU260SprayPump2RunningStatus | Spray pump 2 running status | 喷淋水泵2运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | SprayPump2RunningStatus of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.60 | hwIECEHU260SprayLowLiquidLevelStatus | Spray low liquid level status | 喷淋低液位状态 | 0-Read_Only | 只读 | notTriggered(1),triggered(2),unknown(255) | [1=非触发][2=触发] | SprayLowLiquidLevelStatus of the device running and config table for the IECEHU260. Value1 indicate Not triggered Value2 indicate Triggered
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.61 | hwIECEHU260SprayHighLiquidLevelStatus | Spray high liquid level status | 喷淋高液位状态 | 0-Read_Only | 只读 | notTriggered(1),triggered(2),unknown(255) | [1=非触发][2=触发] | SprayHighLiquidLevelStatus of the device running and config table for the IECEHU260. Value1 indicate Not triggered Value2 indicate Triggered
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.62 | hwIECEHU260SprayOverflowLiquidLevelStatus | Spray overflow liquid level status | 喷淋溢水液位状态 | 0-Read_Only | 只读 | notTriggered(1),triggered(2),unknown(255) | [1=非触发][2=触发] | SprayOverflowLiquidLevelStatus of the device running and config table for the IECEHU260. Value1 indicate Not triggered Value2 indicate Triggered
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.63 | hwIECEHU260SterilizationComponentRunningStatus | Sterilization component running status | 杀菌组件运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | SterilizationComponentRunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.64 | hwIECEHU260SprayWaterInletValveRunningStatus | Spray water inlet valve running status | 喷淋进水阀运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | SprayWaterInletValveRunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.65 | hwIECEHU260SprayDrainValveRunningStatus | Spray drain valve running status | 喷淋排水阀运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | SprayDrainValveRunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.66 | hwIECEHU260ExhaustFan1RunningStatus | Exhaust fan 1 running status | 排风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | ExhaustFan1RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.67 | hwIECEHU260ExhaustFan2RunningStatus | Exhaust fan 2 running status | 排风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | ExhaustFan2RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.68 | hwIECEHU260ExhaustFan3RunningStatus | Exhaust fan 3 running status | 排风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | ExhaustFan3RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.69 | hwIECEHU260ExhaustFan4RunningStatus | Exhaust fan 4 running status | 排风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | ExhaustFan4RunningStatus of the device running and config table for the IECEHU260. SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.70 | hwIECEHU260ExhaustFan1ControlStatus | Exhaust fan 1 control status | 排风机1控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | ExhaustFan1ControlStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.71 | hwIECEHU260ExhaustFan2ControlStatus | Exhaust fan 2 control status | 排风机2控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | ExhaustFan2ControlStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.72 | hwIECEHU260ExhaustFan3ControlStatus | Exhaust fan 3 control status | 排风机3控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | ExhaustFan3ControlStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.73 | hwIECEHU260ExhaustFan4ControlStatus | Exhaust fan 4 control status | 排风机4控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | ExhaustFan4ControlStatus of the device running and config table for the IECEHU260. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.74 | hwIECEHU260StartupOrShutdownControl | Startup or Shutdown control | 控制开关机 | 1-Read_Write | 读写 | off(1),on(2),unknown(255) | off(1),on(2),unknown(255) | StartupOrShutdownControl of the device running and config table for the IECEHU260. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.75 | hwIECEHU260WetModeStartupTemperature | Wet mode startup temperature | 湿模式启用温度 | 1-Read_Write | 读写 | 50..350 | 50..350 | WetModeStartupTemperature of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.76 | hwIECEHU260TemperatureSetpoint | Temperature setpoint | 温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | TemperatureSetpoint of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.77 | hwIECEHU260HumiditySetpoint | Humidity setpoint | 湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | HumiditySetpoint of the device running and config table for the IECEHU260. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.16.1.1.78 | hwIECEHU260Config1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of IECEHU260.

## UMG96-PQ
UMG96-PQ
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.8 | UMG96-PQ | UMG96-PQ | UMG96-PQ | / | / | / | / | UMG96PQ Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1 | hwUMG96PQRunningAndConfig1Table | / | / |  |  | / | / | The running and config table of UMG96PQ
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.1 | hwUMG96PQRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the UMG96PQ
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.2 | hwUMG96PQModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.3 | hwUMG96PQPortNo | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.4 | hwUMG96PQCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.5 | hwUMG96PQL1NVoltage | L1-N voltage | L1-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1NVoltage of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.6 | hwUMG96PQL2NVoltage | L2-N voltage | L2-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2NVoltage of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.7 | hwUMG96PQL3NVoltage | L3-N voltage | L3-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3NVoltage of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.8 | hwUMG96PQL1L2Voltage | L1-L2 voltage | L1-L2 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1L2Voltage of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.9 | hwUMG96PQL2L3Voltage | L2-L3 voltage | L2-L3 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2L3Voltage of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.10 | hwUMG96PQL3L1Voltage | L3-L1 voltage | L3-L1 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3L1Voltage of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.11 | hwUMG96PQL1Current | L1 current | L1 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1Current of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.12 | hwUMG96PQL2Current | L2 current | L2 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2Current of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.13 | hwUMG96PQL3Current | L3 current | L3 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3Current of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.14 | hwUMG96PQTotalCurrent | Total current | 总电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalCurrent of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.15 | hwUMG96PQL1RealPower | L1 real power | L1 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1RealPower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.16 | hwUMG96PQL2RealPower | L2 real power | L2 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2RealPower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.17 | hwUMG96PQL3RealPower | L3 real power | L3 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3RealPower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.18 | hwUMG96PQTotalRealPower | Total real power | 总有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalRealPower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.19 | hwUMG96PQL1ApparentPower | L1 apparent power | L1 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ApparentPower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.20 | hwUMG96PQL2ApparentPower | L2 apparent power | L2 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ApparentPower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.21 | hwUMG96PQL3ApparentPower | L3 apparent power | L3 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ApparentPower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.22 | hwUMG96PQTotalApparentPower | Total apparent power | 总视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalApparentPower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.23 | hwUMG96PQL1ReactivePower | L1 reactive power | L1 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactivePower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.24 | hwUMG96PQL2ReactivePower | L2 reactive power | L2 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactivePower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.25 | hwUMG96PQL3ReactivePower | L3 reactive power | L3 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactivePower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.26 | hwUMG96PQTotalReactivePower | Total reactive power | 总无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalReactivePower of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.27 | hwUMG96PQL1PowerFactor | L1 power factor | L1 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1PowerFactor of the device running and config table for the UMG96PQ. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.28 | hwUMG96PQL2PowerFactor | L2 power factor | L2 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2PowerFactor of the device running and config table for the UMG96PQ. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.29 | hwUMG96PQL3PowerFactor | L3 power factor | L3 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3PowerFactor of the device running and config table for the UMG96PQ. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.30 | hwUMG96PQFrequency | Frequency | 频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.31 | hwUMG96PQL1RealEnergy | L1 real energy | L1 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1RealEnergy of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:Wh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.32 | hwUMG96PQL2RealEnergy | L2 real energy | L2 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2RealEnergy of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:Wh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.33 | hwUMG96PQL3RealEnergy | L3 real energy | L3 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3RealEnergy of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:Wh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.34 | hwUMG96PQTotalRealEnergy | Total real energy | 总有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalRealEnergy of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:Wh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.35 | hwUMG96PQL1ApparentEnergy | L1 apparent energy | L1 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ApparentEnergy of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:VAh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.36 | hwUMG96PQL2ApparentEnergy | L2 apparent energy | L2 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ApparentEnergy of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:VAh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.37 | hwUMG96PQL3ApparentEnergy | L3 apparent energy | L3 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ApparentEnergy of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:VAh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.38 | hwUMG96PQTotalApparentEnergy | Total apparent energy | 总视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalApparentEnergy of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:VAh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.39 | hwUMG96PQL1ReactiveEnergyInductive | L1 reactive energy inductive | L1 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactiveEnergyInductive of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:varh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.40 | hwUMG96PQL2ReactiveEnergyInductive | L2 reactive energy inductive | L2 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactiveEnergyInductive of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:varh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.41 | hwUMG96PQL3ReactiveEnergyInductive | L3 reactive energy inductive | L3 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactiveEnergyInductive of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:varh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.42 | hwUMG96PQTotalReactiveEnergyInductive | Total reactive energy inductive | 总无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalReactiveEnergyInductive of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:varh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.43 | hwUMG96PQL1ReactiveEnergyCapacitive | L1 reactive energy capacitive | L1 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactiveEnergyCapacitive of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:varh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.44 | hwUMG96PQL2ReactiveEnergyCapacitive | L2 reactive energy capacitive | L2 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactiveEnergyCapacitive of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:varh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.45 | hwUMG96PQL3ReactiveEnergyCapacitive | L3 reactive energy capacitive | L3 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactiveEnergyCapacitive of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:varh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.46 | hwUMG96PQL4ReactiveEnergyCapacitive | L4 reactive energy capacitive | 总无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L4ReactiveEnergyCapacitive of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:varh.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.47 | hwUMG96PQL1NThd | L1-N THD | L1-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1NThd of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.48 | hwUMG96PQL2NThd | L2-N THD | L2-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2NThd of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.49 | hwUMG96PQL3NThd | L3-N THD | L3-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3NThd of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.50 | hwUMG96PQL1Thd | L1 THD | L1 THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1Thd of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.51 | hwUMG96PQL2Thd | L2 THD | L2 THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2Thd of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.52 | hwUMG96PQL3Thd | L3 THD | L3 THD | 0-Read_Only | 只读 | / | / | L3Thd of the device running and config table for the UMG96PQ. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.53 | hwUMG96PQStatusDigitalInput1 | Status digital input 1 | 状态量输入1 | 0-Read_Only | 只读 | / | / | StatusDigitalInput1 of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.54 | hwUMG96PQStatusDigitalInput2 | Status digital input 2 | 状态量输入2 | 0-Read_Only | 只读 | / | / | StatusDigitalInput2 of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.55 | hwUMG96PQStatusDigitalInput3 | Status digital input 3 | 状态量输入3 | 0-Read_Only | 只读 | / | / | StatusDigitalInput3 of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.56 | hwUMG96PQStatusDigitalOutput1 | Status digital output 1 | 状态量输出1 | 0-Read_Only | 只读 | / | / | StatusDigitalOutput1 of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.57 | hwUMG96PQStatusDigitalOutput2 | Status digital output 2 | 状态量输出2 | 0-Read_Only | 只读 | / | / | StatusDigitalOutput2 of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.58 | hwUMG96PQStatusDigitalOutput3 | Status digital output 3 | 状态量输出3 | 0-Read_Only | 只读 | / | / | StatusDigitalOutput3 of the device running and config table for the UMG96PQ.
1.3.6.1.4.1.2011.6.178.1.1.130.8.1.1.59 | hwUMG96PQRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UMG96PQ.

## NFS-320E
NFS-320E
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.135.2 | NFS320E | NFS-320E | NFS-320E | / | / | / | / | NFS320E Equipment.
1.3.6.1.4.1.2011.6.178.1.1.135.2.1 | hwNFS320ERunningAndConfig1Table | / | / |  |  | / | / | The running and config table of NFS320E
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.1 | hwNFS320ERunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the NFS320E
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.2 | hwNFS320EModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the NFS320E.
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.3 | hwNFS320EPortNo | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running and config table for the NFS320E.
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.4 | hwNFS320ECommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the NFS320E.
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.5 | hwNFS320ESapAlarmStatus | Sap alarm status | SAP告警状态 | 0-Read_Only | 只读 | normal(1),alarm(2),unknown(255) | [1=正常][2=告警] | SapAlarmStatus of the device running and config table for the NFS320E. Value1 indicate Normal Value2 indicate Alarm
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.6 | hwNFS320ESapCommonFaultStatus | Sap common fault status | SAP常见故障状态 | 0-Read_Only | 只读 | normal(1),fault(2),unknown(255) | [1=正常][2=故障] | SapCommonFaultStatus of the device running and config table for the NFS320E. Value1 indicate Normal Value2 indicate Fault
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.7 | hwNFS320ESapTotalPowerFailure | Sap total power failure | SAP总掉电 | 0-Read_Only | 只读 | normal(1),acFail(2),batteryFail(3),unknown(255) | [1=正常][2=交流电源故障][3=电池故障] | SapTotalPowerFailure of the device running and config table for the NFS320E. Value1 indicate Normal Value2 indicate AC fail Value3 indicate Battery fail
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.8 | hwNFS320EPanelIsolationStatus | Panel isolation status | 面板隔离状态 | 0-Read_Only | 只读 | normal(1),panelIsolation(2),unknown(255) | [0=正常][1=面板隔离] | PanelIsolationStatus of the device running and config table for the NFS320E. Value1 indicate Normal Value2 indicate Panel isolation
1.3.6.1.4.1.2011.6.178.1.1.135.2.1.1.9 | hwNFS320ERunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NFS320E.

## RMU
RMU
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.22 | RMU | RMU | RMU | / | / | / | / | RMU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.22.1 | hwRMURunningAndConfig1Table | / | / |  |  | / | / | The running and config table of RMU
1.3.6.1.4.1.2011.6.178.1.1.9.22.1.1.1 | hwRMURunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the RMU
1.3.6.1.4.1.2011.6.178.1.1.9.22.1.1.2 | hwRMUModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the RMU.
1.3.6.1.4.1.2011.6.178.1.1.9.22.1.1.3 | hwRMUPortNo | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running and config table for the RMU.
1.3.6.1.4.1.2011.6.178.1.1.9.22.1.1.4 | hwRMUCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the RMU.
1.3.6.1.4.1.2011.6.178.1.1.9.22.1.1.5 | hwRMUOutgoingBreakerOnOrOffStatus | Outgoing breaker on or off status | 输出断路器开关状态 | 0-Read_Only | 只读 | open(1),closed(2),unknown(255) | [1=开][2=关] | Outgoing Breaker On Or Off Status of the device running and config table for the RMU. Value1 indicate Open Value2 indicate Closed.
1.3.6.1.4.1.2011.6.178.1.1.9.22.1.1.6 | hwRMURunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of RMU.

## EnvicoolPC6H
英维克PC6H
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.15 | EnvicoolPC6H | EnvicoolPC6H | 英维克PC6H | / | / | / | / | EnvicoolPC6H Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1 | hwEnvicoolPC6HRunningAndConfig1Table | / | / |  |  | / | / | The running table of EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.1 | hwEnvicoolPC6HRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.2 | hwEnvicoolPC6HUnitStatus | Unit status | 工作状态 | 0-Read_Only | 只读 | off(1), running(2), faults(3), unknown(255) | [关机=1]/[运行=2]/[故障=3] | Unit status of the device config table for the EnvicoolPC6H. Value 1 indicate off Value 2 indicate running Value 3 indicate faults
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.3 | hwEnvicoolPC6HIndoorFanStatus | Indoor fan status | 内风机状态 | 0-Read_Only | 只读 | closed(1), running(2), faults(3), unknown(255) | [关闭=1]/[运行=2]/[故障=3] | Indoor fan status of the device config table for the EnvicoolPC6H. Value 1 indicate closed Value 2 indicate running Value 3 indicate faults
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.4 | hwEnvicoolPC6HOutdoorFanStatus | Outdoor fan status | 外风机状态 | 0-Read_Only | 只读 | closed(1), running(2), faults(3), unknown(255) | [关闭=1]/[运行=2]/[故障=3] | Outdoor fan status of the device config table for the EnvicoolPC6H. Value 1 indicate closed Value 2 indicate running Value 3 indicate faults
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.5 | hwEnvicoolPC6HCompressorStatus | Compressor status | 压缩机状态 | 0-Read_Only | 只读 | closed(1), running(2), faults(3), unknown(255) | [关闭=1]/[运行=2]/[故障=3] | Compressor status of the device config table for the EnvicoolPC6H. Value 1 indicate closed Value 2 indicate running Value 3 indicate faults
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.6 | hwEnvicoolPC6HHeaterStatus | Heater status | 加热器状态 | 0-Read_Only | 只读 | closed(1), running(2), faults(3), unknown(255) | [关闭=1]/[运行=2]/[故障=3] | Heater status of the device config table for the EnvicoolPC6H. Value 1 indicate closed Value 2 indicate running Value 3 indicate faults
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.7 | hwEnvicoolPC6HReturnAirTemperature | Return air temperature | 回风温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Return air temperature of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.8 | hwEnvicoolPC6HSupplyAirTemperature | Supply air temperature | 送风温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Supply air temperature of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.9 | hwEnvicoolPC6HOutdoorTemperature | Outdoor temperature | 室外温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Outdoor temperature of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.10 | hwEnvicoolPC6HCondenserTemperature | Condenser temperature | 冷凝器温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Condenser temperature of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.11 | hwEnvicoolPC6HEvaporatorTemperature | Evaporator temperature | 蒸发器温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Evaporator temperature of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.12 | hwEnvicoolPC6HVoltage | Voltage | 运行电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.13 | hwEnvicoolPC6HIndoorFanSpeed | Indoor fan speed | 内风机转速 | 0-Read_Only | 只读 | 0..65000 | 0..65000 | Indoor fan speed of the device config table for the EnvicoolPC6H.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.14 | hwEnvicoolPC6HOutdoorFanSpeed | Outdoor fan speed | 外风机转速 | 0-Read_Only | 只读 | 0..65000 | 0..65000 | Outdoor fan speed of the device config table for the EnvicoolPC6H.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.15 | hwEnvicoolPC6HCompressorTotalRuntime | Compressor total runtime | 压缩机运行时间 | 0-Read_Only | 只读 | 0..4200000000 | 0..4200000000 | Compressor total runtime of the device config table for the EnvicoolPC6H.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.16 | hwEnvicoolPC6HIndoorFanTotalRuntime | Indoor fan total runtime | 内风机运行时间 | 0-Read_Only | 只读 | 0..4200000000 | 0..4200000000 | Indoor fan total runtime of the device config table for the EnvicoolPC6H.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.17 | hwEnvicoolPC6HCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the EnvicoolPC6H. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.18 | hwEnvicoolPC6HPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.19 | hwEnvicoolPC6HModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.20 | hwEnvicoolPC6HSerialNo | Serial No. | SN | 0-Read_Only | 只读 | 0..32 | 0..32 | Serial No. of the device config table for the EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.21 | hwEnvicoolPC6HProtocolVersion | Protocol version | 协议版本 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Protocol version of the device config table for the EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.22 | hwEnvicoolPC6HHardwareVersionOfControlBoard | Hardware version of control board | 硬件版本 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Hardware version of control board of the device config table for the EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.23 | hwEnvicoolPC6HSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Software version of the device config table for the EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.24 | hwEnvicoolPC6HDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the EnvicoolPC6H.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.25 | hwEnvicoolPC6HCoolingStartupTempSp | Cooling startup temp sp | 制冷启动温度点 | 1-Read_Write | 读写 | 200..300 | 200..300 | Cooling startup temp sp of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.26 | hwEnvicoolPC6HCoolingTempHys | Cooling temp hys | 制冷回差 | 1-Read_Write | 读写 | 10..50 | 10..50 | Cooling temp hys of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.27 | hwEnvicoolPC6HHeatingStartupTempSp | Heating startup temp sp | 加热器启动温度点 | 1-Read_Write | 读写 | -400..250 | -400..250 | Heating startup temp sp of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.28 | hwEnvicoolPC6HHeatingTempHys | Heating temp hys | 加热器温度回差 | 1-Read_Write | 读写 | 10..150 | 10..150 | Heating temp hys of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.29 | hwEnvicoolPC6HHighTempAlarmThr | High temp alarm thr | 高温告警点 | 1-Read_Write | 读写 | 350..700 | 350..700 | High temp alarm thr of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.30 | hwEnvicoolPC6HLowTempAlarmThr | Low temp alarm thr | 低温告警点 | 1-Read_Write | 读写 | -400..50 | -400..50 | Low temp alarm thr of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.31 | hwEnvicoolPC6HOvervoltageAlarmThr | Overvoltage alarm thr | 过压告警点 | 1-Read_Write | 读写 | 2200..2760 | 2200..2760 | Overvoltage alarm thr of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.32 | hwEnvicoolPC6HUndervoltageAlarmThr | Undervoltage alarm thr | 欠压告警点 | 1-Read_Write | 读写 | 1600..1900 | 1600..1900 | Undervoltage alarm thr of the device config table for the EnvicoolPC6H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.33 | hwEnvicoolPC6HUnitOnorOffAfterPowerFailure | Unit on/off after power failure | 来电开关机 | 1-Read_Write | 读写 | unitoffafterpowerfailure(1), unitonafterpowerfailure(2), unknown(255) | [来电关机=1]/[来电开机=2] | Unit on/off after power failure of the device config table for the EnvicoolPC6H. Value 1 indicate unitoffafterpowerfailure Value 2 indicate unitonafterpowerfailure
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.34 | hwEnvicoolPC6HStartorShutdownControl | Start/shutdown control | 开/关控制 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Start/shutdown control of the device config table for the EnvicoolPC6H. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.35 | hwEnvicoolPC6HOperationMode | Operation mode | 运行模式 | 1-Read_Write | 读写 | automatic(1), refrigeration(2), heating(3), dehumidification(4), unknown(255) | [自动=1]/[制冷=2]/[制热=3]/[除湿=4] | Operation mode of the device config table for the EnvicoolPC6H. Value 1 indicate automatic Value 2 indicate refrigeration Value 3 indicate heating Value 4 indicate dehumidification
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.36 | hwEnvicoolPC6HReset | Reset | 复位 | 1-Read_Write | 读写 | resetting(1) | [复位=1] | Reset of the device config table for the EnvicoolPC6H. Value 1 indicate resetting
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.37 | hwEnvicoolPC6HClearAlarm | Clear alarm | 告警清除 | 1-Read_Write | 读写 | clear(1) | [清除=1] | Clear alarm of the device config table for the EnvicoolPC6H. Value 1 indicate clear
1.3.6.1.4.1.2011.6.178.1.1.10.15.1.1.300 | hwEnvicoolPC6HRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of EnvicoolPC6H.

## SVG
SVG
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.21 | SVG | SVG | SVG | / | / | / | / | SVG Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1 | hwSVGRunning1Table | / | / |  |  | / | / | The running table of SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.1 | hwSVGRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.2 | hwSVGDeviceStatus | Device status | 装置状态 | 0-Read_Only | 只读 | fault(1), run(2), suspended(3), unknown(255) | [故障=1]/[运行=2]/[停机=3] | Device status of the device config table for the SVG. Value 1 indicate fault Value 2 indicate run Value 3 indicate suspended
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.3 | hwSVGCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the SVG. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.4 | hwSVGPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.5 | hwSVGModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..247 | 1..247 | Modbus address of the device config table for the SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.6 | hwSVGDeviceCompensationCurrentA | Device compensation current A | 装置补偿电流A | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Device compensation current A of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.7 | hwSVGDeviceCompensationCurrentB | Device compensation current B | 装置补偿电流B | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Device compensation current B of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.8 | hwSVGDeviceCompensationCurrentC | Device compensation current C | 装置补偿电流C | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Device compensation current C of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.9 | hwSVGTemperatureOfTheDevice | Temperature of the device | 装置温度 | 0-Read_Only | 只读 | -100..200 | -100..200 | Temperature of the device of the device config table for the SVG.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.10 | hwSVGEffectiveValueOfLoadCurrentA | Effective value of load current A | 负载电流有效值A | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current A of the device config table for the SVG.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.11 | hwSVGEffectiveValueOfLoadCurrentB | Effective value of load current B | 负载电流有效值B | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current B of the device config table for the SVG.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.12 | hwSVGEffectiveValueOfLoadCurrentC | Effective value of load current C | 负载电流有效值C | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current C of the device config table for the SVG.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.13 | hwSVGEffectiveValueOfLineVoltageAb | Effective value of line voltage AB | 线电压有效值AB | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Effective value of line voltage AB of the device config table for the SVG.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.14 | hwSVGEffectiveValueOfLineVoltageBc | Effective value of line voltage BC | 线电压有效值BC | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Effective value of line voltage BC of the device config table for the SVG.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.15 | hwSVGEffectiveValueOfLineVoltageCa | Effective value of line voltage CA | 线电压有效值CA | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Effective value of line voltage CA of the device config table for the SVG.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.16 | hwSVGSystemCurrentDistortionRate | System current distortion rate | 系统电流畸变率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | System current distortion rate of the device config table for the SVG.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.17 | hwSVGSystemPowerFactor | System power factor | 系统功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | System power factor of the device config table for the SVG.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.18 | hwSVGEquipmentLoadRate | Equipment load rate | 设备负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Equipment load rate of the device config table for the SVG.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.19 | hwSVGHmiVersion | HMI version | HMI版本 | 0-Read_Only | 只读 | 0..6 | 0..6 | HMI version of the device config table for the SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.1.1.101 | hwSVGRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2 | hwSVGConfig2Table | / | / |  |  | / | / | The config table of SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.1 | hwSVGConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.2 | hwSVGDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the SVG.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.3 | hwSVGStartAndStopControl | Start and stop control | 启停控制 | 1-Read_Write | 读写 | localcontrol(1), startfromafar(2), stopfromafar(3), unknown(255) | [就地控制=1]/[远方启动=2]/[远方停止=3] | Start and stop control of the device config table for the SVG. Value 1 indicate local control Value 2 indicate start from afar Value 3 indicate stop from afar
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.4 | hwSVGSetDetailModel | Detail model | 详细机型 | 1-Read_Write | 读写 | eightHundredAndOneThousandMm(1), sixHundredAndOneThousandMm(2), unknown(255) | [800 * 1000 mm=1]/[600 * 1000 mm=2] | Detail model of the device config table for the SVG. Value 1 indicate 800 * 1000 mm Value 2 indicate 600 * 1000 mm
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.5 | hwSVGPhAVoltageOfGrid | Phase A voltage of grid | 源侧A相电压 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase A voltage of grid of the device config table for the SVG.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.6 | hwSVGPhBVoltageOfGrid | Phase B voltage of grid | 源侧B相电压 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase B voltage of grid of the device config table for the SVG.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.7 | hwSVGPhCVoltageOfGrid | Phase C voltage of grid | 源侧C相电压 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase C voltage of grid of the device config table for the SVG.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.8 | hwSVGPhALoadCurr | Phase A load current | 负载侧A相电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase A load current of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.9 | hwSVGPhBLoadCurr | Phase B load current | 负载侧B相电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase B load current of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.10 | hwSVGPhCLoadCurr | Phase C load current | 负载侧C相电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase C load current of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.11 | hwSVGPhACompCurr | Phase A compensation current | A相补偿电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase A compensation current of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.12 | hwSVGPhBCompCurr | Phase B compensation current | B相补偿电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase B compensation current of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.13 | hwSVGPhCCompCurr | Phase C compensation current | C相补偿电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Phase C compensation current of the device config table for the SVG.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.14 | hwSVGGridTHDUOfPhA | Grid THDU of phase A | 源侧A相THDU | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid THDU of phase A of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.15 | hwSVGGridTHDUOfPhB | Grid THDU of phase B | 源侧B相THDU | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid THDU of phase B of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.16 | hwSVGGridTHDUOfPhC | Grid THDU of phase C | 源侧C相THDU | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid THDU of phase C of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.17 | hwSVGGridTHDIOfPhA | Grid THDI of phase A | 源侧A相THDI | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid THDI of phase A of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.18 | hwSVGGridTHDIOfPhB | Grid THDI of phase B | 源侧B相THDI | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid THDI of phase B of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.19 | hwSVGGridTHDIOfPhC | Grid THDI of phase C | 源侧C相THDI | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid THDI of phase C of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.20 | hwSVGLoadTHDIOfPhA | Load THDI of phase A | 负载侧A相THDI | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Load THDI of phase A of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.21 | hwSVGLoadTHDIOfPhB | Load THDI of phase B | 负载侧B相THDI | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Load THDI of phase B of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.22 | hwSVGLoadTHDIOfPhC | Load THDI of phase C | 负载侧C相THDI | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Load THDI of phase C of the device config table for the SVG.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.23 | hwSVGLoadReactivePowerOfPhaseA | Load reactive power of phase A | 负载侧A相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Load reactive power of phase A of the device config table for the SVG.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.24 | hwSVGLoadReactivePowerOfPhaseB | Load reactive power of phase B | 负载侧B相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Load reactive power of phase B of the device config table for the SVG.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.25 | hwSVGLoadReactivePowerOfPhaseC | Load reactive power of phase C | 负载侧C相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Load reactive power of phase C of the device config table for the SVG.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.26 | hwSVGGridPowerFactorOfPhA | Grid power factor of phase A | 源侧A相功率因数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid power factor of phase A of the device config table for the SVG.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.27 | hwSVGGridPowerFactorOfPhB | Grid power factor of phase B | 源侧B相功率因数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid power factor of phase B of the device config table for the SVG.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.28 | hwSVGGridPowerFactorOfPhC | Grid power factor of phase C | 源侧C相功率因数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid power factor of phase C of the device config table for the SVG.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.29 | hwSVGGridFrOfPhA | Grid frequency of phase A | 源侧A相频率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid frequency of phase A of the device config table for the SVG.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.30 | hwSVGGridFrOfPhB | Grid frequency of phase B | 源侧B相频率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid frequency of phase B of the device config table for the SVG.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.31 | hwSVGGridFrOfPhC | Grid frequency of phase C | 源侧C相频率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Grid frequency of phase C of the device config table for the SVG.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.32 | hwSVGCompCurrLoadRateOfSVGPhA | Compensation current load rate of SVG phase A | SVG A相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of SVG phase A of the device config table for the SVG.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.33 | hwSVGCompCurrLoadRateOfSVGPhB | Compensation current load rate of SVG phase B | SVG B相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of SVG phase B of the device config table for the SVG.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.34 | hwSVGCompCurrLoadRateOfSVGPhC | Compensation current load rate of SVG phase C | SVG C相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of SVG phase C of the device config table for the SVG.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.35 | hwSVGCompCurrLoadRateOfAPFPhA | Compensation current load rate of APF phase A | APF A相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of APF phase A of the device config table for the SVG.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.36 | hwSVGCompCurrLoadRateOfAPFPhB | Compensation current load rate of APF phase B | APF B相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of APF phase B of the device config table for the SVG.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.37 | hwSVGCompCurrLoadRateOfAPFPhC | Compensation current load rate of APF phase C | APF C相补偿电流负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Compensation current load rate of APF phase C of the device config table for the SVG.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.38 | hwSVGSwitchType | Switch type | 开关类型 | 1-Read_Write | 读写 | ABB(1), HUAWEI(2), unknown(255) | [ABB=1]/[华为=2] | Switch type of the device config table for the SVG. Value 1 indicate ABB Value 2 indicate HUAWEI
1.3.6.1.4.1.2011.6.178.1.1.9.21.2.1.101 | hwSVGConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG.

## HAQ61
空气质量传感器HAQ61
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.135.6 | hwHAQ61 | hwHAQ61 | hwHAQ61 | / | / | / | / | HAQ61 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1 | hwHAQ61RunningAndConfig1Table | / | / | / | / | / | / | The running and config table of HAQ61
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.1 | hwHAQ61RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the HAQ61
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.2 | hwHAQ61ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the HAQ61.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.3 | hwHAQ61PortNodot | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo. of the device running and config table for the HAQ61.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.4 | hwHAQ61CommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the HAQ61.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.5 | hwHAQ61Temperature | Temperature | 温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature of the device running and config table for the HAQ61. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.6 | hwHAQ61Humidity | Humidity | 湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Humidity of the device running and config table for the HAQ61. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.7 | hwHAQ61Pm1dot0 | PM1.0 | PM1.0 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Pm1.0 of the device running and config table for the HAQ61. SigUnitInfo:ug/m³.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.8 | hwHAQ61Pm2dot5 | PM2.5 | PM2.5 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Pm2.5 of the device running and config table for the HAQ61. SigUnitInfo:ug/m³.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.9 | hwHAQ61Pm10 | PM10 | PM10 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Pm10 of the device running and config table for the HAQ61. SigUnitInfo:ug/m³.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.10 | hwHAQ61Co2ConcentrationValue | CO2 concentration value | CO2浓度值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Co2ConcentrationValue of the device running and config table for the HAQ61. SigUnitInfo:ppm.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.11 | hwHAQ61FormaldehydeConcentrationValue | Formaldehyde concentration value | 甲醛浓度值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FormaldehydeConcentrationValue of the device running and config table for the HAQ61. SigUnitInfo:mg/m³.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.12 | hwHAQ61VocConcentrationValue | VOC concentration value | VOC浓度值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | VocConcentrationValue of the device running and config table for the HAQ61. SigUnitInfo:mg/m³.
1.3.6.1.4.1.2011.6.178.1.1.135.6.1.1.13 | hwHAQ61Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of HAQ61.

## TH-802C
TH-802C
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.135.5 | hwTH802C | hwTH802C | hwTH802C | / | / | / | / | TH802C Equipment.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1 | hwTH802CRunningAndConfig1Table | / | / | / | / | / | / | The running and config table of TH802C
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.1 | hwTH802CRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the TH802C
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.2 | hwTH802CModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the TH802C.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.3 | hwTH802CPortNodot | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo. of the device running and config table for the TH802C.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.4 | hwTH802CCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the TH802C.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.5 | hwTH802CTemperature | Temperature | 温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature of the device running and config table for the TH802C. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.6 | hwTH802CHumidity | Humidity | 湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Humidity of the device running and config table for the TH802C. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.7 | hwTH802CDewPointTemperature | Dew point temperature | 露点温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | DewPointTemperature of the device running and config table for the TH802C. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.8 | hwTH802CTemperatureOffset | Temperature offset | 温度偏移量 | 1-Read_Write | 只读 | 0..65535 | 0..65535 | TemperatureOffset of the device running and config table for the TH802C.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.9 | hwTH802CHumidityOffset | Humidity offset | 湿度偏移量 | 1-Read_Write | 只读 | 0..65535 | 0..65535 | HumidityOffset of the device running and config table for the TH802C.
1.3.6.1.4.1.2011.6.178.1.1.135.5.1.1.10 | hwTH802CConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of TH802C.

## HSDP-A100M
压差传感器HSDP-A100M
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.135.7 | hwHSDPA100M | hwHSDPA100M | hwHSDPA100M | / | / | / | / | HSDPA100M Equipment.
1.3.6.1.4.1.2011.6.178.1.1.135.7.1 | hwHSDPA100MRunningAndConfig1Table | / | / | / | / | / | / | The running and config table of HSDPA100M
1.3.6.1.4.1.2011.6.178.1.1.135.7.1.1.1 | hwHSDPA100MRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the HSDPA100M
1.3.6.1.4.1.2011.6.178.1.1.135.7.1.1.2 | hwHSDPA100MModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the HSDPA100M.
1.3.6.1.4.1.2011.6.178.1.1.135.7.1.1.3 | hwHSDPA100MPortNodot | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo. of the device running and config table for the HSDPA100M.
1.3.6.1.4.1.2011.6.178.1.1.135.7.1.1.4 | hwHSDPA100MCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the HSDPA100M.
1.3.6.1.4.1.2011.6.178.1.1.135.7.1.1.5 | hwHSDPA100MPressure | Pressure | 压力值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Pressure of the device running and config table for the HSDPA100M. Multiple:10. SigUnitInfo:Pa.
1.3.6.1.4.1.2011.6.178.1.1.135.7.1.1.6 | hwHSDPA100MRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of HSDPA100M.

## SGA500B
氢气传感器SGA500B
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.135.11 | hwHydrogengasSensorSGA500B | hwHydrogengasSensorSGA500B | hwHydrogengasSensorSGA500B | / | / | / | / | HydrogengasSensorSGA500B Equipment.
1.3.6.1.4.1.2011.6.178.1.1.135.11.1 | hwSGA500BRunningAndConfig1Table | / | / | / | / | / | / | The running and config table of SGA500B
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.1 | hwSGA500BRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the SGA500B
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.2 | hwSGA500BModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the SGA500B.
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.3 | hwSGA500BPortNodot | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNodot of the device running and config table for the SGA500B.
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.4 | hwSGA500BCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the SGA500B.
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.5 | hwSGA500BDeviceState | Device state | 设备状态 | 0-Read_Only | 只读 | normal(1),underReport(2),highReport(3),hydrogenSensorFault(4),unknown(255) | [1=正常][2=低报][3=高报][4=传感器故障] | DeviceState of the device running and config table for the SGA500B. Value1 indicate Normal Value2 indicate Under report Value3 indicate High report Value4 indicate Hydrogen sensor fault .
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.6 | hwSGA500BMeasuredConcentrationValue | Measured concentration value | 测量浓度值 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | MeasuredConcentrationValue of the device running and config table for the SGA500B. Multiple:10. SigUnitInfo:%LEL.
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.7 | hwSGA500BNameOfSubstance | Name of substance | 物质名称 | 0-Read_Only | 只读 | none(1),hydrogenGas(2),unknown(255) | [1=无][2=氢气] | NameOfSubstance of the device running and config table for the SGA500B. Value1 indicate None Value2 indicate Hydrogen gas .
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.8 | hwSGA500BHighAlarmLimit | High alarm limit | 高限报警值 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | HighAlarmLimit of the device running and config table for the SGA500B. Multiple:10. SigUnitInfo:%LEL.
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.9 | hwSGA500BLowAlarmLimit | Low alarm limit | 低限报警值 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | LowAlarmLimit of the device running and config table for the SGA500B. Multiple:10. SigUnitInfo:%LEL.
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.10 | hwSGA500BDetectionRange | Detection range | 检测量程 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | DetectionRange of the device running and config table for the SGA500B. Multiple:10. SigUnitInfo:%LEL.
1.3.6.1.4.1.2011.6.178.1.1.135.11.1.1.11 | hwSGA500BConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SGA500B.

## NetCol8000-C
NetCol8000-C
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.22 | NetCol8000C | NetCol8000-C | NetCol8000-C | / | / | / | / | NetCol8000-C Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1 | hwNetCol8000CRunning1Table | / | / |  |  | / | / | The running table of NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.1 | hwNetCol8000CRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.2 | hwNetCol8000CIndoorFanTotalRuntime | Indoor fan total runtime | 室内风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.3 | hwNetCol8000CIndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 1 total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.4 | hwNetCol8000CIndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 2 total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.5 | hwNetCol8000CIndoorFan3TotalRuntime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 3 total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.6 | hwNetCol8000CIndoorFan4TotalRuntime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 4 total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.7 | hwNetCol8000CHumidifierPumpTotalRuntime | Humidifier pump total runtime | 加湿水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier pump total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.8 | hwNetCol8000CHumidifierTotalRuntime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.9 | hwNetCol8000CElectricHeaterTotalRuntime | Electric heater total runtime | 电加热累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Electric heater total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.10 | hwNetCol8000CElectricHeater1TotalRuntime | Electric heater 1 total runtime | 电加热1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Electric heater 1 total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.11 | hwNetCol8000CElectricHeater2TotalRuntime | Electric heater 2 total runtime | 电加热2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Electric heater 2 total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.12 | hwNetCol8000CDrainPumpTotalRuntime | Drain pump total runtime | 排水水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Drain pump total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.13 | hwNetCol8000CReturnAirFilterTotalRuntime | Return air filter total runtime | 回风过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Return air filter total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.14 | hwNetCol8000CChilledWaterValveTotalRuntime | Chilled water valve total runtime | 冷冻水阀累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Chilled water valve total runtime of the device config table for the NetCol8000-C.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.15 | hwNetCol8000CTotalPowerConsumptionOfTheUnit | Total power consumption of the unit | 机组累计耗电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total power consumption of the unit of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.16 | hwNetCol8000COnorOffStatusOfSystem | On/Off status of system | 机组开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | On/Off status of system of the device config table for the NetCol8000-C. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.17 | hwNetCol8000CCoolingOutput | Cooling output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Cooling output of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.18 | hwNetCol8000CIndoorFanOutput | Indoor fan output | 室内风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan output of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.19 | hwNetCol8000CHumidifyingOutput | Humidifying output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidifying output of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.20 | hwNetCol8000CHeatingOutput | Heating output | 加热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Heating output of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.21 | hwNetCol8000CDehumid | Dehumid | 除湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Dehumid of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.22 | hwNetCol8000CCoolingCapacity | Cooling capacity | 制冷量 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | Cooling capacity of the device config table for the NetCol8000-C.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.23 | hwNetCol8000CTeamworkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), intelligentteamworkcontrol(2), icooling(3), unknown(255) | [单机=1]/[智能群控=2]/[iCooling=3] | Teamwork status of the device config table for the NetCol8000-C. Value 1 indicate single Value 2 indicate intelligentteamworkcontrol Value 3 indicate icooling
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.24 | hwNetCol8000COperatingModeOfTheSystem | Operating mode of the system | 系统运行模式 | 0-Read_Only | 只读 | automaticmode(1), diagnosismode(2), wizard-basedstartup(3), unknown(255) | [自动模式=1]/[诊断模式=2]/[向导式开机=3] | Operating mode of the system of the device config table for the NetCol8000-C. Value 1 indicate automaticmode Value 2 indicate diagnosismode Value 3 indicate wizard-basedstartup
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.25 | hwNetCol8000CPowerFrequency | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | Power frequency of the device config table for the NetCol8000-C.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.26 | hwNetCol8000CABLineVoltage | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | A-B line voltage of the device config table for the NetCol8000-C.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.27 | hwNetCol8000CBCLineVoltage | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | B-C line voltage of the device config table for the NetCol8000-C.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.28 | hwNetCol8000CCALineVoltage | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | C-A line voltage of the device config table for the NetCol8000-C.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.29 | hwNetCol8000CBackupABLineVoltage | Backup A-B line voltage | 备路AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup A-B line voltage of the device config table for the NetCol8000-C.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.30 | hwNetCol8000CBackupBCLineVoltage | Backup B-C line voltage | 备路BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup B-C line voltage of the device config table for the NetCol8000-C.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.31 | hwNetCol8000CBackupCALineVoltage | Backup C-A line voltage | 备路CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup C-A line voltage of the device config table for the NetCol8000-C.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.32 | hwNetCol8000CBackupPowerFrequency | Backup power frequency | 备路电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | Backup power frequency of the device config table for the NetCol8000-C.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.33 | hwNetCol8000CUnitPower | Unit power | 机组功率 | 0-Read_Only | 只读 | 0..4000 | 0..4000 | Unit power of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.34 | hwNetCol8000CPhaseACurrent | Phase A current | 系统电源A相电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase A current of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.35 | hwNetCol8000CPhaseBCurrent | Phase B current | 系统电源B相电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase B current of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.36 | hwNetCol8000CPhaseCCurrent | Phase C current | 系统电源C相电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase C current of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.37 | hwNetCol8000CTemperatureAndHumidityControlType | Temperature and humidity control type | 温湿度控制类型 | 0-Read_Only | 只读 | return-air(1), supply-air(2), cold-aisle(3), hot-aisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | Temperature and humidity control type of the device config table for the NetCol8000-C. Value 1 indicate return-air Value 2 indicate supply-air Value 3 indicate cold-aisle Value 4 indicate hot-aisle
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.38 | hwNetCol8000CCurrentTemperature | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Current temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.39 | hwNetCol8000CCurrentHumidity | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Current humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.40 | hwNetCol8000CAverageSupplyAirTemperature | Average supply air temperature | 送风平均温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average supply air temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.41 | hwNetCol8000CAverageReturnAirTemperature | Average return air temperature | 回风平均温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average return air temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.42 | hwNetCol8000CAverageColdAisleTemperature | Average cold aisle temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average cold aisle temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.43 | hwNetCol8000CAverageHotAisleTemperature | Average hot aisle temperature | 热通道平均温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average hot aisle temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.44 | hwNetCol8000CAverageSupplyAirHumidity | Average supply air humidity | 送风平均湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average supply air humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.45 | hwNetCol8000CAverageReturnAirHumidity | Average return air humidity | 回风平均湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average return air humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.46 | hwNetCol8000CAverageColdAisleHumidity | Average cold aisle humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average cold aisle humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.47 | hwNetCol8000CAverageHotAisleHumidity | Average hot aisle humidity | 热通道平均湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average hot aisle humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.48 | hwNetCol8000CColdAisle1Temperature | Cold aisle 1 temperature | 冷通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 1 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.49 | hwNetCol8000CColdAisle2Temperature | Cold aisle 2 temperature | 冷通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 2 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.50 | hwNetCol8000CColdAisle3Temperature | Cold aisle 3 temperature | 冷通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 3 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.51 | hwNetCol8000CColdAisle4Temperature | Cold aisle 4 temperature | 冷通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 4 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.52 | hwNetCol8000CColdAisle5Temperature | Cold aisle 5 temperature | 冷通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 5 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.53 | hwNetCol8000CColdAisle1Humidity | Cold aisle 1 humidity | 冷通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 1 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.54 | hwNetCol8000CColdAisle2Humidity | Cold aisle 2 humidity | 冷通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 2 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.55 | hwNetCol8000CColdAisle3Humidity | Cold aisle 3 humidity | 冷通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 3 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.56 | hwNetCol8000CColdAisle4Humidity | Cold aisle 4 humidity | 冷通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 4 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.57 | hwNetCol8000CColdAisle5Humidity | Cold aisle 5 humidity | 冷通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 5 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.58 | hwNetCol8000CHotAisle1Temperature | Hot aisle 1 temperature | 热通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 1 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.59 | hwNetCol8000CHotAisle2Temperature | Hot aisle 2 temperature | 热通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 2 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.60 | hwNetCol8000CHotAisle3Temperature | Hot aisle 3 temperature | 热通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 3 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.61 | hwNetCol8000CHotAisle4Temperature | Hot aisle 4 temperature | 热通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 4 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.62 | hwNetCol8000CHotAisle5Temperature | Hot aisle 5 temperature | 热通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 5 temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.63 | hwNetCol8000CHotAisle1Humidity | Hot aisle 1 humidity | 热通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 1 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.64 | hwNetCol8000CHotAisle2Humidity | Hot aisle 2 humidity | 热通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 2 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.65 | hwNetCol8000CHotAisle3Humidity | Hot aisle 3 humidity | 热通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 3 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.66 | hwNetCol8000CHotAisle4Humidity | Hot aisle 4 humidity | 热通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 4 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.67 | hwNetCol8000CHotAisle5Humidity | Hot aisle 5 humidity | 热通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 5 humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.68 | hwNetCol8000CFreshAirTemperature | Fresh air temperature | 新风温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Fresh air temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.69 | hwNetCol8000CFreshAirHumidity | Fresh air humidity | 新风湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Fresh air humidity of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.70 | hwNetCol8000CIndoorFanRunningStatus | Indoor fan running status | 室内风机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan running status of the device config table for the NetCol8000-C.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.71 | hwNetCol8000CIndoorFan1RunningStatus | Indoor fan 1 running status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 1 running status of the device config table for the NetCol8000-C.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.72 | hwNetCol8000CIndoorFan2RunningStatus | Indoor fan 2 running status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 2 running status of the device config table for the NetCol8000-C.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.73 | hwNetCol8000CIndoorFan3RunningStatus | Indoor fan 3 running status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 3 running status of the device config table for the NetCol8000-C.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.74 | hwNetCol8000CIndoorFan4RunningStatus | Indoor fan 4 running status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 4 running status of the device config table for the NetCol8000-C.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.75 | hwNetCol8000CIndoorFanControlStatus | Indoor fan control status | 室内风机控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan control status of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.76 | hwNetCol8000CIndoorFan1ControlStatus | Indoor fan 1 control status | 室内风机1控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan 1 control status of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.77 | hwNetCol8000CIndoorFan2ControlStatus | Indoor fan 2 control status | 室内风机2控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan 2 control status of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.78 | hwNetCol8000CIndoorFan3ControlStatus | Indoor fan 3 control status | 室内风机3控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan 3 control status of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.79 | hwNetCol8000CIndoorFan4ControlStatus | Indoor fan 4 control status | 室内风机4控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan 4 control status of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.80 | hwNetCol8000CWetFilmHumidifierRunningStatus | Wet film humidifier running status | 湿膜加湿运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier running status of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.81 | hwNetCol8000CDrainPumpRunningStatus | Drain pump running status | 排水水泵运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Drain pump running status of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.82 | hwNetCol8000CChilledWaterValveRunningStatus | Chilled water valve running status | 冷冻水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Chilled water valve running status of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.83 | hwNetCol8000CSupplyWaterTemperature | Supply water temperature | 供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply water temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.84 | hwNetCol8000CReturnWaterTemperature | Return water temperature | 回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return water temperature of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.85 | hwNetCol8000CMacAddress | MAC address | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC address of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.86 | hwNetCol8000CELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.87 | hwNetCol8000CCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the NetCol8000-C. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.88 | hwNetCol8000CIpAddress | IP address | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IP address of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.89 | hwNetCol8000CEsn | ESN | ESN号 | 0-Read_Only | 只读 | 0..32 | 0..32 | ESN of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.90 | hwNetCol8000CControlBoardSoftwareVersion | Control board software version | 控制板软件版本号 | 0-Read_Only | 只读 | 0..2 | 0..2 | Control board software version of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.91 | hwNetCol8000CControlBoardHardwareVersion | Control board hardware version | 控制板硬件版本号 | 0-Read_Only | 只读 | 0..2 | 0..2 | Control board hardware version of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.92 | hwNetCol8000CFactoryInfo | Factory info | 厂家信息 | 0-Read_Only | 只读 | 0..20 | 0..20 | Factory info of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.93 | hwNetCol8000CSoftwareVersion | Software version | 版本号 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.94 | hwNetCol8000CActualTotalNumberOfSystemsInThisGroup | Actual total number of systems in this group | 本群组实际机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Actual total number of systems in this group of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.95 | hwNetCol8000CNumberOfActualActiveSystemsInThisGroup | Number of actual active systems in this group | 本群组实际运行机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Number of actual active systems in this group of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.96 | hwNetCol8000CNumberOfActualStandbySystemsInThisGroup | Number of actual standby systems in this group | 本群组实际备机机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Number of actual standby systems in this group of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.97 | hwNetCol8000CNumberOfSystemsInThisGroup | Number of systems in this group | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of systems in this group of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.98 | hwNetCol8000CNumberOfRunningSystemsInThisGroup | Number of running systems in this group | 本群组运行机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of running systems in this group of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.99 | hwNetCol8000CActiveorStandbyFlag | Active/Standby flag | 运行机备机标志 | 0-Read_Only | 只读 | active(1), standby(2), unknown(255) | [运行机=1]/[备机=2] | Active/Standby flag of the device config table for the NetCol8000-C. Value 1 indicate active Value 2 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.10.22.1.1.300 | hwNetCol8000CRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2 | hwNetCol8000CConfig2Table | / | / |  |  | / | / | The config table of NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.1 | hwNetCol8000CConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.2 | hwNetCol8000CStartuporShutdownControl | Startup/Shutdown control | 控制开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Startup/Shutdown control of the device config table for the NetCol8000-C. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.3 | hwNetCol8000CReturnAirHighTemperatureAlarmThreshold | Return Air High Temperature Alarm Threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 250..550 | 250..550 | Return Air High Temperature Alarm Threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.4 | hwNetCol8000CReturnAirLowTemperatureAlarmThreshold | Return Air Low Temperature Alarm Threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Return Air Low Temperature Alarm Threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.5 | hwNetCol8000CSupplyAirHighTemperatureAlarmThreshold | Supply Air High Temperature Alarm Threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Supply Air High Temperature Alarm Threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.6 | hwNetCol8000CSupplyAirLowTemperatureAlarmThreshold | Supply Air Low Temperature Alarm Threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | Supply Air Low Temperature Alarm Threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.7 | hwNetCol8000CColdAisleHighTemperatureAlarmThreshold | Cold aisle high temperature alarm threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Cold aisle high temperature alarm threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.8 | hwNetCol8000CColdAisleLowTemperatureAlarmThreshold | Cold aisle low temperature alarm threshold | 冷通道低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | Cold aisle low temperature alarm threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.9 | hwNetCol8000CHotAisleHighTemperatureAlarmThreshold | Hot aisle high temperature alarm threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Hot aisle high temperature alarm threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.10 | hwNetCol8000CHotAisleLowTemperatureAlarmThreshold | Hot aisle low temperature alarm threshold | 热通道低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Hot aisle low temperature alarm threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.11 | hwNetCol8000CHighHumidityAlarmThreshold | High Humidity Alarm Threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | High Humidity Alarm Threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.12 | hwNetCol8000CLowHumidityAlarmThreshold | Low humidity alarm threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | Low humidity alarm threshold of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.13 | hwNetCol8000CTemperatureSetPoint | Temperature set point | 温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | Temperature set point of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:Degrees Celsius.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.14 | hwNetCol8000CHumiditySetPoint | Humidity set point | 湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Humidity set point of the device config table for the NetCol8000-C.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.15 | hwNetCol8000CTemperatureAndHumiditySetControlType | Temperature and Humidity Control Type | 温湿度控制类型 | 1-Read_Write | 读写 | returnair(1), supplyair(2), coldaisle(3), hotaisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | Temperature and Humidity Control Type of the device config table for the NetCol8000-C. Value 1 indicate return-air Value 2 indicate supply-air Value 3 indicate cold-aisle Value 4 indicate hot-aisle
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.16 | hwNetCol8000CMinimumSpeedOfTheIndoorFan | Minimum speed of the indoor fan | 室内风机最小转速 | 1-Read_Write | 读写 | 15..100 | 15..100 | Minimum speed of the indoor fan of the device config table for the NetCol8000-C.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.17 | hwNetCol8000CDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the NetCol8000-C.
1.3.6.1.4.1.2011.6.178.1.1.10.22.2.1.300 | hwNetCol8000CConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol8000-C.

## Combustible Gas Sensor
可燃气体传感器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.135.10 | CombustibleGasSensor | Combustible Gas Sensor | CO气体传感器 | / | / | / | / | Combustible Gas Sensor Equipment.
1.3.6.1.4.1.2011.6.178.1.1.135.10.1 | hwCombustibleGasSensorRunning1Table | / | / |  |  | / | / | The running table of Combustible Gas Sensor.
1.3.6.1.4.1.2011.6.178.1.1.135.10.1.1.1 | hwCombustibleGasSensorRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Combustible Gas Sensor.
1.3.6.1.4.1.2011.6.178.1.1.135.10.1.1.2 | hwCombustibleGasSensorCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Combustible Gas Sensor. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.135.10.1.1.3 | hwCombustibleGasSensorPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Combustible Gas Sensor.
1.3.6.1.4.1.2011.6.178.1.1.135.10.1.1.4 | hwCombustibleGasSensorModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..247 | 1..247 | Modbus address of the device config table for the Combustible Gas Sensor.
1.3.6.1.4.1.2011.6.178.1.1.135.10.1.1.5 | hwCombustibleGasSensorCurrentGasConcentration | CO current gas concentration | CO当前气体浓度 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | CO current gas concentration of the device config table for the Combustible Gas Sensor.SigUnitInfo:ppm.
1.3.6.1.4.1.2011.6.178.1.1.135.10.1.1.300 | hwCombustibleGasSensorRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Combustible Gas Sensor.
1.3.6.1.4.1.2011.6.178.1.1.135.10.2 | hwCombustibleGasSensorConfig2Table | / | / |  |  | / | / | The config table of Combustible Gas Sensor.
1.3.6.1.4.1.2011.6.178.1.1.135.10.2.1.1 | hwCombustibleGasSensorConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Combustible Gas Sensor.
1.3.6.1.4.1.2011.6.178.1.1.135.10.2.1.2 | hwCombustibleGasSensorDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Combustible Gas Sensor.
1.3.6.1.4.1.2011.6.178.1.1.135.10.2.1.3 | hwCombustibleGasSensorAlarmThreshold | Alarm threshold | 告警阈值 | 1-Read_Write | 读写 | 0..2000 | 0..2000 | Alarm threshold of the device config table for the Combustible Gas Sensor.SigUnitInfo:ppm.
1.3.6.1.4.1.2011.6.178.1.1.135.10.2.1.4 | hwCombustibleGasSensorCollectionInterval | Collection interval | 采集时间间隔 | 1-Read_Write | 读写 | zeroPointOneSecond(1), zeroPointTwoSecond(2), zeroPointThreeSecond(3), zeroPointFiveSecond(4), oneSecond(5), twoSeconds(6), threeSeconds(7), fiveSeconds(8), unknown(255) | [0.1s=1]/[0.2s=2]/[0.3s=3]/[0.5s=4]/[1.0s=5]/[2.0s=6]/[3.0s=7]/[5.0s=8] | Collection interval of the device config table for the Combustible Gas Sensor. Value 1 indicate 0.1s Value 2 indicate 0.2s Value 3 indicate 0.3s Value 4 indicate 0.5s Value 5 indicate 1s Value 6 indicate 2s Value 7 indicate 3s Value 8 indicate 5s
1.3.6.1.4.1.2011.6.178.1.1.135.10.2.1.300 | hwCombustibleGasSensorConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Combustible Gas Sensor.

## APFSINENGASCII
APF-SINENG-ASCII
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.23 | hwAPFSINENGASCII | hwAPFSINENGASCII | hwAPFSINENGASCII | / | / | / | / | APFSINENGASCII Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1 | hwAPFSINENGASCIIRunningAndConfig1Table | / | / |  |  | / | / | The running and config table of APFSINENGASCII
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.1 | hwAPFSINENGASCIIRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the APFSINENGASCII
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.2 | hwAPFSINENGASCIIModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the APFSINENGASCII.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.3 | hwAPFSINENGASCIIPortNo | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running and config table for the APFSINENGASCII.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.4 | hwAPFSINENGASCIICommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the APFSINENGASCII.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.5 | hwAPFSINENGASCIIRmsOfPhaseAAbLineGridVoltage | RMS of Phase-A(AB line)grid voltage | A相(AB线)电网电压有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseAAbLineGridVoltage of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.6 | hwAPFSINENGASCIIRmsOfPhaseBBcLineGridVoltage | RMS of Phase-B(BC line)grid voltage | B相(BC线)电网电压有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseBBcLineGridVoltage of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.7 | hwAPFSINENGASCIIRmsOfPhaseCCaLineGridVoltage | RMS of Phase-C(CA line)grid voltage | C相(CA线)电网电压有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseCCaLineGridVoltage of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.8 | hwAPFSINENGASCIIRmsOfPhaseACurrentOnTheGridSide | RMS of Phase-A current on the grid side | A相电网侧电流有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseACurrentOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.9 | hwAPFSINENGASCIIRmsOfPhaseBCurrentOnTheGridSide | RMS of Phase-B current on the grid side | B相电网侧电流有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseBCurrentOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.10 | hwAPFSINENGASCIIRmsOfPhaseCCurrentOnTheGridSide | RMS of Phase-C current on the grid side | C相电网侧电流有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseCCurrentOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.11 | hwAPFSINENGASCIIRmsOfPhaseACurrentOnTheLoadSide | RMS of Phase-A current on the load side | A相负载侧电流有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseACurrentOnTheLoadSide of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.12 | hwAPFSINENGASCIIRmsOfPhaseBCurrentOnTheLoadSide | RMS of Phase-B current on the load side | B相负载侧电流有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseBCurrentOnTheLoadSide of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.13 | hwAPFSINENGASCIIRmsOfPhaseCCurrentOnTheLoadSide | RMS of Phase-C current on the load side | C相负载侧电流有效值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseCCurrentOnTheLoadSide of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.14 | hwAPFSINENGASCIIRmsOfPhaseACompensatingCurrent | RMS of Phase-A compensating on the load side | A相补偿电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseACompensatingCurrent of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.15 | hwAPFSINENGASCIIRmsOfPhaseBCompensatingCurrent | RMS of Phase-B compensating on the load side | B相补偿电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseBCompensatingCurrent of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.16 | hwAPFSINENGASCIIRmsOfPhaseCCompensatingCurrent | RMS of Phase-C compensating on the load side | C相补偿电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | RmsOfPhaseCCompensatingCurrent of the device running and config table for the APFSINENGASCII. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.17 | hwAPFSINENGASCIIThduOfPhaseAAbLineOnTheGridSide | THDU of Phase-A (AB line) on the grid side | A相(AB线)电网侧THDU | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThduOfPhaseAAbLineOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.18 | hwAPFSINENGASCIIThduOfPhaseBBcLineOnTheGridSide | THDU of Phase-B (BC line) on the grid side | B相(BC线)电网侧THDU | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThduOfPhaseBBcLineOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.19 | hwAPFSINENGASCIIThduOfPhaseCCaLineOnTheGridSide | THDU of Phase-C (CA line) on the grid side | C相(CA线)电网侧THDU | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThduOfPhaseCCaLineOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.20 | hwAPFSINENGASCIIThdiOfPhaseAOnTheGridSide | THDI of Phase-A on the grid side | A相电网侧THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThdiOfPhaseAOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.21 | hwAPFSINENGASCIIThdiOfPhaseBOnTheGridSide | THDI of Phase-B on the grid side | B相电网侧THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThdiOfPhaseBOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.22 | hwAPFSINENGASCIIThdiOfPhaseCOnTheGridSide | THDI of Phase-C on the grid side | C相电网侧THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThdiOfPhaseCOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.23 | hwAPFSINENGASCIIThdiOfPhaseAOnTheLoadSide | THDI of Phase-A on the load side | A相负载侧THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThdiOfPhaseAOnTheLoadSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.24 | hwAPFSINENGASCIIThdiOfPhaseBOnTheLoadSide | THDI of Phase-B on the load side | B相负载侧THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThdiOfPhaseBOnTheLoadSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.25 | hwAPFSINENGASCIIThdiOfPhaseCOnTheLoadSide | THDI of Phase-C on the load side | C相负载侧THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThdiOfPhaseCOnTheLoadSide of the device running and config table for the APFSINENGASCII. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.26 | hwAPFSINENGASCIIPowerFactorOfPhaseAOnTheGridSide | Power factor of Phase-A on the grid side | A相电网侧cosφ | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PowerFactorOfPhaseAOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.27 | hwAPFSINENGASCIIPowerFactorOfPhaseBOnTheGridSide | Power factor of Phase-B on the grid side | B相电网侧cosφ | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PowerFactorOfPhaseBOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.28 | hwAPFSINENGASCIIPowerFactorOfPhaseCOnTheGridSide | Power factor of Phase-C on the grid side | C相电网侧cosφ | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PowerFactorOfPhaseCOnTheGridSide of the device running and config table for the APFSINENGASCII. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.29 | hwAPFSINENGASCIIWorkingStatus | Working status | 工作状态 | 0-Read_Only | 只读 | notWorking(1),working(2),unknown(255) | [未工作=1]/[工作=2] | Working Status of the device running and config table for the APFSINENGASCII. Value1 indicate Not working Value2 indicate Working.
1.3.6.1.4.1.2011.6.178.1.1.9.23.1.1.30 | hwAPFSINENGASCIIRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of APFSINENGASCII.

## UMG96RM
UMG96RM
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.9 | hwUMG96RM | hwUMG96RM | hwUMG96RM | / |  | / |  | UMG96RM Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1 | hwUMG96RMRunningAndConfig1Table | / | / |  |  | / |  | The running and config table of UMG96RM
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.1 | hwAPFSINENGASCIIRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / |  | Index of the device running and config table for the UMG96RM
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.2 | hwAPFSINENGASCIIModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the UMG96RM.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.3 | hwAPFSINENGASCIIPortNo | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running and config table for the UMG96RM.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.4 | hwAPFSINENGASCIICommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the UMG96RM.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.5 | hwUMG96RML1NVoltage | L1-N voltage | L1-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1NVoltage of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.6 | hwUMG96RML2NVoltage | L2-N voltage | L2-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2NVoltage of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.7 | hwUMG96RML3NVoltage | L3-N voltage | L3-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3NVoltage of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.8 | hwUMG96RML1L2Voltage | L1-L2 voltage | L1-L2 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1L2Voltage of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.9 | hwUMG96RML2L3Voltage | L2-L3 voltage | L2-L3 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2L3Voltage of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.10 | hwUMG96RML3L1Voltage | L3-L1 voltage | L3-L1 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3L1Voltage of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.11 | hwUMG96RML1Current | L1 current | L1 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1Current of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.12 | hwUMG96RML2Current | L2 current | L2 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2Current of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.13 | hwUMG96RML3Current | L3 current | L3 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3Current of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.14 | hwUMG96RMTotalCurrent | Total current | 总电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalCurrent of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.15 | hwUMG96RML1RealPower | L1 real power | L1 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1RealPower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.16 | hwUMG96RML2RealPower | L2 real power | L2 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2RealPower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.17 | hwUMG96RML3RealPower | L3 real power | L3 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3RealPower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.18 | hwUMG96RMTotalRealPower | Total real power | 总有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalRealPower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.19 | hwUMG96RML1ApparentPower | L1 apparent power | L1 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ApparentPower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.20 | hwUMG96RML2ApparentPower | L2 apparent power | L2 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ApparentPower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.21 | hwUMG96RML3ApparentPower | L3 apparent power | L3 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ApparentPower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.22 | hwUMG96RMTotalApparentPower | Total apparent power | 总视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalApparentPower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.23 | hwUMG96RML1ReactivePower | L1 reactive power | L1 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactivePower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.24 | hwUMG96RML2ReactivePower | L2 reactive power | L2 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactivePower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.25 | hwUMG96RML3ReactivePower | L3 reactive power | L3 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactivePower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.26 | hwUMG96RMTotalReactivePower | Total reactive power | 总无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalReactivePower of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.27 | hwUMG96RML1PowerFactor | L1 power factor | L1 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1PowerFactor of the device running and config table for the UMG96RM. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.28 | hwUMG96RML2PowerFactor | L2 power factor | L2 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2PowerFactor of the device running and config table for the UMG96RM. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.29 | hwUMG96RML3PowerFactor | L3 power factor | L3 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3PowerFactor of the device running and config table for the UMG96RM. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.30 | hwUMG96RMFrequency | Frequency | 频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.31 | hwUMG96RML1RealEnergy | L1 real energy | L1 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1RealEnergy of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.32 | hwUMG96RML2RealEnergy | L2 real energy | L2 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2RealEnergy of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.33 | hwUMG96RML3RealEnergy | L3 real energy | L3 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3RealEnergy of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.34 | hwUMG96RMTotalRealEnergy | Total real energy | 总有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalRealEnergy of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.35 | hwUMG96RML1ApparentEnergy | L1 apparent energy | L1 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ApparentEnergy of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.36 | hwUMG96RML2ApparentEnergy | L2 apparent energy | L2 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ApparentEnergy of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.37 | hwUMG96RML3ApparentEnergy | L3 apparent energy | L3 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ApparentEnergy of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.38 | hwUMG96RMTotalApparentEnergy | Total apparent energy | 总视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalApparentEnergy of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.39 | hwUMG96RML1ReactiveEnergyInductive | L1 reactive energy inductive | L1 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactiveEnergyInductive of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.40 | hwUMG96RML2ReactiveEnergyInductive | L2 reactive energy inductive | L2 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactiveEnergyInductive of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.41 | hwUMG96RML3ReactiveEnergyInductive | L3 reactive energy inductive | L3 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactiveEnergyInductive of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.42 | hwUMG96RMTotalReactiveEnergyInductive | Total reactive energy inductive | 总无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalReactiveEnergyInductive of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.43 | hwUMG96RML1ReactiveEnergyCapacitive | L1 reactive energy capacitive | L1 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactiveEnergyCapacitive of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.44 | hwUMG96RML2ReactiveEnergyCapacitive | L2 reactive energy capacitive | L2 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactiveEnergyCapacitive of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.45 | hwUMG96RML3ReactiveEnergyCapacitive | L3 reactive energy capacitive | L3 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactiveEnergyCapacitive of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.46 | hwUMG96RMTotalReactiveEnergyCapacitive | Total reactive energy capacitive | 总无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalReactiveEnergyCapacitive of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.47 | hwUMG96RML1NThd | L1-N THD | L1-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1NThd of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.48 | hwUMG96RML2NThd | L2-N THD | L2-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2NThd of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.49 | hwUMG96RML3NThd | L3-N THD | L3-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3NThd of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.50 | hwUMG96RML1Thd | L1 THD | L1 THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1Thd of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.51 | hwUMG96RML2Thd | L2 THD | L2 THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2Thd of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.52 | hwUMG96RML3Thd | L3 THD | L3 THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3Thd of the device running and config table for the UMG96RM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.9.1.1.53 | hwUMG96RMRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UMG96RM.

## UMG96RM-CBM
UMG96RM-CBM
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.16 | hwUMG96RMCBM | hwUMG96RMCBM | hwUMG96RMCBM | / |  | / |  | UMG96RMCBM Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1 | hwUMG96RMCBMRunningAndConfig1Table | / | / |  |  | / |  | The running and config table of UMG96RMCBM
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.1 | hwUMG96RMCBMRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / |  | Index of the device running and config table for the UMG96RMCBM
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.2 | hwUMG96RMCBMModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the UMG96RMCBM.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.3 | hwUMG96RMCBMPortNodot | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNodot of the device running and config table for the UMG96RMCBM.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.4 | hwUMG96RMCBMCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the UMG96RMCBM.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.5 | hwUMG96RMCBMSwitchOnorOffStatus | Switch ON/OFF Status | 开关ON/OFF状态 | 0-Read_Only | 只读 | off(1),on(2),unknown(255) | [1=关][2=开] | SwitchOnorOffStatus of the device running and config table for the UMG96RMCBM. Value1 indicate OFF Value2 indicate ON
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.6 | hwUMG96RMCBMSwitchTripStatus | Switch Trip Status | 开关跳闸状态 | 0-Read_Only | 只读 | normal(1),alarm(2),unknown(255) | [1=正常][2=告警] | SwitchTripStatus of the device running and config table for the UMG96RMCBM. Value1 indicate normal Value2 indicate alarm
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.7 | hwUMG96RMCBMStatus,DigitalInput3 | Status, digital input 3 | 状态 数字输入3 | 0-Read_Only | 只读 | / | / | Status,DigitalInput3 of the device running and config table for the UMG96RMCBM.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.8 | hwUMG96RMCBMStatus,DigitalInput4 | Status, digital input 4 | 状态 数字输入4 | 0-Read_Only | 只读 | / | / | Status,DigitalInput4 of the device running and config table for the UMG96RMCBM.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.9 | hwUMG96RMCBML1NVoltage | L1-N voltage | L1-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1NVoltage of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.10 | hwUMG96RMCBML2NVoltage | L2-N voltage | L2-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2NVoltage of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.11 | hwUMG96RMCBML3NVoltage | L3-N voltage | L3-N 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3NVoltage of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.12 | hwUMG96RMCBML1L2Voltage | L1-L2 voltage | L1-L2 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1L2Voltage of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.13 | hwUMG96RMCBML2L3Voltage | L2-L3 voltage | L2-L3 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2L3Voltage of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.14 | hwUMG96RMCBML3L1Voltage | L3-L1 voltage | L3-L1 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3L1Voltage of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.15 | hwUMG96RMCBML1Current | L1 current | L1 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1Current of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.16 | hwUMG96RMCBML2Current | L2 current | L2 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2Current of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.17 | hwUMG96RMCBML3Current | L3 current | L3 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3Current of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.18 | hwUMG96RMCBMTotalCurrent | Total current | 总电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalCurrent of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.19 | hwUMG96RMCBML1RealPower | L1 real power | L1 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1RealPower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.20 | hwUMG96RMCBML2RealPower | L2 real power | L2 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2RealPower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.21 | hwUMG96RMCBML3RealPower | L3 real power | L3 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3RealPower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.22 | hwUMG96RMCBMTotalRealPower | Total real power | 总有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalRealPower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.23 | hwUMG96RMCBML1ApparentPower | L1 apparent power | L1 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ApparentPower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.24 | hwUMG96RMCBML2ApparentPower | L2 apparent power | L2 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ApparentPower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.25 | hwUMG96RMCBML3ApparentPower | L3 apparent power | L3 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ApparentPower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.26 | hwUMG96RMCBMTotalApparentPower | Total apparent power | 总视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalApparentPower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.27 | hwUMG96RMCBML1ReactivePower | L1 reactive power | L1 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactivePower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.28 | hwUMG96RMCBML2ReactivePower | L2 reactive power | L2 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactivePower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.29 | hwUMG96RMCBML3ReactivePower | L3 reactive power | L3 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactivePower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.30 | hwUMG96RMCBMTotalReactivePower | Total reactive power | 总无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalReactivePower of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.31 | hwUMG96RMCBML1PowerFactor | L1 power factor | L1 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1PowerFactor of the device running and config table for the UMG96RMCBM. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.32 | hwUMG96RMCBML2PowerFactor | L2 power factor | L2 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2PowerFactor of the device running and config table for the UMG96RMCBM. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.33 | hwUMG96RMCBML3PowerFactor | L3 power factor | L3 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3PowerFactor of the device running and config table for the UMG96RMCBM. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.34 | hwUMG96RMCBMFrequency | Frequency | 频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.35 | hwUMG96RMCBML1RealEnergy | L1 real energy | L1 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1RealEnergy of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.36 | hwUMG96RMCBML2RealEnergy | L2 real energy | L2 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2RealEnergy of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.37 | hwUMG96RMCBML3RealEnergy | L3 real energy | L3 有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3RealEnergy of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.38 | hwUMG96RMCBMTotalRealEnergy | Total real energy | 总有功电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalRealEnergy of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.39 | hwUMG96RMCBML1ApparentEnergy | L1 apparent energy | L1 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ApparentEnergy of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.40 | hwUMG96RMCBML2ApparentEnergy | L2 apparent energy | L2 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ApparentEnergy of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.41 | hwUMG96RMCBML3ApparentEnergy | L3 apparent energy | L3 视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ApparentEnergy of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.42 | hwUMG96RMCBMTotalApparentEnergy | Total apparent energy | 总视在电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalApparentEnergy of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.43 | hwUMG96RMCBML1ReactiveEnergyInductive | L1 reactive energy inductive | L1 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactiveEnergyInductive of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.44 | hwUMG96RMCBML2ReactiveEnergyInductive | L2 reactive energy inductive | L2 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactiveEnergyInductive of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.45 | hwUMG96RMCBML3ReactiveEnergyInductive | L3 reactive energy inductive | L3 无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactiveEnergyInductive of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.46 | hwUMG96RMCBMTotalReactiveEnergyInductive | Total reactive energy inductive | 总无功电量 感性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalReactiveEnergyInductive of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.47 | hwUMG96RMCBML1ReactiveEnergyCapacitive | L1 reactive energy capacitive | L1 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1ReactiveEnergyCapacitive of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.48 | hwUMG96RMCBML2ReactiveEnergyCapacitive | L2 reactive energy capacitive | L2 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2ReactiveEnergyCapacitive of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.49 | hwUMG96RMCBML3ReactiveEnergyCapacitive | L3 reactive energy capacitive | L3 无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3ReactiveEnergyCapacitive of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.50 | hwUMG96RMCBMTotalReactiveEnergyCapacitive | Total reactive energy capacitive | 总无功电量 容性 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalReactiveEnergyCapacitive of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.51 | hwUMG96RMCBML1NThd | L1-N THD | L1-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1NThd of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.52 | hwUMG96RMCBML2NThd | L2-N THD | L2-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2NThd of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.53 | hwUMG96RMCBML3NThd | L3-N THD | L3-N THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3NThd of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.54 | hwUMG96RMCBML1Thd | L1 THD | L1 THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1Thd of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.55 | hwUMG96RMCBML2Thd | L2 THD | L2 THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2Thd of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.56 | hwUMG96RMCBML3Thd | L3 THD | L3 THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3Thd of the device running and config table for the UMG96RMCBM. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.16.1.1.57 | hwUMG96RMCBMRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UMG96RMCBM.

## UX1
除湿机UX1
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.18 | hwUX1 | hwUX1 | hwUX1 | / | / | / | / | UX1 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1 | hwUX1RunningAndConfig1Table | / | / | / | / | / | / | The running and config table of UX1
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.1 | hwUX1RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the UX1
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.2 | hwUX1ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the UX1.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.3 | hwUX1PortNodot | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo. of the device running and config table for the UX1.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.4 | hwUX1CommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the UX1.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.5 | hwUX1AccumulatedWorkingTimeOfTheUnit | Accumulated working time of the unit | 机组累计工作时间 | 0-Read_Only | 只读 | / | / | AccumulatedWorkingTimeOfTheUnit of the device running and config table for the UX1. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.6 | hwUX1AccumulatedWorkingTimeOfSupplyFan | Accumulated working time of supply fan | 送风机累计工作时间 | 0-Read_Only | 只读 | / | / | AccumulatedWorkingTimeOfSupplyFan of the device running and config table for the UX1. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.7 | hwUX1Compressor1AccumulatedWorkingTime | Compressor 1 Accumulated Working Time | 压缩机1累计工作时间 | 0-Read_Only | 只读 | / | / | Compressor1AccumulatedWorkingTime of the device running and config table for the UX1. SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.8 | hwUX1PowerFailure1OrFireAlarm1 | Power failure1 or fire alarm1 | 电源故障1/火灾报警1 | 0-Read_Only | 只读 | close(1),open(2),unknown(255) | [1=闭合][2=断开] | PowerFailure1OrFireAlarm1 of the device running and config table for the UX1. Value1 indicate close Value2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.9 | hwUX1SupplyFanOverload | Supply fan overload | 送风机过载 | 0-Read_Only | 只读 | close(1),open(2),unknown(255) | [1=闭合][2=断开] | SupplyFanOverload of the device running and config table for the UX1. Value1 indicate close Value2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.10 | hwUX1CompressorOverloadOrHighPressureProtection | Compressor overload or high pressure protection | 压缩机过载或高压保护 | 0-Read_Only | 只读 | close(1),open(2),unknown(255) | [1=闭合][2=断开] | CompressorOverloadOrHighPressureProtection of the device running and config table for the UX1. Value1 indicate close Value2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.11 | hwUX1CompressorLowPressureProtection | Compressor low pressure protection | 压缩机低压保护 | 0-Read_Only | 只读 | close(1),open(2),unknown(255) | [1=闭合][2=断开] | CompressorLowPressureProtection of the device running and config table for the UX1. Value1 indicate close Value2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.12 | hwUX1Blower | Blower | 送风机 | 0-Read_Only | 只读 | open(1),close(2),unknown(255) | [1=断开][2=闭合] | Blower of the device running and config table for the UX1. Value1 indicate open Value2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.13 | hwUX1Compressor | Compressor | 压缩机 | 0-Read_Only | 只读 | open(1),close(2),unknown(255) | [1=断开][2=闭合] | Compressor of the device running and config table for the UX1. Value1 indicate open Value2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.14 | hwUX1RunningStatusOfTheUnit | Running status of the unit | 机组运行 | 0-Read_Only | 只读 | unitShutdown(1),unitStarted(2),unknown(255) | [1=机组关机][2=机组开机] | RunningStatusOfTheUnit of the device running and config table for the UX1. Value1 indicate Unit shutdown Value2 indicate Unit started
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.15 | hwUX1DehumidificationStatus | Dehumidification status | 除湿状态 | 0-Read_Only | 只读 | close(1),open(2),unknown(255) | [1=关闭][2=开启] | DehumidificationStatus of the device running and config table for the UX1. Value1 indicate no Value2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.16 | hwUX1FaultStatus | Fault Status | 故障状态 | 0-Read_Only | 只读 | normal(1),fault(2),unknown(255) | [1=正常][2=故障] | FaultStatus of the device running and config table for the UX1. Value1 indicate no Value2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.17 | hwUX1ForcedStartupStatus | Forced startup status | 强制启动状态 | 0-Read_Only | 只读 | close(1),open(2),unknown(255) | [1=关闭][2=开启] | ForcedStartupStatus of the device running and config table for the UX1. Value1 indicate no Value2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.18 | hwUX1DefrostStatus | Defrost status | 除霜状态 | 0-Read_Only | 只读 | close(1),open(2),unknown(255) | [1=关闭][2=开启] | DefrostStatus of the device running and config table for the UX1. Value1 indicate no Value2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.19 | hwUX1UnitStatus | Unit status | 机组状态 | 0-Read_Only | 只读 | powerOnStatus(1),faultShutdown(2),monitorShutdown(3),remoteShutdown(4),shutdownStatus(5),manualMode(6),timedShutdown(7),networkShutdown(8),unknown(255) | [1=开机状态][2=故障停机][3=监控关机][4=远端关机][5=关机状态][6=手动模式][7=定时关机][8=网络关机] | UnitStatus of the device running and config table for the UX1. Value2 indicate Power-on status Value3 indicate Fault shutdown Value4 indicate Monitor shutdown Value5 indicate Remote shutdown Value6 indicate Shutdown status Value7 indicate Manual mode Value8 indicate Timed shutdown Value9 indicate Network shutdown
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.20 | hwUX1ReturnAirTemperature | Return air temperature | 回风温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ReturnAirTemperature of the device running and config table for the UX1. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.21 | hwUX1ReturnAirHumidity | Return air humidity | 回风湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ReturnAirHumidity of the device running and config table for the UX1. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.22 | hwUX1EvaporationCoilTemperature | Evaporation coil temperature | 蒸发盘管温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | EvaporationCoilTemperature of the device running and config table for the UX1. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.23 | hwUX1DehumidifierHumiditySettingPoint | Dehumidifier humidity setting point | 除湿湿度设点 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | DehumidifierHumiditySettingPoint of the device running and config table for the UX1. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.18.1.1.24 | hwUX1Config1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UX1.

## SensepointXCD
CO传感器SensepointXCD
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.135 | hwSensor | SensepointXCD | SensepointXCD |  |  | / |  | Sensor Equipment.
1.3.6.1.4.1.2011.6.178.1.1.135.9 | hwCOSensepointXCD | / | / |  |  | / |  | COSensepointXCD Equipment.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1 | hwSensepointXCDRunningAndConfig1Table | / | / | / |  | / |  | The running and config table of SensepointXCD
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.1 | hwSensepointXCDRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / |  | Index of the device running and config table for the SensepointXCD
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.2 | hwSensepointXCDModbusAddress | Modbus Address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus Address of the device running and config table for the SensepointXCD.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.3 | hwSensepointXCDPortNodot | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device running and config table for the SensepointXCD.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.4 | hwSensepointXCDCommonModule | Common Module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Common Module of the device running and config table for the SensepointXCD.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.5 | hwSensepointXCDMainSwVersion | Main SW Version | 主要软件版本 | 0-Read_Only | 只读 | / | / | Main Sw Version of the device running and config table for the SensepointXCD.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.6 | hwSensepointXCDEepromParameterVersion | EEPROM parameter version | EEP版本 | 0-Read_Only | 只读 | / | / | Eeprom Parameter Version of the device running and config table for the SensepointXCD.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.7 | hwSensepointXCDWatchdogSorWVersion | WatchDog s/w Version | 看门狗软件版本 | 0-Read_Only | 只读 | / | / | Watchdog S/W Version of the device running and config table for the SensepointXCD.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.8 | hwSensepointXCDMonitorStatusInstrumentMode | Monitor Status(Instrument Mode) | 监控状态(设备模式) | 0-Read_Only | 只读 | normal(1),inhibit(2),warmUpAfterPowerOn(3),preview(4),unknown(255) | [1=正常][2=抑制][3=通电后预热][4=预览][255=未知] | Monitor Status(Instrument Mode) of the device running and config table for the SensepointXCD. Value1 indicate Normal Value2 indicate Inhibit Value3 indicate Warm up after power on Value4 indicate Preview
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.9 | hwSensepointXCDMonitorStatusFunction | Monitor Status(Function) | 监控状态(功能) | 0-Read_Only | 只读 | monitoringModeOrInConfigurationMode(1),powerOnAfterLoadEeprom(2),previewMode(3),configurationMode:SetCalibration(7),configurationMode:SetRange(9),configurationMode:ConfigureInhibit(10),configurationMode:SetPassword(11),configurationMode:SetCalibrationInterval(12),configurationMode:BumpTest(13),configurationMode:ForceCurrent(14),configurationMode:SetAlarms(15),configurationMode:SetRelays(16),configurationMode:RelayOperation(17),configurationMode:SetLocation(18),configurationMode:TemperatureUnit(19),configurationMode:TestAlarms(20),setId(45),warmUpTimeCountdown(53),abort(No/Yes)(99),unknown(255) | [1=监控模式或配置模式][2=加载EEPROM后上电][ 3=预览模式][7=配置模式：设置校准][9=配置模式：设置范围][10=配置模式：设置抑制值][11=设置模式：设置密码][12=配置模式：设置校准间隔][13=配置模式：冲击测试][14=配置模式：强制电流][14=配置方式：告警设置][16=配置模式：设置继电器][17=配置模式：继电器操作][18=配置模式：设置位置][19=配置模式：温度单位][20=配置方式：测试告警][45=设置ID][53=预热时间倒计时][99=中止(是/否)][255=未知] | Monitor Status(Function) of the device running and config table for the SensepointXCD. Value1 indicate Monitoring Mode or In Configuration Mode Value2 indicate Power ON after Load EEPROM Value3 indicate Preview Mode Value7 indicate Configuration Mode : Set Calibration Value9 indicate Configuration Mode : Set Range Value10 indicate Configuration Mode : Configure Inhibit Value11 indicate Configuration Mode : Set Password Value12 indicate Configuration Mode : Set Calibration Interval Value13 indicate Configuration Mode : Bump Test Value14 indicate Configuration Mode : Force Current Value15 indicate Configuration Mode : Set Alarms Value16 indicate Configuration Mode : Set Relays Value17 indicate Configuration Mode : Relay Operation Value18 indicate Configuration Mode : Set Location Value19 indicate Configuration Mode : Temperature Unit Value20 indicate Configuration Mode : Test Alarms Value45 indicate SET ID Value53 indicate Warm Up Time Countdown Value99 indicate Abort (NO/YES)
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.10 | hwSensepointXCDInhibitCurrent | Inhibit current | 抑制电流 | 0-Read_Only | 只读 | / | / | Inhibit Current of the device running and config table for the SensepointXCD. Multiple:10. SigUnitInfo:mA.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.11 | hwSensepointXCDLatchedAlarmState | Latched Alarm State | 锁存报警状态 | 0-Read_Only | 只读 | normal(1),alarm1(2),alarm2(3),alarm1&Alarm2(4),unknown(255) | [1=正常][2=告警1][3=告警2][4=告警1、告警2][255=未知] | Latched Alarm State of the device running and config table for the SensepointXCD. Value1 indicate Normal Value2 indicate Alarm1 Value3 indicate Alarm2 Value4 indicate Alarm1&Alarm2
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.12 | hwSensepointXCDGasReading | Gas reading | 气体读数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Gas Reading of the device running and config table for the SensepointXCD. Multiple:10. SigUnitInfo:ppm.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.13 | hwSensepointXCDAlarmState | Alarm State | 告警状态 | 0-Read_Only | 只读 | normal(1),alarm1(2),alarm2(3),alarm1&Alarm2(4),unknown(255) | [1=正常][2=告警1][3=告警2][4=告警1、告警2][255=未知] | Alarm State of the device running and config table for the SensepointXCD. Value1 indicate Normal Value2 indicate Alarm1 Value3 indicate Alarm2 Value4 indicate Alarm1&Alarm2
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.14 | hwSensepointXCDFaultorWarningState | Fault/Warning State | 故障/警告状态 | 0-Read_Only | 只读 | normal(1),warning(2),fault(3),warning&Fault(4),unknown(255) | [1=正常][2=警告][3=故障][4=警告、故障][255=未知] | Fault/Warning State of the device running and config table for the SensepointXCD. Value1 indicate Normal Value2 indicate Warning Value3 indicate Fault Value4 indicate Warning&Fault
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.15 | hwSensepointXCDMonitorStateMonitering | Monitor state monitering | 监控状态监控 | 0-Read_Only | 只读 | normal(2),warmUpAfterPowerOn(3),inhibit(4),calibration(13),unknown(255) | [2=正常][3=通电后预热][4=抑制][13=校准][255=未知] | Monitor State Monitering of the device running and config table for the SensepointXCD. Value2 indicate Normal Value3 indicate Warm up after power on Value4 indicate Inhibit Value13 indicate Calibration
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.16 | hwSensepointXCDCalibrationDue | Calibration Due | 校准到期 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Calibration Due of the device running and config table for the SensepointXCD. Multiple:10. SigUnitInfo:day.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.17 | hwSensepointXCDPeakReading | Peak Reading | 峰值读数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Peak Reading of the device running and config table for the SensepointXCD. Multiple:10. SigUnitInfo:ppm.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.18 | hwSensepointXCDTemperatureC | Temperature C | 温度(摄氏度) | 0-Read_Only | 只读 | / | / | Temperature C of the device running and config table for the SensepointXCD. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.19 | hwSensepointXCDMeasuringGasName | Measuring Gas name | 测量气体名称 | 0-Read_Only | 只读 | 0..14 | 0..14 | Measuring Gas Name of the device running and config table for the SensepointXCD.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.20 | hwSensepointXCDTemperatureF | Temperature F | 温度(华氏度) | 0-Read_Only | 只读 | / | / | Temperature F of the device running and config table for the SensepointXCD. SigUnitInfo:°F.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.21 | hwSensepointXCDPowerSupply | Power Supply | 供电 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Power Supply of the device running and config table for the SensepointXCD. Multiple:10. SigUnitInfo:mV.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.22 | hwSensepointXCDCalibrationInterva | Calibration Interva | 校准间隔 | 0-Read_Only | 只读 | / | / | Calibration Interva of the device running and config table for the SensepointXCD. SigUnitInfo:day.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.23 | hwSensepointXCDAlarm1Type | Alarm1 Type | 告警1类型 | 0-Read_Only | 只读 | disable(1),rising(2),falling(3),unknown(255) | [1=关闭][2=上升][3=下降][255=未知] | Alarm1 Type of the device running and config table for the SensepointXCD. Value1 indicate Disable Value2 indicate Rising Value3 indicate Falling
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.24 | hwSensepointXCDAlarm2Type | Alarm2 Type | 告警2类型 | 0-Read_Only | 只读 | disable(1),rising(2),falling(3),unknown(255) | [1=关闭][2=上升][3=下降][255=未知] | Alarm2 Type of the device running and config table for the SensepointXCD. Value1 indicate Disable Value2 indicate Rising Value3 indicate Falling
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.25 | hwSensepointXCDInhibitTimeout | Inhibit timeout | 禁止超时 | 0-Read_Only | 只读 | / | / | Inhibit Timeout of the device running and config table for the SensepointXCD.
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.26 | hwSensepointXCDRelay1Type | Relay1 Type | 继电器1类型 | 0-Read_Only | 只读 | fault(1),alarm1(2),alarm2(3),inhibit(4),unknown(255) | [1=故障][2=告警1][3=告警2][4=禁止][255=未知] | Relay1 Type of the device running and config table for the SensepointXCD. Value1 indicate Fault Value2 indicate Alarm1 Value3 indicate Alarm2 Value4 indicate inhibit
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.27 | hwSensepointXCDRelay2Type | Relay2 Type | 继电器2类型 | 0-Read_Only | 只读 | fault(1),alarm1(2),alarm2(3),inhibit(4),unknown(255) | [1=故障][2=告警1][3=告警2][4=禁止][255=未知] | Relay2 Type of the device running and config table for the SensepointXCD. Value1 indicate Fault Value2 indicate Alarm1 Value3 indicate Alarm2 Value4 indicate inhibit
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.28 | hwSensepointXCDRelay3Type | Relay3 Type | 继电器3类型 | 0-Read_Only | 只读 | fault(1),alarm1(2),alarm2(3),inhibit(4),unknown(255) | [1=故障][2=告警1][3=告警2][4=禁止][255=未知] | Relay3 Type of the device running and config table for the SensepointXCD. Value1 indicate Fault Value2 indicate Alarm1 Value3 indicate Alarm2 Value4 indicate inhibit
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.29 | hwSensepointXCDRelay1Status | Relay1 Status | 继电器1状态 | 0-Read_Only | 只读 | deEnergized(1),energized(2),unknown(255) | [1=断电][2=充能][255=未知] | Relay1 Status of the device running and config table for the SensepointXCD. Value1 indicate De-energized Value2 indicate Energized
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.30 | hwSensepointXCDRelay2Status | Relay2 Status | 继电器2状态 | 0-Read_Only | 只读 | deEnergized(1),energized(2),unknown(255) | [1=断电][2=充能][255=未知] | Relay2 Status of the device running and config table for the SensepointXCD. Value1 indicate De-energized Value2 indicate Energized
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.31 | hwSensepointXCDRelay3Status | Relay3 Status | 继电器3状态 | 0-Read_Only | 只读 | deEnergized(1),energized(2),unknown(255) | [1=断电][2=充能][255=未知] | Relay3 Status of the device running and config table for the SensepointXCD. Value1 indicate De-energized Value2 indicate Energized
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.32 | hwSensepointXCDRelayLatchOption | Relay Latch Option | 继电器锁闭状态 | 0-Read_Only | 只读 | nonLatch(1),latch(2),unknown(255) | [1=非锁闭][2=锁闭][255=未知] | Relay Latch Option of the device running and config table for the SensepointXCD. Value1 indicate Non latch Value2 indicate Latch
1.3.6.1.4.1.2011.6.178.1.1.135.9.1.1.33 | hwSensepointXCDRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SensepointXCD.

## P3T32
RMUP3T32
OID | OID Name | Signal Name |  | Max Access |  | Value List |  | Description
1.3.6.1.4.1.2011.6.178.1.1.9 | hwIDCPDU | IDCPDU | IDCPDU | / |  | / |  | IDCPDU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.29 | hwP3T32 | / | / | / |  | / |  | P3T32 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1 | hwP3T32RunningAndConfig1Table | / | / | / | 只读 | / | / | The running and config table of P3T32
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.1 | hwP3T32RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the P3T32
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.2 | hwP3T32ModbusAddress | Modbus Address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus Address of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.3 | hwP3T32PortNodot | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.4 | hwP3T32CommonModule | Common Module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Common Module of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.5 | hwP3T32Di1CbClose | DI-1 CB Close | DI-1 CB关闭 | 0-Read_Only | 只读 | 0..1 | 0..1 | Di-1 Cb Close of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.6 | hwP3T32Di2CbOpen | DI-2 CB Open | DI-2 CB打开 | 0-Read_Only | 只读 | 0..1 | 0..1 | Di-2 Cb Open of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.7 | hwP3T32Di3DbClose | DI-3 DB Close | DI-3 DB关闭 | 0-Read_Only | 只读 | 0..1 | 0..1 | Di-3 Db Close of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.8 | hwP3T32Di4DbOpen | DI-4 DB Open | DI-4 DB打开 | 0-Read_Only | 只读 | 0..1 | 0..1 | Di-4 Db Open of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.9 | hwP3T32Di5EsClose | DI-5 ES Close | DI-5 ES关闭 | 0-Read_Only | 只读 | 0..1 | 0..1 | Di-5 Es Close of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.10 | hwP3T32Di6EsOpen | DI-6 ES Open | DI-6 ES打开 | 0-Read_Only | 只读 | 0..1 | 0..1 | Di-6 Es Open of the device running and config table for the P3T32.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.11 | hwP3T32PhaseCurrent1A | Phase Current 1A | 相电流1A | 0-Read_Only | 只读 | / | / | Phase Current 1A of the device running and config table for the P3T32. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.12 | hwP3T32PhaseCurrent1B | Phase Current 1B | 相电流1B | 0-Read_Only | 只读 | / | / | Phase Current 1B of the device running and config table for the P3T32. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.13 | hwP3T32PhaseCurrent1C | Phase Current 1C | 相电流1C | 0-Read_Only | 只读 | / | / | Phase Current 1C of the device running and config table for the P3T32. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.14 | hwP3T32Di8WindingTempTrip | DI-8 Winding Temp Trip | DI-8 绕组温度跳闸 | 0-Read_Only | 只读 | normal(1),trip(2),unknown(255) | [1=正常][2=跳闸][255=未知] | Di-8 Winding Temp Trip of the device running and config table for the P3T32. Value1 indicate Normal Value2 indicate Trip
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.15 | hwP3T32Di10SealInRelayTrip | DI-10 Seal in Relay Trip | DI-10 继电器密封跳闸 | 0-Read_Only | 只读 | normal(1),trip(2),unknown(255) | [1=正常][2=跳闸][255=未知] | Di-10 Seal In Relay Trip of the device running and config table for the P3T32. Value1 indicate Normal Value2 indicate Trip
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.16 | hwP3T32Di11OilLevelTrip | DI-11 Oil Level Trip | DI-11 油位跳闸 | 0-Read_Only | 只读 | normal(1),trip(2),unknown(255) | [1=正常][2=跳闸][255=未知] | Di-11 Oil Level Trip of the device running and config table for the P3T32. Value1 indicate Normal Value2 indicate Trip
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.17 | hwP3T3250or511InverseTimeOvercurrent | 50/51 – 1 Inverse Time Overcurrent | 50/51 – 1 反时限过流 | 0-Read_Only | 只读 | normal(1),trip(2),unknown(255) | [1=正常][2=跳闸][255=未知] | 50/51 – 1 Inverse Time Overcurrent of the device running and config table for the P3T32. Value1 indicate Normal Value2 indicate Trip
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.18 | hwP3T3250or512InstantaneousOvercurrent | 50/51 – 2 Instantaneous Overcurrent | 50/51 – 2 瞬时过电流 | 0-Read_Only | 只读 | normal(1),trip(2),unknown(255) | [1=正常][2=跳闸][255=未知] | 50/51 – 2 Instantaneous Overcurrent of the device running and config table for the P3T32. Value1 indicate Normal Value2 indicate Trip
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.19 | hwP3T3287DifferentialRelay | 87 Differential Relay | 87 差动继电器 | 0-Read_Only | 只读 | normal(1),trip(2),unknown(255) | [1=正常][2=跳闸][255=未知] | 87 Differential Relay of the device running and config table for the P3T32. Value1 indicate Normal Value2 indicate Trip
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.20 | hwP3T3250Nor51N1InverseTimeEarthProtection | 50N/51N – 1 Inverse Time Earth Protection | 50N/51N - 1 反时限接地保护 | 0-Read_Only | 只读 | normal(1),trip(2),unknown(255) | [1=正常][2=跳闸][255=未知] | 50N/51N – 1 Inverse Time Earth Protection of the device running and config table for the P3T32. Value1 indicate Normal Value2 indicate Trip
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.21 | hwP3T3250Nor51N2InstantaneousEarthProtection | 50N/51N – 2 Instantaneous Earth Protection | 50N/51N - 2 瞬时接地保护 | 0-Read_Only | 只读 | normal(1),trip(2),unknown(255) | [1=正常][2=跳闸][255=未知] | 50N/51N – 2 Instantaneous Earth Protection of the device running and config table for the P3T32. Value1 indicate Normal Value2 indicate Trip
1.3.6.1.4.1.2011.6.178.1.1.9.29.1.1.22 | hwP3T32Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of P3T32.