## 封面
资料编码
ECC800-Pro V500R023C10SPC250 MIB节点信号信息表
| 文档版本 | 01
| 发布日期 | 2025-02-13
华为数字能源技术有限公司
版权所有 © 华为数字能源技术有限公司 2025。 保留一切权利。
非经本公司书面许可，任何单位和个人不得擅自摘抄、复制本文档内容的部分或全部，并不得以任何形式传播。
商标声明
和其他华为商标均为华为技术有限公司的商标。
本文档提及的其他所有商标或注册商标，由各自的所有人拥有。
注意
您购买的产品、服务或特性等应受华为公司商业合同和条款的约束，本文档中描述的全部或部分产品、服务或特性可能不在您的购买或使用范围之内。除非合同另有约定，华为公司对本文档内容不做任何明示或暗示的声明或保证。
由于产品版本升级或其他原因，本文档内容会不定期进行更新。除非另有约定，本文档仅作为使用指导，本文档中的所有陈述、信息和建议不构成任何明示或暗示的担保。
华为数字能源技术有限公司
地址： | 深圳市福田区华为数字能源安托山基地 邮编：518043
网址： | https://digitalpower.huawei.com/

## 前言
概述
本文档提供了ECC800-Pro V500R023C10SPC250版本在第三方网管展示信息的相关解释说明。
读者对象
本文档（本指南）主要适用于以下工程师 ● 现场工程师 ● 网管工程师 ● 网管操作员
使用说明
本文档（本指南）主要配套使用于以下版本： ● ECC800-Pro V500R023C10SPC250
修改记录
文档版本 | 更新日期 | 更新说明
01 | 2025-02-13 | 第一次生成

## 目录
序号 | 设备名称 | Device Name | 设备OID | 目录索引 | 详细机型
1 | 独立部署AI_DI模块 | Independent Deployment AI_DI Unit | 1.3.6.1.4.1.2011.6.178.1.1.4 | Independent Deployment AI_DI Unit | /
2 | UPS2000G | UPS2000G | 1.3.6.1.4.1.2011.6.178.1.1.5.1 | UPS2000 | /
3 | UPS5000 | UPS5000 | 1.3.6.1.4.1.2011.6.178.1.1.5.3 | UPS5000 | /
4 | iBOX | iBOX | 1.3.6.1.4.1.2011.6.178.1.1.5.4 | iBOX | /
5 | 一体化UPS柜 | Integrated UPS Cabinet | 1.3.6.1.4.1.2011.6.178.1.1.5.5 | Integrated UPS Cabinet | /
6 | UPS2000G_L | UPS2000G_L | 1.3.6.1.4.1.2011.6.178.1.1.5.7 | UPS2000G_L | /
7 | 短信模块 | EnvGPRS | 1.3.6.1.4.1.2011.6.178.1.1.7.1.1 | EnvGPRS | /
8 | ECC800 | ECC800 | 1.3.6.1.4.1.2011.6.178.1.1.7.1.3 | ECC800 | /
9 | ATS | ATS | 1.3.6.1.4.1.2011.6.178.1.1.8.1 | ATS | /
10 | ATS柜 | ATS cabinet | 1.3.6.1.4.1.2011.6.178.1.1.8.2 | ATS cabinet | /
11 | ATS Abb-mx250 | ATS Abb-mx250 | 1.3.6.1.4.1.2011.6.178.1.1.8.3 | ATS Abb-mx250 | /
12 | 一体化配电柜 | Integrated PDU | 1.3.6.1.4.1.2011.6.178.1.1.9.4 | Integrated PDU | /
13 | PDU8000 | PDU8000 | 1.3.6.1.4.1.2011.6.178.1.1.9.5 | PDU8000 | /
14 | PDU2000-M(C) | PDU2000-M(C) | 1.3.6.1.4.1.2011.6.178.1.1.9.6 | PDU2000-M(C) | /
15 | PDU2000-M(H) | PDU2000-M(H) | 1.3.6.1.4.1.2011.6.178.1.1.9.8 | PDU2000-M(H) | /
16 | TP48202B直流列头柜 | TP48202BDCEndCabinet | 1.3.6.1.4.1.2011.6.178.1.1.9.9 | TP48202BDCEndCabinet | /
17 | 馈线柜 | Feeder Cabinet | 1.3.6.1.4.1.2011.6.178.1.1.9.10 | Feeder Cabinet | /
18 | 馈线柜开关 | Feeder cabinet switch | 1.3.6.1.4.1.2011.6.178.1.1.9.11 | Feeder cabinet switch | /
19 | 低压柜 | Low Voltage Cabinet | 1.3.6.1.4.1.2011.6.178.1.1.9.12 | Low Voltage Cabinet | /
20 | 低压柜开关 | LV switchgear switch | 1.3.6.1.4.1.2011.6.178.1.1.9.13 | LV switchgear switch | /
21 | 直流列头柜 | DC End Cabinet | 1.3.6.1.4.1.2011.6.178.1.1.9.14 | DC End Cabinet | /
22 | 配电柜-盛弘-svg100 | PDU-Sinexcel-svg100 | 1.3.6.1.4.1.2011.6.178.1.1.9.16 | PDU-Sinexcel-svg100 | /
23 | 智能PDU | Smart PDU | 1.3.6.1.4.1.2011.6.178.1.1.9.82 | Smart PDU | /
24 | NetCol5000-A010 | NetCol5000-A010 | 1.3.6.1.4.1.2011.6.178.1.1.10.2 | NetCol5000-A010 | NetCol5000-A013HXWE1; NetCol5000-A013HX0E1; NetCol5000-A013HXWD1; NetCol5000-A013HX0D1; NetCol5000-A010HS1301W120E1; NetCol5000-A010HS13010020E1; NetCol5000-A011H61201W120E1; NetCol5000-A011H612010020E1; NetCol5000-A011H71201W120E1; NetCol5000-A011H712010020E1;
25 | NetCol5000-A025 | NetCol5000-A025 | 1.3.6.1.4.1.2011.6.178.1.1.10.3 | NetCol5000-A025 | NetCol5000-A025H412D20020E1; NetCol5000-A025H412D20020E0; NetCol5000-A025H412D2E120E1; NetCol5000-A025H412D2E120E0; NetCol5000-A025H40D2; NetCol5000-A025H412D2E120; NetCol5000-A025H412D20020; NetCol5000-A025H40E2; NetCol5000-A025H40E0; NetCol5000-A025H4WE0; NetCol5000-A021HN12D20020E1; NetCol5000-A021HN0E1; NetCol5000-A021HN12D2E120E1;
26 | NetCol5000-A035 | NetCol5000-A035 | 1.3.6.1.4.1.2011.6.178.1.1.10.4 | NetCol5000-A035 | NetCol5000-A035H512D2E120E0; NetCol5000-A035H512D2E120E1; NetCol5000-A035H512D20020E0; NetCol5000-A035H512D20020E1; NetCol5000-A025H512D2E120E0; NetCol5000-A025H512D2E120E1; NetCol5000-A025H512D20020E0; NetCol5000-A025H512D20020E1;
27 | NetCol5000-C030 | NetCol5000-C030 | 1.3.6.1.4.1.2011.6.178.1.1.10.5 | NetCol5000-C030 | IDSINRWCOL00; IDSNCLH2A200; NetCol5000-C030H2A2010020E0; NetCol5000-C030H; NetCol5000-C030HSB2010020E0; NetCol5000-C030H6B2010020E1; NetCol5000-C030H6B2010020E0; NetCol5000-C025H6B2010020E0; Netcol5000-C030HSB2020020E0; NetCol5000-C030H7B2010020E1; NetCol5000-C030H7B201E120E0; NetCol5000-C030H7B201E120E1; NetCol5000-C030H6B201002FE1; NetCol5000-C030H7A201E120E0; NetCol5000-C030H7A2010020E1; NetCol5000-C030H7A201E120E1;
28 | 依米康SCU-20K | SUNRISE-SCU-20K | 1.3.6.1.4.1.2011.6.178.1.1.10.6 | SUNRISE-SCU-20K | /
29 | NetCol5000-A042 | NetCol5000-A042 | 1.3.6.1.4.1.2011.6.178.1.1.10.7 | NetCol5000-A042 | NetCol5000-A050H4WE0; NetCol5000-A050H40E0; NetCol5000-A050H4WE2; NetCol5000-A050H4WD2; NetCol5000-A050H40D2; NetCol5000-A050H40E2; NetCol5000-A050HRWE2; NetCol5000-A042H412D20020E1; NetCol5000-A042H412D2W120E1; NetCol5000-A042H412D20020E2; NetCol5000-A042H412D20020; NetCol5000-A042H412D2W120E2; NetCol5000-A042H412D2W120; FusionCol5000-A065H4;
30 | 英维克CRU | ENVICOOL-CRU | 1.3.6.1.4.1.2011.6.178.1.1.10.8 | ENVICOOL-CRU | /
31 | NetCol5000CF-110 | NetCol5000CF-110 | 1.3.6.1.4.1.2011.6.178.1.1.10.9 | NetCol5000CF-110 | NetCol5000-C065H9HD0; NetCol5000-C065H9HE0; NetCol5000-C065H90D0; NetCol5000-C080H9HD0; NetCol5000-C080H90D0; NetCol5000-C036H; NetCol5000-C065H9B2020030D0; NetCol5000-C065H9B2020030; NetCol5000-C065H9B2020030D2; NetCol5000-C065H9B202W030D0; NetCol5000-C080H9B2020030D0; NetCol5000-C080H9B202W030D0; NetCol5000-C065H9B2020030E0; NetCol5000-C065H90E2; NetCol5000-C065H9B202W030E0; NetCol5000-C076H4B202E120E0; Netcol5000-C027H90D0; Netcol5000-C027HSB2020020; Netcol5000-C030HSB2020020; NetCol5000-C027HSB2020020E0; NetCol5000-C060H4B2020020E2;
32 | NetCol5000-A | NetCol5000-A | 1.3.6.1.4.1.2011.6.178.1.1.10.10 | NetCol5000-A | NetCol5000-A035H4WE2; NetCol5000-A035H40E2; NetCol5000-A035H4WE0; NetCol5000-A035H40E0; NetCol5000-A025H4WE2; NetCol5000-A025HNWE2;
33 | NetCol8000-A | NetCol8000-A | 1.3.6.1.4.1.2011.6.178.1.1.10.11 | NetCol8000-A | /
34 | iTeaQ Cool Row | iTeaQ Cool Row | 1.3.6.1.4.1.2011.6.178.1.1.10.13 | iTeaQ Cool Row | /
35 | iTeaQ Cool Row-CF | iTeaQ Cool Row-CF | 1.3.6.1.4.1.2011.6.178.1.1.10.12 | iTeaQ Cool Row-CF | /
36 | 智能ETH插座 | Smart ETH Gateway | 1.3.6.1.4.1.2011.6.178.1.1.15 | Smart ETH Gateway | /
37 | WiFi模块 | WiFi Model | 1.3.6.1.4.1.2011.6.178.1.1.16 | WiFi Model | /
38 | 机柜采集器 | Cabinet Collector | 1.3.6.1.4.1.2011.6.178.1.1.17 | Cabinet Collector | /
39 | 机柜电子锁 | E-LOCK | 1.3.6.1.4.1.2011.6.178.1.1.18 | E-LOCK | /
40 | 天窗执行器 | Skylight Actuator | 1.3.6.1.4.1.2011.6.178.1.1.19 | Skylight Actuator | /
41 | WiFi转换器 | WiFi Converter | 1.3.6.1.4.1.2011.6.178.1.1.20 | WiFi Converter | /
42 | 门禁执行器 | Access Actuator | 1.3.6.1.4.1.2011.6.178.1.1.21 | Access Actuator | /
43 | ETH转换器 | ETH Converter | 1.3.6.1.4.1.2011.6.178.1.1.22 | ETH Converter | /
44 | 多功能传感器 | Multi-Func Sensor | 1.3.6.1.4.1.2011.6.178.1.1.23 | Multi-Func Sensor | /
45 | 交流执行器 | AC Actuator | 1.3.6.1.4.1.2011.6.178.1.1.24 | AC Actuator | /
46 | 温湿度传感器 | T/H Sensor | 1.3.6.1.4.1.2011.6.178.1.1.25 | T/H Sensor | /
47 | 新风一体机 | Air Conditioner | 1.3.6.1.4.1.2011.6.178.1.1.26 | Air Conditioner | /
48 | 氢气监测系统 | Hydrogen Monitoring System | 1.3.6.1.4.1.2011.6.178.1.1.27 | Hydrogen Monitoring System | /
49 | 48V直流供电设备 | 48 V DC Power Supply | 1.3.6.1.4.1.2011.6.178.1.1.28 | 48 V DC Power Supply | TP48400B; TP481200B; ETP48400;
50 | 雅达直流电表 | YaDa DC Meter | 1.3.6.1.4.1.2011.6.178.1.1.29 | YaDa DC Meter | /
51 | PD510电表 | PD510 Meter | 1.3.6.1.4.1.2011.6.178.1.1.30 | PD510 Meter | /
52 | 电源模块 | PowerModule | 1.3.6.1.4.1.2011.6.178.1.1.31 | PowerModule | /
53 | LF直流电表 | LF DC Meter | 1.3.6.1.4.1.2011.6.178.1.1.33 | LF DC Meter | /
54 | 红外遥控模块 | Infrared Remote Control Module | 1.3.6.1.4.1.2011.6.178.1.1.34 | Infrared Remote Control Module | /
55 | PMAC615 | PMAC615 | 1.3.6.1.4.1.2011.6.178.1.1.35 | PMAC615 | /
56 | PMAC625 | PMAC625 | 1.3.6.1.4.1.2011.6.178.1.1.36 | PMAC625 | /
57 | 分接单元 | Power Distribution Unit | 1.3.6.1.4.1.2011.6.178.1.1.37 | Power Distribution Unit | /
58 | 始端单元 | General Input Unit | 1.3.6.1.4.1.2011.6.178.1.1.38 | General Input Unit | /
59 | 水浸传感器 | Water Sensor | 1.3.6.1.4.1.2011.6.178.1.1.39 | Water Sensor | /
60 | 系统 | System | 1.3.6.1.4.1.2011.6.178.1.1.40 | VirtualSystem | /
61 | 电量仪-任达-AMC7062HT-4(HI) | PowerMeter-Renda-AMC7062HT-4(HI) | 1.3.6.1.4.1.2011.6.178.1.1.41 | PowerMeter-Renda-AMC7062HT-4(HI) | /
62 | 智能U位管理器 | Smart U Space Manager | 1.3.6.1.4.1.2011.6.178.1.1.46 | Smart U Space Manager | /
63 | rPDU-MPDU | rPDU-MPDU | 1.3.6.1.4.1.2011.6.178.1.1.48 | rPDU-MPDU | /
64 | rPDU-PN | rPDU-PN | 1.3.6.1.4.1.2011.6.178.1.1.50 | rPDU-PN | /
65 | eLight执行器 | eLight Actuator | 1.3.6.1.4.1.2011.6.178.1.1.52 | eLight Actuator | /
66 | NetCol5000CF-110HALF | NetCol5000CF-110HALF | 1.3.6.1.4.1.2011.6.178.1.1.66 | NetCol5000CF-110HALF | NetCol5000-C030H9HD0; NetCol5000-C030H90D0; NetCol5000-C030H9HE0; NetCol5000-C032H9HD0; NetCol5000-C032H90D0; NetCol5000-C030H90E0;
67 | TP483000D直流配电柜 | TP483000D DC PDF | 1.3.6.1.4.1.2011.6.178.1.1.68 | TP483000D DC PDF | /
68 | 空调-分体插框-XR005A | Air Conditioner-Separate Subrack-XR005A | 1.3.6.1.4.1.2011.6.178.1.1.70 | Air Conditioner-Separate Subrack-XR005A | /
69 | rPDU-克莱沃-IPPDUV1 | rPDU-Clever-IPPDUV1 | 1.3.6.1.4.1.2011.6.178.1.1.72 | rPDU-Clever-IPPDUV1 | /
70 | ATS配电挂墙箱 | Wall-mounted ATS PDB | 1.3.6.1.4.1.2011.6.178.1.1.74 | Wall-mounted ATS PDB | /
71 | 空调-机架式-HR04A | Rack-mounted air conditioner HR04A | 1.3.6.1.4.1.2011.6.178.1.1.78 | Rack-mounted air conditioner HR04A | /
72 | 除湿机HT-500 | DehumidifierHT-500 | 1.3.6.1.4.1.2011.6.178.1.1.80 | DehumidifierHT-500 | /
73 | 英维克SC15 | EnvicoolSC15 | 1.3.6.1.4.1.2011.6.178.1.1.82 | EnvicoolSC15 | /
74 | 机柜电子扣锁 | Cabinet Electronic Clasp Lock | 1.3.6.1.4.1.2011.6.178.1.1.84 | Cabinet Electronic Clasp Lock | /
75 | MA01C交流配电柜 | AC_PDC_MA01C | 1.3.6.1.4.1.2011.6.178.1.1.86 | AC_PDC_MA01C | /
76 | UIM | UIM | 1.3.6.1.4.1.2011.6.178.1.1.88 | UIM | /
77 | DDS3366D_W1 | DDS3366D_W1 | 1.3.6.1.4.1.2011.6.178.1.1.90 | DDS3366D_W1 | /
78 | Ac_Hm25rc | Ac_Hm25rc | 1.3.6.1.4.1.2011.6.178.1.1.92 | Ac_Hm25rc | /
79 | STM32高压直流列头柜 | STM32HeadCabinet | 1.3.6.1.4.1.2011.6.178.1.1.94 | STM32HeadCabinet | /
80 | 电池系统 | Battery System | 1.3.6.1.4.1.2011.6.178.1.1.98 | Battery System | /
81 | 锂电柜 | Lithium Battery Cabinet | 1.3.6.1.4.1.2011.6.178.1.1.100 | Lithium Battery Cabinet | /
82 | 5G高密度嵌入式电源 | 5G high density embedded power | 1.3.6.1.4.1.2011.6.178.1.1.102 | 5G high density embedded power | /
83 | 列间变频空调 | Cantal_Ms19_Row_Mb | 1.3.6.1.4.1.2011.6.178.1.1.104 | Cantal_Ms19_Row_Mb | /
84 | 变压器_LD-B10 | Transformer_LD-B10 | 1.3.6.1.4.1.2011.6.178.1.1.106 | Transformer_LD-B10 | /
85 | SVG-英博电气 | SVG-In-Power | 1.3.6.1.4.1.2011.6.178.1.1.108 | SVG-In-Power | /
86 | UPS5000-H | UPS5000-H | 1.3.6.1.4.1.2011.6.178.1.1.112 | UPS5000-H | /
87 | FusionCol-M | FusionCol-M | 1.3.6.1.4.1.2011.6.178.1.1.114 | FusionCol-M | NetCol8000-A013; FusionCol5000-A007; FusionCol5000-A003;
88 | 微模块执行器 | FusionModule Actuator | 1.3.6.1.4.1.2011.6.178.1.1.116 | FusionModule Actuator | /
89 | 变压器-ABB-SCB11-2000 | Transformer-ABB-SCB11-2000 | 1.3.6.1.4.1.2011.6.178.1.1.118 | Transformer-ABB-SCB11-2000 | /
90 | SVG-APF-新能动力 | SVG-APF-NOVTIUM | 1.3.6.1.4.1.2011.6.178.1.1.119 | SVG-APF-NOVTIUM | /
91 | SMU11B | SMU11B | 1.3.6.1.4.1.2011.6.178.1.1.120 | SMU11B | /
92 | 密集母线插接箱 | Tap-off Unit | 1.3.6.1.4.1.2011.6.178.1.1.121 | Tap-off Unit | /
93 | PMC-53A | PMC-53A | 1.3.6.1.4.1.2011.6.178.1.1.122 | PMC-53A | /
94 | MA01D直流配电柜 | MA01D DC PDU | 1.3.6.1.4.1.2011.6.178.1.1.123 | MA01D DC PDU | /
95 | 补偿柜 | CompensatingCabinet | 1.3.6.1.4.1.2011.6.178.1.1.124 | CompensatingCabinet | /
96 | rPDU | rPDU | 1.3.6.1.4.1.2011.6.178.1.1.125 | rPDU | /
97 | iACSENSE | iACSENSE | 1.3.6.1.4.1.2011.6.178.1.1.126 | iACSENSE | /
98 | Schneider_MTZ1_IFM_Module | Schneider_MTZ1_IFM_Module | 1.3.6.1.4.1.2011.6.178.1.1.127 | Schneider_MTZ1_IFM_Module | /
99 | Acrel AMC16ZH Meter | Acrel AMC16ZH Meter | 1.3.6.1.4.1.2011.6.178.1.1.128 | Acrel AMC16ZH Meter | /
100 | PZ96LE4 | PZ96LE4 | 1.3.6.1.4.1.2011.6.178.1.1.130 | PZ96LE4 | /
101 | YD-DEMS AC Meter | YD-DEMS AC Meter | 1.3.6.1.4.1.2011.6.178.1.1.130.1 | YD-DEMS AC Meter | /
102 | YD-DEMS DC Meter | YD-DEMS DC Meter | 1.3.6.1.4.1.2011.6.178.1.1.130.2 | YD-DEMS DC Meter | /
103 | 交流电表-泰豪-qmc | AC Meter-TellHow-qmc | 1.3.6.1.4.1.2011.6.178.1.1.130.4 | AC Meter-TellHow-qmc | /
104 | 交流电表-雅达-yd2060 | Ac Meter-Yada-yd2060 | 1.3.6.1.4.1.2011.6.178.1.1.130.5 | Ac Meter-Yada-yd2060 | /
105 | iWATER | iWATER | 1.3.6.1.4.1.2011.6.178.1.1.131.1 | iWATER | /
106 | iTEMP | iTEMP | 1.3.6.1.4.1.2011.6.178.1.1.131.2 | iTEMP | /
107 | iDOOR | iDOOR | 1.3.6.1.4.1.2011.6.178.1.1.131.3 | iDOOR | /
108 | iSMOKE | iSMOKE | 1.3.6.1.4.1.2011.6.178.1.1.131.4 | iSMOKE | /
109 | iMOTION | iMOTION | 1.3.6.1.4.1.2011.6.178.1.1.131.5 | iMOTION | /
110 | iACMETER | iACMETER | 1.3.6.1.4.1.2011.6.178.1.1.131.6 | iACMETER | /
111 | 锂电池 | Lithium Battery | 1.3.6.1.4.1.2011.6.178.1.1.132.1 | Lithium Battery | /
112 | 智能塑壳断路器 | Smart MCCB | 1.3.6.1.4.1.2011.6.178.1.1.9.15 | Smart MCCB | /
113 | DEMSVD2 | DEMSVD2 | 1.3.6.1.4.1.2011.6.178.1.1.9.17 | DEMSVD2 | /
114 | AYTSC60 | AYTSC60 | 1.3.6.1.4.1.2011.6.178.1.1.8.4 | AYTSC60 | /
115 | GGIC400P3 | GGIC400P3 | 1.3.6.1.4.1.2011.6.178.1.1.9.19 | GGIC400P3 | /
116 | PDU2000M | PDU2000M | 1.3.6.1.4.1.2011.6.178.1.1.9.18 | PDU2000M | /
117 | YD-DEMS-VD2 直流电表 | YD-DEMS-VD2 DC Meter | 1.3.6.1.4.1.2011.6.178.1.1.130.6 | YD-DEMS-VD2 DC Meter | /
118 | PDU2000-MH-3PH | PDU2000-MH-3PH | 1.3.6.1.4.1.2011.6.178.1.1.9.20 | PDU2000-MH-3PH | /
119 | IECEHU260 | IECEHU260 | 1.3.6.1.4.1.2011.6.178.1.1.10.16 | IEC-EHU260 | /
120 | UMG96-PQ | UMG96-PQ | 1.3.6.1.4.1.2011.6.178.1.1.130.8 | UMG96-PQ | /
121 | NFS320E | NFS320E | 1.3.6.1.4.1.2011.6.178.1.1.135.2 | NFS-320E | /
122 | RMU | RMU | 1.3.6.1.4.1.2011.6.178.1.1.9.22 | RMU | /
123 | 英维克PC6H | EnvicoolPC6H | 1.3.6.1.4.1.2011.6.178.1.1.10.15 | EnvicoolPC6H | /
124 | SVG | SVG | 1.3.6.1.4.1.2011.6.178.1.1.9.21 | SVG | /
125 | APF-SINENG-ASCII | APF-SINENG-ASCII | 1.3.6.1.4.1.2011.6.178.1.1.9.23 | APF-SINENG-ASCII | /
126 | UMG96RM | UMG96RM | 1.3.6.1.4.1.2011.6.178.1.1.130.9 | UMG96RM | /
127 | UMG96RM-CBM | UMG96RM-CBM | 1.3.6.1.4.1.2011.6.178.1.1.130.16 | UMG96RM-CBM
128 | 空气质量传感器HAQ61 | HAQ61 | 1.3.6.1.4.1.2011.6.178.1.1.135.6 | HAQ61 | /
129 | 温湿度传感器TH-802C | TH-802C | 1.3.6.1.4.1.2011.6.178.1.1.135.5 | TH-802C | /
130 | 压差传感器HSDP-A100M | HSDP-A100M | 1.3.6.1.4.1.2011.6.178.1.1.135.7 | HSDP-A100M | /
131 | 除湿机UX1 | UX1 | 1.3.6.1.4.1.2011.6.178.1.1.10.18 | UX1 | /
132 | CO传感器SensepointXCD | SensepointXCD | 1.3.6.1.4.1.2011.6.178.1.1.135 | SensepointXCD | /
133 | RMUP3T32 | P3T32 | 1.3.6.1.4.1.2011.6.178.1.1.9 | P3T32 | /
134 | 英维克IFX末端 | Envicool-IFX Terminal | 1.3.6.1.4.1.2011.6.178.1.1.10.14 | Envicool-IFX Terminal | /
135 | MTS9604B_MTS9606B供电设备 | MTS9604B_MTS9606B Power Supply | 1.3.6.1.4.1.2011.6.178.1.1.9.32 | MTS9604B-MTS9606B Power Supply | MTS9604B-N20B1;MTS9606B-N20B1;
136 | 氢气传感器SGA500B | HydrogengasSensorSGA500B | 1.3.6.1.4.1.2011.6.178.1.1.135.11 | SGA500B | /
137 | NetCol8000-C | NetCol8000-C | 1.3.6.1.4.1.2011.6.178.1.1.10.22 | NetCol8000-C | /
138 | 可燃气体传感器 | Combustible Gas Sensor | 1.3.6.1.4.1.2011.6.178.1.1.135.10 | Combustible Gas Sensor | /

## PDU2000M
PDU2000M
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.18 | PDU2000M | PDU2000M | PDU2000M | / | / | / | / | PDU2000M Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1 | hwPDU2000MRunning1Table | / | / |  |  | / | / | The running table of PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.1 | hwPDU2000MRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.2 | hwPDU2000MVoltageValue | Voltage value | 电压值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage value of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.3 | hwPDU2000MCurrentValue | Current value | 电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current value of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.4 | hwPDU2000MLoadRatio | Load ratio | 负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.5 | hwPDU2000MActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.6 | hwPDU2000MReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.7 | hwPDU2000MAppearancePower | Appearance power | 视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.8 | hwPDU2000MPowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.9 | hwPDU2000MThdU | THD-u | 电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.10 | hwPDU2000M5ThThdU | 5th THD-u | x次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | 5th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.11 | hwPDU2000M7ThThdU | 7th THD-u | y次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | 7th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.12 | hwPDU2000M11ThThdU | 11th THD-u | z次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | 11th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.13 | hwPDU2000MThdI | THD-i | 电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.14 | hwPDU2000M5ThThdI | 5th THD-i | x次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | 5th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.15 | hwPDU2000M7ThThdI | 7th THD-i | y次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | 7th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.16 | hwPDU2000M11ThThdI | 11th THD-i | z次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | 11th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.17 | hwPDU2000ML1PhaseVoltage | L1 phase voltage | L1相电压值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 phase voltage of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.18 | hwPDU2000ML2PhaseVoltage | L2 phase voltage | L2相电压值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 phase voltage of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.19 | hwPDU2000ML3PhaseVoltage | L3 phase voltage | L3相电压值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 phase voltage of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.20 | hwPDU2000ML1L2LineVoltage | L1-L2 line voltage | L1L2线电压值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1-L2 line voltage of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.21 | hwPDU2000ML2L3LineVoltage | L2-L3 line voltage | L2L3线电压值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2-L3 line voltage of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.22 | hwPDU2000ML3L1LineVoltage | L3-L1 line voltage | L3L1线电压值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3-L1 line voltage of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.23 | hwPDU2000ML1CurrentValue | L1 current value | L1电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 current value of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.24 | hwPDU2000ML2CurrentValue | L2 current value | L2电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 current value of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.25 | hwPDU2000ML3CurrentValue | L3 current value | L3电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 current value of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.26 | hwPDU2000ML1LoadRatio | L1 load ratio | L1负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | L1 load ratio of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.27 | hwPDU2000ML2LoadRatio | L2 load ratio | L2负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | L2 load ratio of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.28 | hwPDU2000ML3LoadRatio | L3 load ratio | L3负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | L3 load ratio of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.29 | hwPDU2000ML1ActivePower | L1 active power | L1有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 active power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.30 | hwPDU2000ML2ActivePower | L2 active power | L2有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 active power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.31 | hwPDU2000ML3ActivePower | L3 active power | L3有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 active power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.32 | hwPDU2000ML1ReactivePower | L1 reactive power | L1无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 reactive power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.33 | hwPDU2000ML2ReactivePower | L2 reactive power | L2无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 reactive power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.34 | hwPDU2000ML3ReactivePower | L3 reactive power | L3无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 reactive power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.35 | hwPDU2000ML1AppearancePower | L1 Appearance power | L1视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 Appearance power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.36 | hwPDU2000ML2AppearancePower | L2 Appearance power | L2视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 Appearance power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.37 | hwPDU2000ML3AppearancePower | L3 Appearance power | L3视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 Appearance power of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.38 | hwPDU2000ML1PowerFactor | L1 power factor | L1功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L1 power factor of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.39 | hwPDU2000ML2PowerFactor | L2 power factor | L2功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L2 power factor of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.40 | hwPDU2000ML3PowerFactor | L3 power factor | L3功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L3 power factor of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.41 | hwPDU2000ML1ThdU | L1 THD-u | L1 电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.42 | hwPDU2000ML2ThdU | L2 THD-u | L2 电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.43 | hwPDU2000ML3ThdU | L3 THD-u | L3 电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.44 | hwPDU2000ML15ThThdU | L1 5th THD-u | L1 x次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.45 | hwPDU2000ML25ThThdU | L2 5th THD-u | L2 x次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.46 | hwPDU2000ML35ThThdU | L3 5th THD-u | L3 x次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.47 | hwPDU2000ML17ThThdU | L1 7th THD-u | L1 y次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.48 | hwPDU2000ML27ThThdU | L2 7th THD-u | L2 y次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.49 | hwPDU2000ML37ThThdU | L3 7th THD-u | L3 y次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.50 | hwPDU2000ML111ThThdU | L1 11th THD-u | L1 z次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.51 | hwPDU2000ML211ThThdU | L2 11th THD-u | L2 z次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.52 | hwPDU2000ML311ThThdU | L3 11th THD-u | L3 z次电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-u of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.53 | hwPDU2000ML1ThdI | L1 THD-i | L1 电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.54 | hwPDU2000ML2ThdI | L2 THD-i | L2 电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.55 | hwPDU2000ML3ThdI | L3 THD-i | L3 电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.56 | hwPDU2000ML15ThThdI | L1 5th THD-i | L1 x次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.57 | hwPDU2000ML25ThThdI | L2 5th THD-i | L2 x次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.58 | hwPDU2000ML35ThThdI | L3 5th THD-i | L3 x次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.59 | hwPDU2000ML17ThThdI | L1 7th THD-i | L1 y次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.60 | hwPDU2000ML27ThThdI | L2 7th THD-i | L2 y次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.61 | hwPDU2000ML37ThThdI | L3 7th THD-i | L3 y次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.62 | hwPDU2000ML111ThThdI | L1 11th THD-i | L1 z次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.63 | hwPDU2000ML211ThThdI | L2 11th THD-i | L2 z次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.64 | hwPDU2000ML311ThThdI | L3 11th THD-i | L3 z次电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-i of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.65 | hwPDU2000MFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Frequency of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.69 | hwPDU2000MTotalActiveEnergy | Total active energy | 总有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Total active energy of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.71 | hwPDU2000MQF1SwitchStatus | QF1 switch status | QF1开关状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | QF1 switch status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.73 | hwPDU2000MQF2SwitchStatus | QF2 switch status | QF2开关状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | QF2 switch status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.75 | hwPDU2000MQF3SwitchStatus | QF3 switch status | QF3开关状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | QF3 switch status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.77 | hwPDU2000MQF4SwitchStatus | QF4 switch status | QF4开关状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | QF4 switch status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.79 | hwPDU2000MQF5SwitchStatus | QF5 switch status | QF5开关状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | QF5 switch status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.81 | hwPDU2000MQF6SwitchStatus | QF6 switch status | QF6开关状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | QF6 switch status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.82 | hwPDU2000MCurrentOfOutput1 | Current of output 1 | 输出位1电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 1 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.83 | hwPDU2000MLoadRatioOfOutput1 | Load ratio of output 1 | 输出位1负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 1 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.84 | hwPDU2000MActivePowerOfOutput1 | Active power of output 1 | 输出位1有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 1 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.85 | hwPDU2000MReactivePowerOfOutput1 | Reactive power of output 1 | 输出位1无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 1 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.86 | hwPDU2000MAppearancePowerOfOutput1 | Appearance power of output 1 | 输出位1视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 1 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.87 | hwPDU2000MPowerFactorOfOutput1 | Power factor of output 1 | 输出位1功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 1 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.88 | hwPDU2000MActiveEnergyOfOutput1 | Active energy of output 1 | 输出位1有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 1 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.90 | hwPDU2000MStateOfOutput1 | State of output 1 | 输出位1状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 1 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.91 | hwPDU2000MCurrentOfOutput2 | Current of output 2 | 输出位2电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 2 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.92 | hwPDU2000MLoadRatioOfOutput2 | Load ratio of output 2 | 输出位2负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 2 of the device config table for the PDU2000M..Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.93 | hwPDU2000MActivePowerOfOutput2 | Active power of output 2 | 输出位2有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 2 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.94 | hwPDU2000MReactivePowerOfOutput2 | Reactive power of output 2 | 输出位2无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 2 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.95 | hwPDU2000MAppearancePowerOfOutput2 | Appearance power of output 2 | 输出位2视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 2 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.96 | hwPDU2000MPowerFactorOfOutput2 | Power factor of output 2 | 输出位2功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 2 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.97 | hwPDU2000MActiveEnergyOfOutput2 | Active energy of output 2 | 输出位2有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 2 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.99 | hwPDU2000MStateOfOutput2 | State of output 2 | 输出位2状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 2 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.100 | hwPDU2000MCurrentOfOutput3 | Current of output 3 | 输出位3电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 3 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.101 | hwPDU2000MLoadRatioOfOutput3 | Load ratio of output 3 | 输出位3负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 3 of the device config table for the PDU2000M.Multiple:100..SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.102 | hwPDU2000MActivePowerOfOutput3 | Active power of output 3 | 输出位3有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 3 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.103 | hwPDU2000MReactivePowerOfOutput3 | Reactive power of output 3 | 输出位3无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 3 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.104 | hwPDU2000MAppearancePowerOfOutput3 | Appearance power of output 3 | 输出位3视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 3 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.105 | hwPDU2000MPowerFactorOfOutput3 | Power factor of output 3 | 输出位3功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 3 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.106 | hwPDU2000MActiveEnergyOfOutput3 | Active energy of output 3 | 输出位3有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 3 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.108 | hwPDU2000MStateOfOutput3 | State of output 3 | 输出位3状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 3 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.109 | hwPDU2000MCurrentOfOutput4 | Current of output 4 | 输出位4电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 4 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.110 | hwPDU2000MLoadRatioOfOutput4 | Load ratio of output 4 | 输出位4负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 4 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.111 | hwPDU2000MActivePowerOfOutput4 | Active power of output 4 | 输出位4有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 4 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.112 | hwPDU2000MReactivePowerOfOutput4 | Reactive power of output 4 | 输出位4无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 4 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.113 | hwPDU2000MAppearancePowerOfOutput4 | Appearance power of output 4 | 输出位4视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 4 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.114 | hwPDU2000MPowerFactorOfOutput4 | Power factor of output 4 | 输出位4功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 4 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.115 | hwPDU2000MActiveEnergyOfOutput4 | Active energy of output 4 | 输出位4有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 4 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.117 | hwPDU2000MStateOfOutput4 | State of output 4 | 输出位4状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 4 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.118 | hwPDU2000MCurrentOfOutput5 | Current of output 5 | 输出位5电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 5 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.119 | hwPDU2000MLoadRatioOfOutput5 | Load ratio of output 5 | 输出位5负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 5 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.120 | hwPDU2000MActivePowerOfOutput5 | Active power of output 5 | 输出位5有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 5 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.121 | hwPDU2000MReactivePowerOfOutput5 | Reactive power of output 5 | 输出位5无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 5 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.122 | hwPDU2000MAppearancePowerOfOutput5 | Appearance power of output 5 | 输出位5视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 5 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.123 | hwPDU2000MPowerFactorOfOutput5 | Power factor of output 5 | 输出位5功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 5 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.124 | hwPDU2000MActiveEnergyOfOutput5 | Active energy of output 5 | 输出位5有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 5 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.126 | hwPDU2000MStateOfOutput5 | State of output 5 | 输出位5状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 5 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.127 | hwPDU2000MCurrentOfOutput6 | Current of output 6 | 输出位6电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 6 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.128 | hwPDU2000MLoadRatioOfOutput6 | Load ratio of output 6 | 输出位6负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 6 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.129 | hwPDU2000MActivePowerOfOutput6 | Active power of output 6 | 输出位6有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 6 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.130 | hwPDU2000MReactivePowerOfOutput6 | Reactive power of output 6 | 输出位6无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 6 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.131 | hwPDU2000MAppearancePowerOfOutput6 | Appearance power of output 6 | 输出位6视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 6 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.132 | hwPDU2000MPowerFactorOfOutput6 | Power factor of output 6 | 输出位6功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 6 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.133 | hwPDU2000MActiveEnergyOfOutput6 | Active energy of output 6 | 输出位6有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 6 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.135 | hwPDU2000MStateOfOutput6 | State of output 6 | 输出位6状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 6 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.136 | hwPDU2000MCurrentOfOutput7 | Current of output 7 | 输出位7电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 7 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.137 | hwPDU2000MLoadRatioOfOutput7 | Load ratio of output 7 | 输出位7负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 7 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.138 | hwPDU2000MActivePowerOfOutput7 | Active power of output 7 | 输出位7有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 7 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.139 | hwPDU2000MReactivePowerOfOutput7 | Reactive power of output 7 | 输出位7无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 7 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.140 | hwPDU2000MAppearancePowerOfOutput7 | Appearance power of output 7 | 输出位7视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 7 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.141 | hwPDU2000MPowerFactorOfOutput7 | Power factor of output 7 | 输出位7功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 7 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.142 | hwPDU2000MActiveEnergyOfOutput7 | Active energy of output 7 | 输出位7有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 7 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.144 | hwPDU2000MStateOfOutput7 | State of output 7 | 输出位7状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 7 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.145 | hwPDU2000MCurrentOfOutput8 | Current of output 8 | 输出位8电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 8 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.146 | hwPDU2000MLoadRatioOfOutput8 | Load ratio of output 8 | 输出位8负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 8 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.147 | hwPDU2000MActivePowerOfOutput8 | Active power of output 8 | 输出位8有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 8 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.148 | hwPDU2000MReactivePowerOfOutput8 | Reactive power of output 8 | 输出位8无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 8 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.149 | hwPDU2000MAppearancePowerOfOutput8 | Appearance power of output 8 | 输出位8视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 8 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.150 | hwPDU2000MPowerFactorOfOutput8 | Power factor of output 8 | 输出位8功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 8 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.151 | hwPDU2000MActiveEnergyOfOutput8 | Active energy of output 8 | 输出位8有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 8 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.153 | hwPDU2000MStateOfOutput8 | State of output 8 | 输出位8状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 8 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.154 | hwPDU2000MCurrentOfOutput9 | Current of output 9 | 输出位9电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 9 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.155 | hwPDU2000MLoadRatioOfOutput9 | Load ratio of output 9 | 输出位9负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 9 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.156 | hwPDU2000MActivePowerOfOutput9 | Active power of output 9 | 输出位9有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 9 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.157 | hwPDU2000MReactivePowerOfOutput9 | Reactive power of output 9 | 输出位9无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 9 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.158 | hwPDU2000MAppearancePowerOfOutput9 | Appearance power of output 9 | 输出位9视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 9 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.159 | hwPDU2000MPowerFactorOfOutput9 | Power factor of output 9 | 输出位9功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 9 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.160 | hwPDU2000MActiveEnergyOfOutput9 | Active energy of output 9 | 输出位9有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 9 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.162 | hwPDU2000MStateOfOutput9 | State of output 9 | 输出位9状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 9 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.163 | hwPDU2000MCurrentOfOutput10 | Current of output 10 | 输出位10电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 10 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.164 | hwPDU2000MLoadRatioOfOutput10 | Load ratio of output 10 | 输出位10负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 10 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.165 | hwPDU2000MActivePowerOfOutput10 | Active power of output 10 | 输出位10有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 10 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.166 | hwPDU2000MReactivePowerOfOutput10 | Reactive power of output 10 | 输出位10无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 10 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.167 | hwPDU2000MAppearancePowerOfOutput10 | Appearance power of output 10 | 输出位10视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 10 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.168 | hwPDU2000MPowerFactorOfOutput10 | Power factor of output 10 | 输出位10功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 10 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.169 | hwPDU2000MActiveEnergyOfOutput10 | Active energy of output 10 | 输出位10有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 10 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.171 | hwPDU2000MStateOfOutput10 | State of output 10 | 输出位10状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 10 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.172 | hwPDU2000MCurrentOfOutput11 | Current of output 11 | 输出位11电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 11 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.173 | hwPDU2000MLoadRatioOfOutput11 | Load ratio of output 11 | 输出位11负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 11 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.174 | hwPDU2000MActivePowerOfOutput11 | Active power of output 11 | 输出位11有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 11 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.175 | hwPDU2000MReactivePowerOfOutput11 | Reactive power of output 11 | 输出位11无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 11 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.176 | hwPDU2000MAppearancePowerOfOutput11 | Appearance power of output 11 | 输出位11视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 11 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.177 | hwPDU2000MPowerFactorOfOutput11 | Power factor of output 11 | 输出位11功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 11 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.178 | hwPDU2000MActiveEnergyOfOutput11 | Active energy of output 11 | 输出位11有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 11 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.180 | hwPDU2000MStateOfOutput11 | State of output 11 | 输出位11状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 11 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.181 | hwPDU2000MCurrentOfOutput12 | Current of output 12 | 输出位12电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 12 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.182 | hwPDU2000MLoadRatioOfOutput12 | Load ratio of output 12 | 输出位12负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 12 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.183 | hwPDU2000MActivePowerOfOutput12 | Active power of output 12 | 输出位12有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 12 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.184 | hwPDU2000MReactivePowerOfOutput12 | Reactive power of output 12 | 输出位12无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 12 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.185 | hwPDU2000MAppearancePowerOfOutput12 | Appearance power of output 12 | 输出位12视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 12 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.186 | hwPDU2000MPowerFactorOfOutput12 | Power factor of output 12 | 输出位12功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 12 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.187 | hwPDU2000MActiveEnergyOfOutput12 | Active energy of output 12 | 输出位12有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 12 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.189 | hwPDU2000MStateOfOutput12 | State of output 12 | 输出位12状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 12 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.190 | hwPDU2000MCurrentOfOutput13 | Current of output 13 | 输出位13电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 13 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.191 | hwPDU2000MLoadRatioOfOutput13 | Load ratio of output 13 | 输出位13负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 13 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.192 | hwPDU2000MActivePowerOfOutput13 | Active power of output 13 | 输出位13有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 13 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.193 | hwPDU2000MReactivePowerOfOutput13 | Reactive power of output 13 | 输出位13无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 13 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.194 | hwPDU2000MAppearancePowerOfOutput13 | Appearance power of output 13 | 输出位13视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 13 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.195 | hwPDU2000MPowerFactorOfOutput13 | Power factor of output 13 | 输出位13功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 13 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.196 | hwPDU2000MActiveEnergyOfOutput13 | Active energy of output 13 | 输出位13有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 13 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.198 | hwPDU2000MStateOfOutput13 | State of output 13 | 输出位13状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 13 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.199 | hwPDU2000MCurrentOfOutput14 | Current of output 14 | 输出位14电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 14 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.200 | hwPDU2000MLoadRatioOfOutput14 | Load ratio of output 14 | 输出位14负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 14 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.201 | hwPDU2000MActivePowerOfOutput14 | Active power of output 14 | 输出位14有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 14 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.202 | hwPDU2000MReactivePowerOfOutput14 | Reactive power of output 14 | 输出位14无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 14 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.203 | hwPDU2000MAppearancePowerOfOutput14 | Appearance power of output 14 | 输出位14视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 14 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.204 | hwPDU2000MPowerFactorOfOutput14 | Power factor of output 14 | 输出位14功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 14 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.205 | hwPDU2000MActiveEnergyOfOutput14 | Active energy of output 14 | 输出位14有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 14 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.207 | hwPDU2000MStateOfOutput14 | State of output 14 | 输出位14状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 14 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.208 | hwPDU2000MCurrentOfOutput15 | Current of output 15 | 输出位15电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 15 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.209 | hwPDU2000MLoadRatioOfOutput15 | Load ratio of output 15 | 输出位15负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 15 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.210 | hwPDU2000MActivePowerOfOutput15 | Active power of output 15 | 输出位15有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 15 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.211 | hwPDU2000MReactivePowerOfOutput15 | Reactive power of output 15 | 输出位15无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 15 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.212 | hwPDU2000MAppearancePowerOfOutput15 | Appearance power of output 15 | 输出位15视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 15 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.213 | hwPDU2000MPowerFactorOfOutput15 | Power factor of output 15 | 输出位15功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 15 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.214 | hwPDU2000MActiveEnergyOfOutput15 | Active energy of output 15 | 输出位15有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 15 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.216 | hwPDU2000MStateOfOutput15 | State of output 15 | 输出位15状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 15 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.217 | hwPDU2000MCurrentOfOutput16 | Current of output 16 | 输出位16电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 16 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.218 | hwPDU2000MLoadRatioOfOutput16 | Load ratio of output 16 | 输出位16负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 16 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.219 | hwPDU2000MActivePowerOfOutput16 | Active power of output 16 | 输出位16有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 16 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.220 | hwPDU2000MReactivePowerOfOutput16 | Reactive power of output 16 | 输出位16无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 16 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.221 | hwPDU2000MAppearancePowerOfOutput16 | Appearance power of output 16 | 输出位16视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 16 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.222 | hwPDU2000MPowerFactorOfOutput16 | Power factor of output 16 | 输出位16功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 16 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.223 | hwPDU2000MActiveEnergyOfOutput16 | Active energy of output 16 | 输出位16有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 16 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.225 | hwPDU2000MStateOfOutput16 | State of output 16 | 输出位16状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 16 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.226 | hwPDU2000MCurrentOfOutput17 | Current of output 17 | 输出位17电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 17 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.227 | hwPDU2000MLoadRatioOfOutput17 | Load ratio of output 17 | 输出位17负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 17 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.228 | hwPDU2000MActivePowerOfOutput17 | Active power of output 17 | 输出位17有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 17 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.229 | hwPDU2000MReactivePowerOfOutput17 | Reactive power of output 17 | 输出位17无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 17 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.230 | hwPDU2000MAppearancePowerOfOutput17 | Appearance power of output 17 | 输出位17视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 17 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.231 | hwPDU2000MPowerFactorOfOutput17 | Power factor of output 17 | 输出位17功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 17 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.232 | hwPDU2000MActiveEnergyOfOutput17 | Active energy of output 17 | 输出位17有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 17 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.234 | hwPDU2000MStateOfOutput17 | State of output 17 | 输出位17状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 17 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.235 | hwPDU2000MCurrentOfOutput18 | Current of output 18 | 输出位18电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 18 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.236 | hwPDU2000MLoadRatioOfOutput18 | Load ratio of output 18 | 输出位18负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 18 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.237 | hwPDU2000MActivePowerOfOutput18 | Active power of output 18 | 输出位18有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 18 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.238 | hwPDU2000MReactivePowerOfOutput18 | Reactive power of output 18 | 输出位18无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 18 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.239 | hwPDU2000MAppearancePowerOfOutput18 | Appearance power of output 18 | 输出位18视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 18 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.240 | hwPDU2000MPowerFactorOfOutput18 | Power factor of output 18 | 输出位18功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 18 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.241 | hwPDU2000MActiveEnergyOfOutput18 | Active energy of output 18 | 输出位18有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 18 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.243 | hwPDU2000MStateOfOutput18 | State of output 18 | 输出位18状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 18 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.244 | hwPDU2000MCurrentOfOutput19 | Current of output 19 | 输出位19电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 19 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.245 | hwPDU2000MLoadRatioOfOutput19 | Load ratio of output 19 | 输出位19负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 19 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.246 | hwPDU2000MActivePowerOfOutput19 | Active power of output 19 | 输出位19有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 19 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.247 | hwPDU2000MReactivePowerOfOutput19 | Reactive power of output 19 | 输出位19无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 19 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.248 | hwPDU2000MAppearancePowerOfOutput19 | Appearance power of output 19 | 输出位19视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 19 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.249 | hwPDU2000MPowerFactorOfOutput19 | Power factor of output 19 | 输出位19功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 19 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.250 | hwPDU2000MActiveEnergyOfOutput19 | Active energy of output 19 | 输出位19有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 19 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.252 | hwPDU2000MStateOfOutput19 | State of output 19 | 输出位19状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 19 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.253 | hwPDU2000MCurrentOfOutput20 | Current of output 20 | 输出位20电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 20 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.254 | hwPDU2000MLoadRatioOfOutput20 | Load ratio of output 20 | 输出位20负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 20 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.255 | hwPDU2000MActivePowerOfOutput20 | Active power of output 20 | 输出位20有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 20 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.256 | hwPDU2000MReactivePowerOfOutput20 | Reactive power of output 20 | 输出位20无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 20 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.257 | hwPDU2000MAppearancePowerOfOutput20 | Appearance power of output 20 | 输出位20视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 20 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.258 | hwPDU2000MPowerFactorOfOutput20 | Power factor of output 20 | 输出位20功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 20 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.259 | hwPDU2000MActiveEnergyOfOutput20 | Active energy of output 20 | 输出位20有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 20 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.261 | hwPDU2000MStateOfOutput20 | State of output 20 | 输出位20状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 20 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.262 | hwPDU2000MCurrentOfOutput21 | Current of output 21 | 输出位21电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 21 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.263 | hwPDU2000MLoadRatioOfOutput21 | Load ratio of output 21 | 输出位21负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 21 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.264 | hwPDU2000MActivePowerOfOutput21 | Active power of output 21 | 输出位21有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 21 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.265 | hwPDU2000MReactivePowerOfOutput21 | Reactive power of output 21 | 输出位21无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 21 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.266 | hwPDU2000MAppearancePowerOfOutput21 | Appearance power of output 21 | 输出位21视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 21 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.267 | hwPDU2000MPowerFactorOfOutput21 | Power factor of output 21 | 输出位21功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 21 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.268 | hwPDU2000MActiveEnergyOfOutput21 | Active energy of output 21 | 输出位21有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 21 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.270 | hwPDU2000MStateOfOutput21 | State of output 21 | 输出位21状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 21 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.271 | hwPDU2000MCurrentOfOutput22 | Current of output 22 | 输出位22电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 22 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.272 | hwPDU2000MLoadRatioOfOutput22 | Load ratio of output 22 | 输出位22负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 22 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.273 | hwPDU2000MActivePowerOfOutput22 | Active power of output 22 | 输出位22有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 22 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.274 | hwPDU2000MReactivePowerOfOutput22 | Reactive power of output 22 | 输出位22无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 22 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.275 | hwPDU2000MAppearancePowerOfOutput22 | Appearance power of output 22 | 输出位22视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 22 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.276 | hwPDU2000MPowerFactorOfOutput22 | Power factor of output 22 | 输出位22功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 22 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.277 | hwPDU2000MActiveEnergyOfOutput22 | Active energy of output 22 | 输出位22有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 22 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.279 | hwPDU2000MStateOfOutput22 | State of output 22 | 输出位22状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 22 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.280 | hwPDU2000MCurrentOfOutput23 | Current of output 23 | 输出位23电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 23 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.281 | hwPDU2000MLoadRatioOfOutput23 | Load ratio of output 23 | 输出位23负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 23 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.282 | hwPDU2000MActivePowerOfOutput23 | Active power of output 23 | 输出位23有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 23 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.283 | hwPDU2000MReactivePowerOfOutput23 | Reactive power of output 23 | 输出位23无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 23 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.284 | hwPDU2000MAppearancePowerOfOutput23 | Appearance power of output 23 | 输出位23视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 23 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.285 | hwPDU2000MPowerFactorOfOutput23 | Power factor of output 23 | 输出位23功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 23 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.286 | hwPDU2000MActiveEnergyOfOutput23 | Active energy of output 23 | 输出位23有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 23 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.288 | hwPDU2000MStateOfOutput23 | State of output 23 | 输出位23状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 23 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.289 | hwPDU2000MCurrentOfOutput24 | Current of output 24 | 输出位24电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 24 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.290 | hwPDU2000MLoadRatioOfOutput24 | Load ratio of output 24 | 输出位24负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 24 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.291 | hwPDU2000MActivePowerOfOutput24 | Active power of output 24 | 输出位24有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 24 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.292 | hwPDU2000MReactivePowerOfOutput24 | Reactive power of output 24 | 输出位24无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 24 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.293 | hwPDU2000MAppearancePowerOfOutput24 | Appearance power of output 24 | 输出位24视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 24 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.294 | hwPDU2000MPowerFactorOfOutput24 | Power factor of output 24 | 输出位24功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 24 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.295 | hwPDU2000MActiveEnergyOfOutput24 | Active energy of output 24 | 输出位24有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 24 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.1.1.300 | hwPDU2000MRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2 | hwPDU2000MRunning2Table | / | / |  |  | / | / | The running table of PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.1 | hwPDU2000MRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.3 | hwPDU2000MStateOfOutput24 | State of output 24 | 输出位24状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 24 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.4 | hwPDU2000MCurrentOfOutput25 | Current of output 25 | 输出位25电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 25 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.5 | hwPDU2000MLoadRatioOfOutput25 | Load ratio of output 25 | 输出位25负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 25 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.6 | hwPDU2000MActivePowerOfOutput25 | Active power of output 25 | 输出位25有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 25 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.7 | hwPDU2000MReactivePowerOfOutput25 | Reactive power of output 25 | 输出位25无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 25 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.8 | hwPDU2000MAppearancePowerOfOutput25 | Appearance power of output 25 | 输出位25视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 25 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.9 | hwPDU2000MPowerFactorOfOutput25 | Power factor of output 25 | 输出位25功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 25 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.10 | hwPDU2000MActiveEnergyOfOutput25 | Active energy of output 25 | 输出位25有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 25 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.12 | hwPDU2000MStateOfOutput25 | State of output 25 | 输出位25状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 25 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.13 | hwPDU2000MCurrentOfOutput26 | Current of output 26 | 输出位26电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 26 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.14 | hwPDU2000MLoadRatioOfOutput26 | Load ratio of output 26 | 输出位26负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 26 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.15 | hwPDU2000MActivePowerOfOutput26 | Active power of output 26 | 输出位26有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 26 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.16 | hwPDU2000MReactivePowerOfOutput26 | Reactive power of output 26 | 输出位26无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 26 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.17 | hwPDU2000MAppearancePowerOfOutput26 | Appearance power of output 26 | 输出位26视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 26 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.18 | hwPDU2000MPowerFactorOfOutput26 | Power factor of output 26 | 输出位26功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 26 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.19 | hwPDU2000MActiveEnergyOfOutput26 | Active energy of output 26 | 输出位26有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 26 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.21 | hwPDU2000MStateOfOutput26 | State of output 26 | 输出位26状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 26 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.22 | hwPDU2000MCurrentOfOutput27 | Current of output 27 | 输出位27电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 27 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.23 | hwPDU2000MLoadRatioOfOutput27 | Load ratio of output 27 | 输出位27负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 27 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.24 | hwPDU2000MActivePowerOfOutput27 | Active power of output 27 | 输出位27有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 27 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.25 | hwPDU2000MReactivePowerOfOutput27 | Reactive power of output 27 | 输出位27无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 27 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.26 | hwPDU2000MAppearancePowerOfOutput27 | Appearance power of output 27 | 输出位27视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 27 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.27 | hwPDU2000MPowerFactorOfOutput27 | Power factor of output 27 | 输出位27功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 27 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.28 | hwPDU2000MActiveEnergyOfOutput27 | Active energy of output 27 | 输出位27有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 27 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.30 | hwPDU2000MStateOfOutput27 | State of output 27 | 输出位27状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 27 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.31 | hwPDU2000MCurrentOfOutput28 | Current of output 28 | 输出位28电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 28 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.32 | hwPDU2000MLoadRatioOfOutput28 | Load ratio of output 28 | 输出位28负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 28 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.33 | hwPDU2000MActivePowerOfOutput28 | Active power of output 28 | 输出位28有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 28 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.34 | hwPDU2000MReactivePowerOfOutput28 | Reactive power of output 28 | 输出位28无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 28 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.35 | hwPDU2000MAppearancePowerOfOutput28 | Appearance power of output 28 | 输出位28视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 28 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.36 | hwPDU2000MPowerFactorOfOutput28 | Power factor of output 28 | 输出位28功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 28 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.37 | hwPDU2000MActiveEnergyOfOutput28 | Active energy of output 28 | 输出位28有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 28 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.39 | hwPDU2000MStateOfOutput28 | State of output 28 | 输出位28状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 28 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.40 | hwPDU2000MCurrentOfOutput29 | Current of output 29 | 输出位29电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 29 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.41 | hwPDU2000MLoadRatioOfOutput29 | Load ratio of output 29 | 输出位29负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 29 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.42 | hwPDU2000MActivePowerOfOutput29 | Active power of output 29 | 输出位29有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 29 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.43 | hwPDU2000MReactivePowerOfOutput29 | Reactive power of output 29 | 输出位29无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 29 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.44 | hwPDU2000MAppearancePowerOfOutput29 | Appearance power of output 29 | 输出位29视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 29 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.45 | hwPDU2000MPowerFactorOfOutput29 | Power factor of output 29 | 输出位29功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 29 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.46 | hwPDU2000MActiveEnergyOfOutput29 | Active energy of output 29 | 输出位29有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 29 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.48 | hwPDU2000MStateOfOutput29 | State of output 29 | 输出位29状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 29 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.49 | hwPDU2000MCurrentOfOutput30 | Current of output 30 | 输出位30电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current of output 30 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.50 | hwPDU2000MLoadRatioOfOutput30 | Load ratio of output 30 | 输出位30负载率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load ratio of output 30 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.51 | hwPDU2000MActivePowerOfOutput30 | Active power of output 30 | 输出位30有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Active power of output 30 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.52 | hwPDU2000MReactivePowerOfOutput30 | Reactive power of output 30 | 输出位30无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Reactive power of output 30 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.53 | hwPDU2000MAppearancePowerOfOutput30 | Appearance power of output 30 | 输出位30视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Appearance power of output 30 of the device config table for the PDU2000M.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.54 | hwPDU2000MPowerFactorOfOutput30 | Power factor of output 30 | 输出位30功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Power factor of output 30 of the device config table for the PDU2000M.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.55 | hwPDU2000MActiveEnergyOfOutput30 | Active energy of output 30 | 输出位30有功电能 | 0-Read_Only | 只读 | 0..429000000 | 0..429000000 | Active energy of output 30 of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.57 | hwPDU2000MStateOfOutput30 | State of output 30 | 输出位30状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | State of output 30 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.59 | hwPDU2000MAiorDi1DiStatus | DI_1 DI status | DI_1 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_1 DI status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.60 | hwPDU2000MAiorDi1PowerStatus | DI_1 power status | DI_1 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_1 power status of the device config table for the PDU2000M. Value 1 indicate nopowersupply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.61 | hwPDU2000MCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the PDU2000M. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.62 | hwPDU2000MMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.63 | hwPDU2000MEsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.64 | hwPDU2000MELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.65 | hwPDU2000MNCurrent | N current | N线电流 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | N current of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.66 | hwPDU2000MSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..30 | 0..30 | Software version of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.67 | hwPDU2000M12VPowerSupplyStatus | 12 V power supply status | 12V电源供电状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 12 V power supply status of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.69 | hwPDU2000MAiorDi2DiStatus | DI_2 DI status | DI_2 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_2 DI status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.70 | hwPDU2000MAiorDi2PowerStatus | DI_2 power status | DI_2 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_2 power status of the device config table for the PDU2000M. Value 1 indicate nopowersupply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.72 | hwPDU2000MAiorDi3DiStatus | DI_3 DI status | DI_3 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_3 DI status of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.73 | hwPDU2000MAiorDi3PowerStatus | DI_3 power status | DI_3 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_3 power status of the device config table for the PDU2000M. Value 1 indicate nopowersupply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.18.2.1.300 | hwPDU2000MRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3 | hwPDU2000MConfig3Table | / | / |  |  | / | / | The config table of PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.1 | hwPDU2000MConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.2 | hwPDU2000MDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.3 | hwPDU2000MParentDeviceId | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Parent device ID of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.8 | hwPDU2000MXHarmonics | X-th harmonics | x次谐波次数 | 1-Read_Write | 读写 | 2..31 | 2..31 | X harmonics of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.9 | hwPDU2000MYHarmonics | Y-th harmonics | y次谐波次数 | 1-Read_Write | 读写 | 2..31 | 2..31 | Y harmonics of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.10 | hwPDU2000MZHarmonics | Z-th harmonics | z次谐波次数 | 1-Read_Write | 读写 | 2..31 | 2..31 | Z harmonics of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.11 | hwPDU2000MRpduType | rPDU type | rPDU分类 | 1-Read_Write | 读写 | monitoringtype(1), switchingtype(2), unknown(255) | [主路检测型=1]/[开关型=2] | rPDU type of the device config table for the PDU2000M. Value 1 indicate monitoringtype Value 2 indicate switchingtype
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.12 | hwPDU2000MOutputNumbers | output numbers | 输出位数 | 1-Read_Write | 读写 | 0..30 | 0..30 | output numbers of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.14 | hwPDU2000MNumberOfCircuits | Number of Circuits | 回路数 | 1-Read_Write | 读写 | 0..6 | 0..6 | Number of Circuits of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.15 | hwPDU2000MTemperatureAndHumidityQuantity | Temperature and humidity quantity | 温湿度传感器个数 | 1-Read_Write | 读写 | 0..4 | 0..4 | Temperature and humidity quantity of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.16 | hwPDU2000MNumberOfDetectionBoards | Number of detection boards | 检测板个数 | 1-Read_Write | 读写 | 0..3 | 0..3 | Number of detection boards of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.17 | hwPDU2000MOpenPhaseThreshold | Open phase threshold | 缺相告警阈值 | 1-Read_Write | 读写 | 0..60 | 0..60 | Open phase threshold of the device config table for the PDU2000M.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.18 | hwPDU2000MOvervoltageThreshold | Overvoltage threshold | 过压告警阈值 | 1-Read_Write | 读写 | 105..130 | 105..130 | Overvoltage threshold of the device config table for the PDU2000M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.19 | hwPDU2000MUndervoltageThreshold | Undervoltage threshold | 欠压告警阈值 | 1-Read_Write | 读写 | 75..95 | 75..95 | Undervoltage threshold of the device config table for the PDU2000M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.20 | hwPDU2000MOverloadThreshold | Overload threshold | 负载过载阈值 | 1-Read_Write | 读写 | 100..120 | 100..120 | Overload threshold of the device config table for the PDU2000M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.21 | hwPDU2000MOverfrequencyThreshold | Overfrequency threshold | 频率越限阈值 | 1-Read_Write | 读写 | 10..100 | 10..100 | Overfrequency threshold of the device config table for the PDU2000M.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.22 | hwPDU2000MThreePhaseLoadImbalance | Three-phase load imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 15..50 | 15..50 | Three-phase load imbalance of the device config table for the PDU2000M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.23 | hwPDU2000MOvercurrentThreshold | Overcurrent threshold | 电流高阈值越限 | 1-Read_Write | 读写 | 40..100 | 40..100 | Overcurrent threshold of the device config table for the PDU2000M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.24 | hwPDU2000MUndercurrentThreshold | Undercurrent threshold | 电流低阈值越限 | 1-Read_Write | 读写 | 30..80 | 30..80 | Undercurrent threshold of the device config table for the PDU2000M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.25 | hwPDU2000MControlOutputChannel | Control output channel | 输出位通路控制使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Control output channel of the device config table for the PDU2000M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.26 | hwPDU2000MHighTemperatureAlarmThreshold | High temperature alarm threshold | 高温告警点 | 1-Read_Write | 读写 | 20..80 | 20..80 | High temperature alarm threshold of the device config table for the PDU2000M.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.27 | hwPDU2000MLowTemperatureAlarmThreshold | Low temperature alarm threshold | 低温告警点 | 1-Read_Write | 读写 | -20..19 | -20..19 | Low temperature alarm threshold of the device config table for the PDU2000M.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.28 | hwPDU2000MHighHumidityAlarmThreshold | High humidity alarm threshold | 高湿告警点 | 1-Read_Write | 读写 | 50..100 | 50..100 | High humidity alarm threshold of the device config table for the PDU2000M.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.29 | hwPDU2000MLowHumidityAlarmThreshold | Low humidity alarm threshold | 低湿告警点 | 1-Read_Write | 读写 | 0..40 | 0..40 | Low humidity alarm threshold of the device config table for the PDU2000M.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.39 | hwPDU2000MOnOffControlOfOutput1 | On-off control of output 1 | 输出位1通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 1 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.43 | hwPDU2000MOnOffControlOfOutput2 | On-off control of output 2 | 输出位2通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 2 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.47 | hwPDU2000MOnOffControlOfOutput3 | On-off control of output 3 | 输出位3通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 3 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.51 | hwPDU2000MOnOffControlOfOutput4 | On-off control of output 4 | 输出位4通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 4 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.55 | hwPDU2000MOnOffControlOfOutput5 | On-off control of output 5 | 输出位5通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 5 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.59 | hwPDU2000MOnOffControlOfOutput6 | On-off control of output 6 | 输出位6通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 6 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.63 | hwPDU2000MOnOffControlOfOutput7 | On-off control of output 7 | 输出位7通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 7 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.67 | hwPDU2000MOnOffControlOfOutput8 | On-off control of output 8 | 输出位8通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 8 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.71 | hwPDU2000MOnOffControlOfOutput9 | On-off control of output 9 | 输出位9通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 9 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.75 | hwPDU2000MOnOffControlOfOutput10 | On-off control of output 10 | 输出位10通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 10 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.79 | hwPDU2000MOnOffControlOfOutput11 | On-off control of output 11 | 输出位11通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 11 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.83 | hwPDU2000MOnOffControlOfOutput12 | On-off control of output 12 | 输出位12通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 12 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.87 | hwPDU2000MOnOffControlOfOutput13 | On-off control of output 13 | 输出位13通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 13 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.91 | hwPDU2000MOnOffControlOfOutput14 | On-off control of output 14 | 输出位14通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 14 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.95 | hwPDU2000MOnOffControlOfOutput15 | On-off control of output 15 | 输出位15通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 15 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.99 | hwPDU2000MOnOffControlOfOutput16 | On-off control of output 16 | 输出位16通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 16 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.103 | hwPDU2000MOnOffControlOfOutput17 | On-off control of output 17 | 输出位17通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 17 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.107 | hwPDU2000MOnOffControlOfOutput18 | On-off control of output 18 | 输出位18通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 18 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.111 | hwPDU2000MOnOffControlOfOutput19 | On-off control of output 19 | 输出位19通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 19 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.115 | hwPDU2000MOnOffControlOfOutput20 | On-off control of output 20 | 输出位20通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 20 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.119 | hwPDU2000MOnOffControlOfOutput21 | On-off control of output 21 | 输出位21通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 21 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.123 | hwPDU2000MOnOffControlOfOutput22 | On-off control of output 22 | 输出位22通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 22 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.127 | hwPDU2000MOnOffControlOfOutput23 | On-off control of output 23 | 输出位23通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 23 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.131 | hwPDU2000MOnOffControlOfOutput24 | On-off control of output 24 | 输出位24通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 24 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.135 | hwPDU2000MOnOffControlOfOutput25 | On-off control of output 25 | 输出位25通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 25 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.139 | hwPDU2000MOnOffControlOfOutput26 | On-off control of output 26 | 输出位26通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 26 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.143 | hwPDU2000MOnOffControlOfOutput27 | On-off control of output 27 | 输出位27通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 27 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.147 | hwPDU2000MOnOffControlOfOutput28 | On-off control of output 28 | 输出位28通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 28 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.151 | hwPDU2000MOnOffControlOfOutput29 | On-off control of output 29 | 输出位29通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 29 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.155 | hwPDU2000MOnOffControlOfOutput30 | On-off control of output 30 | 输出位30通断控制 | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | On-off control of output 30 of the device config table for the PDU2000M. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.157 | hwPDU2000MCom1BaudRate | COM1 baud rate | COM1的波特率 | 1-Read_Write | 读写 | baudrateNineThousandSixHundred(1), baudrateTwoThousandFourHundred(2), baudrateFourThousandEightHundred(3), baudrateNineteenThousandTwoHundred(4), baudrateOneLakhfifteenThousandTwoHundred(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM1 baud rate of the device config table for the PDU2000M. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.158 | hwPDU2000MCom2BaudRate | COM2 baud rate | COM2的波特率 | 1-Read_Write | 读写 | baudrateNineThousandSixHundred(1), baudrateTwoThousandFourHundred(2), baudrateFourThousandEightHundred(3), baudrateNineteenThousandTwoHundred(4), baudrateOneLakhfifteenThousandTwoHundred(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM2 baud rate of the device config table for the PDU2000M. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.159 | hwPDU2000MCom3BaudRate | COM3 baud rate | COM3的波特率 | 1-Read_Write | 读写 | baudrateNineThousandSixHundred(1), baudrateTwoThousandFourHundred(2), baudrateFourThousandEightHundred(3), baudrateNineteenThousandTwoHundred(4), baudrateOneLakhfifteenThousandTwoHundred(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM3 baud rate of the device config table for the PDU2000M. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.160 | hwPDU2000MCom4BaudRate | COM4 baud rate | COM4的波特率 | 1-Read_Write | 读写 | baudrateNineThousandSixHundred(1), baudrateTwoThousandFourHundred(2), baudrateFourThousandEightHundred(3), baudrateNineteenThousandTwoHundred(4), baudrateOneLakhfifteenThousandTwoHundred(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM4 baud rate of the device config table for the PDU2000M. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.161 | hwPDU2000MCom1ParityBit | COM1 parity bit | COM1的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM1 parity bit of the device config table for the PDU2000M. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.162 | hwPDU2000MCom2ParityBit | COM2 parity bit | COM2的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM2 parity bit of the device config table for the PDU2000M. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.163 | hwPDU2000MCom3ParityBit | COM3 parity bit | COM3的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM3 parity bit of the device config table for the PDU2000M. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.164 | hwPDU2000MCom4ParityBit | COM4 parity bit | COM4的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM4 parity bit of the device config table for the PDU2000M. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.165 | hwPDU2000MDataBitsOfCom1 | Data bits of COM1 | COM1的数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | Data bits of COM1 of the device config table for the PDU2000M. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.166 | hwPDU2000MDataBitsOfCom2 | Data bits of COM2 | COM2的数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | Data bits of COM2 of the device config table for the PDU2000M. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.167 | hwPDU2000MDataBitsOfCom3 | Data bits of COM3 | COM3的数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | Data bits of COM3 of the device config table for the PDU2000M. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.168 | hwPDU2000MDataBitsOfCom4 | Data bits of COM4 | COM4的数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | Data bits of COM4 of the device config table for the PDU2000M. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.169 | hwPDU2000MCom1StopBit | COM1 stop bit | COM1的停止位 | 1-Read_Write | 读写 | stopbit1(1), stopbit2(2), unknown(255) | [停止位1=1]/[停止位2=2] | COM1 stop bit of the device config table for the PDU2000M. Value 1 indicate stopbit1 Value 2 indicate stopbit2
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.170 | hwPDU2000MCom2StopBit | COM2 stop bit | COM2的停止位 | 1-Read_Write | 读写 | stopbit1(1), stopbit2(2), unknown(255) | [停止位1=1]/[停止位2=2] | COM2 stop bit of the device config table for the PDU2000M. Value 1 indicate stopbit1 Value 2 indicate stopbit2
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.171 | hwPDU2000MCom3StopBit | COM3 stop bit | COM3的停止位 | 1-Read_Write | 读写 | stopbit1(1), stopbit2(2), unknown(255) | [停止位1=1]/[停止位2=2] | COM3 stop bit of the device config table for the PDU2000M. Value 1 indicate stopbit1 Value 2 indicate stopbit2
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.172 | hwPDU2000MCom4StopBit | COM4 stop bit | COM4的停止位 | 1-Read_Write | 读写 | stopbit1(1), stopbit2(2), unknown(255) | [停止位1=1]/[停止位2=2] | COM4 stop bit of the device config table for the PDU2000M. Value 1 indicate stopbit1 Value 2 indicate stopbit2
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.173 | hwPDU2000M12VOutputControlForChannel | 12 V output control for channel | 通路12V输出控制 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | 12 V output control for channel of the device config table for the PDU2000M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.174 | hwPDU2000MAiorDi1 | DI_1 | DI_1 | 1-Read_Write | 读写 | 0..50 | 0..50 | AI/DI_1 of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.175 | hwPDU2000MAiorDi1Sensor | DI_1 sensor | DI_1 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_1 sensor of the device config table for the PDU2000M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.176 | hwPDU2000MAiorDi1SensorType | DI_1 sensor type | DI_1 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokesensorNc(5), leaksensor(6), leaksensorRope(7), leaksensorNc(8), leaksensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[水浸(电极式)=9] | AI/DI_1 sensor type of the device config table for the PDU2000M. Value 1 indicate normalopen Value 2 indicate normalclose Value 3 indicate doorsensor Value 4 indicate smokesensor Value 5 indicate smokesensor(nc) Value 6 indicate leaksensor Value 7 indicate leaksensor(rope) Value 8 indicate leaksensor(nc) Value 9 indicate leaksensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.177 | hwPDU2000MAiorDi1AiOrDi | DI_1 AI or DI | DI_1 功能选择 | 1-Read_Write | 读写 | ai(1), di(2), unknown(255) | [AI=1]/[DI=2] | AI/DI_1 AI or DI of the device config table for the PDU2000M. Value 1 indicate ai Value 2 indicate di
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.178 | hwPDU2000MAiorDi1MeasurementUnit | DI_1 measurement unit | DI_1 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_1 measurement unit of the device config table for the PDU2000M. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.183 | hwPDU2000MAiorDi2 | DI_2 | DI_2 | 1-Read_Write | 读写 | 0..50 | 0..50 | AI/DI_2 of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.184 | hwPDU2000MAiorDi2Sensor | DI_2 sensor | DI_2 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_2 sensor of the device config table for the PDU2000M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.185 | hwPDU2000MAiorDi2SensorType | DI_2 sensor type | DI_2 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokesensorNc(5), leaksensor(6), leaksensorRope(7), leaksensorNc(8), leaksensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[水浸(电极式)=9] | AI/DI_2 sensor type of the device config table for the PDU2000M. Value 1 indicate normalopen Value 2 indicate normalclose Value 3 indicate doorsensor Value 4 indicate smokesensor Value 5 indicate smokesensor(nc) Value 6 indicate leaksensor Value 7 indicate leaksensor(rope) Value 8 indicate leaksensor(nc) Value 9 indicate leaksensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.186 | hwPDU2000MAiorDi2AiOrDi | DI_2 AI or DI | DI_2 功能选择 | 1-Read_Write | 读写 | ai(1), di(2), unknown(255) | [AI=1]/[DI=2] | AI/DI_2 AI or DI of the device config table for the PDU2000M. Value 1 indicate ai Value 2 indicate di
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.187 | hwPDU2000MAiorDi2MeasurementUnit | DI_2 measurement unit | DI_2 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_2 measurement unit of the device config table for the PDU2000M. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.192 | hwPDU2000MAiorDi3 | DI_3 | DI_3 | 1-Read_Write | 读写 | 0..50 | 0..50 | AI/DI_3 of the device config table for the PDU2000M.
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.193 | hwPDU2000MAiorDi3Sensor | DI_3 sensor | DI_3 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_3 sensor of the device config table for the PDU2000M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.194 | hwPDU2000MAiorDi3SensorType | DI_3 sensor type | DI_3 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokesensorNc(5), leaksensor(6), leaksensorRope(7), leaksensorNc(8), leaksensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[水浸(电极式)=9] | AI/DI_3 sensor type of the device config table for the PDU2000M. Value 1 indicate normalopen Value 2 indicate normalclose Value 3 indicate doorsensor Value 4 indicate smokesensor Value 5 indicate smokesensor(nc) Value 6 indicate leaksensor Value 7 indicate leaksensor(rope) Value 8 indicate leaksensor(nc) Value 9 indicate leaksensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.195 | hwPDU2000MAiorDi3AiOrDi | DI_3 AI or DI | DI_3 功能选择 | 1-Read_Write | 读写 | ai(1), di(2), unknown(255) | [AI=1]/[DI=2] | AI/DI_3 AI or DI of the device config table for the PDU2000M. Value 1 indicate ai Value 2 indicate di
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.196 | hwPDU2000MAiorDi3MeasurementUnit | DI_3 measurement unit | DI_3 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_3 measurement unit of the device config table for the PDU2000M. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.9.18.3.1.300 | hwPDU2000MConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PDU2000M.

## GGIC400P3
GGIC400P3
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.19 | hwGGIC400P3 | hwGGIC400P3 | hwGGIC400P3 | / | / | / | / | GGIC400P3 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1 | hwDEMSVD2Running1Table | / | / |  |  | / | / | The running table of GGIC400P3
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.1 | hwDEMSVD2Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the GGIC400P3
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.2 | hwModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running table for the GGIC400P3.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.3 | hwPortNo | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running table for the GGIC400P3.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.4 | hwCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running table for the GGIC400P3.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.5 | hwPhaseVoltageU1 | Phase voltage U1 | A相电压UA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PhaseVoltageU1 of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.6 | hwPhaseVoltageU2 | Phase voltage U2 | B相电压UB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PhaseVoltageU2 of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.7 | hwPhaseVoltageU3 | Phase voltage U3 | C相电压UC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PhaseVoltageU3 of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.8 | hwThreePhaseAveragePhaseVoltageVlnavg | Three-phase average phase voltage VLNavg | 三相平均相电压VLNavg | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThreePhaseAveragePhaseVoltageVlnavg of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.9 | hwLineVoltageU12 | Line voltage U12 | AB线电压UAB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | LineVoltageU12 of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.10 | hwLineVoltageU23 | Line voltage U23 | BC线电压UBC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | LineVoltageU23 of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.11 | hwLineVoltageU31 | Line voltage U31 | CA线电压UCA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | LineVoltageU31 of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.12 | hwThreePhaseAverageLineVoltageVllnavg | Three-phase average line voltage VLLNavg | 三相平均线电压VLLNavg | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThreePhaseAverageLineVoltageVllnavg of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.13 | hwPhaseCurrentI1 | Phase current I1 | A相电流IA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PhaseCurrentI1 of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.14 | hwPhaseCurrentI2 | Phase current I2 | B相电流IB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PhaseCurrentI2 of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.15 | hwPhaseCurrentI3 | Phase current I3 | C相电流IC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PhaseCurrentI3 of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.16 | hwThreePhaseAverageLineCurrentIavg | Three-phase average line current Iavg | 三相平均电流Iavg | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ThreePhaseAverageLineCurrentIavg of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.17 | hwNeutralCurrentIn | Neutral current In | 零线电流In | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | NeutralCurrentIn of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.18 | hwActivePowerP1 | Active power P1 | A相有功PA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ActivePowerP1 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.19 | hwActivePowerP2 | Active power P2 | B相有功PB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ActivePowerP2 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.20 | hwActivePowerP3 | Active power P3 | C相有功PC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ActivePowerP3 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.21 | hwSystemActivePowerP | System active power P | 系统有功P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | SystemActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.22 | hwReactivePowerQ1 | Reactive power Q1 | A相无功QA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ReactivePowerQ1 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.23 | hwReactivePowerQ2 | Reactive power Q2 | B相无功QB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ReactivePowerQ2 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.24 | hwReactivePowerQ3 | Reactive power Q3 | C相无功QC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ReactivePowerQ3 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.25 | hwSystemReactiveQ | System reactive Q | 系统无功Q | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | SystemReactiveQ of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.26 | hwApparentPowerS1 | Apparent power S1 | A相视在功率SA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ApparentPowerS1 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.27 | hwApparentPowerS2 | Apparent power S2 | B相视在功率SB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ApparentPowerS2 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.28 | hwApparentPowerS3 | Apparent power S3 | C相视在功率SC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ApparentPowerS3 of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.29 | hwSystemApparentPowerS | System apparent power S | 系统视在功率S | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | SystemApparentPowerS of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.30 | hwPowerFactorPf1 | Power factor PF1 | A相功率因数PFA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PowerFactorPf1 of the device running table for the GGIC400P3. Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.31 | hwPowerFactorPf2 | Power factor PF2 | B相功率因数PFB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PowerFactorPf2 of the device running table for the GGIC400P3. Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.32 | hwPowerFactorPf3 | Power factor PF3 | C相功率因数PFC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PowerFactorPf3 of the device running table for the GGIC400P3. Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.33 | hwSystemPowerFactorPf | System power factor PF | 系统功率因数PF | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | SystemPowerFactorPf of the device running table for the GGIC400P3. Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.34 | hwFrequencyF | Frequency F | 频率F | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FrequencyF of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.35 | hwPositiveActiveEnergy | Positive active energy | 正向有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PositiveActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.36 | hwReverseActiveEnergy | Reverse active energy | 负向有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ReverseActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.37 | hwPositiveReactiveEnergy | Positive reactive energy | 正向无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PositiveReactiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.38 | hwReverseReactiveEnergy | Reverse reactive energy | 负向无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ReverseReactiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.39 | hwTemperature1 | Temperature 1 | 温度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature1 of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.40 | hwTemperature2 | Temperature 2 | 温度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature2 of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.41 | hwHumidity | Humidity | 湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Humidity of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.42 | hwFundamentalWaveVaPrimaryValue | Fundamental wave VA(primary value) | 基波VA（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveVaPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.43 | hwFundamentalWaveVbPrimaryValue | Fundamental wave VB(primary value) | 基波VB（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveVbPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.44 | hwFundamentalWaveVcPrimaryValue | Fundamental wave VC(primary value) | 基波VC（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveVcPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.45 | hwFundamentalWaveIaPrimaryValue | Fundamental wave IA(primary value) | 基波IA（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveIaPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.46 | hwFundamentalWaveIbPrimaryValue | Fundamental wave IB(primary value) | 基波IB（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveIbPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.47 | hwFundamentalWaveIcPrimaryValue | Fundamental wave IC(primary value) | 基波IC（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveIcPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.48 | hwFundamentalWavePaPrimaryValue | Fundamental wave PA(primary value) | 基波PA（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWavePaPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.49 | hwFundamentalWavePbPrimaryValue | Fundamental wave PB(primary value) | 基波PB（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWavePbPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.50 | hwFundamentalWavePcPrimaryValue | Fundamental wave PC(primary value) | 基波PC（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWavePcPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.51 | hwFundamentalWaveActiveElectricalEnergyPrimaryValue | Fundamental wave active electrical energy(primary value) | 基波有功电能（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveActiveElectricalEnergyPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.52 | hwHarmonicVaPrimaryValue | Harmonic VA(primary value) | 谐波VA（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicVaPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.53 | hwHarmonicVbPrimaryValue | Harmonic VB(primary value) | 谐波VB（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicVbPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.54 | hwHarmonicVcPrimaryValue | Harmonic VC(primary value) | 谐波VC（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicVcPrimaryValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.55 | hwHarmonicIaPrimaryValue | Harmonic IA(primary value) | 谐波IA（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicIaPrimaryValue of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.56 | hwHarmonicIbPrimaryValue | Harmonic IB(primary value) | 谐波IB（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicIbPrimaryValue of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.57 | hwHarmonicIcPrimaryValue | Harmonic IC(primary value) | 谐波IC（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicIcPrimaryValue of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.58 | hwHarmonicPaPrimaryValue | Harmonic PA(primary value) | 谐波PA（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicPaPrimaryValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.59 | hwHarmonicPbPrimaryValue | Harmonic PB(primary value) | 谐波PB（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicPbPrimaryValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.60 | hwHarmonicPcPrimaryValue | Harmonic PC(primary value) | 谐波PC（一次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicPcPrimaryValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.61 | hwVaTotalHarmonicDistortionRateThd_Va | VA total harmonic distortion rate THD_VA | VA总谐波畸变率THD_VA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | VaTotalHarmonicDistortionRateThd_Va of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.62 | hwVbTotalHarmonicDistortionRateThd_Vb | VB total harmonic distortion rate THD_VB | VB总谐波畸变率THD_VB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | VbTotalHarmonicDistortionRateThd_Vb of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.63 | hwVcTotalHarmonicDistortionRateThd_Vc | VC total harmonic distortion rate THD_VC | VC总谐波畸变率THD_VC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | VcTotalHarmonicDistortionRateThd_Vc of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.64 | hwAverageTotalHarmonicDistortionRateOfPhaseVoltageThd_V | Average total harmonic distortion rate of phase voltage THD_V | 相电压平均总谐波畸变率THD_V | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AverageTotalHarmonicDistortionRateOfPhaseVoltageThd_V of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.65 | hwIaTotalHarmonicDistortionRateThd_Ia | IA total harmonic distortion rate THD_IA | IA总谐波畸变率THD_IA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | IaTotalHarmonicDistortionRateThd_Ia of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.66 | hwIbTotalHarmonicDistortionRateThd_Ia | IB total harmonic distortion rate THD_IA | IB总谐波畸变率THD_IB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | IbTotalHarmonicDistortionRateThd_Ia of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.67 | hwIcTotalHarmonicDistortionRateThd_Ia | IC total harmonic distortion rate THD_IA | IC总谐波畸变率THD_IC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | IcTotalHarmonicDistortionRateThd_Ia of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.68 | hwPhaseCurrentAverageTotalHarmonicDistortionRateThd_I | Phase current average total harmonic distortion rate THD_I | 相电流平均总谐波畸变率THD_I | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | PhaseCurrentAverageTotalHarmonicDistortionRateThd_I of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.69 | hwFundamentalWaveVaQuadraticValue | Fundamental wave VA(quadratic value) | 基波VA或VAB（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveVaQuadraticValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.70 | hwFundamentalWaveVbQuadraticValue | Fundamental wave VB(quadratic value) | 基波VB或VBC（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveVbQuadraticValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.71 | hwFundamentalWaveVcQuadraticValue | Fundamental wave VC(quadratic value) | 基波VC或VCA（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveVcQuadraticValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.72 | hwFundamentalWaveIaQuadraticValue | Fundamental wave IA(quadratic value) | 基波IA（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveIaQuadraticValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.73 | hwFundamentalWaveIbQuadraticValue | Fundamental wave IB(quadratic value) | 基波IB（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveIbQuadraticValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.74 | hwFundamentalWaveIcQuadraticValue | Fundamental wave IC(quadratic value) | 基波IC（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FundamentalWaveIcQuadraticValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.75 | hwFundamentalWavePaQuadraticValue | Fundamental wave PA(quadratic value) | 基波PA（二次值） | 0-Read_Only | 只读 | / | / | FundamentalWavePaQuadraticValue of the device running table for the GGIC400P3. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.76 | hwFundamentalWavePbQuadraticValue | Fundamental wave PB(quadratic value) | 基波PB（二次值） | 0-Read_Only | 只读 | / | / | FundamentalWavePbQuadraticValue of the device running table for the GGIC400P3. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.77 | hwFundamentalWavePcQuadraticValue | Fundamental wave PC(quadratic value) | 基波PC（二次值） | 0-Read_Only | 只读 | / | / | FundamentalWavePcQuadraticValue of the device running table for the GGIC400P3. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.78 | hwFundamentalWaveActiveElectricalEnergyQuadraticValue | Fundamental wave active electrical energy(quadratic value) | 基波有功电能（二次值） | 0-Read_Only | 只读 | / | / | FundamentalWaveActiveElectricalEnergyQuadraticValue of the device running table for the GGIC400P3. SigUnitInfo:Wh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.79 | hwHarmonicVaQuadraticValue | Harmonic VA(quadratic value) | 谐波VA或VAB（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicVaQuadraticValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.80 | hwHarmonicVbQuadraticValue | Harmonic VB(quadratic value) | 谐波VB或VBC（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicVbQuadraticValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.81 | hwHarmonicVcQuadraticValue | Harmonic VC(quadratic value) | 谐波VC或VCA（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicVcQuadraticValue of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.82 | hwHarmonicIaQuadraticValue | Harmonic IA(quadratic value) | 谐波IA（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicIaQuadraticValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.83 | hwHarmonicIbQuadraticValue | Harmonic IB(quadratic value) | 谐波IB（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicIbQuadraticValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.84 | hwHarmonicIcQuadraticValue | Harmonic IC(quadratic value) | 谐波IC（二次值） | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | HarmonicIcQuadraticValue of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.85 | hwHarmonicPaQuadraticValue | Harmonic PA(quadratic value) | 谐波PA（二次值） | 0-Read_Only | 只读 | / | / | HarmonicPaQuadraticValue of the device running table for the GGIC400P3. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.86 | hwHarmonicPbQuadraticValue | Harmonic PB(quadratic value) | 谐波PB（二次值） | 0-Read_Only | 只读 | / | / | HarmonicPbQuadraticValue of the device running table for the GGIC400P3. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.87 | hwHarmonicPcQuadraticValue | Harmonic PC(quadratic value) | 谐波PC（二次值） | 0-Read_Only | 只读 | / | / | HarmonicPcQuadraticValue of the device running table for the GGIC400P3. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.88 | hwVaOrVabTotalHarmonicDistortionRateThd_Va | VA or VAB total harmonic distortion rate THD_VA | VA或VAB总谐波畸变率 THD_VA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | VaOrVabTotalHarmonicDistortionRateThd_Va of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.89 | hwVbOrVbcTotalHarmonicDistortionRateThd_Vb | VB or VBC total harmonic distortion rate THD_VB | VB或VBC总谐波畸变率 THD_VB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | VbOrVbcTotalHarmonicDistortionRateThd_Vb of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.90 | hwVcOrVcaTotalHarmonicDistortionRateThd_Vc | VC or VCA total harmonic distortion rate THD_VC | VC或VCA总谐波畸变率 THD_VC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | VcOrVcaTotalHarmonicDistortionRateThd_Vc of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.91 | hwAverageTotalHarmonicDistortionRateOfPhaseLineVoltageThd_V | Average total harmonic distortion rate of phase line voltage THD_V | 相/线电压平均总谐波畸变率 THD_V | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AverageTotalHarmonicDistortionRateOfPhaseLineVoltageThd_V of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.92 | hwFeederCircuitIaTotalHarmonicDistortionRateThd_Ia | Feeder circuit IA total harmonic distortion rate THD_IA | IA总谐波畸变率THD_IA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuitIaTotalHarmonicDistortionRateThd_Ia of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.93 | hwFeederCircuitIbTotalHarmonicDistortionRateThd_Ib | Feeder circuit IB total harmonic distortion rate THD_IB | IB总谐波畸变率THD_IB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuitIbTotalHarmonicDistortionRateThd_Ib of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.94 | hwFeederCircuitIcTotalHarmonicDistortionRateThd_Ic | Feeder circuit IC total harmonic distortion rate THD_IC | IC总谐波畸变率THD_IC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuitIcTotalHarmonicDistortionRateThd_Ic of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.95 | hwFeederCircuitPhaseCurrentAverageTotalHarmonicDistortionRateThd_I | Feeder circuit phase current average total harmonic distortion rate THD_I | 相电流平均总谐波畸变率 THD_I | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuitPhaseCurrentAverageTotalHarmonicDistortionRateThd_I of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.96 | hwQf1MainSwitchStatus | QF1 main switch status | QF1主开关状态 | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Qf1MainSwitchStatus of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.97 | hwIsolationTransformerStatus | Isolation transformer status | 隔离变压器状态 | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | IsolationTransformerStatus of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.98 | hwSpdStatus | SPD status | SPD防雷器状态 | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | SpdStatus of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.99 | hwQf2MainSwitchStatus | QF2 main switch status | QF2主开关状态 | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Qf2MainSwitchStatus of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.100 | hwBranch1Qf1SwitchOf | Branch 1 QF1 switch OF | 支路1QF1开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf1SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.101 | hwBranch1Qf2SwitchOf | Branch 1 QF2 switch OF | 支路1QF2开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf2SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.102 | hwBranch1Qf3SwitchOf | Branch 1 QF3 switch OF | 支路1QF3开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf3SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.103 | hwBranch1Qf4SwitchOf | Branch 1 QF4 switch OF | 支路1QF4开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf4SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.104 | hwBranch1Qf5SwitchOf | Branch 1 QF5 switch OF | 支路1QF5开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf5SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.105 | hwBranch1Qf6SwitchOf | Branch 1 QF6 switch OF | 支路1QF6开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf6SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.106 | hwBranch1Qf7SwitchOf | Branch 1 QF7 switch OF | 支路1QF7开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf7SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.107 | hwBranch1Qf8SwitchOf | Branch 1 QF8 switch OF | 支路1QF8开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf8SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.108 | hwBranch1Qf9SwitchOf | Branch 1 QF9 switch OF | 支路1QF9开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf9SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.109 | hwBranch1Qf10SwitchOf | Branch 1 QF10 switch OF | 支路1QF10开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf10SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.110 | hwBranch1Qf11SwitchOf | Branch 1 QF11 switch OF | 支路1QF11开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf11SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.111 | hwBranch1Qf12SwitchOf | Branch 1 QF12 switch OF | 支路1QF12开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf12SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.112 | hwBranch1Qf13SwitchOf | Branch 1 QF13 switch OF | 支路1QF13开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf13SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.113 | hwBranch1Qf14SwitchOf | Branch 1 QF14 switch OF | 支路1QF14开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf14SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.114 | hwBranch1Qf15SwitchOf | Branch 1 QF15 switch OF | 支路1QF15开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf15SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.115 | hwBranch1Qf16SwitchOf | Branch 1 QF16 switch OF | 支路1QF16开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf16SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.116 | hwBranch1Qf17SwitchOf | Branch 1 QF17 switch OF | 支路1QF17开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf17SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.117 | hwBranch1Qf18SwitchOf | Branch 1 QF18 switch OF | 支路1QF18开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf18SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.118 | hwBranch1Qf19SwitchOf | Branch 1 QF19 switch OF | 支路1QF19开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf19SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.119 | hwBranch1Qf20SwitchOf | Branch 1 QF20 switch OF | 支路1QF20开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf20SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.120 | hwBranch1Qf21SwitchOf | Branch 1 QF21 switch OF | 支路1QF21开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf21SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.121 | hwBranch1Qf22SwitchOf | Branch 1 QF22 switch OF | 支路1QF22开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf22SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.122 | hwBranch1Qf23SwitchOf | Branch 1 QF23 switch OF | 支路1QF23开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf23SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.123 | hwBranch1Qf24SwitchOf | Branch 1 QF24 switch OF | 支路1QF24开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf24SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.124 | hwBranch1Qf25SwitchOf | Branch 1 QF25 switch OF | 支路1QF25开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf25SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.125 | hwBranch1Qf26SwitchOf | Branch 1 QF26 switch OF | 支路1QF26开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf26SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.126 | hwBranch1Qf27SwitchOf | Branch 1 QF27 switch OF | 支路1QF27开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf27SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.127 | hwBranch1Qf28SwitchOf | Branch 1 QF28 switch OF | 支路1QF28开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf28SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.128 | hwBranch1Qf29SwitchOf | Branch 1 QF29 switch OF | 支路1QF29开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf29SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.129 | hwBranch1Qf30SwitchOf | Branch 1 QF30 switch OF | 支路1QF30开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf30SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.130 | hwBranch1Qf31SwitchOf | Branch 1 QF31 switch OF | 支路1QF31开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf31SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.131 | hwBranch1Qf32SwitchOf | Branch 1 QF32 switch OF | 支路1QF32开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf32SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.132 | hwBranch1Qf33SwitchOf | Branch 1 QF33 switch OF | 支路1QF33开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf33SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.133 | hwBranch1Qf34SwitchOf | Branch 1 QF34 switch OF | 支路1QF34开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf34SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.134 | hwBranch1Qf35SwitchOf | Branch 1 QF35 switch OF | 支路1QF35开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf35SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.135 | hwBranch1Qf36SwitchOf | Branch 1 QF36 switch OF | 支路1QF36开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf36SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.136 | hwBranch1Qf37SwitchOf | Branch 1 QF37 switch OF | 支路1QF37开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf37SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.137 | hwBranch1Qf38SwitchOf | Branch 1 QF38 switch OF | 支路1QF38开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf38SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.138 | hwBranch1Qf39SwitchOf | Branch 1 QF39 switch OF | 支路1QF39开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf39SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.139 | hwBranch1Qf40SwitchOf | Branch 1 QF40 switch OF | 支路1QF40开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf40SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.140 | hwBranch1Qf41SwitchOf | Branch 1 QF41 switch OF | 支路1QF41开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf41SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.141 | hwBranch1Qf42SwitchOf | Branch 1 QF42 switch OF | 支路1QF42开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf42SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.142 | hwBranch1Qf43SwitchOf | Branch 1 QF43 switch OF | 支路1QF43开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf43SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.143 | hwBranch1Qf44SwitchOf | Branch 1 QF44 switch OF | 支路1QF44开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf44SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.144 | hwBranch1Qf45SwitchOf | Branch 1 QF45 switch OF | 支路1QF45开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf45SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.145 | hwBranch1Qf46SwitchOf | Branch 1 QF46 switch OF | 支路1QF46开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf46SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.146 | hwBranch1Qf47SwitchOf | Branch 1 QF47 switch OF | 支路1QF47开关OF | 0-Read_Only | 只读 | off(0),on(1),unknown(255) | [0=分闸][1=合闸] | Branch1Qf47SwitchOf of the device running table for the GGIC400P3. Value0 indicate Off Value1 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.147 | hwFeederCircuit1VoltageU | Feeder circuit 1 voltage U | 第1回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit1VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.148 | hwFeederCircuit1CurrentI | Feeder circuit 1 current I | 第1回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit1CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.149 | hwFeederCircuit1ActivePowerP | Feeder circuit 1 active power P | 第1回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit1ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.150 | hwFeederCircuit1ActiveEnergy | Feeder circuit 1 active energy | 第1回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit1ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.151 | hwFeederCircuit2VoltageU | Feeder circuit 2 voltage U | 第2回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit2VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.152 | hwFeederCircuit2CurrentI | Feeder circuit 2 current I | 第2回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit2CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.153 | hwFeederCircuit2ActivePowerP | Feeder circuit 2 active power P | 第2回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit2ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.154 | hwFeederCircuit2ActiveEnergy | Feeder circuit 2 active energy | 第2回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit2ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.155 | hwFeederCircuit3VoltageU | Feeder circuit 3 voltage U | 第3回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit3VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.156 | hwFeederCircuit3CurrentI | Feeder circuit 3 current I | 第3回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit3CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.157 | hwFeederCircuit3ActivePowerP | Feeder circuit 3 active power P | 第3回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit3ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.158 | hwFeederCircuit3ActiveEnergy | Feeder circuit 3 active energy | 第3回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit3ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.159 | hwFeederCircuit4VoltageU | Feeder circuit 4 voltage U | 第4回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit4VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.160 | hwFeederCircuit4CurrentI | Feeder circuit 4 current I | 第4回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit4CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.161 | hwFeederCircuit4ActivePowerP | Feeder circuit 4 active power P | 第4回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit4ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.162 | hwFeederCircuit4ActiveEnergy | Feeder circuit 4 active energy | 第4回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit4ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.163 | hwFeederCircuit5VoltageU | Feeder circuit 5 voltage U | 第5回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit5VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.164 | hwFeederCircuit5CurrentI | Feeder circuit 5 current I | 第5回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit5CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.165 | hwFeederCircuit5ActivePowerP | Feeder circuit 5 active power P | 第5回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit5ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.166 | hwFeederCircuit5ActiveEnergy | Feeder circuit 5 active energy | 第5回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit5ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.167 | hwFeederCircuit6VoltageU | Feeder circuit 6 voltage U | 第6回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit6VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.168 | hwFeederCircuit6CurrentI | Feeder circuit 6 current I | 第6回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit6CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.169 | hwFeederCircuit6ActivePowerP | Feeder circuit 6 active power P | 第6回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit6ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.170 | hwFeederCircuit6ActiveEnergy | Feeder circuit 6 active energy | 第6回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit6ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.171 | hwFeederCircuit7VoltageU | Feeder circuit 7 voltage U | 第7回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit7VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.172 | hwFeederCircuit7CurrentI | Feeder circuit 7 current I | 第7回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit7CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.173 | hwFeederCircuit7ActivePowerP | Feeder circuit 7 active power P | 第7回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit7ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.174 | hwFeederCircuit7ActiveEnergy | Feeder circuit 7 active energy | 第7回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit7ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.175 | hwFeederCircuit8VoltageU | Feeder circuit 8 voltage U | 第8回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit8VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.176 | hwFeederCircuit8CurrentI | Feeder circuit 8 current I | 第8回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit8CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.177 | hwFeederCircuit8ActivePowerP | Feeder circuit 8 active power P | 第8回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit8ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.178 | hwFeederCircuit8ActiveEnergy | Feeder circuit 8 active energy | 第8回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit8ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.179 | hwFeederCircuit9VoltageU | Feeder circuit 9 voltage U | 第9回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit9VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.180 | hwFeederCircuit9CurrentI | Feeder circuit 9 current I | 第9回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit9CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.181 | hwFeederCircuit9ActivePowerP | Feeder circuit 9 active power P | 第9回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit9ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.182 | hwFeederCircuit9ActiveEnergy | Feeder circuit 9 active energy | 第9回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit9ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.183 | hwFeederCircuit10VoltageU | Feeder circuit 10 voltage U | 第10回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit10VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.184 | hwFeederCircuit10CurrentI | Feeder circuit 10 current I | 第10回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit10CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.185 | hwFeederCircuit10ActivePowerP | Feeder circuit 10 active power P | 第10回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit10ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.186 | hwFeederCircuit10ActiveEnergy | Feeder circuit 10 active energy | 第10回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit10ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.187 | hwFeederCircuit11VoltageU | Feeder circuit 11 voltage U | 第11回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit11VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.188 | hwFeederCircuit11CurrentI | Feeder circuit 11 current I | 第11回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit11CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.189 | hwFeederCircuit11ActivePowerP | Feeder circuit 11 active power P | 第11回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit11ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.190 | hwFeederCircuit11ActiveEnergy | Feeder circuit 11 active energy | 第11回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit11ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.191 | hwFeederCircuit12VoltageU | Feeder circuit 12 voltage U | 第12回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit12VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.192 | hwFeederCircuit12CurrentI | Feeder circuit 12 current I | 第12回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit12CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.193 | hwFeederCircuit12ActivePowerP | Feeder circuit 12 active power P | 第12回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit12ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.194 | hwFeederCircuit12ActiveEnergy | Feeder circuit 12 active energy | 第12回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit12ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.195 | hwFeederCircuit13VoltageU | Feeder circuit 13 voltage U | 第13回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit13VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.196 | hwFeederCircuit13CurrentI | Feeder circuit 13 current I | 第13回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit13CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.197 | hwFeederCircuit13ActivePowerP | Feeder circuit 13 active power P | 第13回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit13ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.198 | hwFeederCircuit13ActiveEnergy | Feeder circuit 13 active energy | 第13回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit13ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.199 | hwFeederCircuit14VoltageU | Feeder circuit 14 voltage U | 第14回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit14VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.200 | hwFeederCircuit14CurrentI | Feeder circuit 14 current I | 第14回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit14CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.201 | hwFeederCircuit14ActivePowerP | Feeder circuit 14 active power P | 第14回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit14ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.202 | hwFeederCircuit14ActiveEnergy | Feeder circuit 14 active energy | 第14回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit14ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.203 | hwFeederCircuit15VoltageU | Feeder circuit 15 voltage U | 第15回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit15VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.204 | hwFeederCircuit15CurrentI | Feeder circuit 15 current I | 第15回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit15CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.205 | hwFeederCircuit15ActivePowerP | Feeder circuit 15 active power P | 第15回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit15ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.206 | hwFeederCircuit15ActiveEnergy | Feeder circuit 15 active energy | 第15回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit15ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.207 | hwFeederCircuit16VoltageU | Feeder circuit 16 voltage U | 第16回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit16VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.208 | hwFeederCircuit16CurrentI | Feeder circuit 16 current I | 第16回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit16CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.209 | hwFeederCircuit16ActivePowerP | Feeder circuit 16 active power P | 第16回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit16ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.210 | hwFeederCircuit16ActiveEnergy | Feeder circuit 16 active energy | 第16回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit16ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.211 | hwFeederCircuit17VoltageU | Feeder circuit 17 voltage U | 第17回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit17VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.212 | hwFeederCircuit17CurrentI | Feeder circuit 17 current I | 第17回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit17CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.213 | hwFeederCircuit17ActivePowerP | Feeder circuit 17 active power P | 第17回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit17ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.214 | hwFeederCircuit17ActiveEnergy | Feeder circuit 17 active energy | 第17回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit17ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.215 | hwFeederCircuit18VoltageU | Feeder circuit 18 voltage U | 第18回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit18VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.216 | hwFeederCircuit18CurrentI | Feeder circuit 18 current I | 第18回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit18CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.217 | hwFeederCircuit18ActivePowerP | Feeder circuit 18 active power P | 第18回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit18ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.218 | hwFeederCircuit18ActiveEnergy | Feeder circuit 18 active energy | 第18回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit18ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.219 | hwFeederCircuit19VoltageU | Feeder circuit 19 voltage U | 第19回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit19VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.220 | hwFeederCircuit19CurrentI | Feeder circuit 19 current I | 第19回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit19CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.221 | hwFeederCircuit19ActivePowerP | Feeder circuit 19 active power P | 第19回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit19ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.222 | hwFeederCircuit19ActiveEnergy | Feeder circuit 19 active energy | 第19回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit19ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.223 | hwFeederCircuit20VoltageU | Feeder circuit 20 voltage U | 第20回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit20VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.224 | hwFeederCircuit20CurrentI | Feeder circuit 20 current I | 第20回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit20CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.225 | hwFeederCircuit20ActivePowerP | Feeder circuit 20 active power P | 第20回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit20ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.226 | hwFeederCircuit20ActiveEnergy | Feeder circuit 20 active energy | 第20回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit20ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.227 | hwFeederCircuit21VoltageU | Feeder circuit 21 voltage U | 第21回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit21VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.228 | hwFeederCircuit21CurrentI | Feeder circuit 21 current I | 第21回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit21CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.229 | hwFeederCircuit21ActivePowerP | Feeder circuit 21 active power P | 第21回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit21ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.230 | hwFeederCircuit21ActiveEnergy | Feeder circuit 21 active energy | 第21回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit21ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.231 | hwFeederCircuit22VoltageU | Feeder circuit 22 voltage U | 第22回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit22VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.232 | hwFeederCircuit22CurrentI | Feeder circuit 22 current I | 第22回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit22CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.233 | hwFeederCircuit22ActivePowerP | Feeder circuit 22 active power P | 第22回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit22ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.234 | hwFeederCircuit22ActiveEnergy | Feeder circuit 22 active energy | 第22回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit22ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.235 | hwFeederCircuit23VoltageU | Feeder circuit 23 voltage U | 第23回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit23VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.236 | hwFeederCircuit23CurrentI | Feeder circuit 23 current I | 第23回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit23CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.237 | hwFeederCircuit23ActivePowerP | Feeder circuit 23 active power P | 第23回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit23ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.238 | hwFeederCircuit23ActiveEnergy | Feeder circuit 23 active energy | 第23回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit23ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.239 | hwFeederCircuit24VoltageU | Feeder circuit 24 voltage U | 第24回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit24VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.240 | hwFeederCircuit24CurrentI | Feeder circuit 24 current I | 第24回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit24CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.241 | hwFeederCircuit24ActivePowerP | Feeder circuit 24 active power P | 第24回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit24ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.242 | hwFeederCircuit24ActiveEnergy | Feeder circuit 24 active energy | 第24回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit24ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.243 | hwFeederCircuit25VoltageU | Feeder circuit 25 voltage U | 第25回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit25VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.244 | hwFeederCircuit25CurrentI | Feeder circuit 25 current I | 第25回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit25CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.245 | hwFeederCircuit25ActivePowerP | Feeder circuit 25 active power P | 第25回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit25ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.246 | hwFeederCircuit25ActiveEnergy | Feeder circuit 25 active energy | 第25回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit25ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.247 | hwFeederCircuit26VoltageU | Feeder circuit 26 voltage U | 第26回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit26VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.248 | hwFeederCircuit26CurrentI | Feeder circuit 26 current I | 第26回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit26CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.249 | hwFeederCircuit26ActivePowerP | Feeder circuit 26 active power P | 第26回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit26ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.250 | hwFeederCircuit26ActiveEnergy | Feeder circuit 26 active energy | 第26回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit26ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.251 | hwFeederCircuit27VoltageU | Feeder circuit 27 voltage U | 第27回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit27VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.252 | hwFeederCircuit27CurrentI | Feeder circuit 27 current I | 第27回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit27CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.253 | hwFeederCircuit27ActivePowerP | Feeder circuit 27 active power P | 第27回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit27ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.254 | hwFeederCircuit27ActiveEnergy | Feeder circuit 27 active energy | 第27回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit27ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.255 | hwFeederCircuit28VoltageU | Feeder circuit 28 voltage U | 第28回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit28VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.256 | hwFeederCircuit28CurrentI | Feeder circuit 28 current I | 第28回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit28CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.257 | hwFeederCircuit28ActivePowerP | Feeder circuit 28 active power P | 第28回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit28ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.258 | hwFeederCircuit28ActiveEnergy | Feeder circuit 28 active energy | 第28回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit28ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.259 | hwFeederCircuit29VoltageU | Feeder circuit 29 voltage U | 第29回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit29VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.260 | hwFeederCircuit29CurrentI | Feeder circuit 29 current I | 第29回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit29CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.261 | hwFeederCircuit29ActivePowerP | Feeder circuit 29 active power P | 第29回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit29ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.262 | hwFeederCircuit29ActiveEnergy | Feeder circuit 29 active energy | 第29回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit29ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.263 | hwFeederCircuit30VoltageU | Feeder circuit 30 voltage U | 第30回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit30VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.264 | hwFeederCircuit30CurrentI | Feeder circuit 30 current I | 第30回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit30CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.265 | hwFeederCircuit30ActivePowerP | Feeder circuit 30 active power P | 第30回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit30ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.266 | hwFeederCircuit30ActiveEnergy | Feeder circuit 30 active energy | 第30回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit30ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.267 | hwFeederCircuit31VoltageU | Feeder circuit 31 voltage U | 第31回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit31VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.268 | hwFeederCircuit31CurrentI | Feeder circuit 31 current I | 第31回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit31CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.269 | hwFeederCircuit31ActivePowerP | Feeder circuit 31 active power P | 第31回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit31ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.270 | hwFeederCircuit31ActiveEnergy | Feeder circuit 31 active energy | 第31回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit31ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.271 | hwFeederCircuit32VoltageU | Feeder circuit 32 voltage U | 第32回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit32VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.272 | hwFeederCircuit32CurrentI | Feeder circuit 32 current I | 第32回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit32CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.273 | hwFeederCircuit32ActivePowerP | Feeder circuit 32 active power P | 第32回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit32ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.274 | hwFeederCircuit32ActiveEnergy | Feeder circuit 32 active energy | 第32回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit32ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.275 | hwFeederCircuit33VoltageU | Feeder circuit 33 voltage U | 第33回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit33VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.276 | hwFeederCircuit33CurrentI | Feeder circuit 33 current I | 第33回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit33CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.277 | hwFeederCircuit33ActivePowerP | Feeder circuit 33 active power P | 第33回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit33ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.278 | hwFeederCircuit33ActiveEnergy | Feeder circuit 33 active energy | 第33回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit33ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.279 | hwFeederCircuit34VoltageU | Feeder circuit 34 voltage U | 第34回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit34VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.280 | hwFeederCircuit34CurrentI | Feeder circuit 34 current I | 第34回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit34CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.281 | hwFeederCircuit34ActivePowerP | Feeder circuit 34 active power P | 第34回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit34ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.282 | hwFeederCircuit34ActiveEnergy | Feeder circuit 34 active energy | 第34回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit34ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.283 | hwFeederCircuit35VoltageU | Feeder circuit 35 voltage U | 第35回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit35VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.284 | hwFeederCircuit35CurrentI | Feeder circuit 35 current I | 第35回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit35CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.285 | hwFeederCircuit35ActivePowerP | Feeder circuit 35 active power P | 第35回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit35ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.286 | hwFeederCircuit35ActiveEnergy | Feeder circuit 35 active energy | 第35回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit35ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.287 | hwFeederCircuit36VoltageU | Feeder circuit 36 voltage U | 第36回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit36VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.288 | hwFeederCircuit36CurrentI | Feeder circuit 36 current I | 第36回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit36CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.289 | hwFeederCircuit36ActivePowerP | Feeder circuit 36 active power P | 第36回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit36ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.290 | hwFeederCircuit36ActiveEnergy | Feeder circuit 36 active energy | 第36回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit36ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.291 | hwFeederCircuit37VoltageU | Feeder circuit 37 voltage U | 第37回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit37VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.292 | hwFeederCircuit37CurrentI | Feeder circuit 37 current I | 第37回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit37CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.293 | hwFeederCircuit37ActivePowerP | Feeder circuit 37 active power P | 第37回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit37ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.294 | hwFeederCircuit37ActiveEnergy | Feeder circuit 37 active energy | 第37回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit37ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.295 | hwFeederCircuit38VoltageU | Feeder circuit 38 voltage U | 第38回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit38VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.296 | hwFeederCircuit38CurrentI | Feeder circuit 38 current I | 第38回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit38CurrentI of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.297 | hwFeederCircuit38ActivePowerP | Feeder circuit 38 active power P | 第38回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit38ActivePowerP of the device running table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.298 | hwFeederCircuit38ActiveEnergy | Feeder circuit 38 active energy | 第38回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit38ActiveEnergy of the device running table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.299 | hwFeederCircuit39VoltageU | Feeder circuit 39 voltage U | 第39回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit39VoltageU of the device running table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.1.1.300 | hwGGIC400P3Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of GGIC400P3.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2 | hwGGIC400P3RunningAndConfig2Table | / | / |  |  | / | / | The running and config table of GGIC400P3
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.1 | hwGGIC400P3RunningAndConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the GGIC400P3
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.2 | hwFeederCircuit39CurrentI | Feeder circuit 39 current I | 第39回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit39CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.3 | hwFeederCircuit39ActivePowerP | Feeder circuit 39 active power P | 第39回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit39ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.4 | hwFeederCircuit39ActiveEnergy | Feeder circuit 39 active energy | 第39回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit39ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.5 | hwFeederCircuit40VoltageU | Feeder circuit 40 voltage U | 第40回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit40VoltageU of the device running and config table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.6 | hwFeederCircuit40CurrentI | Feeder circuit 40 current I | 第40回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit40CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.7 | hwFeederCircuit40ActivePowerP | Feeder circuit 40 active power P | 第40回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit40ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.8 | hwFeederCircuit40ActiveEnergy | Feeder circuit 40 active energy | 第40回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit40ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.9 | hwFeederCircuit41VoltageU | Feeder circuit 41 voltage U | 第41回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit41VoltageU of the device running and config table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.10 | hwFeederCircuit41CurrentI | Feeder circuit 41 current I | 第41回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit41CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.11 | hwFeederCircuit41ActivePowerP | Feeder circuit 41 active power P | 第41回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit41ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.12 | hwFeederCircuit41ActiveEnergy | Feeder circuit 41 active energy | 第41回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit41ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.13 | hwFeederCircuit42VoltageU | Feeder circuit 42 voltage U | 第42回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit42VoltageU of the device running and config table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.14 | hwFeederCircuit42CurrentI | Feeder circuit 42 current I | 第42回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit42CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.15 | hwFeederCircuit42ActivePowerP | Feeder circuit 42 active power P | 第42回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit42ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.16 | hwFeederCircuit42ActiveEnergy | Feeder circuit 42 active energy | 第42回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit42ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.17 | hwFeederCircuit43VoltageU | Feeder circuit 43 voltage U | 第43回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit43VoltageU of the device running and config table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.18 | hwFeederCircuit43CurrentI | Feeder circuit 43 current I | 第43回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit43CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.19 | hwFeederCircuit43ActivePowerP | Feeder circuit 43 active power P | 第43回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit43ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.20 | hwFeederCircuit43ActiveEnergy | Feeder circuit 43 active energy | 第43回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit43ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.21 | hwFeederCircuit44VoltageU | Feeder circuit 44 voltage U | 第44回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit44VoltageU of the device running and config table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.22 | hwFeederCircuit44CurrentI | Feeder circuit 44 current I | 第44回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit44CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.23 | hwFeederCircuit44ActivePowerP | Feeder circuit 44 active power P | 第44回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit44ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.24 | hwFeederCircuit44ActiveEnergy | Feeder circuit 44 active energy | 第44回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit44ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.25 | hwFeederCircuit45VoltageU | Feeder circuit 45 voltage U | 第45回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit45VoltageU of the device running and config table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.26 | hwFeederCircuit45CurrentI | Feeder circuit 45 current I | 第45回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit45CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.27 | hwFeederCircuit45ActivePowerP | Feeder circuit 45 active power P | 第45回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit45ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.28 | hwFeederCircuit45ActiveEnergy | Feeder circuit 45 active energy | 第45回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit45ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.29 | hwFeederCircuit46VoltageU | Feeder circuit 46 voltage U | 第46回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit46VoltageU of the device running and config table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.30 | hwFeederCircuit46CurrentI | Feeder circuit 46 current I | 第46回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit46CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.31 | hwFeederCircuit46ActivePowerP | Feeder circuit 46 active power P | 第46回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit46ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.32 | hwFeederCircuit46ActiveEnergy | Feeder circuit 46 active energy | 第46回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit46ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.33 | hwFeederCircuit47VoltageU | Feeder circuit 47 voltage U | 第47回路数据电压U | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit47VoltageU of the device running and config table for the GGIC400P3. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.34 | hwFeederCircuit47CurrentI | Feeder circuit 47 current I | 第47回路数据电流I | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit47CurrentI of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.35 | hwFeederCircuit47ActivePowerP | Feeder circuit 47 active power P | 第47回路数据有功功率P | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit47ActivePowerP of the device running and config table for the GGIC400P3. Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.36 | hwFeederCircuit47ActiveEnergy | Feeder circuit 47 active energy | 第47回路数据有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit47ActiveEnergy of the device running and config table for the GGIC400P3. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.19.2.1.37 | hwGGIC400P3Running2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of GGIC400P3.

## AYTSC60
AYTSC60
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.8.4 | hwAYTSC60 | hwAYTSC60 | hwAYTSC60 | / |  | / | / | AYTSC60 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1 | hwAYTSC60RunningAndConfig1Table | / | / |  |  | / | / | The running and config table of AYTSC60
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.1 | hwAYTSC60RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the AYTSC60
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.2 | hwModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.3 | hwPortNo | Port No | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.4 | hwCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.5 | hwPositionIInputState | POSITION I INPUT state | POSITION I 输入端子状态 | 0-Read_Only | 只读 | inputOn(0),inputOff(1),unknown(255) | [0=输入断开]/[1=输入闭合] | PositionIInputState of the device running and config table for the AYTSC60. Value0 indicate input on Value1 indicate input off
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.6 | hwPositionIiInputState | POSITION II INPUT state | POSITION II 输入端子状态 | 0-Read_Only | 只读 | inputOn(0),inputOff(1),unknown(255) | [0=输入断开]/[1=输入闭合] | PositionIiInputState of the device running and config table for the AYTSC60. Value0 indicate input on Value1 indicate input off
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.7 | hwPosition0InputState | POSITION 0 INPUT state | POSITION 0 输入端子状态 | 0-Read_Only | 只读 | inputOn(0),inputOff(1),unknown(255) | [0=输入断开]/[1=输入闭合] | Position0InputState of the device running and config table for the AYTSC60. Value0 indicate input on Value1 indicate input off
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.8 | hwPosition0SwitchOutput | POSITION 0 switch output | 开关0位置反馈信号 | 0-Read_Only | 只读 | noAction(0),action(1),unknown(255) | [0=不动作]/[1=动作] | Position0SwitchOutput of the device running and config table for the AYTSC60. Value0 indicate no action Value1 indicate action
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.9 | hwPositionISwitchOutput | POSITION I switch output | 开关 I 位置反馈信号 | 0-Read_Only | 只读 | noAction(0),action(1),unknown(255) | [0=不动作]/[1=动作] | PositionISwitchOutput of the device running and config table for the AYTSC60. Value0 indicate no action Value1 indicate action
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.10 | hwPositionIiSwitchOutput | POSITION II switch output | 开关 II 位置反馈信号 | 0-Read_Only | 只读 | noAction(0),action(1),unknown(255) | [0=不动作]/[1=动作] | PositionIiSwitchOutput of the device running and config table for the AYTSC60. Value0 indicate no action Value1 indicate action
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.11 | hwIPositionState | I Position state | 开关1状态 | 0-Read_Only | 只读 | switchOff(0),switchOn(1),unknown(255) | [0=开关断开]/[1=开关闭合] | IPositionState of the device running and config table for the AYTSC60. Value0 indicate switch off Value1 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.12 | hwIiPositionState | II Position state | 开关2状态 | 0-Read_Only | 只读 | switchOff(0),switchOn(1),unknown(255) | [0=开关断开]/[1=开关闭合] | IiPositionState of the device running and config table for the AYTSC60. Value0 indicate switch off Value1 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.13 | hw0PositionState | 0 position state | 双分位置状态 | 0-Read_Only | 只读 | switchOff(0),switchOn(1),unknown(255) | [0=开关断开]/[1=开关闭合] | 0PositionState of the device running and config table for the AYTSC60. Value0 indicate switch off Value1 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.14 | hwSource1PowerStatus | Source 1 power status | 1路电源状态 | 0-Read_Only | 只读 | normal(0),missingPhase(1),overVoltage(2),underVoltage(4),unbalancedPhase(8),overFrequency(16),underFrequency(32),phaseNLoss(64),unknown(255) | [0=正常]/[1=缺相]/[2=过压]/[4=欠压]/[8=相不平衡]/[16=过频]/[32=欠频]/[64=断N相] | Source1PowerStatus of the device running and config table for the AYTSC60. Value0 indicate Normal Value1 indicate Missing phase Value2 indicate Over-voltage Value4 indicate Under-voltage Value8 indicate unbalanced phase Value16 indicate Over-frequency Value32 indicate Under-frequency Value64 indicate Phase N loss
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.15 | hwSource2PowerStatus | Source 2 power status | 2路电源状态 | 0-Read_Only | 只读 | normal(0),missingPhase(1),overVoltage(2),underVoltage(4),unbalancedPhase(8),overFrequency(16),underFrequency(32),phaseNLoss(64),unknown(255) | [0=正常]/[1=缺相]/[2=过压]/[4=欠压]/[8=相不平衡]/[16=过频]/[32=欠频]/[64=断N相] | Source2PowerStatus of the device running and config table for the AYTSC60. Value0 indicate Normal Value1 indicate Missing phase Value2 indicate Over-voltage Value4 indicate Under-voltage Value8 indicate unbalanced phase Value16 indicate Over-frequency Value32 indicate Under-frequency Value64 indicate Phase N loss
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.16 | hwSystemTimeSecond | System time-second | 控制器时间-秒 | 0-Read_Only | 只读 | 0..59 | 0..59 | SystemTimeSecond of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.17 | hwSystemTimeMinute | System time-minute | 控制器时间-分 | 0-Read_Only | 只读 | 0..59 | 0..59 | SystemTimeMinute of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.18 | hwSystemTimeHour | System time-hour | 控制器时间-时 | 0-Read_Only | 只读 | 0..23 | 0..23 | SystemTimeHour of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.19 | hwSystemTimeDay | System time-day | 控制器时间-日 | 0-Read_Only | 只读 | 1..31 | 1..31 | SystemTimeDay of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.20 | hwSystemTimeMonth | System time-month | 控制器时间-月 | 0-Read_Only | 只读 | 1..12 | 1..12 | SystemTimeMonth of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.21 | hwSystemTimeYear | System time-year | 控制器时间-年 | 0-Read_Only | 只读 | 2010..2200 | 2010..2200 | SystemTimeYear of the device running and config table for the AYTSC60.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.22 | hwAmbientTemperature | Ambient Temperature | 控制器测量温度值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AmbientTemperature of the device running and config table for the AYTSC60. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.23 | hwSource1APhaseVoltage | Source 1 A phase voltage | 1 路 A 相相电压 | 0-Read_Only | 只读 | / | / | Source1APhaseVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.24 | hwSource1BPhaseVoltage | Source 1 B phase voltage | 1 路 B 相相电压 | 0-Read_Only | 只读 | / | / | Source1BPhaseVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.25 | hwSource1CPhaseVoltage | Source 1 C phase voltage | 1 路 C 相相电压 | 0-Read_Only | 只读 | / | / | Source1CPhaseVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.26 | hwSource1AvgPhaseVoltage | Source 1 avg phase voltage | 1 路平均相电压 | 0-Read_Only | 只读 | / | / | Source1AvgPhaseVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.27 | hwSource1LineVoltageUab | Source 1 line voltage UAB | 1 路线电压UAB | 0-Read_Only | 只读 | / | / | Source1LineVoltageUab of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.28 | hwSource1LineVoltageUbc | Source 1 line voltage UBC | 1 路线电压UBC | 0-Read_Only | 只读 | / | / | Source1LineVoltageUbc of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.29 | hwSource1LineVoltageUca | Source 1 line voltage UCA | 1 路线电压UCA | 0-Read_Only | 只读 | / | / | Source1LineVoltageUca of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.30 | hwSource1AvgLineVoltage | Source 1 avg line voltage | 1 路平均线电压 | 0-Read_Only | 只读 | / | / | Source1AvgLineVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.31 | hwSource1APhaseAngle | Source 1 A phase angle | 1 路 A 相相位角 | 0-Read_Only | 只读 | / | / | Source1APhaseAngle of the device running and config table for the AYTSC60. SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.32 | hwSource1BPhaseAngle | Source 1 B phase angle | 1 路 B 相相位角 | 0-Read_Only | 只读 | / | / | Source1BPhaseAngle of the device running and config table for the AYTSC60. SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.33 | hwSource1CPhaseAngle | Source 1 C phase angle | 1 路 C 相相位角 | 0-Read_Only | 只读 | / | / | Source1CPhaseAngle of the device running and config table for the AYTSC60. SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.34 | hwSource1PhaseSequence | Source 1 phase sequence | 1 路相序 | 0-Read_Only | 只读 | forward(0),reverse(1),unknown(255) | [0=正向]/[1=逆向] | Source1PhaseSequence of the device running and config table for the AYTSC60. Value0 indicate Forward Value1 indicate reverse
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.35 | hwSource1Frequency | Source 1 frequency | 1 路频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Source1Frequency of the device running and config table for the AYTSC60. Multiple:10. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.36 | hwSource2APhaseVoltage | Source 2 A phase voltage | 2 路 A 相相电压 | 0-Read_Only | 只读 | / | / | Source2APhaseVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.37 | hwSource2BPhaseVoltage | Source 2 B phase voltage | 2 路 B 相相电压 | 0-Read_Only | 只读 | / | / | Source2BPhaseVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.38 | hwSource2CPhaseVoltage | Source 2 C phase voltage | 2 路 C 相相电压 | 0-Read_Only | 只读 | / | / | Source2CPhaseVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.39 | hwSource2AvgPhaseVoltage | Source 2 avg phase voltage | 2 路平均相电压 | 0-Read_Only | 只读 | / | / | Source2AvgPhaseVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.40 | hwSource2LineVoltageUab | Source 2 line voltage UAB | 2 路线电压UAB | 0-Read_Only | 只读 | / | / | Source2LineVoltageUab of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.41 | hwSource2LineVoltageUbc | Source 2 line voltage UBC | 2 路线电压UBC | 0-Read_Only | 只读 | / | / | Source2LineVoltageUbc of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.42 | hwSource2LineVoltageUca | Source 2 line voltage UCA | 2 路线电压UCA | 0-Read_Only | 只读 | / | / | Source2LineVoltageUca of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.43 | hwSource2AvgLineVoltage | Source 2 avg line voltage | 2 路平均线电压 | 0-Read_Only | 只读 | / | / | Source2AvgLineVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.44 | hwSource2APhaseAngle | Source 2 A phase angle | 2 路 A 相相位角 | 0-Read_Only | 只读 | / | / | Source2APhaseAngle of the device running and config table for the AYTSC60. SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.45 | hwSource2BPhaseAngle | Source 2 B phase angle | 2 路 B 相相位角 | 0-Read_Only | 只读 | / | / | Source2BPhaseAngle of the device running and config table for the AYTSC60. SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.46 | hwSource2CPhaseAngle | Source 2 C phase angle | 2 路 C 相相位角 | 0-Read_Only | 只读 | / | / | Source2CPhaseAngle of the device running and config table for the AYTSC60. SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.47 | hwSource2PhaseSequence | Source 2 phase sequence | 2 路相序 | 0-Read_Only | 只读 | forward(0),reverse(1),unknown(255) | [0=正向]/[1=逆向] | Source2PhaseSequence of the device running and config table for the AYTSC60. Value0 indicate Forward Value1 indicate reverse
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.48 | hwSource2Frequency | Source 2 frequency | 2 路频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Source2Frequency of the device running and config table for the AYTSC60. Multiple:10. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.49 | hwAtscOperatingMode | ATSC operating mode | 控制器工作模式 | 0-Read_Only | 只读 | prog(1),manu(2),auto(3),test(4),unknown(255) | [1=编程]/[2=手动]/[3=自动]/[4=测试] | AtscOperatingMode of the device running and config table for the AYTSC60. Value1 indicate PROG Value2 indicate MANU Value3 indicate AUTO Value4 indicate TEST
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.50 | hwNpminalNetworkVoltage | NPMinal NetWork voltage | 额定电压 | 0-Read_Only | 只读 | 50..400 | 50..400 | NpminalNetworkVoltage of the device running and config table for the AYTSC60. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.51 | hwSystemRatedFrequency | System rated frequency | 额定频率 | 0-Read_Only | 只读 | fiftyHz(1),sixtyHz(2),unknown(255) | [1=50Hz]/[2=60Hz] | SystemRatedFrequency of the device running and config table for the AYTSC60. Value1 indicate Fifty Hz Value2 indicate Sixty Hz
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.52 | hwNetwork | NetWork | 电网类型 | 0-Read_Only | 只读 | threePhasesFourWires(1),threePhaseThreeWires(2),twoPhasesThreeWires(3),onePhaseTwoWires(4),unknown(255) | [1=三相四线]/[2=三相三线]/[3=两相三线]/[4=单相两线] | Network of the device running and config table for the AYTSC60. Value1 indicate Three phases four wires Value2 indicate Three phase three wires Value3 indicate Two phases three wires Value4 indicate One phase two wires
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.53 | hwPowerSupplyType | Power supply type | 电源转换类型 | 0-Read_Only | 只读 | mainsMains(1),mainsGenset(2),gensetMains(3),unknown(255) | [1=市电市电]/[2=市电发电]/[3=发电市电] | PowerSupplyType of the device running and config table for the AYTSC60. Value1 indicate Mains-Mains Value2 indicate Mains -Genset Value3 indicate Genset-Mains
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.54 | hwPriorNet | Prior Net | 电源优先级 | 0-Read_Only | 只读 | line1AsNormal(1),line2AsNormal(2),unknown(255) | [1=1路主电]/[2=2路主电] | PriorNet of the device running and config table for the AYTSC60. Value1 indicate line1 as normal Value2 indicate line2 as normal
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.55 | hwReturnToMainPowerSupply | Return to main power supply | 主电源返回方式 | 0-Read_Only | 只读 | automaticTransferNotAutomaticRecover(1),automaticTransferAutomaticRecover(2),mutuallyReserved(3),unknown(255) | [1=自投不自复]/[2=自投自复]/[3=互为备用] | ReturnToMainPowerSupply of the device running and config table for the AYTSC60. Value1 indicate Automatic transfer not automatic recover Value2 indicate Automatic transfer automatic recover Value3 indicate mutually reserved
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.56 | hwOffPosition | Off position | 分段位设置 | 0-Read_Only | 只读 | twoOffPosition(1),oneOffPosition(2),noOffPosition(3),unknown(255) | [1=两分段位]/[2=1分段位]/[3=无分段位] | OffPosition of the device running and config table for the AYTSC60. Value1 indicate two off position Value2 indicate one off position Value3 indicate no off position
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.57 | hwPhaseSequenceDetection | Phase sequence detection | 相序检测 | 0-Read_Only | 只读 | l1L2L3(1),l3L2L1(2),off(3),unknown(255) | [1=L1L2L3]/[2=L3L2L1]/[3=关闭] | PhaseSequenceDetection of the device running and config table for the AYTSC60. Value1 indicate L1L2L3 Value2 indicate L3L2L1 Value3 indicate off
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.58 | hwAuxConnector | Aux Connector | 位置反馈触电 | 0-Read_Only | 只读 | threeFeedbacks(1),twoFeedbacks(2),zeroFeedback(3),unknown(255) | [1=3输入]/[2=2输入]/[3=0输入] | AuxConnector of the device running and config table for the AYTSC60. Value1 indicate three feedbacks Value2 indicate two feedbacks Value3 indicate zero feedback
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.59 | hwS1UnderVoltageThreshold | S1 Under-voltage threshold | 一路欠压门限 | 0-Read_Only | 只读 | 70..100 | 70..100 | S1UnderVoltageThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.60 | hwS1UnderVoltageReturnThreshold | S1 Under-voltage return threshold | 一路欠压返回门限 | 0-Read_Only | 只读 | 70..100 | 70..100 | S1UnderVoltageReturnThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.61 | hwS1OverVoltageThreshold | S1 Over-voltage threshold | 一路过压门限 | 0-Read_Only | 只读 | 100..130 | 100..130 | S1OverVoltageThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.62 | hwS1OverVoltageReturnThreshold | S1 Over-voltage return threshold | 一路过压返回门限 | 0-Read_Only | 只读 | 100..130 | 100..130 | S1OverVoltageReturnThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.63 | hwS1OverFrequencyThreshold | S1 Over-frequency threshold | 一路欠频门限 | 0-Read_Only | 只读 | 80..100 | 80..100 | S1OverFrequencyThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.64 | hwS1UnderFrequencyThreshold | S1 Under-frequency threshold | 一路过频门限 | 0-Read_Only | 只读 | 100..120 | 100..120 | S1UnderFrequencyThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.65 | hwS1UnderFrequencyReturnThreshold | S1 Under-frequency return threshold | 一路欠频返回门限 | 0-Read_Only | 只读 | 80..100 | 80..100 | S1UnderFrequencyReturnThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.66 | hwS1OverFrequencyReturnThreshold | S1 Over-frequency return threshold | 一路过频返回门限 | 0-Read_Only | 只读 | 100..120 | 100..120 | S1OverFrequencyReturnThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.67 | hwS2UnderVoltageThreshold | S2 Under-voltage threshold | 二路欠压门限 | 0-Read_Only | 只读 | 70..100 | 70..100 | S2UnderVoltageThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.68 | hwS2UnderVoltageReturnThreshold | S2 Under-voltage return threshold | 二路欠压返回门限 | 0-Read_Only | 只读 | 70..100 | 70..100 | S2UnderVoltageReturnThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.69 | hwS2OverVoltageThreshold | S2 Over-voltage threshold | 二路过压门限 | 0-Read_Only | 只读 | 100..130 | 100..130 | S2OverVoltageThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.70 | hwS2OverVoltageReturnThreshold | S2 Over-voltage return threshold | 二路过压返回门限 | 0-Read_Only | 只读 | 100..130 | 100..130 | S2OverVoltageReturnThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.71 | hwS2UnderFrequencyThreshold | S2 Under-frequency threshold | 二路欠频门限 | 0-Read_Only | 只读 | 80..100 | 80..100 | S2UnderFrequencyThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.72 | hwS2OverFrequencyThreshold | S2 Over-frequency threshold | 二路过频门限 | 0-Read_Only | 只读 | 100..120 | 100..120 | S2OverFrequencyThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.73 | hwS2UnderFrequencyReturnThreshold | S2 Under-frequency return threshold | 二路欠频返回门限 | 0-Read_Only | 只读 | 80..100 | 80..100 | S2UnderFrequencyReturnThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.74 | hwS2OverFrequencyReturnThreshold | S2 Over-frequency return threshold | 二路过频返回门限 | 0-Read_Only | 只读 | 100..120 | 100..120 | S2OverFrequencyReturnThreshold of the device running and config table for the AYTSC60. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.75 | hwPositionSwitch | Position switch | 开关位置转换 | 0-Read_Only | 只读 | positionIi(2),position0(4),positionI(5),unknown(255) | [2=切换到 II 位]/[4=切换到 0 位]/[5=切换到 I 位] | PositionSwitch of the device running and config table for the AYTSC60. Value2 indicate position II Value4 indicate position 0 Value5 indicate position I
1.3.6.1.4.1.2011.6.178.1.1.8.4.1.1.76 | hwAYTSC60Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of AYTSC60.

## DEMSVD2
DEMSVD2
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.17 | hwDEMSVD2 | hwDEMSVD2 | hwDEMSVD2 | / | / | / | / | DEMSVD2 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1 | hwDEMSVD2Running1Table | / | / | / | / | / | / | The running table of DEMSVD2
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.1 | hwDEMSVD2Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DEMSVD2
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.2 | hwModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | ModbusAddress of the device running table for the DEMSVD2.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.3 | hwPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PortNo of the device running table for the DEMSVD2.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.4 | hwCommonModule | Common module | 通用模块 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | CommonModule of the device running table for the DEMSVD2.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.5 | hwInletCircuit1Voltage | Inlet circuit 1-voltage | 第一路进线回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | InletCircuit1Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.6 | hwInletCircuit1Current | Inlet circuit 1-current | 第一路进线回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.7 | hwInletCircuit1Power | Inlet circuit 1-power | 第一路进线回路-功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1Power of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.8 | hwInletCircuit1CombinedEnergy | Inlet circuit 1-combined energy | 第一路进线回路-组合电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1CombinedEnergy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.9 | hwInletCircuit1PositiveEnergy | Inlet circuit 1-positive energy | 第一路进线回路-正向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1PositiveEnergy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.10 | hwInletCircuit1NegativeEnergy | Inlet circuit 1-negative energy | 第一路进线回路-反向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1NegativeEnergy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.11 | hwInletCircuit1PowerRequired | Inlet circuit 1-power required | 第一路进线回路-功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1PowerRequired of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.12 | hwInletCircuit1CurrentRequired | Inlet circuit 1-current required | 第一路进线回路-电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1CurrentRequired of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.13 | hwInletCircuit1VoltagePercentage | Inlet circuit 1-voltage percentage | 第一路进线回路-电压百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | InletCircuit1VoltagePercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.14 | hwInletCircuit1CurrentPercentage | Inlet circuit 1-current percentage | 第一路进线回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | InletCircuit1CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.15 | hwInletCircuit1PositiveInsulationResistance | Inlet circuit 1-positive insulation resistance | 第一路进线回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | InletCircuit1PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.16 | hwInletCircuit1NegativeInsulationResistance | Inlet circuit 1-negative insulation resistance | 第一路进线回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | InletCircuit1NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.17 | hwInletCircuit1Temperature1 | Inlet circuit 1-temperature 1 | 第一路进线回路-温度1 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | InletCircuit1Temperature1 of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.18 | hwInletCircuit1Temperature2 | Inlet circuit 1-temperature 2 | 第一路进线回路-温度2 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | InletCircuit1Temperature2 of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.19 | hwInletCircuit1Humidity | Inlet circuit 1-humidity | 第一路进线回路-湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1Humidity of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.20 | hwInletCircuit1PositiveBusVoltage | Inlet circuit 1-positive bus voltage | 第一路进线回路-母线正向电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1PositiveBusVoltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.21 | hwInletCircuit1NegativeBusVoltage | Inlet circuit 1-negative bus voltage | 第一路进线回路-母线负向电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit1NegativeBusVoltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.22 | hwInletCircuit2Voltage | Inlet circuit 2-voltage | 第二路进线回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | InletCircuit2Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.23 | hwInletCircuit2Current | Inlet circuit 2-current | 第二路进线回路-电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.24 | hwInletCircuit2Power | Inlet circuit 2-power | 第二路进线回路-功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2Power of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.25 | hwInletCircuit2CombinedEnergy | Inlet circuit 2-combined energy | 第二路进线回路-组合电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2CombinedEnergy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.26 | hwInletCircuit2PositiveEnergy | Inlet circuit 2-positive energy | 第二路进线回路-正向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2PositiveEnergy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.27 | hwInletCircuit2NegativeEnergy | Inlet circuit 2-negative energy | 第二路进线回路-反向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2NegativeEnergy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.28 | hwInletCircuit2PowerRequired | Inlet circuit 2-power required | 第二路进线回路-功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2PowerRequired of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.29 | hwInletCircuit2CurrentRequired | Inlet circuit 2-current required | 第二路进线回路-电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2CurrentRequired of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.30 | hwInletCircuit2VoltagePercentage | Inlet circuit 2-voltage percentage | 第二路进线回路-电压百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | InletCircuit2VoltagePercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.31 | hwInletCircuit2CurrentPercentage | Inlet circuit 2-current percentage | 第二路进线回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | InletCircuit2CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.32 | hwInletCircuit2PositiveInsulationResistance | Inlet circuit 2-positive insulation resistance | 第二路进线回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | InletCircuit2PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.33 | hwInletCircuit2NegativeInsulationResistance | Inlet circuit 2-negative insulation resistance | 第二路进线回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | InletCircuit2NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.34 | hwInletCircuit2Temperature1 | Inlet circuit 2-temperature 1 | 第二路进线回路-温度1 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | InletCircuit2Temperature1 of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.35 | hwInletCircuit2Temperature2 | Inlet circuit 2-temperature 2 | 第二路进线回路-温度2 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | InletCircuit2Temperature2 of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:degrees celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.36 | hwInletCircuit2Humidity | Inlet circuit 2-humidity | 第二路进线回路-湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2Humidity of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.37 | hwInletCircuit2PositiveBusVoltage | Inlet circuit 2-positive bus voltage | 第二路进线回路-母线正向电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2PositiveBusVoltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.38 | hwInletCircuit2NegativeBusVoltage | Inlet circuit 2-negative bus voltage | 第二路进线回路-母线负向电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | InletCircuit2NegativeBusVoltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.39 | hwMainCircuit1PrimarySwitchOf | Main circuit 1-primary switch OF | 第一主路主开关OF | 0-Read_Only | 只读 | unknown(255) | unknown(255) | MainCircuit1PrimarySwitchOf of the device running table for the DEMSVD2.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.40 | hwMainCircuit1PrimarySwitchSd | Main circuit 1-primary switch SD | 第一主路主开关SD | 0-Read_Only | 只读 | unknown(255) | unknown(255) | MainCircuit1PrimarySwitchSd of the device running table for the DEMSVD2.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.41 | hwMainCircuit1SpdSwitch | Main circuit 1-SPD switch | 第一主路防雷器开关 | 0-Read_Only | 只读 | unknown(255) | unknown(255) | MainCircuit1SpdSwitch of the device running table for the DEMSVD2.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.42 | hwMainCircuit1SpdSwitchStatus | Main circuit 1-SPD switch status | 第一主路防雷状态 | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit1SpdSwitchStatus of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.43 | hwMainCircuit1StandbySwitchStatus | Main circuit 1-standby switch status | 第一主路备用开关状态 | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit1StandbySwitchStatus of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.44 | hwMainCircuit1StandbySwitchSd | Main circuit 1-standby switch SD | 第一主路备用开关SD | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit1StandbySwitchSd of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.45 | hwMainCircuit2PrimarySwitchOf | Main circuit 2-primary switch OF | 第二主路主开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit2PrimarySwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.46 | hwMainCircuit2PrimarySwitchSd | Main circuit 2-primary switch SD | 第二主路主开关SD | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit2PrimarySwitchSd of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.47 | hwMainCircuit2SpdSwitch | Main circuit 2-SPD switch | 第二主路防雷器开关 | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit2SpdSwitch of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.48 | hwMainCircuit2SpdSwitchStatus | Main circuit 2-SPD switch status | 第二主路防雷状态 | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit2SpdSwitchStatus of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.49 | hwMainCircuit2StandbySwitchStatus | Main circuit 2-standby switch status | 第二主路备用开关状态 | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit2StandbySwitchStatus of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.50 | hwMainCircuit2StandbySwitchSd | Main circuit 2-standby switch SD | 第二主路备用开关SD | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | MainCircuit2StandbySwitchSd of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.51 | hwDo1Status | DO1 status | DO1状态 | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | Do1Status of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.52 | hwDo2Status | DO2 status | DO2状态 | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | Do2Status of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.53 | hwSystemRuntime | System runtime | 系统运行时间 | 0-Read_Only | 只读 |  |  | SystemRuntime of the device running table for the DEMSVD2. SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.54 | hwBranch1SwitchOf | Branch 1 switch OF | 支路1开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[1=合闸] | Branch1SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.55 | hwBranch2SwitchOf | Branch 2 switch OF | 支路2开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[2=合闸] | Branch2SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.56 | hwBranch3SwitchOf | Branch 3 switch OF | 支路3开关OF | 0-Read_Only | 只读 | unknown(255) | [0=分闸]/[3=合闸] | Branch3SwitchOf of the device running table for the DEMSVD2.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.57 | hwBranch4SwitchOf | Branch 4 switch OF | 支路4开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[4=合闸] | Branch4SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.58 | hwBranch5SwitchOf | Branch 5 switch OF | 支路5开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[5=合闸] | Branch5SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.59 | hwBranch6SwitchOf | Branch 6 switch OF | 支路6开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[6=合闸] | Branch6SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.60 | hwBranch7SwitchOf | Branch 7 switch OF | 支路7开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[7=合闸] | Branch7SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.61 | hwBranch8SwitchOf | Branch 8 switch OF | 支路8开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[8=合闸] | Branch8SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.62 | hwBranch9SwitchOf | Branch 9 switch OF | 支路9开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[9=合闸] | Branch9SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.63 | hwBranch10SwitchOf | Branch 10 switch OF | 支路10开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[10=合闸] | Branch10SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.64 | hwBranch11SwitchOf | Branch 11 switch OF | 支路11开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[11=合闸] | Branch11SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.65 | hwBranch12SwitchOf | Branch 12 switch OF | 支路12开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[12=合闸] | Branch12SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.66 | hwBranch13SwitchOf | Branch 13 switch OF | 支路13开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[13=合闸] | Branch13SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.67 | hwBranch14SwitchOf | Branch 14 switch OF | 支路14开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[14=合闸] | Branch14SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.68 | hwBranch15SwitchOf | Branch 15 switch OF | 支路15开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[15=合闸] | Branch15SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.69 | hwBranch16SwitchOf | Branch 16 switch OF | 支路16开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[16=合闸] | Branch16SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.70 | hwBranch17SwitchOf | Branch 17 switch OF | 支路17开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[17=合闸] | Branch17SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.71 | hwBranch18SwitchOf | Branch 18 switch OF | 支路18开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[18=合闸] | Branch18SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.72 | hwBranch19SwitchOf | Branch 19 switch OF | 支路19开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[19=合闸] | Branch19SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.73 | hwBranch20SwitchOf | Branch 20 switch OF | 支路20开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[20=合闸] | Branch20SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.74 | hwBranch21SwitchOf | Branch 21 switch OF | 支路21开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[21=合闸] | Branch21SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.75 | hwBranch22SwitchOf | Branch 22 switch OF | 支路22开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[22=合闸] | Branch22SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.76 | hwBranch23SwitchOf | Branch 23 switch OF | 支路23开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[23=合闸] | Branch23SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.77 | hwBranch24SwitchOf | Branch 24 switch OF | 支路24开关OF | 0-Read_Only | 只读 | off(0), on(1), unknown(255) | [0=分闸]/[24=合闸] | Branch24SwitchOf of the device running table for the DEMSVD2. Value1 indicate Off Value2 indicate On
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.78 | hwFeederCircuit1Voltage | Feeder circuit 1-voltage | 第1路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit1Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.79 | hwFeederCircuit1Current | Feeder circuit 1-current | 第1路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit1Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.80 | hwFeederCircuit1CurrentPercentage | Feeder circuit 1-current percentage | 第1路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit1CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.81 | hwFeederCircuit1Power | Feeder circuit 1-power | 第1路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit1Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.82 | hwFeederCircuit1Energy | Feeder circuit 1-energy | 第1路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit1Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.83 | hwFeederCircuit1PositiveInsulationResistance | Feeder circuit 1-positive insulation resistance | 第1路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit1PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.84 | hwFeederCircuit1NegativeInsulationResistance | Feeder circuit 1-negative insulation resistance | 第1路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit1NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.85 | hwFeederCircuit2Voltage | Feeder circuit 2-voltage | 第2路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit2Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.86 | hwFeederCircuit2Current | Feeder circuit 2-current | 第2路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit2Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.87 | hwFeederCircuit2CurrentPercentage | Feeder circuit 2-current percentage | 第2路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit2CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.88 | hwFeederCircuit2Power | Feeder circuit 2-power | 第2路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit2Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.89 | hwFeederCircuit2Energy | Feeder circuit 2-energy | 第2路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit2Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.90 | hwFeederCircuit2PositiveInsulationResistance | Feeder circuit 2-positive insulation resistance | 第2路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit2PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.91 | hwFeederCircuit2NegativeInsulationResistance | Feeder circuit 2-negative insulation resistance | 第2路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit2NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.92 | hwFeederCircuit3Voltage | Feeder circuit 3-voltage | 第3路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit3Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.93 | hwFeederCircuit3Current | Feeder circuit 3-current | 第3路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit3Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.94 | hwFeederCircuit3CurrentPercentage | Feeder circuit 3-current percentage | 第3路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit3CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.95 | hwFeederCircuit3Power | Feeder circuit 3-power | 第3路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit3Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.96 | hwFeederCircuit3Energy | Feeder circuit 3-energy | 第3路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit3Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.97 | hwFeederCircuit3PositiveInsulationResistance | Feeder circuit 3-positive insulation resistance | 第3路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit3PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.98 | hwFeederCircuit3NegativeInsulationResistance | Feeder circuit 3-negative insulation resistance | 第3路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit3NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.99 | hwFeederCircuit4Voltage | Feeder circuit 4-voltage | 第4路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit4Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.100 | hwFeederCircuit4Current | Feeder circuit 4-current | 第4路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit4Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.101 | hwFeederCircuit4CurrentPercentage | Feeder circuit 4-current percentage | 第4路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit4CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.102 | hwFeederCircuit4Power | Feeder circuit 4-power | 第4路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit4Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.103 | hwFeederCircuit4Energy | Feeder circuit 4-energy | 第4路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit4Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.104 | hwFeederCircuit4PositiveInsulationResistance | Feeder circuit 4-positive insulation resistance | 第4路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit4PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.105 | hwFeederCircuit4NegativeInsulationResistance | Feeder circuit 4-negative insulation resistance | 第4路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit4NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.106 | hwFeederCircuit5Voltage | Feeder circuit 5-voltage | 第5路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit5Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.107 | hwFeederCircuit5Current | Feeder circuit 5-current | 第5路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit5Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.108 | hwFeederCircuit5CurrentPercentage | Feeder circuit 5-current percentage | 第5路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit5CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.109 | hwFeederCircuit5Power | Feeder circuit 5-power | 第5路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit5Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.110 | hwFeederCircuit5Energy | Feeder circuit 5-energy | 第5路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit5Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.111 | hwFeederCircuit5PositiveInsulationResistance | Feeder circuit 5-positive insulation resistance | 第5路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit5PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.112 | hwFeederCircuit5NegativeInsulationResistance | Feeder circuit 5-negative insulation resistance | 第5路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit5NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.113 | hwFeederCircuit6Voltage | Feeder circuit 6-voltage | 第6路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit6Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.114 | hwFeederCircuit6Current | Feeder circuit 6-current | 第6路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit6Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.115 | hwFeederCircuit6CurrentPercentage | Feeder circuit 6-current percentage | 第6路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit6CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.116 | hwFeederCircuit6Power | Feeder circuit 6-power | 第6路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit6Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.117 | hwFeederCircuit6Energy | Feeder circuit 6-energy | 第6路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit6Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.118 | hwFeederCircuit6PositiveInsulationResistance | Feeder circuit 6-positive insulation resistance | 第6路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit6PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.119 | hwFeederCircuit6NegativeInsulationResistance | Feeder circuit 6-negative insulation resistance | 第6路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit6NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.120 | hwFeederCircuit7Voltage | Feeder circuit 7-voltage | 第7路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit7Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.121 | hwFeederCircuit7Current | Feeder circuit 7-current | 第7路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit7Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.122 | hwFeederCircuit7CurrentPercentage | Feeder circuit 7-current percentage | 第7路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit7CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.123 | hwFeederCircuit7Power | Feeder circuit 7-power | 第7路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit7Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.124 | hwFeederCircuit7Energy | Feeder circuit 7-energy | 第7路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit7Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.125 | hwFeederCircuit7PositiveInsulationResistance | Feeder circuit 7-positive insulation resistance | 第7路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit7PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.126 | hwFeederCircuit7NegativeInsulationResistance | Feeder circuit 7-negative insulation resistance | 第7路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit7NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.127 | hwFeederCircuit8Voltage | Feeder circuit 8-voltage | 第8路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit8Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.128 | hwFeederCircuit8Current | Feeder circuit 8-current | 第8路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit8Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.129 | hwFeederCircuit8CurrentPercentage | Feeder circuit 8-current percentage | 第8路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit8CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.130 | hwFeederCircuit8Power | Feeder circuit 8-power | 第8路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit8Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.131 | hwFeederCircuit8Energy | Feeder circuit 8-energy | 第8路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit8Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.132 | hwFeederCircuit8PositiveInsulationResistance | Feeder circuit 8-positive insulation resistance | 第8路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit8PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.133 | hwFeederCircuit8NegativeInsulationResistance | Feeder circuit 8-negative insulation resistance | 第8路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit8NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.134 | hwFeederCircuit9Voltage | Feeder circuit 9-voltage | 第9路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit9Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.135 | hwFeederCircuit9Current | Feeder circuit 9-current | 第9路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit9Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.136 | hwFeederCircuit9CurrentPercentage | Feeder circuit 9-current percentage | 第9路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit9CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.137 | hwFeederCircuit9Power | Feeder circuit 9-power | 第9路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit9Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.138 | hwFeederCircuit9Energy | Feeder circuit 9-energy | 第9路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit9Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.139 | hwFeederCircuit9PositiveInsulationResistance | Feeder circuit 9-positive insulation resistance | 第9路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit9PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.140 | hwFeederCircuit9NegativeInsulationResistance | Feeder circuit 9-negative insulation resistance | 第9路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit9NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.141 | hwFeederCircuit10Voltage | Feeder circuit 10-voltage | 第10路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit10Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.142 | hwFeederCircuit10Current | Feeder circuit 10-current | 第10路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit10Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.143 | hwFeederCircuit10CurrentPercentage | Feeder circuit 10-current percentage | 第10路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit10CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.144 | hwFeederCircuit10Power | Feeder circuit 10-power | 第10路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit10Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.145 | hwFeederCircuit10Energy | Feeder circuit 10-energy | 第10路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit10Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.146 | hwFeederCircuit10PositiveInsulationResistance | Feeder circuit 10-positive insulation resistance | 第10路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit10PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.147 | hwFeederCircuit10NegativeInsulationResistance | Feeder circuit 10-negative insulation resistance | 第10路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit10NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.148 | hwFeederCircuit11Voltage | Feeder circuit 11-voltage | 第11路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit11Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.149 | hwFeederCircuit11Current | Feeder circuit 11-current | 第11路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit11Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.150 | hwFeederCircuit11CurrentPercentage | Feeder circuit 11-current percentage | 第11路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit11CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.151 | hwFeederCircuit11Power | Feeder circuit 11-power | 第11路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit11Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.152 | hwFeederCircuit11Energy | Feeder circuit 11-energy | 第11路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit11Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.153 | hwFeederCircuit11PositiveInsulationResistance | Feeder circuit 11-positive insulation resistance | 第11路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit11PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.154 | hwFeederCircuit11NegativeInsulationResistance | Feeder circuit 11-negative insulation resistance | 第11路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit11NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.155 | hwFeederCircuit12Voltage | Feeder circuit 12-voltage | 第12路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit12Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.156 | hwFeederCircuit12Current | Feeder circuit 12-current | 第12路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit12Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.157 | hwFeederCircuit12CurrentPercentage | Feeder circuit 12-current percentage | 第12路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit12CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.158 | hwFeederCircuit12Power | Feeder circuit 12-power | 第12路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit12Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.159 | hwFeederCircuit12Energy | Feeder circuit 12-energy | 第12路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit12Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.160 | hwFeederCircuit12PositiveInsulationResistance | Feeder circuit 12-positive insulation resistance | 第12路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit12PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.161 | hwFeederCircuit12NegativeInsulationResistance | Feeder circuit 12-negative insulation resistance | 第12路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit12NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.162 | hwFeederCircuit13Voltage | Feeder circuit 13-voltage | 第13路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit13Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.163 | hwFeederCircuit13Current | Feeder circuit 13-current | 第13路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit13Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.164 | hwFeederCircuit13CurrentPercentage | Feeder circuit 13-current percentage | 第13路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit13CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.165 | hwFeederCircuit13Power | Feeder circuit 13-power | 第13路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit13Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.166 | hwFeederCircuit13Energy | Feeder circuit 13-energy | 第13路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit13Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.167 | hwFeederCircuit13PositiveInsulationResistance | Feeder circuit 13-positive insulation resistance | 第13路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit13PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.168 | hwFeederCircuit13NegativeInsulationResistance | Feeder circuit 13-negative insulation resistance | 第13路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit13NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.169 | hwFeederCircuit14Voltage | Feeder circuit 14-voltage | 第14路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit14Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.170 | hwFeederCircuit14Current | Feeder circuit 14-current | 第14路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit14Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.171 | hwFeederCircuit14CurrentPercentage | Feeder circuit 14-current percentage | 第14路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit14CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.172 | hwFeederCircuit14Power | Feeder circuit 14-power | 第14路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit14Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.173 | hwFeederCircuit14Energy | Feeder circuit 14-energy | 第14路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit14Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.174 | hwFeederCircuit14PositiveInsulationResistance | Feeder circuit 14-positive insulation resistance | 第14路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit14PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.175 | hwFeederCircuit14NegativeInsulationResistance | Feeder circuit 14-negative insulation resistance | 第14路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit14NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.176 | hwFeederCircuit15Voltage | Feeder circuit 15-voltage | 第15路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit15Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.177 | hwFeederCircuit15Current | Feeder circuit 15-current | 第15路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit15Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.178 | hwFeederCircuit15CurrentPercentage | Feeder circuit 15-current percentage | 第15路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit15CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.179 | hwFeederCircuit15Power | Feeder circuit 15-power | 第15路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit15Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.180 | hwFeederCircuit15Energy | Feeder circuit 15-energy | 第15路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit15Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.181 | hwFeederCircuit15PositiveInsulationResistance | Feeder circuit 15-positive insulation resistance | 第15路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit15PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.182 | hwFeederCircuit15NegativeInsulationResistance | Feeder circuit 15-negative insulation resistance | 第15路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit15NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.183 | hwFeederCircuit16Voltage | Feeder circuit 16-voltage | 第16路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit16Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.184 | hwFeederCircuit16Current | Feeder circuit 16-current | 第16路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit16Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.185 | hwFeederCircuit16CurrentPercentage | Feeder circuit 16-current percentage | 第16路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit16CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.186 | hwFeederCircuit16Power | Feeder circuit 16-power | 第16路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit16Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.187 | hwFeederCircuit16Energy | Feeder circuit 16-energy | 第16路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit16Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.188 | hwFeederCircuit16PositiveInsulationResistance | Feeder circuit 16-positive insulation resistance | 第16路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit16PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.189 | hwFeederCircuit16NegativeInsulationResistance | Feeder circuit 16-negative insulation resistance | 第16路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit16NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.190 | hwFeederCircuit17Voltage | Feeder circuit 17-voltage | 第17路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit17Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.191 | hwFeederCircuit17Current | Feeder circuit 17-current | 第17路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit17Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.192 | hwFeederCircuit17CurrentPercentage | Feeder circuit 17-current percentage | 第17路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit17CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.193 | hwFeederCircuit17Power | Feeder circuit 17-power | 第17路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit17Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.194 | hwFeederCircuit17Energy | Feeder circuit 17-energy | 第17路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit17Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.195 | hwFeederCircuit17PositiveInsulationResistance | Feeder circuit 17-positive insulation resistance | 第17路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit17PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.196 | hwFeederCircuit17NegativeInsulationResistance | Feeder circuit 17-negative insulation resistance | 第17路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit17NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.197 | hwFeederCircuit18Voltage | Feeder circuit 18-voltage | 第18路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit18Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.198 | hwFeederCircuit18Current | Feeder circuit 18-current | 第18路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit18Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.199 | hwFeederCircuit18CurrentPercentage | Feeder circuit 18-current percentage | 第18路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit18CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.200 | hwFeederCircuit18Power | Feeder circuit 18-power | 第18路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit18Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.201 | hwFeederCircuit18Energy | Feeder circuit 18-energy | 第18路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit18Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.202 | hwFeederCircuit18PositiveInsulationResistance | Feeder circuit 18-positive insulation resistance | 第18路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit18PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.203 | hwFeederCircuit18NegativeInsulationResistance | Feeder circuit 18-negative insulation resistance | 第18路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit18NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.204 | hwFeederCircuit19Voltage | Feeder circuit 19-voltage | 第19路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit19Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.205 | hwFeederCircuit19Current | Feeder circuit 19-current | 第19路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit19Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.206 | hwFeederCircuit19CurrentPercentage | Feeder circuit 19-current percentage | 第19路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit19CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.207 | hwFeederCircuit19Power | Feeder circuit 19-power | 第19路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit19Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.208 | hwFeederCircuit19Energy | Feeder circuit 19-energy | 第19路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit19Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.209 | hwFeederCircuit19PositiveInsulationResistance | Feeder circuit 19-positive insulation resistance | 第19路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit19PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.210 | hwFeederCircuit19NegativeInsulationResistance | Feeder circuit 19-negative insulation resistance | 第19路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit19NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.211 | hwFeederCircuit20Voltage | Feeder circuit 20-voltage | 第20路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit20Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.212 | hwFeederCircuit20Current | Feeder circuit 20-current | 第20路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit20Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.213 | hwFeederCircuit20CurrentPercentage | Feeder circuit 20-current percentage | 第20路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit20CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.214 | hwFeederCircuit20Power | Feeder circuit 20-power | 第20路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit20Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.215 | hwFeederCircuit20Energy | Feeder circuit 20-energy | 第20路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit20Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.216 | hwFeederCircuit20PositiveInsulationResistance | Feeder circuit 20-positive insulation resistance | 第20路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit20PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.217 | hwFeederCircuit20NegativeInsulationResistance | Feeder circuit 20-negative insulation resistance | 第20路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit20NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.218 | hwFeederCircuit21Voltage | Feeder circuit 21-voltage | 第21路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit21Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.219 | hwFeederCircuit21Current | Feeder circuit 21-current | 第21路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit21Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.220 | hwFeederCircuit21CurrentPercentage | Feeder circuit 21-current percentage | 第21路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit21CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.221 | hwFeederCircuit21Power | Feeder circuit 21-power | 第21路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit21Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.222 | hwFeederCircuit21Energy | Feeder circuit 21-energy | 第21路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit21Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.223 | hwFeederCircuit21PositiveInsulationResistance | Feeder circuit 21-positive insulation resistance | 第21路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit21PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.224 | hwFeederCircuit21NegativeInsulationResistance | Feeder circuit 21-negative insulation resistance | 第21路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit21NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.225 | hwFeederCircuit22Voltage | Feeder circuit 22-voltage | 第22路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit22Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.226 | hwFeederCircuit22Current | Feeder circuit 22-current | 第22路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit22Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.227 | hwFeederCircuit22CurrentPercentage | Feeder circuit 22-current percentage | 第22路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit22CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.228 | hwFeederCircuit22Power | Feeder circuit 22-power | 第22路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit22Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.229 | hwFeederCircuit22Energy | Feeder circuit 22-energy | 第22路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit22Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.230 | hwFeederCircuit22PositiveInsulationResistance | Feeder circuit 22-positive insulation resistance | 第22路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit22PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.231 | hwFeederCircuit22NegativeInsulationResistance | Feeder circuit 22-negative insulation resistance | 第22路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit22NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.232 | hwFeederCircuit23Voltage | Feeder circuit 23-voltage | 第23路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit23Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.233 | hwFeederCircuit23Current | Feeder circuit 23-current | 第23路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit23Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.234 | hwFeederCircuit23CurrentPercentage | Feeder circuit 23-current percentage | 第23路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit23CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.235 | hwFeederCircuit23Power | Feeder circuit 23-power | 第23路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit23Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.236 | hwFeederCircuit23Energy | Feeder circuit 23-energy | 第23路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit23Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.237 | hwFeederCircuit23PositiveInsulationResistance | Feeder circuit 23-positive insulation resistance | 第23路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit23PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.238 | hwFeederCircuit23NegativeInsulationResistance | Feeder circuit 23-negative insulation resistance | 第23路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit23NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.239 | hwFeederCircuit24Voltage | Feeder circuit 24-voltage | 第24路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit24Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.240 | hwFeederCircuit24Current | Feeder circuit 24-current | 第24路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit24Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.241 | hwFeederCircuit24CurrentPercentage | Feeder circuit 24-current percentage | 第24路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit24CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.242 | hwFeederCircuit24Power | Feeder circuit 24-power | 第24路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit24Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.243 | hwFeederCircuit24Energy | Feeder circuit 24-energy | 第24路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit24Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.244 | hwFeederCircuit24PositiveInsulationResistance | Feeder circuit 24-positive insulation resistance | 第24路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit24PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.245 | hwFeederCircuit24NegativeInsulationResistance | Feeder circuit 24-negative insulation resistance | 第24路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit24NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.246 | hwFeederCircuit25Voltage | Feeder circuit 25-voltage | 第25路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit25Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.247 | hwFeederCircuit25Current | Feeder circuit 25-current | 第25路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit25Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.248 | hwFeederCircuit25CurrentPercentage | Feeder circuit 25-current percentage | 第25路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit25CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.249 | hwFeederCircuit25Power | Feeder circuit 25-power | 第25路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit25Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.250 | hwFeederCircuit25Energy | Feeder circuit 25-energy | 第25路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit25Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.251 | hwFeederCircuit25PositiveInsulationResistance | Feeder circuit 25-positive insulation resistance | 第25路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit25PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.252 | hwFeederCircuit25NegativeInsulationResistance | Feeder circuit 25-negative insulation resistance | 第25路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit25NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.253 | hwFeederCircuit26Voltage | Feeder circuit 26-voltage | 第26路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit26Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.254 | hwFeederCircuit26Current | Feeder circuit 26-current | 第26路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit26Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.255 | hwFeederCircuit26CurrentPercentage | Feeder circuit 26-current percentage | 第26路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit26CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.256 | hwFeederCircuit26Power | Feeder circuit 26-power | 第26路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit26Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.257 | hwFeederCircuit26Energy | Feeder circuit 26-energy | 第26路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit26Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.258 | hwFeederCircuit26PositiveInsulationResistance | Feeder circuit 26-positive insulation resistance | 第26路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit26PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.259 | hwFeederCircuit26NegativeInsulationResistance | Feeder circuit 26-negative insulation resistance | 第26路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit26NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.260 | hwFeederCircuit27Voltage | Feeder circuit 27-voltage | 第27路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit27Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.261 | hwFeederCircuit27Current | Feeder circuit 27-current | 第27路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit27Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.262 | hwFeederCircuit27CurrentPercentage | Feeder circuit 27-current percentage | 第27路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit27CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.263 | hwFeederCircuit27Power | Feeder circuit 27-power | 第27路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit27Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.264 | hwFeederCircuit27Energy | Feeder circuit 27-energy | 第27路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit27Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.265 | hwFeederCircuit27PositiveInsulationResistance | Feeder circuit 27-positive insulation resistance | 第27路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit27PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.266 | hwFeederCircuit27NegativeInsulationResistance | Feeder circuit 27-negative insulation resistance | 第27路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit27NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.267 | hwFeederCircuit28Voltage | Feeder circuit 28-voltage | 第28路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit28Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.268 | hwFeederCircuit28Current | Feeder circuit 28-current | 第28路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit28Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.269 | hwFeederCircuit28CurrentPercentage | Feeder circuit 28-current percentage | 第28路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit28CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.270 | hwFeederCircuit28Power | Feeder circuit 28-power | 第28路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit28Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.271 | hwFeederCircuit28Energy | Feeder circuit 28-energy | 第28路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit28Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.272 | hwFeederCircuit28PositiveInsulationResistance | Feeder circuit 28-positive insulation resistance | 第28路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit28PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.273 | hwFeederCircuit28NegativeInsulationResistance | Feeder circuit 28-negative insulation resistance | 第28路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit28NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.274 | hwFeederCircuit29Voltage | Feeder circuit 29-voltage | 第29路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit29Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.275 | hwFeederCircuit29Current | Feeder circuit 29-current | 第29路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit29Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.276 | hwFeederCircuit29CurrentPercentage | Feeder circuit 29-current percentage | 第29路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit29CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.277 | hwFeederCircuit29Power | Feeder circuit 29-power | 第29路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit29Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.278 | hwFeederCircuit29Energy | Feeder circuit 29-energy | 第29路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit29Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.279 | hwFeederCircuit29PositiveInsulationResistance | Feeder circuit 29-positive insulation resistance | 第29路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit29PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.280 | hwFeederCircuit29NegativeInsulationResistance | Feeder circuit 29-negative insulation resistance | 第29路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit29NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.281 | hwFeederCircuit30Voltage | Feeder circuit 30-voltage | 第30路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit30Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.282 | hwFeederCircuit30Current | Feeder circuit 30-current | 第30路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit30Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.283 | hwFeederCircuit30CurrentPercentage | Feeder circuit 30-current percentage | 第30路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit30CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.284 | hwFeederCircuit30Power | Feeder circuit 30-power | 第30路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit30Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.285 | hwFeederCircuit30Energy | Feeder circuit 30-energy | 第30路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit30Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.286 | hwFeederCircuit30PositiveInsulationResistance | Feeder circuit 30-positive insulation resistance | 第30路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit30PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.287 | hwFeederCircuit30NegativeInsulationResistance | Feeder circuit 30-negative insulation resistance | 第30路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit30NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.288 | hwFeederCircuit31Voltage | Feeder circuit 31-voltage | 第31路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit31Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.289 | hwFeederCircuit31Current | Feeder circuit 31-current | 第31路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit31Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.290 | hwFeederCircuit31CurrentPercentage | Feeder circuit 31-current percentage | 第31路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit31CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.291 | hwFeederCircuit31Power | Feeder circuit 31-power | 第31路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit31Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.292 | hwFeederCircuit31Energy | Feeder circuit 31-energy | 第31路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit31Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.293 | hwFeederCircuit31PositiveInsulationResistance | Feeder circuit 31-positive insulation resistance | 第31路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit31PositiveInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.294 | hwFeederCircuit31NegativeInsulationResistance | Feeder circuit 31-negative insulation resistance | 第31路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit31NegativeInsulationResistance of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.295 | hwFeederCircuit32Voltage | Feeder circuit 32-voltage | 第32路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit32Voltage of the device running table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.296 | hwFeederCircuit32Current | Feeder circuit 32-current | 第32路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit32Current of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.297 | hwFeederCircuit32CurrentPercentage | Feeder circuit 32-current percentage | 第32路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit32CurrentPercentage of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.298 | hwFeederCircuit32Power | Feeder circuit 32-power | 第32路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit32Power of the device running table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.299 | hwFeederCircuit32Energy | Feeder circuit 32-energy | 第32路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit32Energy of the device running table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.1.1.300 | hwDEMSVD2Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DEMSVD2.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2 | hwDEMSVD2RunningAndConfig2Table | / | / | / | / | / | / | The running and config table of DEMSVD2
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.1 | hwDEMSVD2RunningAndConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the DEMSVD2
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.2 | hwFeederCircuit32PositiveInsulationResistance | Feeder circuit 32-positive insulation resistance | 第32路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit32PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.3 | hwFeederCircuit32NegativeInsulationResistance | Feeder circuit 32-negative insulation resistance | 第32路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit32NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.4 | hwFeederCircuit33Voltage | Feeder circuit 33-voltage | 第33路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit33Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.5 | hwFeederCircuit33Current | Feeder circuit 33-current | 第33路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit33Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.6 | hwFeederCircuit33CurrentPercentage | Feeder circuit 33-current percentage | 第33路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit33CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.7 | hwFeederCircuit33Power | Feeder circuit 33-power | 第33路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit33Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.8 | hwFeederCircuit33Energy | Feeder circuit 33-energy | 第33路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit33Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.9 | hwFeederCircuit33PositiveInsulationResistance | Feeder circuit 33-positive insulation resistance | 第33路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit33PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.10 | hwFeederCircuit33NegativeInsulationResistance | Feeder circuit 33-negative insulation resistance | 第33路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit33NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.11 | hwFeederCircuit34Voltage | Feeder circuit 34-voltage | 第34路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit34Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.12 | hwFeederCircuit34Current | Feeder circuit 34-current | 第34路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit34Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.13 | hwFeederCircuit34CurrentPercentage | Feeder circuit 34-current percentage | 第34路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit34CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.14 | hwFeederCircuit34Power | Feeder circuit 34-power | 第34路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit34Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.15 | hwFeederCircuit34Energy | Feeder circuit 34-energy | 第34路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit34Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.16 | hwFeederCircuit34PositiveInsulationResistance | Feeder circuit 34-positive insulation resistance | 第34路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit34PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.17 | hwFeederCircuit34NegativeInsulationResistance | Feeder circuit 34-negative insulation resistance | 第34路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit34NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.18 | hwFeederCircuit35Voltage | Feeder circuit 35-voltage | 第35路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit35Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.19 | hwFeederCircuit35Current | Feeder circuit 35-current | 第35路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit35Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.20 | hwFeederCircuit35CurrentPercentage | Feeder circuit 35-current percentage | 第35路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit35CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.21 | hwFeederCircuit35Power | Feeder circuit 35-power | 第35路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit35Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.22 | hwFeederCircuit35Energy | Feeder circuit 35-energy | 第35路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit35Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.23 | hwFeederCircuit35PositiveInsulationResistance | Feeder circuit 35-positive insulation resistance | 第35路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit35PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.24 | hwFeederCircuit35NegativeInsulationResistance | Feeder circuit 35-negative insulation resistance | 第35路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit35NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.25 | hwFeederCircuit36Voltage | Feeder circuit 36-voltage | 第36路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit36Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.26 | hwFeederCircuit36Current | Feeder circuit 36-current | 第36路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit36Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.27 | hwFeederCircuit36CurrentPercentage | Feeder circuit 36-current percentage | 第36路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit36CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.28 | hwFeederCircuit36Power | Feeder circuit 36-power | 第36路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit36Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.29 | hwFeederCircuit36Energy | Feeder circuit 36-energy | 第36路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit36Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.30 | hwFeederCircuit36PositiveInsulationResistance | Feeder circuit 36-positive insulation resistance | 第36路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit36PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.31 | hwFeederCircuit36NegativeInsulationResistance | Feeder circuit 36-negative insulation resistance | 第36路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit36NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.32 | hwFeederCircuit37Voltage | Feeder circuit 37-voltage | 第37路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit37Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.33 | hwFeederCircuit37Current | Feeder circuit 37-current | 第37路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit37Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.34 | hwFeederCircuit37CurrentPercentage | Feeder circuit 37-current percentage | 第37路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit37CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.35 | hwFeederCircuit37Power | Feeder circuit 37-power | 第37路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit37Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.36 | hwFeederCircuit37Energy | Feeder circuit 37-energy | 第37路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit37Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.37 | hwFeederCircuit37PositiveInsulationResistance | Feeder circuit 37-positive insulation resistance | 第37路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit37PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.38 | hwFeederCircuit37NegativeInsulationResistance | Feeder circuit 37-negative insulation resistance | 第37路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit37NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.39 | hwFeederCircuit38Voltage | Feeder circuit 38-voltage | 第38路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit38Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.40 | hwFeederCircuit38Current | Feeder circuit 38-current | 第38路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit38Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.41 | hwFeederCircuit38CurrentPercentage | Feeder circuit 38-current percentage | 第38路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit38CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.42 | hwFeederCircuit38Power | Feeder circuit 38-power | 第38路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit38Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.43 | hwFeederCircuit38Energy | Feeder circuit 38-energy | 第38路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit38Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.44 | hwFeederCircuit38PositiveInsulationResistance | Feeder circuit 38-positive insulation resistance | 第38路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit38PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.45 | hwFeederCircuit38NegativeInsulationResistance | Feeder circuit 38-negative insulation resistance | 第38路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit38NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.46 | hwFeederCircuit39Voltage | Feeder circuit 39-voltage | 第39路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit39Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.47 | hwFeederCircuit39Current | Feeder circuit 39-current | 第39路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit39Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.48 | hwFeederCircuit39CurrentPercentage | Feeder circuit 39-current percentage | 第39路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit39CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.49 | hwFeederCircuit39Power | Feeder circuit 39-power | 第39路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit39Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.50 | hwFeederCircuit39Energy | Feeder circuit 39-energy | 第39路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit39Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.51 | hwFeederCircuit39PositiveInsulationResistance | Feeder circuit 39-positive insulation resistance | 第39路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit39PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.52 | hwFeederCircuit39NegativeInsulationResistance | Feeder circuit 39-negative insulation resistance | 第39路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit39NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.53 | hwFeederCircuit40Voltage | Feeder circuit 40-voltage | 第40路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit40Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.54 | hwFeederCircuit40Current | Feeder circuit 40-current | 第40路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit40Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.55 | hwFeederCircuit40CurrentPercentage | Feeder circuit 40-current percentage | 第40路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit40CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.56 | hwFeederCircuit40Power | Feeder circuit 40-power | 第40路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit40Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.57 | hwFeederCircuit40Energy | Feeder circuit 40-energy | 第40路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit40Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.58 | hwFeederCircuit40PositiveInsulationResistance | Feeder circuit 40-positive insulation resistance | 第40路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit40PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.59 | hwFeederCircuit40NegativeInsulationResistance | Feeder circuit 40-negative insulation resistance | 第40路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit40NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.60 | hwFeederCircuit41Voltage | Feeder circuit 41-voltage | 第41路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit41Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.61 | hwFeederCircuit41Current | Feeder circuit 41-current | 第41路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit41Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.62 | hwFeederCircuit41CurrentPercentage | Feeder circuit 41-current percentage | 第41路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit41CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.63 | hwFeederCircuit41Power | Feeder circuit 41-power | 第41路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit41Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.64 | hwFeederCircuit41Energy | Feeder circuit 41-energy | 第41路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit41Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.65 | hwFeederCircuit41PositiveInsulationResistance | Feeder circuit 41-positive insulation resistance | 第41路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit41PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.66 | hwFeederCircuit41NegativeInsulationResistance | Feeder circuit 41-negative insulation resistance | 第41路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit41NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.67 | hwFeederCircuit42Voltage | Feeder circuit 42-voltage | 第42路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit42Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.68 | hwFeederCircuit42Current | Feeder circuit 42-current | 第42路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit42Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.69 | hwFeederCircuit42CurrentPercentage | Feeder circuit 42-current percentage | 第42路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit42CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.70 | hwFeederCircuit42Power | Feeder circuit 42-power | 第42路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit42Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.71 | hwFeederCircuit42Energy | Feeder circuit 42-energy | 第42路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit42Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.72 | hwFeederCircuit42PositiveInsulationResistance | Feeder circuit 42-positive insulation resistance | 第42路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit42PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.73 | hwFeederCircuit42NegativeInsulationResistance | Feeder circuit 42-negative insulation resistance | 第42路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit42NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.74 | hwFeederCircuit43Voltage | Feeder circuit 43-voltage | 第43路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit43Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.75 | hwFeederCircuit43Current | Feeder circuit 43-current | 第43路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit43Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.76 | hwFeederCircuit43CurrentPercentage | Feeder circuit 43-current percentage | 第43路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit43CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.77 | hwFeederCircuit43Power | Feeder circuit 43-power | 第43路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit43Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.78 | hwFeederCircuit43Energy | Feeder circuit 43-energy | 第43路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit43Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.79 | hwFeederCircuit43PositiveInsulationResistance | Feeder circuit 43-positive insulation resistance | 第43路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit43PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.80 | hwFeederCircuit43NegativeInsulationResistance | Feeder circuit 43-negative insulation resistance | 第43路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit43NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.81 | hwFeederCircuit44Voltage | Feeder circuit 44-voltage | 第44路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit44Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.82 | hwFeederCircuit44Current | Feeder circuit 44-current | 第44路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit44Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.83 | hwFeederCircuit44CurrentPercentage | Feeder circuit 44-current percentage | 第44路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit44CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.84 | hwFeederCircuit44Power | Feeder circuit 44-power | 第44路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit44Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.85 | hwFeederCircuit44Energy | Feeder circuit 44-energy | 第44路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit44Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.86 | hwFeederCircuit44PositiveInsulationResistance | Feeder circuit 44-positive insulation resistance | 第44路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit44PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.87 | hwFeederCircuit44NegativeInsulationResistance | Feeder circuit 44-negative insulation resistance | 第44路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit44NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.88 | hwFeederCircuit45Voltage | Feeder circuit 45-voltage | 第45路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit45Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.89 | hwFeederCircuit45Current | Feeder circuit 45-current | 第45路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit45Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.90 | hwFeederCircuit45CurrentPercentage | Feeder circuit 45-current percentage | 第45路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit45CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.91 | hwFeederCircuit45Power | Feeder circuit 45-power | 第45路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit45Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.92 | hwFeederCircuit45Energy | Feeder circuit 45-energy | 第45路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit45Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.93 | hwFeederCircuit45PositiveInsulationResistance | Feeder circuit 45-positive insulation resistance | 第45路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit45PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.94 | hwFeederCircuit45NegativeInsulationResistance | Feeder circuit 45-negative insulation resistance | 第45路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit45NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.95 | hwFeederCircuit46Voltage | Feeder circuit 46-voltage | 第46路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit46Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.96 | hwFeederCircuit46Current | Feeder circuit 46-current | 第46路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit46Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.97 | hwFeederCircuit46CurrentPercentage | Feeder circuit 46-current percentage | 第46路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit46CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.98 | hwFeederCircuit46Power | Feeder circuit 46-power | 第46路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit46Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.99 | hwFeederCircuit46Energy | Feeder circuit 46-energy | 第46路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit46Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.100 | hwFeederCircuit46PositiveInsulationResistance | Feeder circuit 46-positive insulation resistance | 第46路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit46PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.101 | hwFeederCircuit46NegativeInsulationResistance | Feeder circuit 46-negative insulation resistance | 第46路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit46NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.102 | hwFeederCircuit47Voltage | Feeder circuit 47-voltage | 第47路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit47Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.103 | hwFeederCircuit47Current | Feeder circuit 47-current | 第47路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit47Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.104 | hwFeederCircuit47CurrentPercentage | Feeder circuit 47-current percentage | 第47路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit47CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.105 | hwFeederCircuit47Power | Feeder circuit 47-power | 第47路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit47Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.106 | hwFeederCircuit47Energy | Feeder circuit 47-energy | 第47路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit47Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.107 | hwFeederCircuit47PositiveInsulationResistance | Feeder circuit 47-positive insulation resistance | 第47路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit47PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.108 | hwFeederCircuit47NegativeInsulationResistance | Feeder circuit 47-negative insulation resistance | 第47路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit47NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.109 | hwFeederCircuit48Voltage | Feeder circuit 48-voltage | 第48路馈出回路-电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit48Voltage of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.110 | hwFeederCircuit48Current | Feeder circuit 48-current | 第48路馈出回路-电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | FeederCircuit48Current of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.111 | hwFeederCircuit48CurrentPercentage | Feeder circuit 48-current percentage | 第48路馈出回路-电流百分比 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit48CurrentPercentage of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.112 | hwFeederCircuit48Power | Feeder circuit 48-power | 第48路馈出回路-功率 | 0-Read_Only | 只读 |  |  | FeederCircuit48Power of the device running and config table for the DEMSVD2. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.113 | hwFeederCircuit48Energy | Feeder circuit 48-energy | 第48路馈出回路-电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | FeederCircuit48Energy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.114 | hwFeederCircuit48PositiveInsulationResistance | Feeder circuit 48-positive insulation resistance | 第48路馈出回路-正极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit48PositiveInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.115 | hwFeederCircuit48NegativeInsulationResistance | Feeder circuit 48-negative insulation resistance | 第48路馈出回路-负极绝缘电阻 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | FeederCircuit48NegativeInsulationResistance of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kilohm.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.116 | hwItLoadsInBranchACurrentTotalActiveEnergy | IT loads in branch A-current total active energy | 当前A支路IT负载-当前总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchACurrentTotalActiveEnergy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.117 | hwItLoadsInBranchATotalActiveEnergyInCurrentMonth | IT loads in branch A-total active energy in current month | 当前A支路IT负载-本月总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchATotalActiveEnergyInCurrentMonth of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.118 | hwItLoadsInBranchATotalActiveEnergyOfLastMonth | IT loads in branch A-total active energy of last month | 当前A支路IT负载-上1月总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchATotalActiveEnergyOfLastMonth of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.119 | hwItLoadsInBranchATotalActiveEnergyOfLastTwoMonths | IT loads in branch A-total active energy of last two months | 当前A支路IT负载-上2月总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchATotalActiveEnergyOfLastTwoMonths of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.120 | hwItLoadsInBranchATotalActiveEnergyOfLastThreeMonths | IT loads in branch A-total active energy of last three months | 当前A支路IT负载-上3月总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchATotalActiveEnergyOfLastThreeMonths of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.121 | hwItLoadsInBranchBTurrentTotalActiveEnergy | IT loads in branch B-turrent total active energy | 当前B支路IT负载-当前总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchBTurrentTotalActiveEnergy of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.122 | hwItLoadsInBranchBTotalActiveEnergyInCurrentMonth | IT loads in branch B-total active energy in current month | 当前B支路IT负载-本月总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchBTotalActiveEnergyInCurrentMonth of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.123 | hwItLoadsInBranchBTotalActiveEnergyOfLastMonth | IT loads in branch B-total active energy of last month | 当前B支路IT负载-上1月总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchBTotalActiveEnergyOfLastMonth of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.124 | hwItLoadsInBranchBTotalActiveEnergyOfLastTwoMonths | IT loads in branch B-total active energy of last two months | 当前B支路IT负载-上2月总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchBTotalActiveEnergyOfLastTwoMonths of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.125 | hwItLoadsInBranchBTotalActiveEnergyOfLastThreeMonths | IT loads in branch B-total active energy of last three months | 当前B支路IT负载-上3月总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | ItLoadsInBranchBTotalActiveEnergyOfLastThreeMonths of the device running and config table for the DEMSVD2. Multiple:100. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.126 | hwTotalInputCurrent | Total input current | 总输入电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalInputCurrent of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.127 | hwTotalInputPower | Total input power | 总输入功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalInputPower of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.128 | hwTotalInputEnergy | Total input energy | 总输入电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalInputEnergy of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.129 | hwTotalOutputCurrent | Total output current | 总输出电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalOutputCurrent of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.130 | hwTotalOutputPower | Total output power | 总输出功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalOutputPower of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.131 | hwTotalOutputEnergy | Total output energy | 总输出电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | TotalOutputEnergy of the device running and config table for the DEMSVD2. Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.17.2.1.132 | hwDEMSVD2Running2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DEMSVD2.

## Independent Deployment AI-DI
独立部署AI_DI模块
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.4 | IndependentDeploymentAIDIUnit | Independent Deployment AI_DI Unit | 独立部署AI_DI模块 | / | / | / | / | The MUE06 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.4.1 | hwIndependentDeploymentAIDIUnitConfigTable | / | / |  |  | / | / | Independent Deployment AI and DI Board config table. Use this table to get equipment ID and equipment name, to set sensors attribute and control channels power output as well.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.1 | hwIndependentDeploymentAIDIUnitConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device configuration table for the Independent Deployment AI and DI Board.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.2 | hwIndependentDeploymentAIDIUnitEquipId | / | / | 0-Read_Only | 只读 | 31..38 | 31..38 | Independent Deployment AI and DI Board's equipment ID.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.3 | hwIndependentDeploymentAIDIUnitDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Equipment name, of the character string type, is used to specify the Deployment AI and DI Board. Users can configure it. Otherwise, the configured character can not be any other languages except English.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.4 | hwIndependentDeploymentAIDIUnitCh1Enable | AI/DI_1 sensor | AI/DI_1 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_1 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.5 | hwIndependentDeploymentAIDIUnitCh1SensorName | AI/DI_1 | AI/DI_1 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_1 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.6 | hwIndependentDeploymentAIDIUnitCh1SensorType | AI/DI_1 sensor type | AI/DI_1 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10] | AI/DI_1 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.7 | hwIndependentDeploymentAIDIUnitCh1SensorUints | AI/DI_1 measurement unit | AI/DI_1 测量单位 | 1-Read_Write | 读写 | centigrade(1), percent(2), volt(3), ampere(4), other(5) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_1 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicates centigrade. Value 2 indicates percent. Value 3 indicates volt. Value 4 indicates ampere. Value 5 indicates other.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.8 | hwIndependentDeploymentAIDIUnitCh1MeasureUpperLimit | AI/DI_1 upper measurement thresh. | AI/DI_1 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.9 | hwIndependentDeploymentAIDIUnitCh1MeasureLowerLimit | AI/DI_1 lower measurement thresh. | AI/DI_1 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.10 | hwIndependentDeploymentAIDIUnitCh1AlarmUpperLimit | AI/DI_1 upper alarm threshold | AI/DI_1 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.11 | hwIndependentDeploymentAIDIUnitCh1AlarmLowerLimit | AI/DI_1 lower alarm threshold | AI/DI_1 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.12 | hwIndependentDeploymentAIDIUnitCh1PowerOutput | AI/DI_1 power supply | AI/DI_1 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_1 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.13 | hwIndependentDeploymentAIDIUnitCh2Enable | AI/DI_2 sensor | AI/DI_2 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_2 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.14 | hwIndependentDeploymentAIDIUnitCh2SensorName | AI/DI_2 | AI/DI_2 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_2 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.15 | hwIndependentDeploymentAIDIUnitCh2SensorType | AI/DI_2 sensor type | AI/DI_2 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10] | AI/DI_2 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.16 | hwIndependentDeploymentAIDIUnitCh2SensorUints | AI/DI_2 measurement unit | AI/DI_2 测量单位 | 1-Read_Write | 读写 | centigrade(1), percent(2), volt(3), ampere(4), other(5) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_2 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicates centigrade. Value 2 indicates percent. Value 3 indicates volt. Value 4 indicates ampere. Value 5 indicates other.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.17 | hwIndependentDeploymentAIDIUnitCh2MeasureUpperLimit | AI/DI_2 upper measurement thresh. | AI/DI_2 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.18 | hwIndependentDeploymentAIDIUnitCh2MeasureLowerLimit | AI/DI_2 lower measurement thresh. | AI/DI_2 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.19 | hwIndependentDeploymentAIDIUnitCh2AlarmUpperLimit | AI/DI_2 upper alarm threshold | AI/DI_2 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.20 | hwIndependentDeploymentAIDIUnitCh2AlarmLowerLimit | AI/DI_2 lower alarm threshold | AI/DI_2 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.21 | hwIndependentDeploymentAIDIUnitCh2PowerOutput | AI/DI_2 power supply | AI/DI_2 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_2 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.22 | hwIndependentDeploymentAIDIUnitCh3Enable | AI/DI_3 sensor | AI/DI_3 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_3 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.23 | hwIndependentDeploymentAIDIUnitCh3SensorName | AI/DI_3 | AI/DI_3 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_3 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.24 | hwIndependentDeploymentAIDIUnitCh3SensorType | AI/DI_3 sensor type | AI/DI_3 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10] | AI/DI_3 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.25 | hwIndependentDeploymentAIDIUnitCh3SensorUints | AI/DI_3 measurement unit | AI/DI_3 测量单位 | 1-Read_Write | 读写 | centigrade(1), percent(2), volt(3), ampere(4), other(5) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_3 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicates centigrade. Value 2 indicates percent. Value 3 indicates volt. Value 4 indicates ampere. Value 5 indicates other.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.26 | hwIndependentDeploymentAIDIUnitCh3MeasureUpperLimit | AI/DI_3 upper measurement thresh. | AI/DI_3 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.27 | hwIndependentDeploymentAIDIUnitCh3MeasureLowerLimit | AI/DI_3 lower measurement thresh. | AI/DI_3 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.28 | hwIndependentDeploymentAIDIUnitCh3AlarmUpperLimit | AI/DI_3 upper alarm threshold | AI/DI_3 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.29 | hwIndependentDeploymentAIDIUnitCh3AlarmLowerLimit | AI/DI_3 lower alarm threshold | AI/DI_3 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.30 | hwIndependentDeploymentAIDIUnitCh3PowerOutput | AI/DI_3 power supply | AI/DI_3 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_3 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.31 | hwIndependentDeploymentAIDIUnitCh4Enable | AI/DI_4 sensor | AI/DI_4 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_4 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.32 | hwIndependentDeploymentAIDIUnitCh4SensorName | AI/DI_4 | AI/DI_4 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_4 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.33 | hwIndependentDeploymentAIDIUnitCh4SensorType | AI/DI_4 sensor type | AI/DI_4 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10] | AI/DI_4 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.34 | hwIndependentDeploymentAIDIUnitCh4SensorUints | AI/DI_4 measurement unit | AI/DI_4 测量单位 | 1-Read_Write | 读写 | centigrade(1), percent(2), volt(3), ampere(4), other(5) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_4 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicates centigrade. Value 2 indicates percent. Value 3 indicates volt. Value 4 indicates ampere. Value 5 indicates other.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.35 | hwIndependentDeploymentAIDIUnitCh4MeasureUpperLimit | AI/DI_4 upper measurement thresh. | AI/DI_4 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.36 | hwIndependentDeploymentAIDIUnitCh4MeasureLowerLimit | AI/DI_4 lower measurement thresh. | AI/DI_4 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.37 | hwIndependentDeploymentAIDIUnitCh4AlarmUpperLimit | AI/DI_4 upper alarm threshold | AI/DI_4 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.38 | hwIndependentDeploymentAIDIUnitCh4AlarmLowerLimit | AI/DI_4 lower alarm threshold | AI/DI_4 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.39 | hwIndependentDeploymentAIDIUnitCh4PowerOutput | AI/DI_4 power supply | AI/DI_4 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_4 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.40 | hwIndependentDeploymentAIDIUnitCh5Enable | AI/DI_5 sensor | AI/DI_5 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_5 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.41 | hwIndependentDeploymentAIDIUnitCh5SensorName | AI/DI_5 | AI/DI_5 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_5 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.42 | hwIndependentDeploymentAIDIUnitCh5SensorType | AI/DI_5 sensor type | AI/DI_5 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10] | AI/DI_5 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.43 | hwIndependentDeploymentAIDIUnitCh5SensorUints | AI/DI_5 measurement unit | AI/DI_5 测量单位 | 1-Read_Write | 读写 | centigrade(1), percent(2), volt(3), ampere(4), other(5) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_5 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicates centigrade. Value 2 indicates percent. Value 3 indicates volt. Value 4 indicates ampere. Value 5 indicates other.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.44 | hwIndependentDeploymentAIDIUnitCh5MeasureUpperLimit | AI/DI_5 upper measurement thresh. | AI/DI_5 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.45 | hwIndependentDeploymentAIDIUnitCh5MeasureLowerLimit | AI/DI_5 lower measurement thresh. | AI/DI_5 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.46 | hwIndependentDeploymentAIDIUnitCh5AlarmUpperLimit | AI/DI_5 upper alarm threshold | AI/DI_5 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.47 | hwIndependentDeploymentAIDIUnitCh5AlarmLowerLimit | AI/DI_5 lower alarm threshold | AI/DI_5 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.48 | hwIndependentDeploymentAIDIUnitCh5PowerOutput | AI/DI_5 power supply | AI/DI_5 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_5 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.49 | hwIndependentDeploymentAIDIUnitCh6Enable | AI/DI_6 sensor | AI/DI_6 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_6 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.50 | hwIndependentDeploymentAIDIUnitCh6SensorName | AI/DI_6 | AI/DI_6 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_6 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.51 | hwIndependentDeploymentAIDIUnitCh6SensorType | AI/DI_6 sensor type | AI/DI_6 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10] | AI/DI_6 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.52 | hwIndependentDeploymentAIDIUnitCh6SensorUints | AI/DI_6 measurement unit | AI/DI_6 测量单位 | 1-Read_Write | 读写 | centigrade(1), percent(2), volt(3), ampere(4), other(5) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_6 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicates centigrade. Value 2 indicates percent. Value 3 indicates volt. Value 4 indicates ampere. Value 5 indicates other.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.53 | hwIndependentDeploymentAIDIUnitCh6MeasureUpperLimit | AI/DI_6 upper measurement thresh. | AI/DI_6 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.54 | hwIndependentDeploymentAIDIUnitCh6MeasureLowerLimit | AI/DI_6 lower measurement thresh. | AI/DI_6 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.55 | hwIndependentDeploymentAIDIUnitCh6AlarmUpperLimit | AI/DI_6 upper alarm threshold | AI/DI_6 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.56 | hwIndependentDeploymentAIDIUnitCh6AlarmLowerLimit | AI/DI_6 lower alarm threshold | AI/DI_6 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.57 | hwIndependentDeploymentAIDIUnitCh6PowerOutput | AI/DI_6 power supply | AI/DI_6 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_6 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.58 | hwIndependentDeploymentAIDIUnitCh7Enable | AI/DI_7 sensor | AI/DI_7 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_7 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.59 | hwIndependentDeploymentAIDIUnitCh7SensorName | AI/DI_7 | AI/DI_7 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_7 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.60 | hwIndependentDeploymentAIDIUnitCh7SensorType | AI/DI_7 sensor type | AI/DI_7 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10] | AI/DI_7 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.61 | hwIndependentDeploymentAIDIUnitCh7SensorUints | AI/DI_7 measurement unit | AI/DI_7 测量单位 | 1-Read_Write | 读写 | centigrade(1), percent(2), volt(3), ampere(4), other(5) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_7 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicates centigrade. Value 2 indicates percent. Value 3 indicates volt. Value 4 indicates ampere. Value 5 indicates other.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.62 | hwIndependentDeploymentAIDIUnitCh7MeasureUpperLimit | AI/DI_7 upper measurement thresh. | AI/DI_7 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.63 | hwIndependentDeploymentAIDIUnitCh7MeasureLowerLimit | AI/DI_7 lower measurement thresh. | AI/DI_7 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.64 | hwIndependentDeploymentAIDIUnitCh7AlarmUpperLimit | AI/DI_7 upper alarm threshold | AI/DI_7 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.65 | hwIndependentDeploymentAIDIUnitCh7AlarmLowerLimit | AI/DI_7 lower alarm threshold | AI/DI_7 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.66 | hwIndependentDeploymentAIDIUnitCh7PowerOutput | AI/DI_7 power supply | AI/DI_7 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_7 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.67 | hwIndependentDeploymentAIDIUnitCh8Enable | AI/DI_8 sensor | AI/DI_8 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_8 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.68 | hwIndependentDeploymentAIDIUnitCh8SensorName | AI/DI_8 | AI/DI_8 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_8 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.69 | hwIndependentDeploymentAIDIUnitCh8SensorType | AI/DI_8 sensor type | AI/DI_8 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10] | AI/DI_8 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.70 | hwIndependentDeploymentAIDIUnitCh8SensorUints | AI/DI_8 measurement unit | AI/DI_8 测量单位 | 1-Read_Write | 读写 | centigrade(1), percent(2), volt(3), ampere(4), other(5) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_8 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicates centigrade. Value 2 indicates percent. Value 3 indicates volt. Value 4 indicates ampere. Value 5 indicates other.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.71 | hwIndependentDeploymentAIDIUnitCh8MeasureUpperLimit | AI/DI_8 upper measurement thresh. | AI/DI_8 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.72 | hwIndependentDeploymentAIDIUnitCh8MeasureLowerLimit | AI/DI_8 lower measurement thresh. | AI/DI_8 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.73 | hwIndependentDeploymentAIDIUnitCh8AlarmUpperLimit | AI/DI_8 upper alarm threshold | AI/DI_8 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.74 | hwIndependentDeploymentAIDIUnitCh8AlarmLowerLimit | AI/DI_8 lower alarm threshold | AI/DI_8 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.75 | hwIndependentDeploymentAIDIUnitCh8PowerOutput | AI/DI_8 power supply | AI/DI_8 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_8 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.4.1.1.100 | hwIndependentDeploymentAIDIUnitConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of Independent Deployment AI and DI Board's config table
1.3.6.1.4.1.2011.6.178.1.1.4.2 | hwIndependentDeploymentAIDIUnitRunning1Table | / | / |  |  | / | / | Independent Deployment AI and DI Board running table. Use this table to getIndependent Deployment AI and DI Board's presence status,slot number,etc.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.1 | hwIndependentDeploymentAIDIUnitRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Independent Deployment AI and DI Board.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.2 | hwIndependentDeploymentAIDIUnitPresenceStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | notDetected(1), detected(2) | [通信失败=1]/[通信正常=2] | Independent Deployment AI and DI Board's presence status. it is an enumeration type: If the enumeration value is 1, it indicates device is not detected; If the enumeration value is 2, it indicates device is detected;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.3 | hwIndependentDeploymentAIDIUnitSlotNo | / | / | 0-Read_Only | 只读 | 1..16 | / | Independent Deployment AI and DI Board's slot number.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.4 | hwIndependentDeploymentAIDIUnitPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..15 | 1..15 | RS485 communication card's port number.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.5 | hwIndependentDeploymentAIDIUnitModbusAddr | Communication address | 通信地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Independent Deployment AI and DI Board's modbus address.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.6 | hwIndependentDeploymentAIDIUnitCh1DiStatus | AI/DI_1 DI status | AI/DI_1 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_1 channel digital input status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is open; If the enumeration value is 2, it indicates sensor status is closed; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.7 | hwIndependentDeploymentAIDIUnitCh1AiValue | AI/DI_1 AI value | AI/DI_1 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_1 channel analog input signal's value. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.8 | hwIndependentDeploymentAIDIUnitCh1SensorStatus | AI/DI_1 sensor status | AI/DI_1 传感器状态 | 0-Read_Only | 只读 | normal(1), invalidOrDisconnectedl(2), unknown(255) | [正常=1]/[失效或未接=2] | AI/DI_1 channel sensor status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is normal; If the enumeration value is 2, it indicates sensor status is Invalid or disconnected; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.9 | hwIndependentDeploymentAIDIUnitCh1PowerOutputStatus | AI/DI_1 power status | AI/DI_1 供电状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_1 channel power output status. it is an enumeration type: If the enumeration value is 1, it indicates the power is turned off; If the enumeration value is 2, it indicates the power is turned on; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.10 | hwIndependentDeploymentAIDIUnitCh1PowerOutputAlarmStatus | AI/DI_1 12V output alarm | AI/DI_1 12V输出告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | AI/DI_1 channel power alarm status. it is an enumeration type: If the enumeration value is 1, it indicates the power status is normal; If the enumeration value is 2, it indicates the power status is abnormal; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.11 | hwIndependentDeploymentAIDIUnitCh2DiStatus | AI/DI_2 DI status | AI/DI_2 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_2 channel digital input status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is open; If the enumeration value is 2, it indicates sensor status is closed; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.12 | hwIndependentDeploymentAIDIUnitCh2AiValue | AI/DI_2 AI value | AI/DI_2 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_2 channel analog input signal's value. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.13 | hwIndependentDeploymentAIDIUnitCh2SensorStatus | AI/DI_2 sensor status | AI/DI_2 传感器状态 | 0-Read_Only | 只读 | normal(1), invalidOrDisconnectedl(2), unknown(255) | [正常=1]/[失效或未接=2] | AI/DI_2 channel sensor status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is normal; If the enumeration value is 2, it indicates sensor status is Invalid or disconnected; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.14 | hwIndependentDeploymentAIDIUnitCh2PowerOutputStatus | AI/DI_2 power status | AI/DI_2 供电状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_2 channel power output status. it is an enumeration type: If the enumeration value is 1, it indicates the power is turned off; If the enumeration value is 2, it indicates the power is turned on; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.15 | hwIndependentDeploymentAIDIUnitCh2PowerOutputAlarmStatus | AI/DI_2 12V output alarm | AI/DI_2 12V输出告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | AI/DI_2 channel power alarm status. it is an enumeration type: If the enumeration value is 1, it indicates the power status is normal; If the enumeration value is 2, it indicates the power status is abnormal; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.16 | hwIndependentDeploymentAIDIUnitCh3DiStatus | AI/DI_3 DI status | AI/DI_3 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_3 channel digital input status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is open; If the enumeration value is 2, it indicates sensor status is closed; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.17 | hwIndependentDeploymentAIDIUnitCh3AiValue | AI/DI_3 AI value | AI/DI_3 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_3 channel analog input signal's value. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.18 | hwIndependentDeploymentAIDIUnitCh3SensorStatus | AI/DI_3 sensor status | AI/DI_3 传感器状态 | 0-Read_Only | 只读 | normal(1), invalidOrDisconnectedl(2), unknown(255) | [正常=1]/[失效或未接=2] | AI/DI_3 channel sensor status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is normal; If the enumeration value is 2, it indicates sensor status is Invalid or disconnected; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.19 | hwIndependentDeploymentAIDIUnitCh3PowerOutputStatus | AI/DI_3 power status | AI/DI_3 供电状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_3 channel power output status. it is an enumeration type: If the enumeration value is 1, it indicates the power is turned off; If the enumeration value is 2, it indicates the power is turned on; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.20 | hwIndependentDeploymentAIDIUnitCh3PowerOutputAlarmStatus | AI/DI_3 12V output alarm | AI/DI_3 12V输出告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | AI/DI_3 channel power alarm status. it is an enumeration type: If the enumeration value is 1, it indicates the power status is normal; If the enumeration value is 2, it indicates the power status is abnormal; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.21 | hwIndependentDeploymentAIDIUnitCh4DiStatus | AI/DI_4 DI status | AI/DI_4 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_4 channel digital input status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is open; If the enumeration value is 2, it indicates sensor status is closed; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.22 | hwIndependentDeploymentAIDIUnitCh4AiValue | AI/DI_4 AI value | AI/DI_4 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_4 channel analog input signal's value. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.23 | hwIndependentDeploymentAIDIUnitCh4SensorStatus | AI/DI_4 sensor status | AI/DI_4 传感器状态 | 0-Read_Only | 只读 | normal(1), invalidOrDisconnectedl(2), unknown(255) | [正常=1]/[失效或未接=2] | AI/DI_4 channel sensor status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is normal; If the enumeration value is 2, it indicates sensor status is Invalid or disconnected; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.24 | hwIndependentDeploymentAIDIUnitCh4PowerOutputStatus | AI/DI_4 power status | AI/DI_4 供电状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_4 channel power output status. it is an enumeration type: If the enumeration value is 1, it indicates the power is turned off; If the enumeration value is 2, it indicates the power is turned on; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.25 | hwIndependentDeploymentAIDIUnitCh4PowerOutputAlarmStatus | AI/DI_4 12V output alarm | AI/DI_4 12V输出告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | AI/DI_4 channel power alarm status. it is an enumeration type: If the enumeration value is 1, it indicates the power status is normal; If the enumeration value is 2, it indicates the power status is abnormal; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.26 | hwIndependentDeploymentAIDIUnitCh5DiStatus | AI/DI_5 DI status | AI/DI_5 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_5 channel digital input status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is open; If the enumeration value is 2, it indicates sensor status is closed; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.27 | hwIndependentDeploymentAIDIUnitCh5AiValue | AI/DI_5 AI value | AI/DI_5 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_5 channel analog input signal's value. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.28 | hwIndependentDeploymentAIDIUnitCh5SensorStatus | AI/DI_5 sensor status | AI/DI_5 传感器状态 | 0-Read_Only | 只读 | normal(1), invalidOrDisconnectedl(2), unknown(255) | [正常=1]/[失效或未接=2] | AI/DI_5 channel sensor status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is normal; If the enumeration value is 2, it indicates sensor status is Invalid or disconnected; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.29 | hwIndependentDeploymentAIDIUnitCh5PowerOutputStatus | AI/DI_5 power status | AI/DI_5 供电状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_5 channel power output status. it is an enumeration type: If the enumeration value is 1, it indicates the power is turned off; If the enumeration value is 2, it indicates the power is turned on; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.30 | hwIndependentDeploymentAIDIUnitCh5PowerOutputAlarmStatus | AI/DI_5 12V output alarm | AI/DI_5 12V输出告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | AI/DI_5 channel power alarm status. it is an enumeration type: If the enumeration value is 1, it indicates the power status is normal; If the enumeration value is 2, it indicates the power status is abnormal; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.31 | hwIndependentDeploymentAIDIUnitCh6DiStatus | AI/DI_6 DI status | AI/DI_6 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_6 channel digital input status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is open; If the enumeration value is 2, it indicates sensor status is closed; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.32 | hwIndependentDeploymentAIDIUnitCh6AiValue | AI/DI_6 AI value | AI/DI_6 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_6 channel analog input signal's value. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.33 | hwIndependentDeploymentAIDIUnitCh6SensorStatus | AI/DI_6 sensor status | AI/DI_6 传感器状态 | 0-Read_Only | 只读 | normal(1), invalidOrDisconnectedl(2), unknown(255) | [正常=1]/[失效或未接=2] | AI/DI_6 channel sensor status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is normal; If the enumeration value is 2, it indicates sensor status is Invalid or disconnected; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.34 | hwIndependentDeploymentAIDIUnitCh6PowerOutputStatus | AI/DI_6 power status | AI/DI_6 供电状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_6 channel power output status. it is an enumeration type: If the enumeration value is 1, it indicates the power is turned off; If the enumeration value is 2, it indicates the power is turned on; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.35 | hwIndependentDeploymentAIDIUnitCh6PowerOutputAlarmStatus | AI/DI_6 12V output alarm | AI/DI_6 12V输出告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | AI/DI_6 channel power alarm status. it is an enumeration type: If the enumeration value is 1, it indicates the power status is normal; If the enumeration value is 2, it indicates the power status is abnormal; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.36 | hwIndependentDeploymentAIDIUnitCh7DiStatus | AI/DI_7 DI status | AI/DI_7 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_7 channel digital input status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is open; If the enumeration value is 2, it indicates sensor status is closed; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.37 | hwIndependentDeploymentAIDIUnitCh7AiValue | AI/DI_7 AI value | AI/DI_7 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_7 channel analog input signal's value. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.38 | hwIndependentDeploymentAIDIUnitCh7SensorStatus | AI/DI_7 sensor status | AI/DI_7 传感器状态 | 0-Read_Only | 只读 | normal(1), invalidOrDisconnectedl(2), unknown(255) | [正常=1]/[失效或未接=2] | AI/DI_7 channel sensor status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is normal; If the enumeration value is 2, it indicates sensor status is Invalid or disconnected; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.39 | hwIndependentDeploymentAIDIUnitCh7PowerOutputStatus | AI/DI_7 power status | AI/DI_7 供电状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_7 channel power output status. it is an enumeration type: If the enumeration value is 1, it indicates the power is turned off; If the enumeration value is 2, it indicates the power is turned on; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.40 | hwIndependentDeploymentAIDIUnitCh7PowerOutputAlarmStatus | AI/DI_7 12V output alarm | AI/DI_7 12V输出告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | AI/DI_7 channel power alarm status. it is an enumeration type: If the enumeration value is 1, it indicates the power status is normal; If the enumeration value is 2, it indicates the power status is abnormal; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.41 | hwIndependentDeploymentAIDIUnitCh8DiStatus | AI/DI_8 DI status | AI/DI_8 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_8 channel digital input status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is open; If the enumeration value is 2, it indicates sensor status is closed; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.42 | hwIndependentDeploymentAIDIUnitCh8AiValue | AI/DI_8 AI value | AI/DI_8 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_8 channel analog input signal's value. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.43 | hwIndependentDeploymentAIDIUnitCh8SensorStatus | AI/DI_8 sensor status | AI/DI_8 传感器状态 | 0-Read_Only | 只读 | normal(1), invalidOrDisconnectedl(2), unknown(255) | [正常=1]/[失效或未接=2] | AI/DI_8 channel sensor status. it is an enumeration type: If the enumeration value is 1, it indicates sensor status is normal; If the enumeration value is 2, it indicates sensor status is Invalid or disconnected; If the enumeration value is 3, it indicates sensor status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.44 | hwIndependentDeploymentAIDIUnitCh8PowerOutputStatus | AI/DI_8 power status | AI/DI_8 供电状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_8 channel power output status. it is an enumeration type: If the enumeration value is 1, it indicates the power is turned off; If the enumeration value is 2, it indicates the power is turned on; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.45 | hwIndependentDeploymentAIDIUnitCh8PowerOutputAlarmStatus | AI/DI_8 12V output alarm | AI/DI_8 12V输出告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | AI/DI_8 channel power alarm status. it is an enumeration type: If the enumeration value is 1, it indicates the power status is normal; If the enumeration value is 2, it indicates the power status is abnormal; If the enumeration value is 3, it indicates the power status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.46 | hwIndependentDeploymentAIDIUnitPowerVoltageLowAlarmStatus | Low power voltage alarm status | 电源电压低告警状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | Independent Deployment AI and DI Board's power input alarm status, it is an enumeration type: If the enumeration value is 1, it indicates the power input status is normal; If the enumeration value is 2, it indicates the power input status is abnormal; If the enumeration value is 3, it indicates the power input status is unknown;
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.47 | hwIndependentDeploymentAIDIUnitEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.4.2.1.100 | hwIndependentDeploymentAIDIUnitOper1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of Independent Deployment AI and DI Board's running table
1.3.6.1.4.1.2011.6.178.1.1.4.4 | hwIndependentDeploymentAIDIUnitOper2Table | / | / |  |  | / | / | Independent Deployment AI and DI Board running table. Use this table to getIndependent Deployment AI and DI Board's presence status,slot number,etc.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.1 | hwIndependentDeploymentAIDIUnitOper2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Independent Deployment AI and DI Board,.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.2 | hwIndependentDeploymentAIDIUnitSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..25 | 0..25 | Independent Deployment AI and DI Board's Software Version.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.3 | hwIndependentDeploymentAIDIUnitHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..25 | 0..25 | Independent Deployment AI and DI Board's Hardware Version.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.4 | hwIndependentDeploymentAIDIUnitAIDI1SensorConnectionStatus | AI/DI_1 sensor connection status | AI/DI_1 传感器接线状态 | 0-Read_Only | 只读 | correct(1), incorrect(2), unknown(255) | [正确=1]/[错误=2] | AIDI1SensorConnectionStatus: Value 1 indicates Correct. Value 2 indicates Incorrect.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.5 | hwIndependentDeploymentAIDIUnitAIDI2SensorConnectionStatus | AI/DI_2 sensor connection status | AI/DI_2 传感器接线状态 | 0-Read_Only | 只读 | correct(1), incorrect(2), unknown(255) | [正确=1]/[错误=2] | AIDI2SensorConnectionStatus: Value 1 indicates Correct. Value 2 indicates Incorrect.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.6 | hwIndependentDeploymentAIDIUnitAIDI3SensorConnectionStatus | AI/DI_3 sensor connection status | AI/DI_3 传感器接线状态 | 0-Read_Only | 只读 | correct(1), incorrect(2), unknown(255) | [正确=1]/[错误=2] | AIDI3SensorConnectionStatus: Value 1 indicates Correct. Value 2 indicates Incorrect.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.7 | hwIndependentDeploymentAIDIUnitAIDI4SensorConnectionStatus | AI/DI_4 sensor connection status | AI/DI_4 传感器接线状态 | 0-Read_Only | 只读 | correct(1), incorrect(2), unknown(255) | [正确=1]/[错误=2] | AIDI4SensorConnectionStatus: Value 1 indicates Correct. Value 2 indicates Incorrect.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.8 | hwIndependentDeploymentAIDIUnitAIDI5SensorConnectionStatus | AI/DI_5 sensor connection status | AI/DI_5 传感器接线状态 | 0-Read_Only | 只读 | correct(1), incorrect(2), unknown(255) | [正确=1]/[错误=2] | AIDI5SensorConnectionStatus: Value 1 indicates Correct. Value 2 indicates Incorrect.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.9 | hwIndependentDeploymentAIDIUnitAIDI6SensorConnectionStatus | AI/DI_6 sensor connection status | AI/DI_6 传感器接线状态 | 0-Read_Only | 只读 | correct(1), incorrect(2), unknown(255) | [正确=1]/[错误=2] | AIDI6SensorConnectionStatus: Value 1 indicates Correct. Value 2 indicates Incorrect.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.10 | hwIndependentDeploymentAIDIUnitAIDI7SensorConnectionStatus | AI/DI_7 sensor connection status | AI/DI_7 传感器接线状态 | 0-Read_Only | 只读 | correct(1), incorrect(2), unknown(255) | [正确=1]/[错误=2] | AIDI7SensorConnectionStatus: Value 1 indicates Correct. Value 2 indicates Incorrect.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.11 | hwIndependentDeploymentAIDIUnitAIDI8SensorConnectionStatus | AI/DI_8 sensor connection status | AI/DI_8 传感器接线状态 | 0-Read_Only | 只读 | correct(1), incorrect(2), unknown(255) | [正确=1]/[错误=2] | AIDI8SensorConnectionStatus: Value 1 indicates Correct. Value 2 indicates Incorrect.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.12 | hwIndependentDeploymentAIDIUnitElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | Independent Deployment AI and DI Board's Elabel.
1.3.6.1.4.1.2011.6.178.1.1.4.4.1.100 | hwIndependentDeploymentAIDIUnitConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of Independent Deployment AI and DI Board's config table

## EnvGPRS
短信模块
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.7.1.1 | EnvGPRS |  |  | / | / | / | / | The GPRS equipment.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.1 | hwEnvGPRSBoardSlot | / | / | 0-Read_Only | 只读 | 1..6 | / | the Slot of Device.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.2 | hwEnvGPRSName | / | / | 1-Read_Write | 读写 |  |  | the Name of Device.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.3 | hwEnvGPRSDI1 | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | DI_1 Status: value 1 indicates close. value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.4 | hwEnvGPRSDI2 | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | DI_2 Status: value 1 indicates close. value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.5 | hwEnvGPRSDI3 | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | DI_3 Status: value 1 indicates close. value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.6 | hwEnvGPRSDI4 | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | DI_4 Status: value 1 indicates close. value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.7 | hwEnvGPRSDI5 | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | DI_5 Status: value 1 indicates close. value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.8 | hwEnvGPRSDI6 | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | DI_6 Status: value 1 indicates close. value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9 | hwEnvGPRSStatus | / | / | 0-Read_Only | 只读 | / | / | The Status of GPRS equipment.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.1 | hwEnvGPRSExist | / | / | 0-Read_Only | 只读 | notdetected(1), detected(2), unknown(255) | / | The GPRS Equipment exist status: value 1 indicates notdetected. value 2 indicates detected.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.2 | hwEnvGPRSSIMcardExist | / | / | 0-Read_Only | 只读 | notdetected(1), detected(2), unknown(255) | / | The GPRS SIM card exist status: value 1 indicates notdetected. value 2 indicates detected.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.3 | hwEnvGPRSSMSStatus | / | / | 0-Read_Only | 只读 | failure(1), success(2), unknown(255) | / | The GPRS SMS service status: value 1 indicates failure. value 2 indicates success.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.4 | hwEnvGPRSSignalStrength | / | / | 0-Read_Only | 只读 | 0..100 | / | The strength of GPRS signal.Unit : %RH.Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.5 | hwGPRSBoardDO1Status | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | Do 1 status of the device running table for the GPRS board. value 1 indicates Close. value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.6 | hwGPRSBoardDO2Status | / | / | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | / | Do 2 status of the device running table for the GPRS board. value 1 indicates Close. value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.7 | hwGPRSBoardNameClear | / | / | 0-Read_Only | 只读 | 0..1 | / | Name clear of the device running table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.8 | hwGPRSBoardNameWarning | / | / | 0-Read_Only | 只读 | 0..1 | / | Name warning of the device running table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.9 | hwGPRSBoardNameMinor | / | / | 0-Read_Only | 只读 | 0..1 | / | Name minor of the device running table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.10 | hwGPRSBoardNameMajor | / | / | 0-Read_Only | 只读 | 0..1 | / | Name major of the device running table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.9.11 | hwGPRSBoardNameCritical | / | / | 0-Read_Only | 只读 | 0..1 | / | Name critical of the device running table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20 | hwEnvGPRSConfig | / | / | 0-Read_Only | 只读 |  | / | Config table of GPRS.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.1 | hwEnvGPRSEnableDI1 | / | / | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | / | DI_1 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is enabled; If the enumeration value is 2, it indicates the channel is disabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.2 | hwEnvGPRSConfigDI1Level | / | / | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | / | DI6 channel level,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is nc; If the enumeration value is 2, it indicates the channel is no;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.3 | hwEnvGPRSEnableDI2 | / | / | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | / | DI_2 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is enabled; If the enumeration value is 2, it indicates the channel is disabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.4 | hwEnvGPRSConfigDI2Level | / | / | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | / | DI_2 channel level,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is nc; If the enumeration value is 2, it indicates the channel is no;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.5 | hwEnvGPRSEnableDI3 | / | / | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | / | DI_3 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is enabled; If the enumeration value is 2, it indicates the channel is disabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.6 | hwEnvGPRSConfigDI3Level | / | / | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | / | DI_4 channel level,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is nc; If the enumeration value is 2, it indicates the channel is no;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.7 | hwEnvGPRSEnableDI4 | / | / | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | / | DI_4 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is enabled; If the enumeration value is 2, it indicates the channel is disabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.8 | hwEnvGPRSConfigDI4Level | / | / | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | / | DI_4 channel level,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is nc; If the enumeration value is 2, it indicates the channel is no;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.9 | hwEnvGPRSEnableDI5 | / | / | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | / | DI_5 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is enabled; If the enumeration value is 2, it indicates the channel is disabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.10 | hwEnvGPRSConfigDI5Level | / | / | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | / | DI_5 channel level,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is nc; If the enumeration value is 2, it indicates the channel is no;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.11 | hwEnvGPRSEnableDI6 | / | / | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | / | DI_6 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is enabled; If the enumeration value is 2, it indicates the channel is disabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.12 | hwEnvGPRSConfigDI6Level | / | / | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | / | DI_6 channel level,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is nc; If the enumeration value is 2, it indicates the channel is no;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.13 | hwEnvGPRSEnableDO1 | / | / | 1-Read_Write | 读写 | manual(1), disable(2), associate(3) | / | DO1 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is manual; If the enumeration value is 2, it indicates the channel is disable; If the enumeration value is 3, it indicates the channel is dassociate;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.14 | hwEnvGPRSConfigDO1Level | / | / | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | / | DO2 channel level,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is nc; If the enumeration value is 2, it indicates the channel is no;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.15 | hwEnvGPRSEnableDO2 | / | / | 1-Read_Write | 读写 | manual(1), disable(2), associate(3) | / | DO2 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is manual; If the enumeration value is 2, it indicates the channel is disable; If the enumeration value is 3, it indicates the channel is dassociate;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.16 | hwEnvGPRSConfigDO2Level | / | / | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | / | DO2 channel level,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is nc; If the enumeration value is 2, it indicates the channel is no;
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.17 | hwGPRSBoardTelNum1 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 1 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.18 | hwGPRSBoardTelNum2 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 2 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.19 | hwGPRSBoardTelNum3 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 3 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.20 | hwGPRSBoardTelNum4 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 4 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.21 | hwGPRSBoardTelNum5 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 5 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.22 | hwGPRSBoardTelNum6 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 6 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.23 | hwGPRSBoardTelNum7 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 7 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.24 | hwGPRSBoardTelNum8 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 8 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.25 | hwGPRSBoardTelNum9 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 9 of the device config table for the GPRS board.
1.3.6.1.4.1.2011.6.178.1.1.7.1.1.20.26 | hwGPRSBoardTelNum10 | / | / | 0-Read_Only | 只读 | 0..16 | / | Tel num 10 of the device config table for the GPRS board.

## ECC800
ECC800
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.7.1.3 | EnvECCAIDI | ECC800 | ECC800 | / | / | / | / | The ecc ai di equipment.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1 | hwEnvECCAIDIParameter | / | / | 0-Read_Only | 只读 |  | / | The ecc ai di parameter.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.1 | hwEnvECCAIDI1DIstatus | AI/DI_1 DI status | AI/DI_1 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | ECC AIDI1 DI status Value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.2 | hwEnvECCAIDI1AIvalue | AI/DI_1 AI value | AI/DI_1 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | The ECC AIDI1 AI value. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.4 | hwEnvECCAIDI1powerstatus | AI/DI_1 power status | AI/DI_1 供电状态 | 0-Read_Only | 只读 | nopower(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | ECC AIDI1 power status. Value 1 indicates no power. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.6 | hwEnvECCAIDI2DIstatus | AI/DI_2 DI status | AI/DI_2 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | ECC AIDI1 DI status. Value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.7 | hwEnvECCAIDI2AIvalue | AI/DI_2 AI value | AI/DI_2 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | The ECC AIDI2 AI value. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.9 | hwEnvECCAIDI2powerstatus | AI/DI_2 power status | AI/DI_2 供电状态 | 0-Read_Only | 只读 | nopower(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | ECC AIDI2 power status. Value 1 indicates no power. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.11 | hwEnvECCAIDI3DIstatus | AI/DI_3 DI status | AI/DI_3 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | ECC AIDI3 DI status. Value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.12 | hwEnvECCAIDI3AIvalue | AI/DI_3 AI value | AI/DI_3 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | The ECC AIDI3 AI value. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.14 | hwEnvECCAIDI3powerstatus | AI/DI_3 power status | AI/DI_3 供电状态 | 0-Read_Only | 只读 | nopower(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | ECC AIDI3 power status. Value 1 indicates no power. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.16 | hwEnvECCAIDI4DIstatus | AI/DI_4 DI status | AI/DI_4 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | ECC AIDI4 DI status Value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.17 | hwEnvECCAIDI4AIvalue | AI/DI_4 AI value | AI/DI_4 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | The ECC AIDI4 AI value. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.19 | hwEnvECCAIDI4powerstatus | AI/DI_4 power status | AI/DI_4 供电状态 | 0-Read_Only | 只读 | nopower(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | ECC AIDI4 power status. Value 1 indicates no power. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.21 | hwEnvECCAIDI5DIstatus | AI/DI_5 DI status | AI/DI_5 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | ECC AIDI5 DI status. Value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.22 | hwEnvECCAIDI5AIvalue | AI/DI_5 AI value | AI/DI_5 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | The ECC AIDI5 AI value. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.24 | hwEnvECCAIDI5powerstatus | AI/DI_5 power status | AI/DI_5 供电状态 | 0-Read_Only | 只读 | nopower(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | ECC AIDI5 power status. Value 1 indicates nopower. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.26 | hwEnvECCAIDI6DIstatus | AI/DI_6 DI status | AI/DI_6 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | ECC AIDI6 DI status. Value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.27 | hwEnvECCAIDI6AIvalue | AI/DI_6 AI value | AI/DI_6 AI值 | 0-Read_Only | 只读 | -1000..51000 | -1000..51000 | The ECC AIDI6 AI value. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.29 | hwEnvECCAIDI6powerstatus | AI/DI_6 power status | AI/DI_6 供电状态 | 0-Read_Only | 只读 | nopower(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | ECC AIDI6 power status. Value 1 indicates no power. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.40 | hwEIC800IPAddress1 | WAN_1 IP address | A7 WAN_1 IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EIC800 IP address,
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.41 | hwEIC800SubnetMask1 | WAN_1 subnet mask | A7 WAN_1 子网掩码 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EIC800 Subnet Mask.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.42 | hwEIC800DefaultGateway1 | WAN_1 default gateway | A7 WAN_1 默认网关 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EIC800 Default Gateway.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.43 | hwEIC800DNSAddress1 | Perffer DNS addr 1 | A7 首选DNS_1 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EIC800 DNS Address_1.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.1.44 | hwEIC800DNSAddress2 | Spare DNS addr 1 | A7 备用DNS_1 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EIC800 DNS Address_2.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2 | hwEnvECCAIDIConfig | / | / | 0-Read_Only | 只读 |  | / | The ecc ai di parameter config.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.1 | hwECCAIDI1Enable | AI/DI_1 sensor | AI/DI_1 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_1 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.2 | hwECCAIDI1SensorName | AI/DI_1 | AI/DI_1 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_1 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.3 | hwECCAIDI1SensorType | AI/DI_1 sensor type | AI/DI_1 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_1 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA. Value 11 indicates leakSensorElectroc.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.4 | hwECCAIDI1SensorUints | AI/DI_1 measurement unit | AI/DI_1 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_1 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicate degrees celcius Value 2 indicate relative humidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.5 | hwECCAIDI1MeasureUpperLimit | AI/DI_1 upper measurement thresh. | AI/DI_1 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.6 | hwECCAIDI1MeasureLowerLimit | AI/DI_1 lower measurement thresh. | AI/DI_1 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.7 | hwECCAIDI1AlarmUpperLimit | AI/DI_1 upper alarm threshold | AI/DI_1 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.8 | hwECCAIDI1AlarmLowerLimit | AI/DI_1 lower alarm threshold | AI/DI_1 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.9 | hwECCAIDI1PowerOutput | AI/DI_1 power supply | AI/DI_1 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_1 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.10 | hwECCAIDI2Enable | AI/DI_2 sensor | AI/DI_2 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_2 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.11 | hwECCAIDI2SensorName | AI/DI_2 | AI/DI_2 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_2 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.12 | hwECCAIDI2SensorType | AI/DI_2 sensor type | AI/DI_2 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_2 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA. Value 11 indicates leakSensorElectroc.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.13 | hwECCAIDI2SensorUints | AI/DI_2 measurement unit | AI/DI_2 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_2 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicate degrees celcius Value 2 indicate relative humidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.14 | hwECCAIDI2MeasureUpperLimit | AI/DI_2 upper measurement thresh. | AI/DI_2 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.15 | hwECCAIDI2MeasureLowerLimit | AI/DI_2 lower measurement thresh. | AI/DI_2 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.16 | hwECCAIDI2AlarmUpperLimit | AI/DI_2 upper alarm threshold | AI/DI_2 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.17 | hwECCAIDI2AlarmLowerLimit | AI/DI_2 lower alarm threshold | AI/DI_2 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.18 | hwECCAIDI2PowerOutput | AI/DI_2 power supply | AI/DI_2 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_2 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.19 | hwECCAIDI3Enable | AI/DI_3 sensor | AI/DI_3 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_3 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.20 | hwECCAIDI3SensorName | AI/DI_3 | AI/DI_3 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_3 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.21 | hwECCAIDI3SensorType | AI/DI_3 sensor type | AI/DI_3 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_3 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA. Value 11 indicates leakSensorElectroc.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.22 | hwECCAIDI3SensorUints | AI/DI_3 measurement unit | AI/DI_3 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_3 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicate degrees celcius Value 2 indicate relative humidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.23 | hwECCAIDI3MeasureUpperLimit | AI/DI_3 upper measurement thresh. | AI/DI_3 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.24 | hwECCAIDI3MeasureLowerLimit | AI/DI_3 lower measurement thresh. | AI/DI_3 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.25 | hwECCAIDI3AlarmUpperLimit | AI/DI_3 upper alarm threshold | AI/DI_3 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.26 | hwECCAIDI3AlarmLowerLimit | AI/DI_3 lower alarm threshold | AI/DI_3 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.27 | hwECCAIDI3PowerOutput | AI/DI_3 power supply | AI/DI_3 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_3 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.28 | hwECCAIDI4Enable | AI/DI_4 sensor | AI/DI_4 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_4 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.29 | hwECCAIDI4SensorName | AI/DI_4 | AI/DI_4 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_4 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.30 | hwECCAIDI4SensorType | AI/DI_4 sensor type | AI/DI_4 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_4 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA. Value 11 indicates leakSensorElectroc.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.31 | hwECCAIDI4SensorUints | AI/DI_4 measurement unit | AI/DI_4 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_4 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicate degrees celcius Value 2 indicate relative humidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.32 | hwECCAIDI4MeasureUpperLimit | AI/DI_4 upper measurement thresh. | AI/DI_4 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.33 | hwECCAIDI4MeasureLowerLimit | AI/DI_4 lower measurement thresh. | AI/DI_4 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.34 | hwECCAIDI4AlarmUpperLimit | AI/DI_4 upper alarm threshold | AI/DI_4 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.35 | hwECCAIDI4AlarmLowerLimit | AI/DI_4 lower alarm threshold | AI/DI_4 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.36 | hwECCAIDI4PowerOutput | AI/DI_4 power supply | AI/DI_4 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_4 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.37 | hwECCAIDI5Enable | AI/DI_5 sensor | AI/DI_5 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_5 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.38 | hwECCAIDI5SensorName | AI/DI_5 | AI/DI_5 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_5 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.39 | hwECCAIDI5SensorType | AI/DI_5 sensor type | AI/DI_5 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_5 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA. Value 11 indicates leakSensorElectroc.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.40 | hwECCAIDI5SensorUints | AI/DI_5 measurement unit | AI/DI_5 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_5 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicate degrees celcius Value 2 indicate relative humidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.41 | hwECCAIDI5MeasureUpperLimit | AI/DI_5 upper measurement thresh. | AI/DI_5 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.42 | hwECCAIDI5MeasureLowerLimit | AI/DI_5 lower measurement thresh. | AI/DI_5 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.43 | hwECCAIDI5AlarmUpperLimit | AI/DI_5 upper alarm threshold | AI/DI_5 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.44 | hwECCAIDI5AlarmLowerLimit | AI/DI_5 lower alarm threshold | AI/DI_5 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.45 | hwECCAIDI5PowerOutput | AI/DI_5 power supply | AI/DI_5 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_5 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.46 | hwECCAIDI6Enable | AI/DI_6 sensor | AI/DI_6 使能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | AI/DI_6 channel enable,which user must enable it if want to insert sensors, is an enumeration type: If the enumeration value is 1, it indicates the channel is disabled; If the enumeration value is 2, it indicates the channel is enabled;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.47 | hwECCAIDI6SensorName | AI/DI_6 | AI/DI_6 | 0-Read_Only | 只读 | 1..50 | 1..50 | AI/DI_6 channel's sensor name,which users can configure,is zero-length by default.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.48 | hwECCAIDI6SensorType | AI/DI_6 sensor type | AI/DI_6 传感器类型 | 1-Read_Write | 读写 | no(1), nc(2), door(3), smoke(4), smokeNc(5), leak(6), leakRope(7), leakNc(8), tempNtc(9), generalSensor4to20mA(10), leakSensorElectroc(11), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_6 channel's sensor type,which user can configure,is normally open dry contact by default. Value 1 indicates no. Value 2 indicates nc. Value 3 indicates door. Value 4 indicates smoke. Value 5 indicates smokeNc. Value 6 indicates leak. Value 7 indicates leakRope. Value 8 indicates leakNc. Value 9 indicates tempNtc. Value 10 indicates generalSensor4to20mA. Value 11 indicates leakSensorElectroc.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.49 | hwECCAIDI6SensorUints | AI/DI_6 measurement unit | AI/DI_6 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), ppm(6), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5]/[Ppm=6] | AI/DI_6 channel's sensor unit,which user can configure,is centigrade by default. Value 1 indicate degrees celcius Value 2 indicate relative humidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other Value 6 indicate ppm
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.50 | hwECCAIDI6MeasureUpperLimit | AI/DI_6 upper measurement thresh. | AI/DI_6 测量上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.51 | hwECCAIDI6MeasureLowerLimit | AI/DI_6 lower measurement thresh. | AI/DI_6 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor measurement range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.52 | hwECCAIDI6AlarmUpperLimit | AI/DI_6 upper alarm threshold | AI/DI_6 告警上限 | 1-Read_Write | 读写 | 25..5000 | 25..5000 | The upper limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.53 | hwECCAIDI6AlarmLowerLimit | AI/DI_6 lower alarm threshold | AI/DI_6 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | The lower limit of sensor alarm range.
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.54 | hwECCAIDI6PowerOutput | AI/DI_6 power supply | AI/DI_6 供电使能 | 1-Read_Write | 读写 | yes(1), no(2) | [是=1]/[否=2] | AI/DI_6 channel power output, which users can use it to turn on or off the power, is an enumeration type: If the enumeration value is 1, it indicates turn on the power; If the enumeration value is 2, it indicates turn off the power;
1.3.6.1.4.1.2011.6.178.1.1.7.1.3.2.80 | hwEnvECCSynchronizesystemtimetodevice | Synchronize system time to device | 同步系统时间到设备 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | ECC Synchronize system time to device: Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.11.1 | hwSystemInstantPue | Instant PUE | 瞬时PUE | 0-Read_Only | 只读 |  |  | Instant PUE of the device config table for the system.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.11.2 | hwSystemPue | PUE | PUE | 0-Read_Only | 只读 |  |  | PUE of the device config table for the system.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.1.1.1 | hwMonitorESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..32 | 0..32 | Monitor identity,Its unique value is bar code of main control board
1.3.6.1.4.1.2011.6.178.1.1.1.1.2 | hwMonitorName | Micro-module/Container name | 微模块名称/集装箱名称 | 0-Read_Only | 只读 | 0..50 | 0..50 | Monitor name, which users can configure, is used to specify a monitor. Otherwise, the configured character can not be any other languages except English.
1.3.6.1.4.1.2011.6.178.1.1.1.1.3 | hwMonitorIp | WAN_1 IP address | WAN_1 IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Monitor IP address, default value is 192.168.1.168. Users need to configure the monitor IP address.
1.3.6.1.4.1.2011.6.178.1.1.1.1.4 | hwMonitorNetmask | WAN_1 subnet mask | WAN_1 子网掩码 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Monitor netmask, default value is 255.255.255.0. Users need to configure the monitor netmask.
1.3.6.1.4.1.2011.6.178.1.1.1.1.5 | hwMonitorGateway | WAN_1 default gateway | WAN_1 默认网关 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Monitor gateway, default value is 192.168.1.1. Users need to configure the monitor gateway.
1.3.6.1.4.1.2011.6.178.1.1.1.1.6 | hwMonitorSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..25 | 0..25 | Monitor Software Version.
1.3.6.1.4.1.2011.6.178.1.1.1.1.7 | hwMonitorHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..4 | 0..4 | Monitor Hardware Version.
1.3.6.1.4.1.2011.6.178.1.1.1.1.8 | hwMonitorDO1AlarmConduct | DO1 normal status | DO1 正常触点状态 | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | [常闭=0]/[常开=1] | Do1 alarm conduct status. Value 1 indicates nc. Value 2 indicates no.
1.3.6.1.4.1.2011.6.178.1.1.1.1.9 | hwMonitorDO2AlarmConduct | DO2 normal status | DO2 正常触点状态 | 1-Read_Write | 读写 | nc(1), no(2), unknown(255) | [常闭=0]/[常开=1] | Do2 alarm conduct status. Value 1 indicates nc. Value 2 indicates no.
1.3.6.1.4.1.2011.6.178.1.1.1.1.10 | hwMonitorEquipAdd | Board software matching status | 单板软件匹配状态 | 1-Read_Write | 读写 | 0..20 | 0..20 | Monitor add equipment.String Type. Format: 'equip type index'-'slot number'-'port number'-'equip address'-'timeout'. For example,Adding UPS on port3 and Address1,wait for 5 Seconds, value is '1-0-3-1-5'. The 'equip type index' is: Value 1 indicates UPS. Value 3 indicates Temp/Humi Sensor. Value 7 indicates NetCol5000-A035. Value 8 indicates PDU8000. Value 9 indicates ABB ATS. Value 12 indicates Independent Deployment AI_DI Unit. Value 13 indicates Hydrogen Monitoring System. Value 14 indicates PD510 Meter. Value 15 indicates YaDa DC Meter. Value 16 indicates 48V DC Power Supply. Value 18 indicates NEW_AIRCON. Value 21 indicates NetCol5000-C030. Value 22 indicates NETCOL_REMOTER. Value 23 indicates PMAC615 Meter. Value 24 indicates PMAC625 Meter. Value 25 indicates SUNRISE-SCU-20K. Value 26 indicates PDU2000-M(C). Value 27 indicates Water Sensor. Value 28 indicates ENVICOOL-CRU Value 29 indicates PDU2000-M(H) Value 30 indicates PDU5000 Value 31 indicates ENVICOOL-CyberMate
1.3.6.1.4.1.2011.6.178.1.1.1.1.11 | hwMonitorDeleteComFailEquip | Delete device with communication failure | WAN_1 默认网关 | 1-Read_Write | 读写 | yes(1) | [是=0] | Delete communication fail equipment. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.1.1.13 | hwMonitorReleaseSoftwareVersion | Release Software Version | 系统软件版本 | 0-Read_Only | 只读 | 0..25 | 0..25 | The release software version of the monitor device.
1.3.6.1.4.1.2011.6.178.1.1.1.1.14 | hwMonitorReflashConfig | Reflash config | 复制配置到内存 | 0-Read_Only | 只读 | yes(1) | [是=0] | Copy configuration to flash Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.1.3 | hwNetPointTable | / | / | / | / | 1..31 | 1..31 | The Table of Net Point.
1.3.6.1.4.1.2011.6.178.1.1.1.3.1.1 | hwNetPointIndex | / | / | / | / | / | / | Index of Net Point 1 to 31.
1.3.6.1.4.1.2011.6.178.1.1.1.3.1.2 | hwNetPointName | IP device 1 | IP设备1 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Name of Net Point.
1.3.6.1.4.1.2011.6.178.1.1.1.3.1.3 | hwNetPointCheckEnable | Enable online detection IP device 1 | IP设备1 在线检测使能 | 1-Read_Write | 读写 | disable(1), enable(2), testing(3), unknown(255) | [禁止=0]/[使能=1]/[测试=2] | Set the status of the netpoint: value 1 indicates disable. value 2 indicates enable. Value 3 indicates testing.
1.3.6.1.4.1.2011.6.178.1.1.1.3.1.4 | hwNetPointState | IP device 1 status | IP设备1 状态 | 0-Read_Only | 只读 | offline(1), online(2), unknown(255) | [离线=0]/[在线=1] | the connect status of NetPoint. Value 1 indicates offline. Value 2 indicates online.
1.3.6.1.4.1.2011.6.178.1.1.1.3.1.5 | hwNetPointIp | IP device 1 address | IP设备1 地址 | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | the IP address of NoetPoint.
1.3.6.1.4.1.2011.6.178.1.1.1.4 | hwNetPointExtendTable | / | / | / | / | 117,123,129, | 117,123,129, | The Extended Table of Net Point.
1.3.6.1.4.1.2011.6.178.1.1.1.4.1 | hwNetPointExtend1Table | / | / | / | / | [118,122] | [118,122] | The Extended 1 Table of Net Point.
1.3.6.1.4.1.2011.6.178.1.1.1.4.1.1.1 | hwNetPointExtend1Index | / | / | / | / | 0 | 0 | Index of Net Point 32 to 62.
1.3.6.1.4.1.2011.6.178.1.1.1.4.1.1.2 | hwNetPointExtend1Name | IP device 32 | IP设备32 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Name of Net Point Extend1.
1.3.6.1.4.1.2011.6.178.1.1.1.4.1.1.3 | hwNetPointExtend1CheckEnable | Enable online detection IP device 32 | IP设备32 在线检测使能 | 1-Read_Write | 读写 | disable(1), enable(2), testing(3), unknown(255) | [禁止=0]/[使能=1]/[测试=2] | Set the status of the netpoint: value 1 indicates disable. value 2 indicates enable. Value 3 indicates testing.
1.3.6.1.4.1.2011.6.178.1.1.1.4.1.1.4 | hwNetPointExtend1State | IP device 33 status | IP设备32 状态 | 0-Read_Only | 只读 | offline(1), online(2), unknown(255) | [离线=0]/[在线=1] | the connect status of NetPoint. Value 1 indicates offline. Value 2 indicates online.
1.3.6.1.4.1.2011.6.178.1.1.1.4.1.1.5 | hwNetPointExtend1Ip | IP device 96 address | IP设备96 地址 | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | the IP address of NoetPoint.
1.3.6.1.4.1.2011.6.178.1.1.1.4.2 | hwNetPointExtend2Table | / | / | / | / | [118,122] | [118,122] | The Extended 1 Table of Net Point.
1.3.6.1.4.1.2011.6.178.1.1.1.4.2.1.1 | hwNetPointExtend2Index | / | / | / | / | 0 | 0 | Index of Net Point 32 to 62.
1.3.6.1.4.1.2011.6.178.1.1.1.4.2.1.2 | hwNetPointExtend2Name | IP device 63 | IP设备63 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Name of Net Point Extend1.
1.3.6.1.4.1.2011.6.178.1.1.1.4.2.1.3 | hwNetPointExtend2CheckEnable | Enable online detection IP device 63 | IP设备63 在线检测使能 | 1-Read_Write | 读写 | disable(1), enable(2), testing(3), unknown(255) | [禁止=0]/[使能=1]/[测试=2] | Set the status of the netpoint: value 1 indicates disable. value 2 indicates enable. Value 3 indicates testing.
1.3.6.1.4.1.2011.6.178.1.1.1.4.2.1.4 | hwNetPointExtend2State | IP device 63 status | IP设备63 状态 | 0-Read_Only | 只读 | offline(1), online(2), unknown(255) | [离线=0]/[在线=1] | the connect status of NetPoint. Value 1 indicates offline. Value 2 indicates online.
1.3.6.1.4.1.2011.6.178.1.1.1.4.2.1.5 | hwNetPointExtend2Ip | IP device 63 address | IP设备63 地址 | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | the IP address of NoetPoint.
1.3.6.1.4.1.2011.6.178.1.1.1.4.3 | hwNetPointExtend3Table | / | / | / | / | [118,122] | [118,122] | The Extended 1 Table of Net Point.
1.3.6.1.4.1.2011.6.178.1.1.1.4.3.1.1 | hwNetPointExtend3Index | / | / | / | / | 0 | 0 | Index of Net Point 32 to 62.
1.3.6.1.4.1.2011.6.178.1.1.1.4.3.1.2 | hwNetPointExtend3Name | IP device 30 | IP设备30 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Name of Net Point Extend1.
1.3.6.1.4.1.2011.6.178.1.1.1.4.3.1.3 | hwNetPointExtend3CheckEnable | Enable online detection IP device 30 | IP设备30 在线检测使能 | 1-Read_Write | 读写 | disable(1), enable(2), testing(3), unknown(255) | [禁止=0]/[使能=1]/[测试=2] | Set the status of the netpoint: value 1 indicates disable. value 2 indicates enable. Value 3 indicates testing.
1.3.6.1.4.1.2011.6.178.1.1.1.4.3.1.4 | hwNetPointExtend3State | IP device 30 status | IP设备30 状态 | 0-Read_Only | 只读 | offline(1), online(2), unknown(255) | [离线=0]/[在线=1] | the connect status of NetPoint. Value 1 indicates offline. Value 2 indicates online.
1.3.6.1.4.1.2011.6.178.1.1.1.4.3.1.5 | hwNetPointExtend3Ip | IP device 30 address | IP设备96 地址 | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | the IP address of NoetPoint.

## ATS
ATS
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.8.1 | OMD800 | ATS | ATS | / | / | / | / | ATS OMD800 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1 | hwOMD800RunningTable | / | / |  |  | / | / | The Running table of OMD800.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.1 | hwOMD800RunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the OMD800.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.2 | hwOMD800DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | the name of device.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.3 | hwOMD800CommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.4 | hwOMD800DefaultConfigOK | / | / | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | / | the default config flag. Value 1 indicates no. Value 2 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.5 | hwOMD800PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | the Port No. of Device.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.6 | hwOMD800ModbusAddr | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | the modbus Address of the device.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.7 | hwOMD800SoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | Device software version number. A string of characters.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.8 | hwOMD800ESN | ESN | ESN | 0-Read_Only | 只读 | 0..20 | 0..20 | ESN of the master device used for setting up a NetEco model. A string of characters.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.9 | hwOMD800LN1PowerStatus | LN1 power status | LN1电源状态 | 0-Read_Only | 只读 | voltagenormal(1), voltageIsZero(2), undervoltage(3), overvoltage(4), phasemissing(5), phasevolunbalance(6), phasesequenceerror(7), frequencyoutofrange(8), unknown(255) | [电压正常=1]/[电压为零=2]/[欠压=3]/[过压=4]/[缺相=5]/[相电压不平衡=6]/[相序错误=7]/[频率超出范围=8] | LN1 Power Status. Value 1 indicates VoltageNormal. Value 2 indicates VoltageIsZero. Value 3 indicates Undervoltage. Value 4 indicates Overvoltage. Value 5 indicates PhaseMissing. Value 6 indicates PhaseVolUnbalance. Value 7 indicates PhaseSequenceError. Value 8 indicates FrequencyOutOfRange.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.10 | hwOMD800LN2PowerStatus | LN2 power status | LN2电源状态 | 0-Read_Only | 只读 | voltagenormal(1), voltageIsZero(2), undervoltage(3), overvoltage(4), phasemissing(5), phasevolunbalance(6), phasesequenceerror(7), frequencyoutofrange(8), unknown(255) | [电压正常=1]/[电压为零=2]/[欠压=3]/[过压=4]/[缺相=5]/[相电压不平衡=6]/[相序错误=7]/[频率超出范围=8] | LN2 Power Status. Value 1 indicates VoltageNormal. Value 2 indicates VoltageIsZero. Value 3 indicates Undervoltage. Value 4 indicates Overvoltage. Value 5 indicates PhaseMissing. Value 6 indicates PhaseVolUnbalance. Value 7 indicates PhaseSequenceError. Value 8 indicates FrequencyOutOfRange.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.11 | hwOMD800SwitchStatus | Switch status | 开关状态 | 0-Read_Only | 只读 | noconversion(1), converting(2), converted(3), convertingBackTomain(4), convertfail(5), unknown(255) | [不需要转换=1]/[正在转换=2]/[转换结束=3]/[正在转换回主电路=4]/[转换失败=5] | Switch Status. Value 1 indicates NoConversion. Value 2 indicates Converting. Value 3 indicates Converted. Value 4 indicates ConvertingBackToMain. Value 5 indicates ConvertFail.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.12 | hwOMD800GeneratorStatus | Generator status | 发电机状态 | 0-Read_Only | 只读 | stop(1), run(2), unknown(255) | [停止=1]/[运行=2] | Generator Status. Value 1 indicates Stop. Value 2 indicates Run.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.13 | hwOMD800ChangeSwitchIStatus | Change switch I status | 转换开关I状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Change Switch I Status. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.14 | hwOMD800ChangeSwitchIIStatus | Change switch II status | 转换开关II状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Change Switch II Status. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.15 | hwOMD800SecLoadStatus | Secondary load status | 次要负载状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Sec. Load Status. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.16 | hwOMD800LN1Phase1Voltage | LN1 power phase 1 voltage | LN1电源L1相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | LN1 Phase 1 Voltage of the device OMD800. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.17 | hwOMD800LN1Phase2Voltage | LN1 power phase 2 voltage | LN1电源L2相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | LN1 Phase 2 Voltage of the device OMD800. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.18 | hwOMD800LN1Phase3Voltage | LN1 power phase 3 voltage | LN1电源L3相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | LN1 Phase 3 Voltage of the device OMD800. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.19 | hwOMD800LN2Phase1Voltage | LN2 power phase 1 voltage | LN2电源L1相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | LN2 Phase 1 Voltage of the device OMD800. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.20 | hwOMD800LN2Phase2Voltage | LN2 power phase 2 voltage | LN2电源L2相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | LN2 Phase 2 Voltage of the device OMD800. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.21 | hwOMD800LN2Phase3Voltage | LN2 power phase 3 voltage | LN2电源L3相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | LN2 Phase 3 Voltage of the device OMD800. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.22 | hwOMD800ControllerStatus | Controller status | 控制器状态 | 0-Read_Only | 只读 | automatic(1), manual(2), testingprogram(3), standby(4), unknown(255) | [自动=1]/[手动=2]/[测试程序=3]/[待机=4] | Controller Status. Value 1 indicates Automatic. Value 2 indicates Manual. Value 3 indicates Testing Program. Value 4 indicates Standby .
1.3.6.1.4.1.2011.6.178.1.1.8.1.1.1.100 | hwOMD800RunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The rowstatus of OMD800.
1.3.6.1.4.1.2011.6.178.1.1.8.1.2 | hwOMD800Running2Table | / | / |  |  | / | / | The Running 2 table of OMD800.
1.3.6.1.4.1.2011.6.178.1.1.8.1.2.1.1 | hwOMD800Running2Index | / | / | 0-Read_Only | 只读 | / | / | 2 Index of the device config table for the OMD800.
1.3.6.1.4.1.2011.6.178.1.1.8.1.2.1.2 | hwOMD800LN1Frequency | LN1 power frequency | LN1电源频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The inameLN1Frequency.Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.8.1.2.1.3 | hwOMD800LN2Frequency | LN2 power frequency | LN2电源频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The inameLN2Frequency.Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.8.1.2.1.4 | hwOMD800DetailModel | Detail model | 详细机型 | 1-Read_Write | 读写 | otmCD(1), atsZeroTwoTwo(2), unknown(255) | [OTM_C_D=1]/[ATS022=2] | Detail model of the device config table for the OMD800. Value 1 indicate otm_c_d Value 2 indicate ats022
1.3.6.1.4.1.2011.6.178.1.1.8.1.2.1.100 | hwOMD800Running2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The rowstatus of OMD800.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3 | hwOMD800RunningAndConfig3Table | / | / |  |  | / | / | The running and config table of OMD800.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.1 | hwOMD800RunningAndConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the OMD800.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.69 | hwATSOperatingMode8D | Operating mode | 工作模式 | 0-Read_Only | 只读 | local(1), remote(2), unknown(255) | [本地=1]/[远程=2] | Operating mode 8D of the device config table for the ATS. Value 1 indicate local Value 2 indicate remote
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.70 | hwATSDeviceStatus8D | Device status | 控制器状态 | 0-Read_Only | 只读 | autoMatic(1), manual(2), testSequence(3), standby(4), unknown(255) | [自动=1]/[手动=2]/[测试程序=3]/[待机=4] | Device status 8D of the device config table for the ATS. Value 1 indicate automatic Value 2 indicate manual Value 3 indicate testsequence Value 4 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.71 | hwATSLn1Phases8D | LN1 phases | LN1电源相数 | 0-Read_Only | 只读 | onePhase(1), threePhaseWithOutN(2), threePhaseWithN(3), unknown(255) | [单相=1]/[三相=2]/[具有N极的三相=3] | LN1 phases 8D of the device config table for the ATS. Value 1 indicate 1phase Value 2 indicate 3phaseswithoutn Value 3 indicate 3phaseswithn
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.72 | hwATSRatedVoltage8D | Rated voltage | 额定电压 | 0-Read_Only | 只读 | oneHundredOrFiftySeven(1), oneHundredAndFifteenOrSixtySix(2), oneHundredAndTwentyOrSeventy(3), twoHundredAndEightOrOneHundredAndTwenty(4), twoHundredAndTwentyOrOneHundredAndTwentySeven(5), twoHundredAndThirtyOrOneHundredAndThirtyTwo(6), twoHundredAndfortyOrOneHundredAndThirtyEigth(7), twoHundredAndSeventySevenOrOneHundredAndsixty(8), threeHundredAndfortySevenOrTwoHundred(9), threeHundredAndeightyOrTwoHundredAndTwenty(10), fourHundredOrTwoHundredAndThirty(11), fourHundredAndFifteenOrTwoHundredAndForty(12), fourHundredAndFortyOrTwoHundredAndForty(13), fourHundredAndeightyOrTwoHundredAndSeventySeven(14), unknown(255) | [100/57V=1]/[115/66V=2]/[120/70V=3]/[208/120V=4]/[220/127V=5]/[230/132V=6]/[240/138V=7]/[277/160V=8]/[347/200V=9]/[380/220V=10]/[400/230V=11]/[415/240V=12]/[440/254V=13]/[480/277V=14] | Rated voltage 8D of the device config table for the ATS. Value 1 indicate 100/57V Value 2 indicate 115/66V Value 3 indicate 120/70V Value 4 indicate 208/120V Value 5 indicate 220/127V Value 6 indicate 230/132V Value 7 indicate 240/138V Value 8 indicate 277/160V Value 9 indicate 347/200V Value 10 indicate 380/220V Value 11 indicate 400/230V Value 12 indicate 415/240V Value 13 indicate 440/254V Value 14 indicate 480/277V
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.73 | hwATSRatedFrequency8D | Rated frequency | 电源频率 | 0-Read_Only | 只读 | fiftyHertz(1), sixtyHertz(2), unknown(255) | [50Hz=1]/[60Hz=2] | Rated frequency 8D of the device config table for the ATS. Value 1 indicate 50hz Value 2 indicate 60hz
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.74 | hwATSSecondaryLoad8D | Secondary load | 次要负载 | 0-Read_Only | 只读 | notUsed(1), openingOnly(2), openingAndClosing(3), openingPulse(4), openingOrClosingPulse(5), unknown(255) | [不使用=1]/[仅断开=2]/[断开和接通=3]/[仅断开脉冲=4]/[断开和闭合脉冲=5] | Secondary load 8D of the device config table for the ATS. Value 1 indicate notused Value 2 indicate openingonly Value 3 indicate openingandclosing Value 4 indicate openingpulse Value 5 indicate opening/closingpulse
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.75 | hwATSGeneratorUsage8D | Generator usage | 发电机应用 | 0-Read_Only | 只读 | noGenerator(1), generatorInUse(2), unknown(255) | [不使用发电机=1]/[使用发电机=2] | Generator usage 8D of the device config table for the ATS. Value 1 indicate nogenerator Value 2 indicate generatorinuse
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.76 | hwATSLinePriority8D | Line priority | 电源优先级 | 0-Read_Only | 只读 | noPriority(1), lineIAndswitch1(2), lineIIAndswitch2(3), unknown(255) | [互为备用=1]/[电源1（LN1）开关I=2]/[电源2（LN2）开关II=3] | Line priority 8D of the device config table for the ATS. Value 1 indicate nopriority Value 2 indicate linei-switch1 Value 3 indicate lineii-switch2
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.77 | hwATSExtVtPresent8D | Ext vt present | 外部变压器 | 0-Read_Only | 只读 | notUsed(1), present(2), unknown(255) | [不使用=1]/[使用=2] | Ext vt present 8D of the device config table for the ATS. Value 1 indicate notused Value 2 indicate present
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.78 | hwATSExtVtPrimary8D | Ext vt primary | 外部变压器原边电压 | 0-Read_Only | 只读 | oneHundredOrFiftySeven(1), oneHundredAndFifteenOrSixtySix(2), oneHundredAndTwentyOrSeventy(3), twoHundredAndEightOrOneHundredAndTwenty(4), twoHundredAndTwentyOrOneHundredAndTwentySeven(5), twoHundredAndThirtyOrOneHundredAndThirtyTwo(6), twoHundredAndfortyOrOneHundredAndThirtyEigth(7), twoHundredAndSeventySevenOrOneHundredAndsixty(8), threeHundredAndfortySevenOrTwoHundred(9), threeHundredAndeightyOrTwoHundredAndTwenty(10), fourHundredOrTwoHundredAndThirty(11), fourHundredAndFifteenOrTwoHundredAndForty(12), fourHundredAndFortyOrTwoHundredAndForty(13), fourHundredAndeightyOrTwoHundredAndSeventySeven(14), fiveHundredOrTwoHundredAndEightyEight(15), fiveHundredAndFiftyOrThreeHundredSeventeen(16), sixHundredOrThreeHundredAndFortyseven(17), sixHundredAndSixtyOrThreeHundredAndeighty(18), sixHundredAndNinetyOrFourHundred(19), nineHundredAndTenOrFiveHundredAndTewntyFive(20), nineHundredAndfiftyOrFiveHundredAndFifty(21), oneThousandOrFiveHundredAndSeventySeven(22), oneThousandAndOneHundredFiftyOrSixHundredAndSixty(23), unknown(255) | [100/57V=1]/[115/66V=2]/[120/70V=3]/[208/120V=4]/[220/127V=5]/[230/132V=6]/[240/138V=7]/[277/160V=8]/[347/200V=9]/[380/220V=10]/[400/230V=11]/[415/240V=12]/[440/254V=13]/[480/277V=14]/[500/288V=15]/[550/317V=16]/[600/347V=17]/[660/380V=18]/[690/400V=19]/[910/525V=20]/[950/550V=21]/[1000/577V=22]/[1150/660V=23] | Ext vt primary 8D of the device config table for the ATS. Value 1 indicate 100/57V Value 2 indicate 115/66V Value 3 indicate 120/70V Value 4 indicate 208/120V Value 5 indicate 220/127V Value 6 indicate 230/132V Value 7 indicate 240/138V Value 8 indicate 277/160V Value 9 indicate 347/200V Value 10 indicate 380/220V Value 11 indicate 400/230V Value 12 indicate 415/240V Value 13 indicate 440/254V Value 14 indicate 480/277V Value 15 indicate 500/288V Value 16 indicate 550/317V Value 17 indicate 600/347V Value 18 indicate 660/380V Value 19 indicate 690/400V Value 20 indicate 910/525V Value 21 indicate 950/550V Value 22 indicate 1000/577V Value 23 indicate 1150/660V
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.79 | hwATSExtVtSecondary8D | Ext vt secondary | 外部变压器副边电压 | 0-Read_Only | 只读 | oneHundredOrFiftySeven(1), oneHundredAndFifteenOrSixtySix(2), oneHundredAndTwentyOrSeventy(3), twoHundredAndEightOrOneHundredAndTwenty(4), twoHundredAndTwentyOrOneHundredAndTwentySeven(5), twoHundredAndThirtyOrOneHundredAndThirtyTwo(6), twoHundredAndfortyOrOneHundredAndThirtyEigth(7), twoHundredAndSeventySevenOrOneHundredAndsixty(8), threeHundredAndfortySevenOrTwoHundred(9), threeHundredAndeightyOrTwoHundredAndTwenty(10), fourHundredOrTwoHundredAndThirty(11), fourHundredAndFifteenOrTwoHundredAndForty(12), fourHundredAndFortyOrTwoHundredAndForty(13), fourHundredAndeightyOrTwoHundredAndSeventySeven(14), unknown(255) | [100/57V=1]/[115/66V=2]/[120/70V=3]/[208/120V=4]/[220/127V=5]/[230/132V=6]/[240/138V=7]/[277/160V=8]/[347/200V=9]/[380/220V=10]/[400/230V=11]/[415/240V=12]/[440/254V=13]/[480/277V=14] | Ext vt secondary 8D of the device config table for the ATS. Value 1 indicate 100/57V Value 2 indicate 115/66V Value 3 indicate 120/70V Value 4 indicate 208/120V Value 5 indicate 220/127V Value 6 indicate 230/132V Value 7 indicate 240/138V Value 8 indicate 277/160V Value 9 indicate 347/200V Value 10 indicate 380/220V Value 11 indicate 400/230V Value 12 indicate 415/240V Value 13 indicate 440/254V Value 14 indicate 480/277V
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.80 | hwATSLn2Phases8D | LN2 phases | LN2电源相数 | 0-Read_Only | 只读 | onePhase(1), threePhaseWithoutN(2), threePhaseWithN(3), unknown(255) | [单相=1]/[三相=2]/[具有N极的三相=3] | LN2 phases 8D of the device config table for the ATS. Value 1 indicate 1phase Value 2 indicate 3phaseswithoutn Value 3 indicate 3phaseswithn
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.81 | hwATSManualBackSwitching8D | Manual back switching | 返回常用方式 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [自投自复=1]/[自投不自复=2] | Manual back switching 8D of the device config table for the ATS. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.82 | hwATSGeneratorShutdown8D | Generator shutdown | 关闭发电机 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [不关闭发电机=1]/[关闭发电机=2] | Generator shutdown 8D of the device config table for the ATS. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.83 | hwATSAutoSwitchToO8D | Auto switch to o | 自动至双分位置O | 0-Read_Only | 只读 | off(1), lnOneToo(2), lnTwoToo(3), lnOneAndlnTwoToo(4), unknown(255) | [关闭=1]/[LN1至O=2]/[LN2至O=3]/[LN1&LN2至O=4] | Auto switch to o 8D of the device config table for the ATS. Value 1 indicate off Value 2 indicate ln1too Value 3 indicate ln2too Value 4 indicate ln1&ln2too
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.84 | hwATSSwitchType8D | Switch type | 转换开关类型 | 0-Read_Only | 只读 | autoMaticotmcd(1), motorizedotmc(2), unknown(255) | [自动转换开关 OTM_C_D=1]/[电动转换开关 OTM_C=2] | Switch type 8D of the device config table for the ATS. Value 1 indicate automaticotm_c_d Value 2 indicate motorizedotm_c
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.85 | hwATSVoltThresholdLn1Min8D | Volt threshold LN1 min | LN1电源电压欠压阈值 | 0-Read_Only | 只读 | 5..30 | 5..30 | Volt threshold LN1 min 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.86 | hwATSVoltThresholdLn1Max8D | Volt threshold LN1 max | LN1电源电压过压阈值 | 0-Read_Only | 只读 | 5..30 | 5..30 | Volt threshold LN1 max 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.87 | hwATSVoltThresholdLn2Min8D | Volt threshold LN2 min | LN2电源电压欠压阈值 | 0-Read_Only | 只读 | 5..30 | 5..30 | Volt threshold LN2 min 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.88 | hwATSVoltThresholdLn2Max8D | Volt threshold LN2 max | LN2电源电压过压阈值 | 0-Read_Only | 只读 | 5..30 | 5..30 | Volt threshold LN2 max 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.89 | hwATSVoltHysteresisLn1Min8D | Volt hysteresis LN1 min | LN1电源电压欠压迟滞 | 0-Read_Only | 只读 | 4..29 | 4..29 | Volt hysteresis LN1 min 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.90 | hwATSVoltHysteresisLn1Max8D | Volt hysteresis LN1 max | LN1电源电压过压迟滞 | 0-Read_Only | 只读 | 4..29 | 4..29 | Volt hysteresis LN1 max 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.91 | hwATSVoltHysteresisLn2Min8D | Volt hysteresis LN2 min | LN2电源电压欠压迟滞 | 0-Read_Only | 只读 | 4..29 | 4..29 | Volt hysteresis LN2 min 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.92 | hwATSVoltHysteresisLn2Max8D | Volt hysteresis LN2 max | LN2电源电压过压迟滞 | 0-Read_Only | 只读 | 4..29 | 4..29 | Volt hysteresis LN2 max 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.93 | hwATSFreqThresholdLn1Min8D | Freq threshold LN1 min | LN1电源频率低频阈值 | 0-Read_Only | 只读 | 1..10 | 1..10 | Freq threshold LN1 min 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.94 | hwATSFreqThresholdLn1Max8D | Freq threshold LN1 max | LN1电源频率高频阈值 | 0-Read_Only | 只读 | 1..10 | 1..10 | Freq threshold LN1 max 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.95 | hwATSFreqThresholdLn2Min8D | Freq threshold LN2 min | LN2电源频率低频阈值 | 0-Read_Only | 只读 | 1..10 | 1..10 | Freq threshold LN2 min 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.96 | hwATSFreqThresholdLn2Max8D | Freq threshold LN2 max | LN2电源频率高频阈值 | 0-Read_Only | 只读 | 1..10 | 1..10 | Freq threshold LN2 max 8D of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.97 | hwATSFreqHysteresisLn1Min8D | Freq hysteresis LN1 min | LN1电源频率低频迟滞 | 0-Read_Only | 只读 | 8..98 | 8..98 | Freq hysteresis LN1 min 8D of the device config table for the ATS.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.98 | hwATSFreqHysteresisLn1Max8D | Freq hysteresis LN1 max | LN1电源频率高频迟滞 | 0-Read_Only | 只读 | 8..98 | 8..98 | Freq hysteresis LN1 max 8D of the device config table for the ATS.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.99 | hwATSFreqHysteresisLn2Min8D | Freq hysteresis LN2 min | LN2电源频率低频迟滞 | 0-Read_Only | 只读 | 8..98 | 8..98 | Freq hysteresis LN2 min 8D of the device config table for the ATS.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.100 | hwATSFreqHysteresisLn2Max8D | Freq hysteresis LN2 max | LN2电源频率高频迟滞 | 0-Read_Only | 只读 | 8..98 | 8..98 | Freq hysteresis LN2 max 8D of the device config table for the ATS.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.101 | hwATSDelayTs8D | Delay TS | 自投延时 TS | 0-Read_Only | 只读 | 0..60 | 0..60 | Delay TS 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.102 | hwATSDelayDs8D | Delay DS | 闭合II 延时 DS | 0-Read_Only | 只读 | 0..60 | 0..60 | Delay DS 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.103 | hwATSDelayTbs8D | Delay TBS | 自复延时 TBS | 0-Read_Only | 只读 | 0..5400 | 0..5400 | Delay TBS 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.104 | hwATSDelayDbs8D | Delay DBS | 闭合 I 延时 DBS | 0-Read_Only | 只读 | 0..60 | 0..60 | Delay DBS 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.105 | hwATSDelayGs8D | Delay GS | 发电机停止延时 GS | 0-Read_Only | 只读 | 0..1800 | 0..1800 | Delay GS 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.106 | hwATSDelayTt8D | Delay TT | 转换延时 TT | 0-Read_Only | 只读 | 0..600 | 0..600 | Delay TT 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.107 | hwATSLcdTimer8D | LCD timer | LCD背光定时 | 0-Read_Only | 只读 | 0..3600 | 0..3600 | LCD timer 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.108 | hwATSDelayTp8D | Delay TP | 预转换信号I-II延时TP | 0-Read_Only | 只读 | 0..120 | 0..120 | Delay TP 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.109 | hwATSDelayTbp8D | Delay TBP | 预转换信号II-I延时TBP | 0-Read_Only | 只读 | 0..120 | 0..120 | Delay TBP 8D of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.110 | hwATSOperatingMode022 | Operating mode | 工作模式 | 0-Read_Only | 只读 | local(1), remote(2), unknown(255) | [本地=1]/[远程=2] | Operating mode 022 of the device config table for the ATS. Value 1 indicate local Value 2 indicate remote
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.111 | hwATSDeviceStatus022 | Device status | 装置状态 | 0-Read_Only | 只读 | autoMatic(1), manual(2), testSequence(3), standby(4), generatorTest(5), unknown(255) | [自动=1]/[手动=2]/[测试程序=3]/[待机=4]/[发电机测试=5] | Device status 022 of the device config table for the ATS. Value 1 indicate automatic Value 2 indicate manual Value 3 indicate testsequence Value 4 indicate standby Value 5 indicate generatortest
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.112 | hwATSLine1Configuration022 | Line 1 configuration | LN1电源设置 | 0-Read_Only | 只读 | onePhase(1), threePhaseWithoutn(2), threePhaseWithn(3), unknown(255) | [单相=1]/[三相三线=2]/[三相四线=3] | Line 1 configuration 022 of the device config table for the ATS. Value 1 indicate 1phase Value 2 indicate 3phaseswithoutn Value 3 indicate 3phaseswithn
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.113 | hwATSNominalVoltage022 | Nominal voltage | 名义输入电压 | 0-Read_Only | 只读 | oneHundredOrFiftySeven(1), oneHundredAndFifteenOrSixtySix(2), oneHundredAndTwentyOrSeventy(3), twoHundredAndEightOrOneHundredAndTwenty(4), twoHundredAndTwentyOrOneHundredAndTwentySeven(5), twoHundredAndThirtyOrOneHundredAndThirtyTwo(6), twoHundredAndfortyOrOneHundredAndThirtyEigth(7), twoHundredAndSeventySevenOrOneHundredAndsixty(8), threeHundredAndfortySevenOrTwoHundred(9), threeHundredAndeightyOrTwoHundredAndTwenty(10), fourHundredOrTwoHundredAndThirty(11), fourHundredAndFifteenOrTwoHundredAndForty(12), fourHundredAndFortyOrTwoHundredAndForty(13), fourHundredAndeightyOrTwoHundredAndSeventySeven(14), unknown(255) | [100/57V=1]/[115/66V=2]/[120/70V=3]/[208/120V=4]/[220/127V=5]/[230/132V=6]/[240/138V=7]/[277/160V=8]/[347/200V=9]/[380/220V=10]/[400/230V=11]/[415/240V=12]/[440/254V=13]/[480/277V=14] | Nominal voltage 022 of the device config table for the ATS. Value 1 indicate Value 2 indicate Value 3 indicate Value 4 indicate Value 5 indicate Value 6 indicate Value 7 indicate Value 8 indicate Value 9 indicate Value 10 indicate Value 11 indicate Value 12 indicate Value 13 indicate Value 14 indicate Value 15 indicate Value 16 indicate Value 17 indicate Value 18 indicate Value 19 indicate Value 20 indicate Value 21 indicate Value 22 indicate Value 23 indicate Value 24 indicate Value 25 indicate Value 26 indicate Value 27 indicate Value 28 indicate
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.114 | hwATSFrequency022 | Frequency | 电源频率 | 0-Read_Only | 只读 | sixteenHertz(1), fiftyHertz(2), sixtyHertz(3), fourHundredHertz(4), unknown(255) | [16Hz=1]/[50Hz=2]/[60Hz=3]/[400Hz=4] | Frequency 022 of the device config table for the ATS. Value 1 indicate 16hz Value 2 indicate 50hz Value 3 indicate 60hz Value 4 indicate 400hz
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.115 | hwATSProtectionDevices022 | Protection devices | 保护设备 | 0-Read_Only | 只读 | cbs(1), bustie(2), nplBustie(3), nplFeederOpenAndClose(4), nplFeederOnlyOpen(5), unknown(255) | [双电源=1]/[双电源带母联=2]/[母联式次要负载=3]/[次要负载控制:断开和闭合=4]/[次要负载控制:仅断开=5] | Protection devices 022 of the device config table for the ATS. Value 1 indicate cbs Value 2 indicate bustie Value 3 indicate nplbustie Value 4 indicate nplfeederopen&close Value 5 indicate nplfeederonlyopen
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.116 | hwATSGenratorUsage022 | Genrator usage | 发电机使用 | 0-Read_Only | 只读 | notInUse(1), inUse(2), unknown(255) | [无发电机=1]/[有发电机=2] | Genrator usage 022 of the device config table for the ATS. Value 1 indicate notinuse Value 2 indicate inuse
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.117 | hwATSLinePriority022 | Line priority | 电源优先级 | 0-Read_Only | 只读 | noPriority(1), lineIAndSwitchOne(2), lineIIAndSwitchTwo(3), unknown(255) | [互为备用=1]/[电源1（LN1）开关I=2]/[电源2（LN2）开关II=3] | Line priority 022 of the device config table for the ATS. Value 1 indicate nopriority Value 2 indicate linei-switch1 Value 3 indicate lineii-switch2
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.118 | hwATSExtVtPresent022 | Ext vt present | 外部变压器 | 0-Read_Only | 只读 | notUsed(1), present(2), unknown(255) | [不使用=1]/[使用=2] | Ext vt present 022 of the device config table for the ATS. Value 1 indicate notused Value 2 indicate present
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.119 | hwATSExtVtPrimary022 | Ext vt primary | 外部变压器原边电压 | 0-Read_Only | 只读 | oneHundredOrFiftySeven(1), oneHundredAndFifteenOrSixtySix(2), oneHundredAndTwentyOrSeventy(3), twoHundredAndEightOrOneHundredAndTwenty(4), twoHundredAndTwentyOrOneHundredAndTwentySeven(5), twoHundredAndThirtyOrOneHundredAndThirtyTwo(6), twoHundredAndfortyOrOneHundredAndThirtyEigth(7), twoHundredAndSeventySevenOrOneHundredAndsixty(8), threeHundredAndfortySevenOrTwoHundred(9), threeHundredAndeightyOrTwoHundredAndTwenty(10), fourHundredOrTwoHundredAndThirty(11), fourHundredAndFifteenOrTwoHundredAndForty(12), fourHundredAndFortyOrTwoHundredAndForty(13), fourHundredAndeightyOrTwoHundredAndSeventySeven(14), fiveHundredOrTwoHundredAndEightyEight(15), fiveHundredAndFiftyOrThreeHundredSeventeen(16), sixHundredOrThreeHundredAndFortyseven(17), sixHundredAndSixtyOrThreeHundredAndeighty(18), sixHundredAndNinetyOrFourHundred(19), nineHundredAndTenOrFiveHundredAndTewntyFive(20), nineHundredAndfiftyOrFiveHundredAndFifty(21), oneThousandOrFiveHundredAndSeventySeven(22), oneThousandAndOneHundredFiftyOrSixHundredAndSixty(23), unknown(255) | [100/57V=1]/[115/66V=2]/[120/70V=3]/[208/120V=4]/[220/127V=5]/[230/132V=6]/[240/138V=7]/[277/160V=8]/[347/200V=9]/[380/220V=10]/[400/230V=11]/[415/240V=12]/[440/254V=13]/[480/277V=14]/[500/288V=15]/[550/317V=16]/[600/347V=17]/[660/380V=18]/[690/400V=19]/[910/525V=20]/[950/550V=21]/[1000/577V=22]/[1150/660V=23] | Ext vt primary 022 of the device config table for the ATS. Value 1 indicate 100/57V Value 2 indicate 115/66V Value 3 indicate 120/70V Value 4 indicate 208/120V Value 5 indicate 220/127V Value 6 indicate 230/132V Value 7 indicate 240/138V Value 8 indicate 277/160V Value 9 indicate 347/200V Value 10 indicate 380/220V Value 11 indicate 400/230V Value 12 indicate 415/240V Value 13 indicate 440/254V Value 14 indicate 480/277V Value 15 indicate 500/288V Value 16 indicate 550/317V Value 17 indicate 600/347V Value 18 indicate 660/380V Value 19 indicate 690/400V Value 20 indicate 910/525V Value 21 indicate 950/550V Value 22 indicate 1000/577V Value 23 indicate 1150/660V
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.120 | hwATSExtVtSecondary022 | Ext vt secondary | 外部变压器副边电压 | 0-Read_Only | 只读 | oneHundredOrFiftySeven(1), oneHundredAndFifteenOrSixtySix(2), oneHundredAndTwentyOrSeventy(3), twoHundredAndEightOrOneHundredAndTwenty(4), twoHundredAndTwentyOrOneHundredAndTwentySeven(5), twoHundredAndThirtyOrOneHundredAndThirtyTwo(6), twoHundredAndfortyOrOneHundredAndThirtyEigth(7), twoHundredAndSeventySevenOrOneHundredAndsixty(8), threeHundredAndfortySevenOrTwoHundred(9), threeHundredAndeightyOrTwoHundredAndTwenty(10), fourHundredOrTwoHundredAndThirty(11), fourHundredAndFifteenOrTwoHundredAndForty(12), fourHundredAndFortyOrTwoHundredAndForty(13), fourHundredAndeightyOrTwoHundredAndSeventySeven(14), unknown(255) | [100/57V=1]/[115/66V=2]/[120/70V=3]/[208/120V=4]/[220/127V=5]/[230/132V=6]/[240/138V=7]/[277/160V=8]/[347/200V=9]/[380/220V=10]/[400/230V=11]/[415/240V=12]/[440/254V=13]/[480/277V=14] | Ext vt secondary 022 of the device config table for the ATS. Value 1 indicate 100/57V Value 2 indicate 115/66V Value 3 indicate 120/70V Value 4 indicate 208/120V Value 5 indicate 220/127V Value 6 indicate 230/132V Value 7 indicate 240/138V Value 8 indicate 277/160V Value 9 indicate 347/200V Value 10 indicate 380/220V Value 11 indicate 400/230V Value 12 indicate 415/240V Value 13 indicate 440/254V Value 14 indicate 480/277V
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.121 | hwATSLine2Configuration022 | Line 2 configuration | LN2电源设置 | 0-Read_Only | 只读 | onePhase(1), threePhaseWithoutN(2), threePhaseWithN(3), unknown(255) | [单相=1]/[三相三线=2]/[三相四线=3] | Line 2 configuration 022 of the device config table for the ATS. Value 1 indicate 1phase Value 2 indicate 3phaseswithoutn Value 3 indicate 3phaseswithn
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.122 | hwATSManualBackSwitching022 | Manual back switching | 返回常用方式 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [自投自复=1]/[自投不自复=2] | Manual back switching 022 of the device config table for the ATS. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.123 | hwATSThresholdVmin022 | Threshold Vmin | 欠压阀值设置 | 0-Read_Only | 只读 | 5..30 | 5..30 | Threshold Vmin 022 of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.124 | hwATSThresholdVmax022 | Threshold Vmax | 过压阀值设置 | 0-Read_Only | 只读 | 5..30 | 5..30 | Threshold Vmax 022 of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.125 | hwATSThresholdFmin022 | Threshold Fmin | 低频阀值设置 | 0-Read_Only | 只读 | 1..10 | 1..10 | Threshold Fmin 022 of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.126 | hwATSThresholdFmax022 | Threshold Fmax | 高频阀值设置 | 0-Read_Only | 只读 | 1..10 | 1..10 | Threshold Fmax 022 of the device config table for the ATS.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.127 | hwATSDelayTs022 | Delay TS | 延时TS | 0-Read_Only | 只读 | 0..30 | 0..30 | Delay TS 022 of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.128 | hwATSDelayTce022 | Delay TCE | 延时TCE | 0-Read_Only | 只读 | 0..60 | 0..60 | Delay TCE 022 of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.129 | hwATSDelayTbs022 | Delay TBS | 延时TBS | 0-Read_Only | 只读 | 0..59 | 0..59 | Delay TBS 022 of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.130 | hwATSDelayTcn022 | Delay TCN | 延时TCN | 0-Read_Only | 只读 | 0..60 | 0..60 | Delay TCN 022 of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.131 | hwATSDelayTgoff022 | Delay TGOFF | 发电机停止延时 | 0-Read_Only | 只读 | 0..59 | 0..59 | Delay TGOFF 022 of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.132 | hwATSDelayTc022 | Delay TC | 延时TC | 0-Read_Only | 只读 | 0..60 | 0..60 | Delay TC 022 of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.133 | hwATSDelayLcdTimer022 | Delay LCD timer | LCD背光定时 | 0-Read_Only | 只读 | 0..59 | 0..59 | Delay LCD timer 022 of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.134 | hwATSDelayTl022 | Delay TL | 延时TL | 0-Read_Only | 只读 | 0..60 | 0..60 | Delay TL 022 of the device config table for the ATS.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.1.3.1.300 | hwOMD800RunningAndConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of OMD800.

## Smart ETH Gateway
智能ETH插座
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.15 | SmartETHJack | Smart ETH Gateway | 智能ETH插座 | / | / | / | / | The SmartJack Equipment.
1.3.6.1.4.1.2011.6.178.1.1.15.1 | hwSmartETHJackRunning1Table | / | / |  |  | / | / | The running table of Huawei SmartJack Equipment.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.1 | hwSmartETHJackRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SmartJack.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.2 | hwSmartETHJackCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.3 | hwSmartETHJackEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.4 | hwSmartETHJackMACAddress | / | / | 0-Read_Only | 只读 | 1..28 | / | MACAddress of the device running table for the SmartJack.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.5 | hwSmartETHJackSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | SoftWareVersion of the device running table for the SmartJack.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.6 | hwSmartETHJackHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | hardWareVersion of the device running table for the SmartJack.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.7 | hwSmartETHJackLine1POESwitchState | / | / | 0-Read_Only | 只读 | poweron(1), poweroff(2), unknown(255) | / | Line 1 POE Switch state the device running table for the SmartJack. Value 1 indicates Power On. Value 2 indicates Power Off.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.8 | hwSmartETHJackLine2POESwitchState | / | / | 0-Read_Only | 只读 | poweron(1), poweroff(2), unknown(255) | / | Line 1 POE Switch state the device running table for the SmartJack. Value 1 indicates Power On. Value 2 indicates Power Off.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.9 | hwSmartETHJackLine3POESwitchState | / | / | 0-Read_Only | 只读 | poweron(1), poweroff(2), unknown(255) | / | Line 1 POE Switch state the device running table for the SmartJack. Value 1 indicates Power On. Value 2 indicates Power Off.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.10 | hwSmartETHJackLine4POESwitchState | / | / | 0-Read_Only | 只读 | poweron(1), poweroff(2), unknown(255) | / | Line 1 POE Switch state the device running table for the SmartJack. Value 1 indicates Power On. Value 2 indicates Power Off.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.11 | hwSmartETHJackCLine1POELinkState | / | / | 0-Read_Only | 只读 | link(1), broken(2), unknown(255) | / | Line 1 POE link state the device running table for the SmartJack. Value 1 indicates Link. Value 2 indicates Broken.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.12 | hwSmartETHJackCLine2POELinkState | / | / | 0-Read_Only | 只读 | link(1), broken(2), unknown(255) | / | Line 1 POE link state the device running table for the SmartJack. Value 1 indicates Link. Value 2 indicates Broken.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.13 | hwSmartETHJackCLine3POELinkState | / | / | 0-Read_Only | 只读 | link(1), broken(2), unknown(255) | / | Line 1 POE link state the device running table for the SmartJack. Value 1 indicates Link. Value 2 indicates Broken.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.14 | hwSmartETHJackCLine4POELinkState | / | / | 0-Read_Only | 只读 | link(1), broken(2), unknown(255) | / | Line 1 POE link state the device running table for the SmartJack. Value 1 indicates Link. Value 2 indicates Broken.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.15 | hwSmartETHJackLine1FELinkState | / | / | 0-Read_Only | 只读 | link(1), broken(2), unknown(255) | / | Line 1 FE link state the device running table for the SmartJack. Value 1 indicates Link. Value 2 indicates Broken.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.16 | hwSmartETHJackLine2FELinkState | / | / | 0-Read_Only | 只读 | link(1), broken(2), unknown(255) | / | Line 1 FE link state the device running table for the SmartJack. Value 1 indicates Link. Value 2 indicates Broken.
1.3.6.1.4.1.2011.6.178.1.1.15.1.1.100 | hwSmartETHJack1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the SmartJack.
1.3.6.1.4.1.2011.6.178.1.1.15.2 | hwSmartETHJackRunning2Table | / | / |  |  | / | / | The running table of Huawei SmartJack Equipment.
1.3.6.1.4.1.2011.6.178.1.1.15.2.1.1 | hwSmartETHJackRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SmartJack.
1.3.6.1.4.1.2011.6.178.1.1.15.2.1.2 | hwSmartETHJackelabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | Elabel of the device running table for the SmartJack.
1.3.6.1.4.1.2011.6.178.1.1.15.2.1.3 | hwSmartETHJackDevicename | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The Device name of SmartJack Equipment.
1.3.6.1.4.1.2011.6.178.1.1.15.2.1.100 | hwSmartETHJack2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the SmartJack.

## WiFi Model
WiFi模块
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.16 | WIFIModel |  |  | / | / | / | / | WIFIModel Equipments.
1.3.6.1.4.1.2011.6.178.1.1.16.1 | hwWIFIModelCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.

## Cabinet Collector
机柜采集器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.17 | ITCabinet | Cabinet Collector | 机柜采集器 | / | / | / | / | The ITCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.17.1 | hwITCabinetRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei ITCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.1 | hwITCabinetRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.2 | hwITCabinetPortCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.4 | hwITCabinetEquipESN | / | / | 0-Read_Only | 只读 | 0..31 | / | The ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.5 | hwITCabinetPortMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MACAddress of the device running table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.6 | hwITCabinetSoftVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | SoftWareVersion of the device running table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.7 | hwITCabinetHardVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | HardWareVersion of the device running table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.8 | hwITCabinetLine1NtcTemperature | Upper-front temperature(NTC1) | 前上温度(NTC1) | 0-Read_Only | 只读 | -500..850 | -500..850 | Line 1 Ntc Temperature of the device running table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.9 | hwITCabinetLine2NtcTemperature | Middle-front temperature(NTC2) | 前中温度(NTC2) | 0-Read_Only | 只读 | -500..850 | -500..850 | Line 2 Ntc Temperature of the device running table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.10 | hwITCabinetLine3NtcTemperature | Lower-front temperature(NTC3) | 前下温度(NTC3) | 0-Read_Only | 只读 | -500..850 | -500..850 | Line 3 Ntc Temperature of the device running table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.11 | hwITCabinetLine4NtcTemperature | Upper-rear temperature(NTC4) | 后上温度(NTC4) | 0-Read_Only | 只读 | -500..850 | -500..850 | Line 4 Ntc Temperature of the device running table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.12 | hwITCabinetLine5NtcTemperature | Middle-rear temperature(NTC5) | 后中温度(NTC5) | 0-Read_Only | 只读 | -500..850 | -500..850 | Line 5 Ntc Temperature of the device running table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.13 | hwITCabinetLine6NtcTemperature | Lower-rear temperature(NTC6) | 后下温度(NTC6) | 0-Read_Only | 只读 | -500..850 | -500..850 | Line 6 Ntc Temperature of the device running table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.14 | hwITCabinetDoState | DO status | DO状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | The Do State of Device. Value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.15 | hwITCabinetCom1PowerSwitchState | COM1 power switch status | COM1供电开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | The Com 1 Power Switch State of Device. Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.16 | hwITCabinetCom2PowerSwitchState | COM2 power switch status | COM2供电开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | The Com 2 Power Switch State of Device. Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.17 | hwITCabinetAidi1DIStatus | Front door status(AI/DI_1) | 前门门磁状态(AI/DI_1) | 0-Read_Only | 只读 | dooropen(1), doorclose(2), unknown(255) | [开门=1]/[关门=2] | Aidi 1 DI Status. Value 1 indicates door open. Value 2 indicates door close.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.18 | hwITCabinetAidi2DIStatus | Rear door status(AI/DI_2) | 后门门磁状态(AI/DI_2) | 0-Read_Only | 只读 | dooropen(1), doorclose(2), unknown(255) | [开门=1]/[关门=2] | Aidi 2 DI Status. Value 1 indicates door open. Value 2 indicates door close.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.19 | hwITCabinetCom1Baudrate | COM1 baud rate | COM1的波特率 | 1-Read_Write | 读写 | baud2400(1), baud4800(2), baud9600(3), baud19200(4), baud115200(5), unknown(255) | [2400=1]/[4800=2]/[9600=3]/[19200=4]/[115200=5] | COM1 Baudrate. Value 1 indicates 2400. Value 2 indicates 4800. Value 3 indicates 9600. Value 4 indicates 19200. Value 5 indicates 115200.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.20 | hwITCabinetCom1Checkbit | COM1 parity | COM1的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无校验=1]/[奇校验=2]/[偶校验=3] | COM1 Checkbit. Value 1 indicates none. Value 2 indicates odd. Value 3 indicates even.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.21 | hwITCabinetCom1Databit | COM1 data bit | COM1的数据位 | 1-Read_Write | 读写 | baud8(1) | [8位=1] | COM1 Databit. Value 1 indicates 8.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.22 | hwITCabinetCom1Stopbit | COM1 stop bit | COM1的停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM1 stopbit of the device config table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.23 | hwITCabinetCom1SplitFrameTime | COM1 split frame time | COM1断帧时间 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | COM1 split frame time of the device config table for the ITCabinet. SigUnitInfo:ms
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.24 | hwITCabinetCom1PowerSupplyState | COM1 power control | COM1供电控制 | 1-Read_Write | 读写 | poweron(1), poweroff(2), unknown(255) | [供电=1]/[断电=2] | COM1 Power supply state. Value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.25 | hwITCabinetCom2Baudrate | COM2 baud rate | COM2的波特率 | 1-Read_Write | 读写 | baud2400(1), baud4800(2), baud9600(3), baud19200(4), baud115200(5), unknown(255) | [2400=1]/[4800=2]/[9600=3]/[19200=4]/[115200=5] | COM2 Baudrate. Value 1 indicates 2400. Value 2 indicates 4800. Value 3 indicates 9600. Value 4 indicates 19200. Value 5 indicates 115200.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.26 | hwITCabinetCom2Checkbit | COM2 parity | COM2的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无校验=1]/[奇校验=2]/[偶校验=3] | COM2 Checkbit. Value 1 indicates none. Value 2 indicates odd. Value 3 indicates even.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.27 | hwITCabinetCom2Databit | COM2 data bit | COM2的数据位 | 1-Read_Write | 读写 | baud8(1) | [8位=1] | COM2 Databit. Value 1 indicates 8.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.28 | hwITCabinetCom2Stopbit | COM2 stop bit | COM2的停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM2 stopbit of the device config table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.29 | hwITCabinetCom2SplitFrameTime | COM2 split frame time | COM2断帧时间 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | COM2 split frame time of the device config table for the ITCabinet. SigUnitInfo:ms
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.30 | hwITCabinetCom2PowerSupplyState | COM2 power control | COM2供电控制 | 1-Read_Write | 读写 | poweron(1), poweroff(2), unknown(255) | [供电=1]/[断电=2] | COM2 Power supply state. Value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.31 | hwITCabinetCom3Baudrate | COM3 baud rate | COM3的波特率 | 1-Read_Write | 读写 | baud2400(1), baud4800(2), baud9600(3), baud19200(4), baud115200(5), unknown(255) | [2400=1]/[4800=2]/[9600=3]/[19200=4]/[115200=5] | COM3 Baudrate. Value 1 indicates 2400. Value 2 indicates 4800. Value 3 indicates 9600. Value 4 indicates 19200. Value 5 indicates 115200.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.32 | hwITCabinetCom3Checkbit | COM3 parity | COM3的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无校验=1]/[奇校验=2]/[偶校验=3] | COM3 Checkbit. Value 1 indicates none. Value 2 indicates odd. Value 3 indicates even.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.33 | hwITCabinetCom3Databit | COM3 data bit | COM3的数据位 | 1-Read_Write | 读写 | baud8(1) | [8位=1] | COM3 Databit. Value 1 indicates 8.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.34 | hwITCabinetCom3Stopbit | COM3 stop bit | COM3的停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM3 stopbit of the device config table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.35 | hwITCabinetCom3SplitFrameTime | COM3 split frame time | COM3断帧时间 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | COM3 split frame time of the device config table for the ITCabinet. SigUnitInfo:ms
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.36 | hwITCabinetCom4Baudrate | COM4 baud rate | COM4的波特率 | 1-Read_Write | 读写 | baud2400(1), baud4800(2), baud9600(3), baud19200(4), baud115200(5), unknown(255) | [2400=1]/[4800=2]/[9600=3]/[19200=4]/[115200=5] | COM4 Baudrate. Value 1 indicates 2400. Value 2 indicates 4800. Value 3 indicates 9600. Value 4 indicates 19200. Value 5 indicates 115200.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.37 | hwITCabinetCom4Checkbit | COM4 parity | COM4的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无校验=1]/[奇校验=2]/[偶校验=3] | COM4 Checkbit. Value 1 indicates none. Value 2 indicates odd. Value 3 indicates even.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.38 | hwITCabinetCom4Databit | COM4 data bit | COM4的数据位 | 1-Read_Write | 读写 | baud8(1) | [8位=1] | COM4 Databit. Value 1 indicates 8.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.39 | hwITCabinetCom4Stopbit | COM4 stop bit | COM4的停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM4 stopbit of the device config table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.40 | hwITCabinetCom4SplitFrameTime | COM4 split frame time | COM4断帧时间 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | COM4 split frame time of the device config table for the ITCabinet. SigUnitInfo:ms
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.41 | hwITCabinetDoorCloseTimeout | Door open timeout duration | 门未关超时时间 | 1-Read_Write | 读写 | 1..60 | 1..60 | Door Close Timeout of the device config table for the ITCabinet. SigUnitInfo:min
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.42 | hwITCabinetNtc1HighTemperatureThreshold | Upper-front overtemperature alarm threshold(NTC1) | 前上高温告警门限(NTC1) | 1-Read_Write | 读写 | 200..800 | 200..800 | NTC1 High Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.43 | hwITCabinetNtc2HighTemperatureThreshold | Middle-front overtemperature alarm threshold(NTC2) | 前中高温告警门限(NTC2) | 1-Read_Write | 读写 | 200..800 | 200..800 | NTC2 High Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.44 | hwITCabinetNtc3HighTemperatureThreshold | Lower-front overtemperature alarm threshold(NTC3) | 前下高温告警门限(NTC3) | 1-Read_Write | 读写 | 200..800 | 200..800 | NTC3 High Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.45 | hwITCabinetNtc4HighTemperatureThreshold | Upper-rear overtemperature alarm threshold(NTC4) | 后上高温告警门限(NTC4) | 1-Read_Write | 读写 | 200..800 | 200..800 | NTC4 High Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.46 | hwITCabinetNtc5HighTemperatureThreshold | Middle-rear overtemperature alarm threshold(NTC5) | 后中高温告警门限(NTC5) | 1-Read_Write | 读写 | 200..800 | 200..800 | NT51 High Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.47 | hwITCabinetNtc6HighTemperatureThreshold | Lower-rear overtemperature alarm threshold(NTC6) | 后下高温告警门限(NTC6) | 1-Read_Write | 读写 | 200..800 | 200..800 | NT61 High Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.48 | hwITCabinetNtc1LowTemperatureThreshold | Upper-front undertemperature alarm threshold(NTC1) | 前上低温告警门限(NTC1) | 1-Read_Write | 读写 | -190..200 | -190..200 | NTC1 Low Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.49 | hwITCabinetNtc2LowTemperatureThreshold | Middle-front undertemperature alarm threshold(NTC2) | 前中低温告警门限(NTC2) | 1-Read_Write | 读写 | -190..200 | -190..200 | NTC2 Low Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.50 | hwITCabinetNtc3LowTemperatureThreshold | Lower-front undertemperature alarm threshold(NTC3) | 前下低温告警门限(NTC3) | 1-Read_Write | 读写 | -190..200 | -190..200 | NTC3 Low Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.51 | hwITCabinetNtc4LowTemperatureThreshold | Upper-rear undertemperature alarm threshold(NTC4) | 后上低温告警门限(NTC4) | 1-Read_Write | 读写 | -190..200 | -190..200 | NTC4 Low Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.52 | hwITCabinetNtc5LowTemperatureThreshold | Middle-rear undertemperature alarm threshold(NTC5) | 后中低温告警门限(NTC5) | 1-Read_Write | 读写 | -190..200 | -190..200 | NTC5 Low Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.53 | hwITCabinetNtc6LowTemperatureThreshold | Lower-rear undertemperature alarm threshold(NTC6) | 后下低温告警门限(NTC6) | 1-Read_Write | 读写 | -190..200 | -190..200 | NTC6 Low Temperature Threshold of the device config table for the ITCabinet. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.54 | hwITCabinetDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of the device config table for the ITCabinet.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.55 | hwITCabinetAidi1Enable | AI/DI_1 sensor | AI/DI_1 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AIDI1 Enable. Value 1 indicates disable. Value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.56 | hwITCabinetAidi2Enable | AI/DI_2 sensor | AI/DI_2 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AIDI2 Enable. Value 1 indicates disable. Value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.17.1.1.100 | hwITCabinetRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the ITCabinet.

## E-LOCK
机柜电子锁
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.18 | ELock | E-LOCK | 机柜电子锁 | / | / | / | / | The ELock Equipment.
1.3.6.1.4.1.2011.6.178.1.1.18.1 | hwELockRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei ELock Equipment.
1.3.6.1.4.1.2011.6.178.1.1.18.1.1.1 | hwELockRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Elock.
1.3.6.1.4.1.2011.6.178.1.1.18.1.1.2 | hwELockPortCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.18.1.1.3 | hwELockPortMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device.
1.3.6.1.4.1.2011.6.178.1.1.18.1.1.4 | hwELockLockStatus | Lock status | 锁状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [开=1]/[关=2] | The Lock Status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.18.1.1.5 | hwELockOpenELock | Unlock remotely | 远程开锁 | 1-Read_Write | 读写 | yes(1) | [是=1] | Open Elock. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.18.1.1.6 | hwELockDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of the device running table for the Elock.
1.3.6.1.4.1.2011.6.178.1.1.18.1.1.7 | hwELockSyncAuthState | / | / | 1-Read_Write | 读写 | notsynchronized(1), synchronizationinprogress(2), synchronizationcompleted(3), synchronizationfailed(4), unknown(255) | / | Elock Sync Auth State. Value 1 indicates not synchronized. Value 2 indicates synchronization in progress. Value 3 indicates synchronization completed. Value 4 indicates synchronization failed.
1.3.6.1.4.1.2011.6.178.1.1.18.1.1.100 | hwELockRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the Elock.

## Skylight Actuator
天窗执行器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.19 | SkylightActuator | Skylight Actuator | 天窗执行器 | / | / | / | / | The Skylight Actuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.19.1 | hwSkylightActuatorRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei Skylight Actuator..
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.1 | hwSkylightActuatorRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Skylight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.2 | hwSkylightActuatorCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.3 | hwSkylightActuatorElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | the E-label of Device.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.4 | hwSkylightActuatorESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.5 | hwSkylightActuatorMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MACAddress of the device running table for the Skylight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.6 | hwSkylightActuatorSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | SoftWareVersion of the device running table for the Skylight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.7 | hwSkylightActuatorHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | hardWareVersion of the device running table for the Skylight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.8 | hwSkylightActuatorMagneticLockPowerState | Magnetic lock power state | 磁力锁供电状态 | 0-Read_Only | 只读 | poweron(1), poweroff(2), unknown(255) | [供电=1]/[断电=2] | The Magnetic Lock PowerState: value 1 indicates power on, value 2 indicates poweroff,
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.9 | hwSkylightActuatorWirelessCommStatus | / | / | 0-Read_Only | 只读 | abnormal1(1), abnormal2(2), normal(3), abnormal3(4), unknown(255) | / | The Wireless Communication Status. value 1 indicates commfail, value 2 indicates commfail, value 3 indicates commok, value 4 indicates commfail,
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.10 | hwSkylightActuatorPOECommStatus | / | / | 0-Read_Only | 只读 | abnormal1(1), abnormal2(2), normal(3), abnormal3(4), unstabitily(5), unknown(255) | / | The POE Communication Status. value 1 indicates commfail, value 2 indicates commfail, value 3 indicates commok, value 4 indicates commfail, value 5 indicates unstabitily,
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.11 | hwSkylightActuatorDI1AlarmLevel | / | / | 1-Read_Write | 读写 | lowvoltagealarm(1), highvoltagealarm(2), unknown(255) | / | The DI1 Alarm Level: value 1 indicates low voltage alarm value 2 indicates high voltage alarm
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.12 | hwSkylightActuatorDI2AlarmLevel | / | / | 1-Read_Write | 读写 | lowvoltagealarm(1), highvoltagealarm(2), unknown(255) | / | The DI2 Alarm Level: value 1 indicates low voltage alarm value 2 indicates high voltage alarm
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.13 | hwSkylightActuatorDI3AlarmLevel | / | / | 1-Read_Write | 读写 | lowvoltagealarm(1), highvoltagealarm(2), unknown(255) | / | The DI3 Alarm Level: value 1 indicates low voltage alarm value 2 indicates high voltage alarm
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.14 | hwSkylightActuatorRemoteSkylightOpening | Remote open scuttle | 远程开窗 | 1-Read_Write | 读写 | yes(1) | [是=1] | The Remote Skylight Opening: value 1 indicates YES.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.15 | hwSkylightActuatorDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The device name of the Skylight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.19.1.1.100 | hwSkylightActuatorRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the Skylight Actuator config table.

## WiFi Converter
WiFi转换器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.20 | WiFiConverter | WiFi Converter | WiFi转换器 | / | / | / | / | The WiFi Converter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.20.1 | hwWiFiConverterRunningAndConfigTable | / | / |  |  | / | / | The running table of WiFi Converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.1 | hwWiFiConverterRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the WiFi Converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.2 | hwWiFiConverterCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.3 | hwWiFiConverterElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | the E-label of Device.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.4 | hwWiFiConverterESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.5 | hwWiFiConverterMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MACAddress of the device running table for the WiFi Converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.6 | hwWiFiConverterSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | SoftWareVersion of the device running table for the WiFi Converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.7 | hwWiFiConverterHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | HardWareVersion of the device running table for the WiFi Converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.8 | hwWiFiConverterAccessDeviceQty | Access device qty. | 接入设备个数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Access Device Qty of WiFi Converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.9 | hwWiFiConverterDevice1MAC | Device 1 MAC | 设备1 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device1.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.10 | hwWiFiConverterDevice2MAC | Device 2 MAC | 设备2 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device2.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.11 | hwWiFiConverterDevice3MAC | Device 3 MAC | 设备3 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device3.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.12 | hwWiFiConverterDevice4MAC | Device 4 MAC | 设备4 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device4.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.13 | hwWiFiConverterDevice5MAC | Device 5 MAC | 设备5 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device5.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.14 | hwWiFiConverterDevice6MAC | Device 6 MAC | 设备6 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device6.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.15 | hwWiFiConverterDevice7MAC | Device 7 MAC | 设备7 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device7.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.16 | hwWiFiConverterDevice8MAC | Device 8 MAC | 设备8 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device8.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.17 | hwWiFiConverterDevice9MAC | Device 9 MAC | 设备9 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device9.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.18 | hwWiFiConverterDevice10MAC | Device 10 MAC | 设备10 MAC | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device10.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.19 | hwWiFiConverterWPSCommand | / | / | 1-Read_Write | 读写 | yes(1) | / | The WPS Command: value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.20 | hwWiFiConverterSSID | SSID | SSID | 0-Read_Only | 只读 | 0..65 | 0..65 | The SSID of the wifi converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.21 | hwWiFiConverterPassword | Password | 加密密码 | 0-Read_Only | 只读 | 0..32 | 0..32 | The password of the wifi converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.22 | hwWiFiConverterEnable | Wifi AP enable | 热点使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The WiFi Converter Equipment enable value: value 1 indicates disable. value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.23 | hwWiFiConverterDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The device name of the wifi converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.24 | hwWiFiConverterIsChangePassword | / | / | 1-Read_Write | 读写 | notchanged(1), changed(2), unknown(255) | / | Is Change the password of the wifi converter: value 1 indicates not changed. value 2 indicates changed.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.25 | hwWiFiConverterSettingChannel | / | / | 1-Read_Write | 读写 | 0..13 | / | The setting channel of wifi converter.
1.3.6.1.4.1.2011.6.178.1.1.20.1.1.100 | hwWiFiConverterRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the WiFi Converter config table.

## Access Actuator
门禁执行器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.21 | AccessActuator | Access Actuator | 门禁执行器 | / | / | / | / | The Access Actuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.21.1 | hwAccessActuatorRunningAndConfigTable | / | / |  |  | / | / | The running table of Access Actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.1 | hwAccessActuatorRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Access Actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.2 | hwAccessActuatorCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.3 | hwAccessActuatorESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.4 | hwAccessActuatorMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MACAddress of the device running table for the Access Actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.5 | hwAccessActuatorSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | SoftWareVersion of the device running table for the Access Actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.6 | hwAccessActuatorHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | HardWareVersion of the device running table for the Access Actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.7 | hwAccessActuatorDoorState | Door state | 门状态 | 0-Read_Only | 只读 | doorclose(1), dooropen(2), unknown(255) | [门关=1]/[门开=2] | The Access Actuator State: value 1 indicates door close. value 2 indicates door open.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.8 | hwAccessActuatorMagneticLockPortState | Magnetic lock port state | 端口状态 | 0-Read_Only | 只读 | poweredon(1), poweredoff(2), unknown(255) | [供电=1]/[断电=2] | The Access Actuator State: value 1 indicates powered on. value 2 indicates powered off.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.9 | hwAccessActuatorCommAddress | Communication address | 通信地址 | 0-Read_Only | 只读 | 0..15 | 0..15 | The communication address of Access Actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.10 | hwAccessActuatorWirelessCommStatus | / | / | 0-Read_Only | 只读 | abnormal1(1), abnormal2(2), normal(3), abnormal3(4), unknown(255) | / | The Wireless Communication Status. value 1 indicates commfail. value 2 indicates commfail. value 3 indicates commok. value 4 indicates commfail.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.11 | hwAccessActuatorPOECommStatus | / | / | 0-Read_Only | 只读 | abnormal1(1), abnormal2(2), normal(3), abnormal3(4), unstabitily(5), unknown(255) | / | The POE Communication Status. value 1 indicates commfail. value 2 indicates commfail. value 3 indicates commok. value 4 indicates commfail. value 5 indicates unstabitily.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.12 | hwAccessActuatorMagneticLockOpenLevel | Magnetic lock open level | 门磁开电平 | 1-Read_Write | 读写 | lowlevelavail(1), highlevelavail(2), unknown(255) | [低电平有效=1]/[高电平有效=2] | The Magnetic Lock Open Level: value 1 indicates low level avail. value 2 indicates high level avail.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.13 | hwAccessActuatorButtonLogic | External button DI state logic | 外部按钮DI状态逻辑 | 1-Read_Write | 读写 | lowlevelavail(1), highlevelavail(2), unknown(255) | [低电平有效=1]/[高电平有效=2] | The ButtonLogic: value 1 indicates low level avail. value 2 indicates high level avail.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.14 | hwAccessActuatorFireLogic | Fire fighting DI state logic | 消防联动DI状态逻辑 | 1-Read_Write | 读写 | lowlevelavail(1), highlevelavail(2), unknown(255) | [低电平有效=1]/[高电平有效=2] | The Fire Logic: value 1 indicates low level avail. value 2 indicates high level avail.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.15 | hwAccessActuatorRemoteDoorOpening | Remote door opening | 远程开门 | 1-Read_Write | 读写 | yes(1) | [是=1] | The Remote Door Opening: value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.16 | hwAccessActuatorDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The device name of the access actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.17 | hwAccessActuatorCOMBaudRate | COM baud rate | COM的波特率 | 1-Read_Write | 读写 | baud2400(1), baud4800(2), baud9600(3), baud19200(4), baud38400(5), baud115200(6), unknown(255) | [2400=1]/[4800=2]/[9600=3]/[19200=4]/[38400=5]/[115200=6] | The COM BuadRate: value 1 indicates the com buad rate 2400 bps. value 2 indicates the com buad rate 4800 bps. value 3 indicates the com buad rate 9600 bps. value 4 indicates the com buad rate 19200 bps. value 5 indicates the com buad rate 38400 bps. value 6 indicates the com buad rate 115200 bps.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.18 | hwAccessActuatorCOMParity | COM check bit | COM的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无校验=1]/[奇校验=2]/[偶校验=3] | The access actuator COM Parity: value 1 indicates the com parity is none value 2 indicates the com parity is odd value 3 indicates the com parity is even
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.19 | hwAccessActuatorCOMDataBit | COM data bit | COM的数据位 | 1-Read_Write | 读写 | eightbit(1) | [8位=1] | Setting the COM data bit access actuator: value 1 indicates 8 bit.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.20 | hwAccessActuatorCOMStopBit | COM stop bit | COM的停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | Setting the stop bit of access actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.21 | hwAccessActuatorCOMSplitFrameTime | COM split frame time | COM口断帧时间 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | Setting the COM frame internal time of access actuator time. SigUnitInfo:ms
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.22 | hwAccessActuatorCardreader1RemovedConfigElectricLevel | Logical level configuration for reader 1 removed | 读卡器1被拆告警逻辑电平配置 | 1-Read_Write | 读写 | lowvoltagealarm(1), highvoltagealarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | The Cardreader1 Removed Config Electric Level: value 1 indicates low voltage alarm. value 2 indicates high voltage alarm.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.23 | hwAccessActuatorCardreader2RemovedConfigElectricLevel | Logical level configuration for reader 2 removed | 读卡器2被拆告警逻辑电平配置 | 1-Read_Write | 读写 | lowvoltagealarm(1), highvoltagealarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | The Cardreader2 Removed Config Electric Level: value 1 indicates low voltage alarm. value 2 indicates high voltage alarm.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.30 | hwAccessActuatorDoorNum | Number of doors | 门数量 | 1-Read_Write | 读写 | 0..10 | 0..10 | Door Num of access actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.31 | hwAccessActuatorDoorChannel | Door No. | 门通道 | 1-Read_Write | 读写 | 1..10 | 1..10 | Door Channel of access actuator.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.32 | hwAccessActuatorRFZEnable | RF_Z enable | RF_Z使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | RF_Z enable of access actuator: value 1 indicates RF_Z disable. value 2 indicates RF_Z enable.
1.3.6.1.4.1.2011.6.178.1.1.21.1.1.100 | hwAccessActuatorRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the Access Actuator config table.

## ETH Converter
ETH转换器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.22 | ETHConverter | ETH Converter | ETH转换器 | / | / | / | / | The ETH Converter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.22.1 | hwETHConverterRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei ETH Converter.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.1 | hwETHConverterRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the ETH Converter.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.2 | hwETHConverterCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.3 | hwETHConverterElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | the E-label of Device.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.4 | hwETHConverterESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.5 | hwETHConverterMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MACAddress of the device running table for the ETH Converter.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.6 | hwETHConverterSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | SoftWareVersion of the device running table for the ETH Converter.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.7 | hwETHConverterHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | hardWareVersion of the device running table for the ETH Converter.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.9 | hwETHConverterCOMBaudRate | COM baud rate | COM 波特率 | 1-Read_Write | 读写 | baud2400(1), baud4800(2), baud9600(3), baud19200(4), baud115200(5), unknown(255) | [2400=1]/[4800=2]/[9600=3]/[19200=4]/[115200=5] | The ETH Converter COM BuadRate: value 1 indicates the com buad rate 2400 bps. value 2 indicates the com buad rate 4800 bps. value 3 indicates the com buad rate 9600 bps. value 4 indicates the com buad rate 19200 bps. value 5 indicates the com buad rate 115200 bps.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.10 | hwETHConverterCOMParity | COM parity | COM 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | The ETH Converter COM Parity: value 1 indicates the com parity is none value 2 indicates the com parity is odd value 3 indicates the com parity is even
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.11 | hwETHConverterCOMDataBit | COM data bit | COM 数据位 | 1-Read_Write | 读写 | eightbit(1) | [8位=1] | Setting the COM data bit ETH Converter: value 1 indicates 8 bit.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.12 | hwETHConverterCOMStopBit | COM stop bit | COM 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | Setting the stop bit of ETH Converter.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.13 | hwETHConverterCOMFrameInternalTime | COM frame internal time | COM 断帧时间 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | Setting the COM frame internal time of ETH Converter time. SigUnitInfo:ms
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.14 | hwETHConverterCANBaudRateSetting | CAN baud rate setting | CAN口波特率设置 | 1-Read_Write | 读写 | 10..1024 | 10..1024 | Setting the CAN baud rate . SigUnitInfo:kbps
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.16 | hwETHConverterDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Setting the device name of the ETH Converter.
1.3.6.1.4.1.2011.6.178.1.1.22.1.1.100 | hwETHConverterRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of ETH Converter config table.

## Multi-Func Sensor
多功能传感器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.23 | MultiFuncSensor | Multi-Func Sensor | 多功能传感器 | / | / | / | / | The Multi-Func Sensor Equipment.
1.3.6.1.4.1.2011.6.178.1.1.23.1 | hwMultiFuncSensorRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei Multi-Func Sensor.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.1 | hwMultiFuncSensorRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Multi-Func Sensor.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.2 | hwMultiFuncSensorCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.3 | hwMultiFuncSensorElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | the E-label of Device.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.4 | hwMultiFuncSensorESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.5 | hwMultiFuncSensorMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MACAddress of the device running table for the Multi-Func Sensor.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.6 | hwMultiFuncSensorSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | SoftWareVersion of the device running table for the Multi-Func Sensor.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.7 | hwMultiFuncSensorHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | hardWareVersion of the device running table for the Multi-Func Sensor.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.8 | hwMultiFuncSensorTemperature | Temperature | 温度 | 0-Read_Only | 只读 | -400..850 | -400..850 | The temperature of the Multi-Func Sensor. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.9 | hwMultiFuncSensorHumidity | Humidity | 湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | The humidity of the Multi-Func Sensor. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.10 | hwMultiFuncSensorWirelessCommStatus | / | / | 0-Read_Only | 只读 | abnormal1(1), abnormal2(2), normal(3), abnormal3(4), unknown(255) | / | The Wireless Communication Status of the Multi-Func Sensor: value 1 indicates commfail, value 2 indicates commfail, value 3 indicates commok, value 4 indicates commfail,
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.11 | hwMultiFuncSensorPOECommStatus | / | / | 0-Read_Only | 只读 | abnormal1(1), abnormal2(2), normal(3), abnormal3(4), unstabitily(5), unknown(255) | / | The POE Communication Status of the Multi-Func Sensor: value 1 indicates commfail, value 2 indicates commfail, value 3 indicates commok, value 4 indicates commfail, value 5 indicates unstabitily,
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.12 | hwMultiFuncSensorHighTemperatureAlarmThreshold | High temperature alarm threshold | 高温告警门限 | 1-Read_Write | 读写 | 200..850 | 200..850 | Setting the High Temperature Alarm Threshold of the Multi-Func Sensor. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.13 | hwMultiFuncSensorLowTemperatureAlarmThreshold | Low temperature alarm threshold | 低温告警门限 | 1-Read_Write | 读写 | -400..190 | -400..190 | Setting the Low Temperature Alarm Threshold of the Multi-Func Sensor. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.14 | hwMultiFuncSensorHighHumidityAlarmThreshold | High humidity alarm threshold | 高湿告警门限 | 1-Read_Write | 读写 | 50..100 | 50..100 | Setting the High Humidity Alarm Threshold of the Multi-Func Sensor. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.15 | hwMultiFuncSensorLowHumidityAlarmThreshold | Low humidity alarm threshold | 低湿告警门限 | 1-Read_Write | 读写 | 0..40 | 0..40 | Setting the Low Humidity Alarm Threshold of the Multi-Func Sensor. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.16 | hwMultiFuncSensorSmokeEnable | Smoke enable | 烟雾使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The Multi-Func Sensor Smoke Enable: value 1 indicates disable. value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.17 | hwMultiFuncSensorInfraredEnable | Infrared enable | 红外使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The Multi-Func Sensor Infrared Enable: value 1 indicates disable. value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.18 | hwMultiFuncSensorTempEnable | Temp enable | 温湿度使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The Multi-Func Sensor TempEnable: value 1 indicates disable. value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.19 | hwMultiFuncSensorDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The device name of the Multi-Func Sensor.
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.20 | hwMultiFuncSensorSmokeSensorStatus | Smoke sensor status | 烟雾传感器状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | The smoke sensor status of the Multi-Func Sensor: value 1 indicates normal, value 2 indicates alarm,
1.3.6.1.4.1.2011.6.178.1.1.23.1.1.100 | hwMultiFuncSensorRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the Multi-Func Sensor config table.

## AC Actuator
交流执行器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.24 | AcActuator | AC Actuator | 交流执行器 | / | / | / | / | The AcActuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.24.1 | hwAcActuatorRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei AcActuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.1 | hwAcActuatorRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the AcActuator.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.2 | hwAcActuatorCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.3 | hwAcActuatorEquipElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 1..2048 | 1..2048 | the Elabel of Device.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.4 | hwAcActuatorEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 1..31 | 1..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.5 | hwAcActuatorMACAddress | MAC | MAC地址 | 0-Read_Only | 只读 | 1..28 | 1..28 | MAC Address of the device running table for the AcActuator.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.6 | hwAcActuatorSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Software Version of the device running table for the AcActuator.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.7 | hwAcActuatorHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Hardware Version of the device running table for the AcActuator.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.8 | hwAcActuatorInfraredState | / | / | 0-Read_Only | 只读 | unattended(1), attended(2), unknown(255) | / | Infrared State of the device running table for the AcActuator. Value 1 indicates unattended. Value 2 indicates attended.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.9 | hwAcActuatorLine1SwitchState | Switch 1 status | 第1路开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Line 1 Switch State of the device running table for the AcActuator. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.10 | hwAcActuatorLine2SwitchState | Switch 2 status | 第2路开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Line 2 Switch State of the device running table for the AcActuator. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.11 | hwAcActuatorLoadCurrent | Load current | 负载电流 | 0-Read_Only | 只读 | 0..200 | 0..200 | Load Currentof the device running table for the AcActuator. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.12 | hwAcActuatorLoadVoltage | Load voltage | 负载电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Load Voltage of the device running table for the AcActuator. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.13 | hwAcActuatorLoadPower | Load power | 负载功率 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Load Power of the device running table for the AcActuator. Multiple:10. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.14 | hwAcActuatorSwitchState | / | / | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | / | Switch State of the device running table for the AcActuator. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.15 | hwAcActuatorRelay1LifePercent | Relay 1 life | 继电器1寿命 | 0-Read_Only | 只读 | 0..100 | 0..100 | Relay 1 Life Percent of the device running table for the AcActuator. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.16 | hwAcActuatorRelay2LifePercent | Relay 2 life | 继电器2寿命 | 0-Read_Only | 只读 | 0..100 | 0..100 | Relay 1 Life Percent of the device running table for the AcActuator. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.17 | hwAcActuatorOvercurrentAlarmThreshold | Overcurrent alarm threshold | 电流过流告警门限 | 1-Read_Write | 读写 | 0..100 | 0..100 | Overcurrent Alarm Threshold of the device config table for the AcActuator. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.18 | hwAcActuatorRelayLifePreAlarmThreshold | Relay life pre alarm threshold | 继电器寿命预告警门限 | 1-Read_Write | 读写 | 0..100 | 0..100 | Relay Life Pre Alarm Threshold of the device config table for the AcActuator. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.19 | hwAcActuatorRelayLifeAlarmThreshold | Relay life alarm threshold | 继电器寿命告警门限 | 1-Read_Write | 读写 | 0..100 | 0..100 | Relay Life Alarm Threshold of the device config table for the AcActuator. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.20 | hwAcActuatorLinkage | / | / | 1-Read_Write | 读写 | nonLinkages(1), linkages(2), unknown(255) | / | Set linkage. Value 1 indicates non linkages. Value 2 indicates linkages.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.21 | hwAcActuatorLine1Linkage | Route 1 control mode | 第1路控制模式 | 1-Read_Write | 读写 | none(1), light(2), unknown(255) | [无=1]/[照明=2] | Line 1 linkage. Value 1 indicates none. Value 2 indicates light. Value 3 indicates PAD charing.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.22 | hwAcActuatorLine2Linkage | Route 2 control mode | 第2路控制模式 | 1-Read_Write | 读写 | none(1), padCharing(2), unknown(255) | [无=1]/[PAD充电=2] | Line 2 linkage. Value 1 indicates none. Value 2 indicates light. Value 3 indicates PAD charing.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.23 | hwAcActuatorLightModel | Set light mode | 照明控制模式 | 1-Read_Write | 读写 | automaticMode(1), manualMode(2), unknown(255) | [自动=1]/[手动=2] | Set light model. Value 1 indicates automatic mode. Value 2 indicates manual mode.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.24 | hwAcActuatorDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of the device config table for the AcActuator.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.25 | hwAcActuatorPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..5 | 1..5 | the Port No of Device.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.26 | hwAcActuatorModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | the Modbus Address of Device.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.30 | hwAcActuatorLightcontrol | Light control | 开关灯控制 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关=1]/[开=2] | Light control. Value 1 indicates OFF. Value 2 indicates ON.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.31 | hwAcActuatorInputMode | Input mode | 接入方式 | 0-Read_Only | 只读 | zigbee(1), rtu(2), unknown(255) | [Modbus_Zigbee=1]/[Modbus_RTU=2] | Inut mode. Value 1 indicates Modbus Zigbee. Value 2 indicates Modbus RTU.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.32 | hwACActuatorPadBatteryLevelThresholdToStartCharging | PAD battery level threshold to start charging | PAD低电量充电阈值 | 1-Read_Write | 读写 | 30..50 | 30..50 | PAD battery level threshold to start charging of the device config table for the AC Actuator.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.33 | hwACActuatorPadBatteryLevelThresholdToStopCharging | PAD battery level threshold to stop charging | PAD高电量停止充电阈值 | 1-Read_Write | 读写 | 60..75 | 60..75 | PAD battery level threshold to stop charging of the device config table for the AC Actuator.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.24.1.1.100 | hwAcActuatoRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the AcActuator.

## T H Sensor
温湿度传感器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.25 | TempHum | T/H Sensor | 温湿度传感器 | / | / | / | / | The TempHum Equipment.
1.3.6.1.4.1.2011.6.178.1.1.25.1 | hwTempHumRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei TempHum Equipment.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.1 | hwTempHumRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the TempHum.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.2 | hwTempHumCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.3 | hwTempHumPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | the PortNo of Device.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.4 | hwTempHumTempSensor | Temperature | 温度 | 0-Read_Only | 只读 | -400..800 | -400..800 | the temperature of Device. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.5 | hwTempHumHumSensor | Humidity | 湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | the humidity of Device. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.6 | hwTempHumModbusAddr | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus Address of the device running table for the TempHum.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.7 | hwTempHumTempHighter | High temperature alarm threshold | 高温告警点 | 1-Read_Write | 读写 | 200..800 | 200..800 | Temp Highter of the device config table for the TempHum. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.8 | hwTempHumTempLower | Low temperature alarm threshold | 低温告警点 | 1-Read_Write | 读写 | -200..190 | -200..190 | Temp Lower of the device config table for the TempHum. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.9 | hwTempHumHumHighter | High humidity alarm threshold | 高湿告警点 | 1-Read_Write | 读写 | 500..1000 | 500..1000 | Hum Highter of the device config table for the TempHum. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.10 | hwTempHumHumLower | Low humidity alarm threshold | 低湿告警点 | 1-Read_Write | 读写 | 0..400 | 0..400 | Hum Lower of the device config table for the TempHum. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.11 | hwTempHumDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of the device config table for the TempHum.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.12 | hwTempHumEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | The ESN of the TempHum.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.13 | hwTempHumSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Software Version of the TempHum.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.14 | hwTempHumHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Hardware Version of the TempHum.
1.3.6.1.4.1.2011.6.178.1.1.25.1.1.100 | hwTempHumRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the TempHum.
1.3.6.1.4.1.2011.6.178.1.1.25.2 | hwTempHumRunning1Table | / | / |  |  | / | / | The running table of Huawei TempHum Equipment.
1.3.6.1.4.1.2011.6.178.1.1.25.2.1.1 | hwTempHumRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the TempHum.
1.3.6.1.4.1.2011.6.178.1.1.25.2.1.2 | hwTempHumTempSensorNTC1 | NTC1 | NTC1 | 0-Read_Only | 只读 | -500..850 | -500..850 | The NTC1 of Device. Multiple:10. SigUnitInfo:Degrees Celcius..
1.3.6.1.4.1.2011.6.178.1.1.25.2.1.3 | hwTempHumHumSensorNTC2 | NTC2 | NTC2 | 0-Read_Only | 只读 | -500..850 | -500..850 | The NTC2 of Device. Multiple:10. SigUnitInfo:Degrees Celcius..
1.3.6.1.4.1.2011.6.178.1.1.25.2.1.4 | hwTempHumTempSensorNTC3 | NTC3 | NTC3 | 0-Read_Only | 只读 | -500..850 | -500..850 | The NTC3 of Device. Multiple:10. SigUnitInfo:Degrees Celcius..
1.3.6.1.4.1.2011.6.178.1.1.25.2.1.5 | hwTempHumHumSensorNTC4 | NTC4 | NTC4 | 0-Read_Only | 只读 | -500..850 | -500..850 | The NTC4 of Device. Multiple:10. SigUnitInfo:Degrees Celcius..
1.3.6.1.4.1.2011.6.178.1.1.25.2.1.6 | hwTempHumTempSensorNTC5 | NTC5 | NTC5 | 0-Read_Only | 只读 | -500..850 | -500..850 | The NTC5 of Device. Multiple:10. SigUnitInfo:Degrees Celcius..
1.3.6.1.4.1.2011.6.178.1.1.25.2.1.7 | hwTempHumHumSensorNTC6 | NTC6 | NTC6 | 0-Read_Only | 只读 | -500..850 | -500..850 | The NTC6 of Device. Multiple:10. SigUnitInfo:Degrees Celcius..
1.3.6.1.4.1.2011.6.178.1.1.25.2.1.100 | hwTempHumRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the TempHum.

## Air Conditioner
新风一体机
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.26 | NewAirCon | Air Conditioner | 新风一体机 | / | / | / | / | The New Air Con Equipment.
1.3.6.1.4.1.2011.6.178.1.1.26.1 | hwNewAirConRunningAndConfigTable | / | / |  |  | / | / | The running and config table of Huawei New Air Con Equipment.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.1 | hwNewAirConRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the New Air Con.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.2 | hwNewAirConCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Comm Status of the device config table for the New AirCon. Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.3 | hwNewAirConComNumber | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The com number of New Air Con.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.4 | hwNewAirConModbusAddr | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The modbus addr of New Air Con.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.5 | hwNewAirConleTemperature | Temperature | 温度 | 0-Read_Only | 只读 | -2000..10000 | -2000..10000 | The sensor 1 of New Air Con. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.7 | hwNewAirConleCompressor | Compressor status | 压缩机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | The output 2 status of New Air Con: Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.8 | hwNewAirConleElectricHeater | Electric heater status | 电加热状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | The output 3 status of New Air Con: Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.9 | hwNewAirconleOnOffStatus | On/Off status | 开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | New Aircon Sample On Off Status: value 1 indicates off. value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.10 | hwNewAirconSetOnOffCtrl | On/Off control | 开启/关闭控制 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | New Aircon Set On Off Ctrl. value 1 indicates off. value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.11 | hwNewAirconSetDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | New Aircon Set Device Name.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.12 | hwNewAirConleAirDamper | / | / | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | / | The output 1 status of New Air Con: Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.26.1.1.100 | hwNewAirConRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the New Air Con.

## Hydrogen Monitoring System
氢气监测系统
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.27 | HydrogenMonitor | Hydrogen Monitoring System | 氢气监测系统 | / | / | / | / | The Hydrogen Monitor Equipment.
1.3.6.1.4.1.2011.6.178.1.1.27.1 | hwHydrogenMonitorRunningAndConfigTable | / | / | / | / | / | / | The running table of Huawei Hydrogen Monitor Equipment.
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.1 | hwHydrogenMonitorRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Hydrogen Monitor.
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.2 | hwHydrogenMonitorH2CommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Comm Status of the device config table for the Hydrogen Monitor. value 1 indicates normal. value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.3 | hwHydrogenMonitorH2ComNumber | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The H2 Samp Com Number of the Hydrogen Monitor.
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.4 | hwHydrogenMonitorH2ModbusAddr | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The H2 Samp Modbus Addr of the Hydrogen Monitor.
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.5 | hwHydrogenMonitorH2H2Concentration1 | Hydrogen concentration 1 | 氢气浓度值1 | 0-Read_Only | 只读 | 0..100 | 0..100 | The H2 Samp H2 Concentration 1 of the Hydrogen Monitor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.6 | hwHydrogenMonitorH2H2Concentration2 | Hydrogen concentration 2 | 氢气浓度值2 | 0-Read_Only | 只读 | 0..100 | 0..100 | The H2 Samp H2 Concentration 2 of the Hydrogen Monitor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.7 | hwHydrogenMonitorH2H2Concentration3 | Hydrogen concentration 3 | 氢气浓度值3 | 0-Read_Only | 只读 | 0..100 | 0..100 | The H2 Samp H2 Concentration 3 of the Hydrogen Monitor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.8 | hwHydrogenMonitorH2H2Concentration4 | Hydrogen concentration 4 | 氢气浓度值4 | 0-Read_Only | 只读 | 0..100 | 0..100 | The H2 Samp H2 Concentration 4 of the Hydrogen Monitor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.9 | hwHydrogenMonitorVirSysDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 1..50 | 1..50 | The Vir Sys Device Name of the Hydrogen Monitor.
1.3.6.1.4.1.2011.6.178.1.1.27.1.1.100 | hwHydrogenMonitorRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Hydrogen Monitor.

## 48 V DC Power Supply
48V直流供电设备
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.28 | 48VDCPowerSupply | 48 V DC Power Supply | 48V直流供电设备 | / | / | / | / | The Hydrogen Monitor Equipment.
1.3.6.1.4.1.2011.6.178.1.1.28.1 | hw48VDCPowerSupplyRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.1 | hw48VDCPowerSupplyRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.2 | hw48VDCPowerSupplyCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Comm Status of the device config table for the 48 V DC Power Supply. Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.3 | hw48VDCPowerSupplyComNumber | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The Com Number of the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.4 | hw48VDCPowerSupplyModbusAddr | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Modbus Addr of the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.5 | hw48VDCPowerSupplySystemType | System type | 系统类型 | 0-Read_Only | 只读 | 0..30 | 0..30 | The System Type of the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.6 | hw48VDCPowerSupplySoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Software Version of the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.7 | hw48VDCPowerSupplyHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Hardware Version of the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.8 | hw48VDCPowerSupplyDcVolt | System voltage | 系统电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Dc Volt of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.9 | hw48VDCPowerSupplyTotalLoadCurr | Total DC load current | 总负载电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Total Load Curr of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.10 | hw48VDCPowerSupplyAcVolt | AC voltage | 交流电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The Ac Volt of the 48 V DC Power Supply . Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.11 | hw48VDCPowerSupplyAcCurr | AC current | 交流电流 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | The Ac Curr of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.12 | hw48VDCPowerSupplyPhaseAVolt | Phase L1 voltage | L1相电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The Phase A Volt of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.13 | hw48VDCPowerSupplyPhaseBVolt | Phase L2 voltage | L2相电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The Phase B Volt of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.14 | hw48VDCPowerSupplyPhaseCVolt | Phase L3 voltage | L3相电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The Phase C Volt of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.15 | hw48VDCPowerSupplyPhaseACurr | Phase L1 current | L1相电流 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | The Phase A Curr of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.16 | hw48VDCPowerSupplyPhaseBCurr | Phase L2 current | L2相电流 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | The Phase B Curr of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.17 | hw48VDCPowerSupplyPhaseCCurr | Phase L3 current | L3相电流 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | The Phase C Curr of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.18 | hw48VDCPowerSupplyAcFrequency | AC frequency | 交流频率 | 0-Read_Only | 只读 | 0..65 | 0..65 | The Ac Frequency of the 48 V DC Power Supply. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.19 | hw48VDCPowerSupplyEnvTemp | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -20..80 | -20..80 | The Env Temp of the 48 V DC Power Supply. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.20 | hw48VDCPowerSupplyEnvHum | Ambient humidity | 环境湿度 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Env Hum of the 48 V DC Power Supply. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.21 | hw48VDCPowerSupplyPsuGroupTotalCurr | Rectifier total output current | 模块总输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Psu Group Total Curr of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.22 | hw48VDCPowerSupplyPsuGroupFoundNum | Rectifier amount | 整流模块个数 | 0-Read_Only | 只读 | 0..8 | 0..8 | The Psu Group Found Num of the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.23 | hw48VDCPowerSupplyPsuGroupDcTotalPower | Rectifier total DC power | 直流总功率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | The Psu Group Dc Total Power of the 48 V DC Power Supply. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.24 | hw48VDCPowerSupplyBattState | Battery status | 电池状态 | 0-Read_Only | 只读 | floatcharging(1), equalizedcharging(2), discharge(3), hibernated(4), unknown(255) | [浮充=1]/[均充=2]/[放电=3]/[休眠=4] | The Batt State of the 48 V DC Power Supply. Value 1 indicate floatCharging Value 2 indicate equalizedCharging Value 3 indicate discharge Value 4 indicate hibernated
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.25 | hw48VDCPowerSupplyBattTotalCurr | Total battery current | 电池总电流 | 0-Read_Only | 只读 | -10000..10000 | -10000..10000 | The Batt Total Curr of the 48 V DC Power Supply. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.26 | hw48VDCPowerSupplyBattTotalCapPercent | Total remaining capacity percentage | 总剩余容量百分比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Batt Total Cap Percent of the 48 V DC Power Supply. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.27 | hw48VDCPowerSupplyBattTemp | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Batt Temp of the 48 V DC Power Supply. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.28 | hw48VDCPowerSupplyBattGroupNum | Battery string quantity | 电池串数 | 0-Read_Only | 只读 | 0..6 | 0..6 | The Batt Group Num of the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.29 | hw48VDCPowerSupplyCabPsunum | Combined cabinet module quantity | 组合柜模块数量 | 0-Read_Only | 只读 | 0..60 | 0..60 | TP48 400B Samp Cab Psu num.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.30 | hw48VDCPowerSupplyCabLoadFuseNum | Combined cabinet load fuse quantity | 组合柜负载熔丝路数 | 0-Read_Only | 只读 | 0..42 | 0..42 | TP48 400B Samp Cab Load Fuse Num.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.31 | hw48VDCPowerSupplyCabBattFuseNum | Combined cabinet battery fuse quantity | 组合柜电池熔丝路数 | 0-Read_Only | 只读 | 0..10 | 0..10 | TP48 400B Samp Cab Batt Fuse Num4
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.32 | hw48VDCPowerSupplyDcTotalEnergy | Total DC load electricity | 总负载直流电量 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | TP48 400B Samp Dc Total Energy. Multiple:100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.33 | hw48VDCPowerSupplySetLlvd1Enabled | LLVD1 enable | LLVD1使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | 48 V DC Power Supply Set Llvd1 Enabled. value 1 indicate unable. value 2 indicate enable.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.34 | hw48VDCPowerSupplySetLlvd1OffVolt | LLVD1 disconnection voltage | LLVD1下电电压 | 1-Read_Write | 读写 | 350..560 | 350..560 | 48 V DC Power Supply Set Llvd1 Off Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.35 | hw48VDCPowerSupplySetLlvd1OnVolt | LLVD1 connection voltage | LLVD1上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | 48 V DC Power Supply Set Llvd1 On Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.36 | hw48VDCPowerSupplySetLlvd2Allow | LLVD2 enable | LLVD2使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | 48 V DC Power Supply Set Llvd2 Allow. value 1 indicate unable. value 2 indicate enable.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.37 | hw48VDCPowerSupplySetLlvd2OffVolt | LLVD2 disconnection voltage | LLVD2下电电压 | 1-Read_Write | 读写 | 350..560 | 350..560 | 48 V DC Power Supply Set Llvd2 Off Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.38 | hw48VDCPowerSupplySetLlvd2OnVolt | LLVD2 connection voltage | LLVD2上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | 48 V DC Power Supply Set Llvd2 On Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.39 | hw48VDCPowerSupplySetDcOverVolt | DC overvoltage threshold | 直流过压告警点 | 1-Read_Write | 读写 | 530..600 | 530..600 | 48 V DC Power Supply Set Dc Over Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.40 | hw48VDCPowerSupplySetDcUnderVolt | DC undervoltage threshold | 直流欠压告警点 | 1-Read_Write | 读写 | 350..570 | 350..570 | 48 V DC Power Supply Set Dc Under Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.41 | hw48VDCPowerSupplySetAcOverVolt | AC overvoltage threshold | 交流过压告警点 | 1-Read_Write | 读写 | 60..300 | 60..300 | 48 V DC Power Supply Set Ac Over Volt. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.42 | hw48VDCPowerSupplySetAcUnderVolt | AC undervoltage threshold | 交流欠压告警点 | 1-Read_Write | 读写 | 60..300 | 60..300 | 48 V DC Power Supply Set Ac Under Volt. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.43 | hw48VDCPowerSupplySetAcFreqOv | AC high frequency threshold | 交流频率过高告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | 48 V DC Power Supply Set Ac Freq Ov. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.44 | hw48VDCPowerSupplySetAcFreqUn | AC low frequency threshold | 交流频率过低告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | 48 V DC Power Supply Set Ac Freq Un. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.45 | hw48VDCPowerSupplySetBattCapacity | Battery rated capacity | 电池额定容量 | 1-Read_Write | 读写 | 5..10000 | 5..10000 | 48 V DC Power Supply Set Batt Capacity. SigUnitInfo:Ah
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.46 | hw48VDCPowerSupplySetBattFloatVolt | Float charging voltage | 浮充电压 | 1-Read_Write | 读写 | 420..583 | 420..583 | 48 V DC Power Supply Set Batt Float Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.47 | hw48VDCPowerSupplySetBattBoostVolt | Boost charging voltage | 均充电压 | 1-Read_Write | 读写 | 420..583 | 420..583 | 48 V DC Power Supply Set Batt Boost Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.48 | hw48VDCPowerSupplySetBattOffEnable | BLVD enable | BLVD使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | 48 V DC Power Supply Set Batt Off Enable. value 1 indicates no. value 2 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.49 | hw48VDCPowerSupplySetBattVoltLowOff | BLVD disconnection voltage | BLVD下电电压 | 1-Read_Write | 读写 | 350..560 | 350..560 | 48 V DC Power Supply Set Batt Volt Low Off. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.50 | hw48VDCPowerSupplySetBattBlvdOnVolt | BLVD connection voltage | BLVD上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | 48 V DC Power Supply Set Batt Blvd On Volt. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.51 | hw48VDCPowerSupplyChargeCurrentLimitCoefficient | Charge current limit coefficient | 充电限流点系数 | 1-Read_Write | 读写 | 5..25 | 5..25 | 48 V DC Power Supply Set Charge current limit coefficient. Multiple:100. SigUnitInfo:C10
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.52 | hw48VDCPowerSupplySetResetBoard | Reset control | 监控复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | 48 V DC Power Supply Set Reset Board. value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.53 | hw48VDCPowerSupplySetSmokeReset | Reset smoke sensor | 烟感复位 | 1-Read_Write | 读写 | yes(1) | [是=1] | 48 V DC Power Supply Set Smoke Reset. value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.54 | hw48VDCPowerSupplyDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | 48 V DC Power Supply Device Name.
1.3.6.1.4.1.2011.6.178.1.1.28.1.1.100 | hw48VDCPowerSupplyRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running and config table for the Hydrogen Monitor.
1.3.6.1.4.1.2011.6.178.1.1.28.2 | hw48VDCPowerSupplyRunning1Table | / | / |  |  | / | / | The running table of 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.1 | hw48VDCPowerSupplyRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.2 | hw48VDCPowerSupplyAcVoltage2 | AC voltage 2 | 交流电压2 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | AC voltage 2 of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.3 | hw48VDCPowerSupplyAcCurrent2 | AC current 2 | 交流电流2 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | AC current 2 of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.4 | hw48VDCPowerSupplyPhaseL1Voltage2 | Phase L1 voltage 2 | L1相电压2 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Phase L1 voltage 2 of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.5 | hw48VDCPowerSupplyPhaseL2Voltage2 | Phase L2 voltage 2 | L2相电压2 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Phase L2 voltage 2 of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.6 | hw48VDCPowerSupplyPhaseL3Voltage2 | Phase L3 voltage 2 | L3相电压2 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Phase L3 voltage 2 of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.7 | hw48VDCPowerSupplyPhaseL1Current2 | Phase L1 current 2 | L1相电流2 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | Phase L1 current 2 of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.8 | hw48VDCPowerSupplyPhaseL2Current2 | Phase L2 current 2 | L2相电流2 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | Phase L2 current 2 of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.9 | hw48VDCPowerSupplyPhaseL3Current2 | Phase L3 current 2 | L3相电流2 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | Phase L3 current 2 of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.10 | hw48VDCPowerSupplyAcFrequency2 | AC frequency 2 | 交流频率2 | 0-Read_Only | 只读 | 0..65 | 0..65 | AC frequency 2 of the device config table for the 48 V DC Power Supply.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.11 | hw48VDCPowerSupplyHourlyMainsPowerConsumption | Hourly mains power consumption | 市电小时耗电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hourly mains power consumption of the device config table for the 48 V DC Power Supply.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.12 | hw48VDCPowerSupplyCumulativeMainsPowerConsumption | Cumulative mains power consumption | 市电累计功耗 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cumulative mains power consumption of the device config table for the 48 V DC Power Supply.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.13 | hw48VDCPowerSupplyLithiumBatteryNumber | Lithium battery number | 锂电池个数 | 0-Read_Only | 只读 | 0..16 | 0..16 | Lithium battery number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.14 | hw48VDCPowerSupplyLithiumBattery1BatteryVoltage | Lithium battery 1 battery voltage | 锂电池1电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.15 | hw48VDCPowerSupplyEquipmentType | Equipment type | 设备型号 | 0-Read_Only | 只读 | smu02b(1), smu05a(2), unknown(255) | [SMU02B=1]/[SMU05A=2] | Equipment type of the device config table for the 48 V DC Power Supply. Value 1 indicate smu02b Value 2 indicate smu05a
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.16 | hw48VDCPowerSupplySoftwareEntireVersion | Software entire version | 软件整版 | 0-Read_Only | 只读 | 0..30 | 0..30 | Software entire version of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.17 | hw48VDCPowerSupplyLithiumBattery2BatteryVoltage | Lithium battery 2 battery voltage | 锂电池2电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.18 | hw48VDCPowerSupplyLithiumBattery3BatteryVoltage | Lithium battery 3 battery voltage | 锂电池3电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.19 | hw48VDCPowerSupplyLithiumBattery4BatteryVoltage | Lithium battery 4 battery voltage | 锂电池4电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.20 | hw48VDCPowerSupplyLithiumBattery5BatteryVoltage | Lithium battery 5 battery voltage | 锂电池5电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.21 | hw48VDCPowerSupplyLithiumBattery6BatteryVoltage | Lithium battery 6 battery voltage | 锂电池6电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.22 | hw48VDCPowerSupplyLithiumBattery7BatteryVoltage | Lithium battery 7 battery voltage | 锂电池7电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.23 | hw48VDCPowerSupplyLithiumBattery8BatteryVoltage | Lithium battery 8 battery voltage | 锂电池8电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.24 | hw48VDCPowerSupplyLithiumBattery9BatteryVoltage | Lithium battery 9 battery voltage | 锂电池9电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.25 | hw48VDCPowerSupplyLithiumBattery10BatteryVoltage | Lithium battery 10 battery voltage | 锂电池10电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.26 | hw48VDCPowerSupplyLithiumBattery11BatteryVoltage | Lithium battery 11 battery voltage | 锂电池11电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.27 | hw48VDCPowerSupplyLithiumBattery12BatteryVoltage | Lithium battery 12 battery voltage | 锂电池12电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.28 | hw48VDCPowerSupplyLithiumBattery13BatteryVoltage | Lithium battery 13 battery voltage | 锂电池13电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.29 | hw48VDCPowerSupplyLithiumBattery14BatteryVoltage | Lithium battery 14 battery voltage | 锂电池14电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.30 | hw48VDCPowerSupplyLithiumBattery15BatteryVoltage | Lithium battery 15 battery voltage | 锂电池15电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.31 | hw48VDCPowerSupplyLithiumBattery16BatteryVoltage | Lithium battery 16 battery voltage | 锂电池16电池电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 battery voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.32 | hw48VDCPowerSupplyLithiumBattery1BatteryCurrent | Lithium battery 1 battery current | 锂电池1电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.33 | hw48VDCPowerSupplyLithiumBattery2BatteryCurrent | Lithium battery 2 battery current | 锂电池2电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.34 | hw48VDCPowerSupplyLithiumBattery3BatteryCurrent | Lithium battery 3 battery current | 锂电池3电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.35 | hw48VDCPowerSupplyLithiumBattery4BatteryCurrent | Lithium battery 4 battery current | 锂电池4电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.36 | hw48VDCPowerSupplyLithiumBattery5BatteryCurrent | Lithium battery 5 battery current | 锂电池5电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.37 | hw48VDCPowerSupplyLithiumBattery6BatteryCurrent | Lithium battery 6 battery current | 锂电池6电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.38 | hw48VDCPowerSupplyLithiumBattery7BatteryCurrent | Lithium battery 7 battery current | 锂电池7电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.39 | hw48VDCPowerSupplyLithiumBattery8BatteryCurrent | Lithium battery 8 battery current | 锂电池8电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.40 | hw48VDCPowerSupplyLithiumBattery9BatteryCurrent | Lithium battery 9 battery current | 锂电池9电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.41 | hw48VDCPowerSupplyLithiumBattery10BatteryCurrent | Lithium battery 10 battery current | 锂电池10电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.42 | hw48VDCPowerSupplyLithiumBattery11BatteryCurrent | Lithium battery 11 battery current | 锂电池11电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.43 | hw48VDCPowerSupplyLithiumBattery12BatteryCurrent | Lithium battery 12 battery current | 锂电池12电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.44 | hw48VDCPowerSupplyLithiumBattery13BatteryCurrent | Lithium battery 13 battery current | 锂电池13电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.45 | hw48VDCPowerSupplyLithiumBattery14BatteryCurrent | Lithium battery 14 battery current | 锂电池14电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.46 | hw48VDCPowerSupplyLithiumBattery15BatteryCurrent | Lithium battery 15 battery current | 锂电池15电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.47 | hw48VDCPowerSupplyLithiumBattery16BatteryCurrent | Lithium battery 16 battery current | 锂电池16电池电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 battery current of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.48 | hw48VDCPowerSupplyLithiumBattery1BatterySoc | Lithium battery 1 battery SOC | 锂电池1电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.49 | hw48VDCPowerSupplyLithiumBattery2BatterySoc | Lithium battery 2 battery SOC | 锂电池2电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.50 | hw48VDCPowerSupplyLithiumBattery3BatterySoc | Lithium battery 3 battery SOC | 锂电池3电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.51 | hw48VDCPowerSupplyLithiumBattery4BatterySoc | Lithium battery 4 battery SOC | 锂电池4电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.52 | hw48VDCPowerSupplyLithiumBattery5BatterySoc | Lithium battery 5 battery SOC | 锂电池5电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.53 | hw48VDCPowerSupplyLithiumBattery6BatterySoc | Lithium battery 6 battery SOC | 锂电池6电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.54 | hw48VDCPowerSupplyLithiumBattery7BatterySoc | Lithium battery 7 battery SOC | 锂电池7电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.55 | hw48VDCPowerSupplyLithiumBattery8BatterySoc | Lithium battery 8 battery SOC | 锂电池8电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.56 | hw48VDCPowerSupplyLithiumBattery9BatterySoc | Lithium battery 9 battery SOC | 锂电池9电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.57 | hw48VDCPowerSupplyLithiumBattery10BatterySoc | Lithium battery 10 battery SOC | 锂电池10电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.58 | hw48VDCPowerSupplyLithiumBattery11BatterySoc | Lithium battery 11 battery SOC | 锂电池11电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.59 | hw48VDCPowerSupplyLithiumBattery12BatterySoc | Lithium battery 12 battery SOC | 锂电池12电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.60 | hw48VDCPowerSupplyLithiumBattery13BatterySoc | Lithium battery 13 battery SOC | 锂电池13电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.61 | hw48VDCPowerSupplyLithiumBattery14BatterySoc | Lithium battery 14 battery SOC | 锂电池14电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.62 | hw48VDCPowerSupplyLithiumBattery15BatterySoc | Lithium battery 15 battery SOC | 锂电池15电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.63 | hw48VDCPowerSupplyLithiumBattery16BatterySoc | Lithium battery 16 battery SOC | 锂电池16电池SOC | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 battery SOC of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.64 | hw48VDCPowerSupplyLithiumBattery1CellsNumber | Lithium battery 1 cells number | 锂电池1电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.65 | hw48VDCPowerSupplyLithiumBattery2CellsNumber | Lithium battery 2 cells number | 锂电池2电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.66 | hw48VDCPowerSupplyLithiumBattery3CellsNumber | Lithium battery 3 cells number | 锂电池3电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.67 | hw48VDCPowerSupplyLithiumBattery4CellsNumber | Lithium battery 4 cells number | 锂电池4电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.68 | hw48VDCPowerSupplyLithiumBattery5CellsNumber | Lithium battery 5 cells number | 锂电池5电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.69 | hw48VDCPowerSupplyLithiumBattery6CellsNumber | Lithium battery 6 cells number | 锂电池6电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.70 | hw48VDCPowerSupplyLithiumBattery7CellsNumber | Lithium battery 7 cells number | 锂电池7电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.71 | hw48VDCPowerSupplyLithiumBattery8CellsNumber | Lithium battery 8 cells number | 锂电池8电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.72 | hw48VDCPowerSupplyLithiumBattery9CellsNumber | Lithium battery 9 cells number | 锂电池9电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.73 | hw48VDCPowerSupplyLithiumBattery10CellsNumber | Lithium battery 10 cells number | 锂电池10电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.74 | hw48VDCPowerSupplyLithiumBattery11CellsNumber | Lithium battery 11 cells number | 锂电池11电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.75 | hw48VDCPowerSupplyLithiumBattery12CellsNumber | Lithium battery 12 cells number | 锂电池12电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.76 | hw48VDCPowerSupplyLithiumBattery13CellsNumber | Lithium battery 13 cells number | 锂电池13电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.77 | hw48VDCPowerSupplyLithiumBattery14CellsNumber | Lithium battery 14 cells number | 锂电池14电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.78 | hw48VDCPowerSupplyLithiumBattery15CellsNumber | Lithium battery 15 cells number | 锂电池15电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.79 | hw48VDCPowerSupplyLithiumBattery16CellsNumber | Lithium battery 16 cells number | 锂电池16电芯个数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cells number of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.80 | hw48VDCPowerSupplyLithiumBattery1Cell1Temperature | Lithium battery 1 cell 1 temperature | 锂电池1电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.81 | hw48VDCPowerSupplyLithiumBattery2Cell1Temperature | Lithium battery 2 cell 1 temperature | 锂电池2电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.82 | hw48VDCPowerSupplyLithiumBattery3Cell1Temperature | Lithium battery 3 cell 1 temperature | 锂电池3电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.83 | hw48VDCPowerSupplyLithiumBattery4Cell1Temperature | Lithium battery 4 cell 1 temperature | 锂电池4电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.84 | hw48VDCPowerSupplyLithiumBattery5Cell1Temperature | Lithium battery 5 cell 1 temperature | 锂电池5电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.85 | hw48VDCPowerSupplyLithiumBattery6Cell1Temperature | Lithium battery 6 cell 1 temperature | 锂电池6电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.86 | hw48VDCPowerSupplyLithiumBattery7Cell1Temperature | Lithium battery 7 cell 1 temperature | 锂电池7电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.87 | hw48VDCPowerSupplyLithiumBattery8Cell1Temperature | Lithium battery 8 cell 1 temperature | 锂电池8电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.88 | hw48VDCPowerSupplyLithiumBattery9Cell1Temperature | Lithium battery 9 cell 1 temperature | 锂电池9电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.89 | hw48VDCPowerSupplyLithiumBattery10Cell1Temperature | Lithium battery 10 cell 1 temperature | 锂电池10电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.90 | hw48VDCPowerSupplyLithiumBattery11Cell1Temperature | Lithium battery 11 cell 1 temperature | 锂电池11电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.91 | hw48VDCPowerSupplyLithiumBattery12Cell1Temperature | Lithium battery 12 cell 1 temperature | 锂电池12电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.92 | hw48VDCPowerSupplyLithiumBattery13Cell1Temperature | Lithium battery 13 cell 1 temperature | 锂电池13电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.93 | hw48VDCPowerSupplyLithiumBattery14Cell1Temperature | Lithium battery 14 cell 1 temperature | 锂电池14电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.94 | hw48VDCPowerSupplyLithiumBattery15Cell1Temperature | Lithium battery 15 cell 1 temperature | 锂电池15电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.95 | hw48VDCPowerSupplyLithiumBattery16Cell1Temperature | Lithium battery 16 cell 1 temperature | 锂电池16电芯1温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 1 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.96 | hw48VDCPowerSupplyLithiumBattery1Cell2Temperature | Lithium battery 1 cell 2 temperature | 锂电池1电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.97 | hw48VDCPowerSupplyLithiumBattery2Cell2Temperature | Lithium battery 2 cell 2 temperature | 锂电池2电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.98 | hw48VDCPowerSupplyLithiumBattery3Cell2Temperature | Lithium battery 3 cell 2 temperature | 锂电池3电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.99 | hw48VDCPowerSupplyLithiumBattery4Cell2Temperature | Lithium battery 4 cell 2 temperature | 锂电池4电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.100 | hw48VDCPowerSupplyLithiumBattery5Cell2Temperature | Lithium battery 5 cell 2 temperature | 锂电池5电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.101 | hw48VDCPowerSupplyLithiumBattery6Cell2Temperature | Lithium battery 6 cell 2 temperature | 锂电池6电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.102 | hw48VDCPowerSupplyLithiumBattery7Cell2Temperature | Lithium battery 7 cell 2 temperature | 锂电池7电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.103 | hw48VDCPowerSupplyLithiumBattery8Cell2Temperature | Lithium battery 8 cell 2 temperature | 锂电池8电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.104 | hw48VDCPowerSupplyLithiumBattery9Cell2Temperature | Lithium battery 9 cell 2 temperature | 锂电池9电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.105 | hw48VDCPowerSupplyLithiumBattery10Cell2Temperature | Lithium battery 10 cell 2 temperature | 锂电池10电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.106 | hw48VDCPowerSupplyLithiumBattery11Cell2Temperature | Lithium battery 11 cell 2 temperature | 锂电池11电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.107 | hw48VDCPowerSupplyLithiumBattery12Cell2Temperature | Lithium battery 12 cell 2 temperature | 锂电池12电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.108 | hw48VDCPowerSupplyLithiumBattery13Cell2Temperature | Lithium battery 13 cell 2 temperature | 锂电池13电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.109 | hw48VDCPowerSupplyLithiumBattery14Cell2Temperature | Lithium battery 14 cell 2 temperature | 锂电池14电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.110 | hw48VDCPowerSupplyLithiumBattery15Cell2Temperature | Lithium battery 15 cell 2 temperature | 锂电池15电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.111 | hw48VDCPowerSupplyLithiumBattery16Cell2Temperature | Lithium battery 16 cell 2 temperature | 锂电池16电芯2温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 2 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.112 | hw48VDCPowerSupplyLithiumBattery1Cell3Temperature | Lithium battery 1 cell 3 temperature | 锂电池1电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.113 | hw48VDCPowerSupplyLithiumBattery2Cell3Temperature | Lithium battery 2 cell 3 temperature | 锂电池2电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.114 | hw48VDCPowerSupplyLithiumBattery3Cell3Temperature | Lithium battery 3 cell 3 temperature | 锂电池3电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.115 | hw48VDCPowerSupplyLithiumBattery4Cell3Temperature | Lithium battery 4 cell 3 temperature | 锂电池4电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.116 | hw48VDCPowerSupplyLithiumBattery5Cell3Temperature | Lithium battery 5 cell 3 temperature | 锂电池5电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.117 | hw48VDCPowerSupplyLithiumBattery6Cell3Temperature | Lithium battery 6 cell 3 temperature | 锂电池6电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.118 | hw48VDCPowerSupplyLithiumBattery7Cell3Temperature | Lithium battery 7 cell 3 temperature | 锂电池7电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.119 | hw48VDCPowerSupplyLithiumBattery8Cell3Temperature | Lithium battery 8 cell 3 temperature | 锂电池8电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.120 | hw48VDCPowerSupplyLithiumBattery9Cell3Temperature | Lithium battery 9 cell 3 temperature | 锂电池9电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.121 | hw48VDCPowerSupplyLithiumBattery10Cell3Temperature | Lithium battery 10 cell 3 temperature | 锂电池10电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.122 | hw48VDCPowerSupplyLithiumBattery11Cell3Temperature | Lithium battery 11 cell 3 temperature | 锂电池11电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.123 | hw48VDCPowerSupplyLithiumBattery12Cell3Temperature | Lithium battery 12 cell 3 temperature | 锂电池12电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.124 | hw48VDCPowerSupplyLithiumBattery13Cell3Temperature | Lithium battery 13 cell 3 temperature | 锂电池13电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.125 | hw48VDCPowerSupplyLithiumBattery14Cell3Temperature | Lithium battery 14 cell 3 temperature | 锂电池14电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.126 | hw48VDCPowerSupplyLithiumBattery15Cell3Temperature | Lithium battery 15 cell 3 temperature | 锂电池15电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.127 | hw48VDCPowerSupplyLithiumBattery16Cell3Temperature | Lithium battery 16 cell 3 temperature | 锂电池16电芯3温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 3 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.128 | hw48VDCPowerSupplyLithiumBattery1Cell4Temperature | Lithium battery 1 cell 4 temperature | 锂电池1电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.129 | hw48VDCPowerSupplyLithiumBattery2Cell4Temperature | Lithium battery 2 cell 4 temperature | 锂电池2电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.130 | hw48VDCPowerSupplyLithiumBattery3Cell4Temperature | Lithium battery 3 cell 4 temperature | 锂电池3电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.131 | hw48VDCPowerSupplyLithiumBattery4Cell4Temperature | Lithium battery 4 cell 4 temperature | 锂电池4电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.132 | hw48VDCPowerSupplyLithiumBattery5Cell4Temperature | Lithium battery 5 cell 4 temperature | 锂电池5电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.133 | hw48VDCPowerSupplyLithiumBattery6Cell4Temperature | Lithium battery 6 cell 4 temperature | 锂电池6电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.134 | hw48VDCPowerSupplyLithiumBattery7Cell4Temperature | Lithium battery 7 cell 4 temperature | 锂电池7电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.135 | hw48VDCPowerSupplyLithiumBattery8Cell4Temperature | Lithium battery 8 cell 4 temperature | 锂电池8电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.136 | hw48VDCPowerSupplyLithiumBattery9Cell4Temperature | Lithium battery 9 cell 4 temperature | 锂电池9电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.137 | hw48VDCPowerSupplyLithiumBattery10Cell4Temperature | Lithium battery 10 cell 4 temperature | 锂电池10电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.138 | hw48VDCPowerSupplyLithiumBattery11Cell4Temperature | Lithium battery 11 cell 4 temperature | 锂电池11电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.139 | hw48VDCPowerSupplyLithiumBattery12Cell4Temperature | Lithium battery 12 cell 4 temperature | 锂电池12电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.140 | hw48VDCPowerSupplyLithiumBattery13Cell4Temperature | Lithium battery 13 cell 4 temperature | 锂电池13电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.141 | hw48VDCPowerSupplyLithiumBattery14Cell4Temperature | Lithium battery 14 cell 4 temperature | 锂电池14电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.142 | hw48VDCPowerSupplyLithiumBattery15Cell4Temperature | Lithium battery 15 cell 4 temperature | 锂电池15电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.143 | hw48VDCPowerSupplyLithiumBattery16Cell4Temperature | Lithium battery 16 cell 4 temperature | 锂电池16电芯4温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 4 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.144 | hw48VDCPowerSupplyLithiumBattery1Cell5Temperature | Lithium battery 1 cell 5 temperature | 锂电池1电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.145 | hw48VDCPowerSupplyLithiumBattery2Cell5Temperature | Lithium battery 2 cell 5 temperature | 锂电池2电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.146 | hw48VDCPowerSupplyLithiumBattery3Cell5Temperature | Lithium battery 3 cell 5 temperature | 锂电池3电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.147 | hw48VDCPowerSupplyLithiumBattery4Cell5Temperature | Lithium battery 4 cell 5 temperature | 锂电池4电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.148 | hw48VDCPowerSupplyLithiumBattery5Cell5Temperature | Lithium battery 5 cell 5 temperature | 锂电池5电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.149 | hw48VDCPowerSupplyLithiumBattery6Cell5Temperature | Lithium battery 6 cell 5 temperature | 锂电池6电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.150 | hw48VDCPowerSupplyLithiumBattery7Cell5Temperature | Lithium battery 7 cell 5 temperature | 锂电池7电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.151 | hw48VDCPowerSupplyLithiumBattery8Cell5Temperature | Lithium battery 8 cell 5 temperature | 锂电池8电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.152 | hw48VDCPowerSupplyLithiumBattery9Cell5Temperature | Lithium battery 9 cell 5 temperature | 锂电池9电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.153 | hw48VDCPowerSupplyLithiumBattery10Cell5Temperature | Lithium battery 10 cell 5 temperature | 锂电池10电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.154 | hw48VDCPowerSupplyLithiumBattery11Cell5Temperature | Lithium battery 11 cell 5 temperature | 锂电池11电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.155 | hw48VDCPowerSupplyLithiumBattery12Cell5Temperature | Lithium battery 12 cell 5 temperature | 锂电池12电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.156 | hw48VDCPowerSupplyLithiumBattery13Cell5Temperature | Lithium battery 13 cell 5 temperature | 锂电池13电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.157 | hw48VDCPowerSupplyLithiumBattery14Cell5Temperature | Lithium battery 14 cell 5 temperature | 锂电池14电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.158 | hw48VDCPowerSupplyLithiumBattery15Cell5Temperature | Lithium battery 15 cell 5 temperature | 锂电池15电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.159 | hw48VDCPowerSupplyLithiumBattery16Cell5Temperature | Lithium battery 16 cell 5 temperature | 锂电池16电芯5温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 5 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.160 | hw48VDCPowerSupplyLithiumBattery1Cell6Temperature | Lithium battery 1 cell 6 temperature | 锂电池1电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.161 | hw48VDCPowerSupplyLithiumBattery2Cell6Temperature | Lithium battery 2 cell 6 temperature | 锂电池2电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.162 | hw48VDCPowerSupplyLithiumBattery3Cell6Temperature | Lithium battery 3 cell 6 temperature | 锂电池3电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.163 | hw48VDCPowerSupplyLithiumBattery4Cell6Temperature | Lithium battery 4 cell 6 temperature | 锂电池4电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.164 | hw48VDCPowerSupplyLithiumBattery5Cell6Temperature | Lithium battery 5 cell 6 temperature | 锂电池5电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.165 | hw48VDCPowerSupplyLithiumBattery6Cell6Temperature | Lithium battery 6 cell 6 temperature | 锂电池6电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.166 | hw48VDCPowerSupplyLithiumBattery7Cell6Temperature | Lithium battery 7 cell 6 temperature | 锂电池7电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.167 | hw48VDCPowerSupplyLithiumBattery8Cell6Temperature | Lithium battery 8 cell 6 temperature | 锂电池8电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.168 | hw48VDCPowerSupplyLithiumBattery9Cell6Temperature | Lithium battery 9 cell 6 temperature | 锂电池9电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.169 | hw48VDCPowerSupplyLithiumBattery10Cell6Temperature | Lithium battery 10 cell 6 temperature | 锂电池10电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.170 | hw48VDCPowerSupplyLithiumBattery11Cell6Temperature | Lithium battery 11 cell 6 temperature | 锂电池11电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.171 | hw48VDCPowerSupplyLithiumBattery12Cell6Temperature | Lithium battery 12 cell 6 temperature | 锂电池12电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.172 | hw48VDCPowerSupplyLithiumBattery13Cell6Temperature | Lithium battery 13 cell 6 temperature | 锂电池13电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.173 | hw48VDCPowerSupplyLithiumBattery14Cell6Temperature | Lithium battery 14 cell 6 temperature | 锂电池14电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.174 | hw48VDCPowerSupplyLithiumBattery15Cell6Temperature | Lithium battery 15 cell 6 temperature | 锂电池15电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.175 | hw48VDCPowerSupplyLithiumBattery16Cell6Temperature | Lithium battery 16 cell 6 temperature | 锂电池16电芯6温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 6 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.176 | hw48VDCPowerSupplyLithiumBattery1Cell7Temperature | Lithium battery 1 cell 7 temperature | 锂电池1电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.177 | hw48VDCPowerSupplyLithiumBattery2Cell7Temperature | Lithium battery 2 cell 7 temperature | 锂电池2电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.178 | hw48VDCPowerSupplyLithiumBattery3Cell7Temperature | Lithium battery 3 cell 7 temperature | 锂电池3电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.179 | hw48VDCPowerSupplyLithiumBattery4Cell7Temperature | Lithium battery 4 cell 7 temperature | 锂电池4电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.180 | hw48VDCPowerSupplyLithiumBattery5Cell7Temperature | Lithium battery 5 cell 7 temperature | 锂电池5电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.181 | hw48VDCPowerSupplyLithiumBattery6Cell7Temperature | Lithium battery 6 cell 7 temperature | 锂电池6电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.182 | hw48VDCPowerSupplyLithiumBattery7Cell7Temperature | Lithium battery 7 cell 7 temperature | 锂电池7电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.183 | hw48VDCPowerSupplyLithiumBattery8Cell7Temperature | Lithium battery 8 cell 7 temperature | 锂电池8电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.184 | hw48VDCPowerSupplyLithiumBattery9Cell7Temperature | Lithium battery 9 cell 7 temperature | 锂电池9电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.185 | hw48VDCPowerSupplyLithiumBattery10Cell7Temperature | Lithium battery 10 cell 7 temperature | 锂电池10电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.186 | hw48VDCPowerSupplyLithiumBattery11Cell7Temperature | Lithium battery 11 cell 7 temperature | 锂电池11电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.187 | hw48VDCPowerSupplyLithiumBattery12Cell7Temperature | Lithium battery 12 cell 7 temperature | 锂电池12电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.188 | hw48VDCPowerSupplyLithiumBattery13Cell7Temperature | Lithium battery 13 cell 7 temperature | 锂电池13电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.189 | hw48VDCPowerSupplyLithiumBattery14Cell7Temperature | Lithium battery 14 cell 7 temperature | 锂电池14电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.190 | hw48VDCPowerSupplyLithiumBattery15Cell7Temperature | Lithium battery 15 cell 7 temperature | 锂电池15电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.191 | hw48VDCPowerSupplyLithiumBattery16Cell7Temperature | Lithium battery 16 cell 7 temperature | 锂电池16电芯7温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 7 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.192 | hw48VDCPowerSupplyLithiumBattery1Cell8Temperature | Lithium battery 1 cell 8 temperature | 锂电池1电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.193 | hw48VDCPowerSupplyLithiumBattery2Cell8Temperature | Lithium battery 2 cell 8 temperature | 锂电池2电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.194 | hw48VDCPowerSupplyLithiumBattery3Cell8Temperature | Lithium battery 3 cell 8 temperature | 锂电池3电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.195 | hw48VDCPowerSupplyLithiumBattery4Cell8Temperature | Lithium battery 4 cell 8 temperature | 锂电池4电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.196 | hw48VDCPowerSupplyLithiumBattery5Cell8Temperature | Lithium battery 5 cell 8 temperature | 锂电池5电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.197 | hw48VDCPowerSupplyLithiumBattery6Cell8Temperature | Lithium battery 6 cell 8 temperature | 锂电池6电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.198 | hw48VDCPowerSupplyLithiumBattery7Cell8Temperature | Lithium battery 7 cell 8 temperature | 锂电池7电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.199 | hw48VDCPowerSupplyLithiumBattery8Cell8Temperature | Lithium battery 8 cell 8 temperature | 锂电池8电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.200 | hw48VDCPowerSupplyLithiumBattery9Cell8Temperature | Lithium battery 9 cell 8 temperature | 锂电池9电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.201 | hw48VDCPowerSupplyLithiumBattery10Cell8Temperature | Lithium battery 10 cell 8 temperature | 锂电池10电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.202 | hw48VDCPowerSupplyLithiumBattery11Cell8Temperature | Lithium battery 11 cell 8 temperature | 锂电池11电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.203 | hw48VDCPowerSupplyLithiumBattery12Cell8Temperature | Lithium battery 12 cell 8 temperature | 锂电池12电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.204 | hw48VDCPowerSupplyLithiumBattery13Cell8Temperature | Lithium battery 13 cell 8 temperature | 锂电池13电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.205 | hw48VDCPowerSupplyLithiumBattery14Cell8Temperature | Lithium battery 14 cell 8 temperature | 锂电池14电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.206 | hw48VDCPowerSupplyLithiumBattery15Cell8Temperature | Lithium battery 15 cell 8 temperature | 锂电池15电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.207 | hw48VDCPowerSupplyLithiumBattery16Cell8Temperature | Lithium battery 16 cell 8 temperature | 锂电池16电芯8温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 8 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.208 | hw48VDCPowerSupplyLithiumBattery1Cell9Temperature | Lithium battery 1 cell 9 temperature | 锂电池1电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.209 | hw48VDCPowerSupplyLithiumBattery2Cell9Temperature | Lithium battery 2 cell 9 temperature | 锂电池2电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.210 | hw48VDCPowerSupplyLithiumBattery3Cell9Temperature | Lithium battery 3 cell 9 temperature | 锂电池3电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.211 | hw48VDCPowerSupplyLithiumBattery4Cell9Temperature | Lithium battery 4 cell 9 temperature | 锂电池4电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.212 | hw48VDCPowerSupplyLithiumBattery5Cell9Temperature | Lithium battery 5 cell 9 temperature | 锂电池5电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.213 | hw48VDCPowerSupplyLithiumBattery6Cell9Temperature | Lithium battery 6 cell 9 temperature | 锂电池6电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.214 | hw48VDCPowerSupplyLithiumBattery7Cell9Temperature | Lithium battery 7 cell 9 temperature | 锂电池7电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.215 | hw48VDCPowerSupplyLithiumBattery8Cell9Temperature | Lithium battery 8 cell 9 temperature | 锂电池8电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.216 | hw48VDCPowerSupplyLithiumBattery9Cell9Temperature | Lithium battery 9 cell 9 temperature | 锂电池9电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.217 | hw48VDCPowerSupplyLithiumBattery10Cell9Temperature | Lithium battery 10 cell 9 temperature | 锂电池10电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.218 | hw48VDCPowerSupplyLithiumBattery11Cell9Temperature | Lithium battery 11 cell 9 temperature | 锂电池11电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.219 | hw48VDCPowerSupplyLithiumBattery12Cell9Temperature | Lithium battery 12 cell 9 temperature | 锂电池12电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.220 | hw48VDCPowerSupplyLithiumBattery13Cell9Temperature | Lithium battery 13 cell 9 temperature | 锂电池13电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.221 | hw48VDCPowerSupplyLithiumBattery14Cell9Temperature | Lithium battery 14 cell 9 temperature | 锂电池14电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.222 | hw48VDCPowerSupplyLithiumBattery15Cell9Temperature | Lithium battery 15 cell 9 temperature | 锂电池15电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.223 | hw48VDCPowerSupplyLithiumBattery16Cell9Temperature | Lithium battery 16 cell 9 temperature | 锂电池16电芯9温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 9 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.224 | hw48VDCPowerSupplyLithiumBattery1Cell10Temperature | Lithium battery 1 cell 10 temperature | 锂电池1电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.225 | hw48VDCPowerSupplyLithiumBattery2Cell10Temperature | Lithium battery 2 cell 10 temperature | 锂电池2电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.226 | hw48VDCPowerSupplyLithiumBattery3Cell10Temperature | Lithium battery 3 cell 10 temperature | 锂电池3电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.227 | hw48VDCPowerSupplyLithiumBattery4Cell10Temperature | Lithium battery 4 cell 10 temperature | 锂电池4电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.228 | hw48VDCPowerSupplyLithiumBattery5Cell10Temperature | Lithium battery 5 cell 10 temperature | 锂电池5电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.229 | hw48VDCPowerSupplyLithiumBattery6Cell10Temperature | Lithium battery 6 cell 10 temperature | 锂电池6电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.230 | hw48VDCPowerSupplyLithiumBattery7Cell10Temperature | Lithium battery 7 cell 10 temperature | 锂电池7电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.231 | hw48VDCPowerSupplyLithiumBattery8Cell10Temperature | Lithium battery 8 cell 10 temperature | 锂电池8电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.232 | hw48VDCPowerSupplyLithiumBattery9Cell10Temperature | Lithium battery 9 cell 10 temperature | 锂电池9电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.233 | hw48VDCPowerSupplyLithiumBattery10Cell10Temperature | Lithium battery 10 cell 10 temperature | 锂电池10电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.234 | hw48VDCPowerSupplyLithiumBattery11Cell10Temperature | Lithium battery 11 cell 10 temperature | 锂电池11电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.235 | hw48VDCPowerSupplyLithiumBattery12Cell10Temperature | Lithium battery 12 cell 10 temperature | 锂电池12电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.236 | hw48VDCPowerSupplyLithiumBattery13Cell10Temperature | Lithium battery 13 cell 10 temperature | 锂电池13电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.237 | hw48VDCPowerSupplyLithiumBattery14Cell10Temperature | Lithium battery 14 cell 10 temperature | 锂电池14电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.238 | hw48VDCPowerSupplyLithiumBattery15Cell10Temperature | Lithium battery 15 cell 10 temperature | 锂电池15电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.239 | hw48VDCPowerSupplyLithiumBattery16Cell10Temperature | Lithium battery 16 cell 10 temperature | 锂电池16电芯10温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 10 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.240 | hw48VDCPowerSupplyLithiumBattery1Cell11Temperature | Lithium battery 1 cell 11 temperature | 锂电池1电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.241 | hw48VDCPowerSupplyLithiumBattery2Cell11Temperature | Lithium battery 2 cell 11 temperature | 锂电池2电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.242 | hw48VDCPowerSupplyLithiumBattery3Cell11Temperature | Lithium battery 3 cell 11 temperature | 锂电池3电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.243 | hw48VDCPowerSupplyLithiumBattery4Cell11Temperature | Lithium battery 4 cell 11 temperature | 锂电池4电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.244 | hw48VDCPowerSupplyLithiumBattery5Cell11Temperature | Lithium battery 5 cell 11 temperature | 锂电池5电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.245 | hw48VDCPowerSupplyLithiumBattery6Cell11Temperature | Lithium battery 6 cell 11 temperature | 锂电池6电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.246 | hw48VDCPowerSupplyLithiumBattery7Cell11Temperature | Lithium battery 7 cell 11 temperature | 锂电池7电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.247 | hw48VDCPowerSupplyLithiumBattery8Cell11Temperature | Lithium battery 8 cell 11 temperature | 锂电池8电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.248 | hw48VDCPowerSupplyLithiumBattery9Cell11Temperature | Lithium battery 9 cell 11 temperature | 锂电池9电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.249 | hw48VDCPowerSupplyLithiumBattery10Cell11Temperature | Lithium battery 10 cell 11 temperature | 锂电池10电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.250 | hw48VDCPowerSupplyLithiumBattery11Cell11Temperature | Lithium battery 11 cell 11 temperature | 锂电池11电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.251 | hw48VDCPowerSupplyLithiumBattery12Cell11Temperature | Lithium battery 12 cell 11 temperature | 锂电池12电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.252 | hw48VDCPowerSupplyLithiumBattery13Cell11Temperature | Lithium battery 13 cell 11 temperature | 锂电池13电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.253 | hw48VDCPowerSupplyLithiumBattery14Cell11Temperature | Lithium battery 14 cell 11 temperature | 锂电池14电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.254 | hw48VDCPowerSupplyLithiumBattery15Cell11Temperature | Lithium battery 15 cell 11 temperature | 锂电池15电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.255 | hw48VDCPowerSupplyLithiumBattery16Cell11Temperature | Lithium battery 16 cell 11 temperature | 锂电池16电芯11温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 11 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.256 | hw48VDCPowerSupplyLithiumBattery1Cell12Temperature | Lithium battery 1 cell 12 temperature | 锂电池1电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.257 | hw48VDCPowerSupplyLithiumBattery2Cell12Temperature | Lithium battery 2 cell 12 temperature | 锂电池2电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.258 | hw48VDCPowerSupplyLithiumBattery3Cell12Temperature | Lithium battery 3 cell 12 temperature | 锂电池3电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.259 | hw48VDCPowerSupplyLithiumBattery4Cell12Temperature | Lithium battery 4 cell 12 temperature | 锂电池4电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.260 | hw48VDCPowerSupplyLithiumBattery5Cell12Temperature | Lithium battery 5 cell 12 temperature | 锂电池5电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.261 | hw48VDCPowerSupplyLithiumBattery6Cell12Temperature | Lithium battery 6 cell 12 temperature | 锂电池6电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.262 | hw48VDCPowerSupplyLithiumBattery7Cell12Temperature | Lithium battery 7 cell 12 temperature | 锂电池7电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.263 | hw48VDCPowerSupplyLithiumBattery8Cell12Temperature | Lithium battery 8 cell 12 temperature | 锂电池8电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.264 | hw48VDCPowerSupplyLithiumBattery9Cell12Temperature | Lithium battery 9 cell 12 temperature | 锂电池9电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.265 | hw48VDCPowerSupplyLithiumBattery10Cell12Temperature | Lithium battery 10 cell 12 temperature | 锂电池10电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.266 | hw48VDCPowerSupplyLithiumBattery11Cell12Temperature | Lithium battery 11 cell 12 temperature | 锂电池11电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.267 | hw48VDCPowerSupplyLithiumBattery12Cell12Temperature | Lithium battery 12 cell 12 temperature | 锂电池12电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.268 | hw48VDCPowerSupplyLithiumBattery13Cell12Temperature | Lithium battery 13 cell 12 temperature | 锂电池13电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.269 | hw48VDCPowerSupplyLithiumBattery14Cell12Temperature | Lithium battery 14 cell 12 temperature | 锂电池14电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.270 | hw48VDCPowerSupplyLithiumBattery15Cell12Temperature | Lithium battery 15 cell 12 temperature | 锂电池15电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.271 | hw48VDCPowerSupplyLithiumBattery16Cell12Temperature | Lithium battery 16 cell 12 temperature | 锂电池16电芯12温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 12 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.272 | hw48VDCPowerSupplyLithiumBattery1Cell13Temperature | Lithium battery 1 cell 13 temperature | 锂电池1电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.273 | hw48VDCPowerSupplyLithiumBattery2Cell13Temperature | Lithium battery 2 cell 13 temperature | 锂电池2电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.274 | hw48VDCPowerSupplyLithiumBattery3Cell13Temperature | Lithium battery 3 cell 13 temperature | 锂电池3电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.275 | hw48VDCPowerSupplyLithiumBattery4Cell13Temperature | Lithium battery 4 cell 13 temperature | 锂电池4电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.276 | hw48VDCPowerSupplyLithiumBattery5Cell13Temperature | Lithium battery 5 cell 13 temperature | 锂电池5电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.277 | hw48VDCPowerSupplyLithiumBattery6Cell13Temperature | Lithium battery 6 cell 13 temperature | 锂电池6电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.278 | hw48VDCPowerSupplyLithiumBattery7Cell13Temperature | Lithium battery 7 cell 13 temperature | 锂电池7电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.279 | hw48VDCPowerSupplyLithiumBattery8Cell13Temperature | Lithium battery 8 cell 13 temperature | 锂电池8电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.280 | hw48VDCPowerSupplyLithiumBattery9Cell13Temperature | Lithium battery 9 cell 13 temperature | 锂电池9电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.281 | hw48VDCPowerSupplyLithiumBattery10Cell13Temperature | Lithium battery 10 cell 13 temperature | 锂电池10电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.282 | hw48VDCPowerSupplyLithiumBattery11Cell13Temperature | Lithium battery 11 cell 13 temperature | 锂电池11电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.283 | hw48VDCPowerSupplyLithiumBattery12Cell13Temperature | Lithium battery 12 cell 13 temperature | 锂电池12电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.284 | hw48VDCPowerSupplyLithiumBattery13Cell13Temperature | Lithium battery 13 cell 13 temperature | 锂电池13电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.285 | hw48VDCPowerSupplyLithiumBattery14Cell13Temperature | Lithium battery 14 cell 13 temperature | 锂电池14电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.286 | hw48VDCPowerSupplyLithiumBattery15Cell13Temperature | Lithium battery 15 cell 13 temperature | 锂电池15电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.287 | hw48VDCPowerSupplyLithiumBattery16Cell13Temperature | Lithium battery 16 cell 13 temperature | 锂电池16电芯13温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 13 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.288 | hw48VDCPowerSupplyLithiumBattery1Cell14Temperature | Lithium battery 1 cell 14 temperature | 锂电池1电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.289 | hw48VDCPowerSupplyLithiumBattery2Cell14Temperature | Lithium battery 2 cell 14 temperature | 锂电池2电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.290 | hw48VDCPowerSupplyLithiumBattery3Cell14Temperature | Lithium battery 3 cell 14 temperature | 锂电池3电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.291 | hw48VDCPowerSupplyLithiumBattery4Cell14Temperature | Lithium battery 4 cell 14 temperature | 锂电池4电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.292 | hw48VDCPowerSupplyLithiumBattery5Cell14Temperature | Lithium battery 5 cell 14 temperature | 锂电池5电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.293 | hw48VDCPowerSupplyLithiumBattery6Cell14Temperature | Lithium battery 6 cell 14 temperature | 锂电池6电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.294 | hw48VDCPowerSupplyLithiumBattery7Cell14Temperature | Lithium battery 7 cell 14 temperature | 锂电池7电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.295 | hw48VDCPowerSupplyLithiumBattery8Cell14Temperature | Lithium battery 8 cell 14 temperature | 锂电池8电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.296 | hw48VDCPowerSupplyLithiumBattery9Cell14Temperature | Lithium battery 9 cell 14 temperature | 锂电池9电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.297 | hw48VDCPowerSupplyLithiumBattery10Cell14Temperature | Lithium battery 10 cell 14 temperature | 锂电池10电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.298 | hw48VDCPowerSupplyLithiumBattery11Cell14Temperature | Lithium battery 11 cell 14 temperature | 锂电池11电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.299 | hw48VDCPowerSupplyLithiumBattery12Cell14Temperature | Lithium battery 12 cell 14 temperature | 锂电池12电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.2.1.300 | hw48VDCPowerSupplyRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.3 | hw48VDCPowerSupplyRunning2Table | / | / |  |  | / | / | The running table of 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.1 | hw48VDCPowerSupplyRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.2 | hw48VDCPowerSupplyLithiumBattery13Cell14Temperature | Lithium battery 13 cell 14 temperature | 锂电池13电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.3 | hw48VDCPowerSupplyLithiumBattery14Cell14Temperature | Lithium battery 14 cell 14 temperature | 锂电池14电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.4 | hw48VDCPowerSupplyLithiumBattery15Cell14Temperature | Lithium battery 15 cell 14 temperature | 锂电池15电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.5 | hw48VDCPowerSupplyLithiumBattery16Cell14Temperature | Lithium battery 16 cell 14 temperature | 锂电池16电芯14温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 14 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.6 | hw48VDCPowerSupplyLithiumBattery1Cell15Temperature | Lithium battery 1 cell 15 temperature | 锂电池1电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.7 | hw48VDCPowerSupplyLithiumBattery2Cell15Temperature | Lithium battery 2 cell 15 temperature | 锂电池2电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.8 | hw48VDCPowerSupplyLithiumBattery3Cell15Temperature | Lithium battery 3 cell 15 temperature | 锂电池3电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.9 | hw48VDCPowerSupplyLithiumBattery4Cell15Temperature | Lithium battery 4 cell 15 temperature | 锂电池4电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.10 | hw48VDCPowerSupplyLithiumBattery5Cell15Temperature | Lithium battery 5 cell 15 temperature | 锂电池5电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.11 | hw48VDCPowerSupplyLithiumBattery6Cell15Temperature | Lithium battery 6 cell 15 temperature | 锂电池6电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.12 | hw48VDCPowerSupplyLithiumBattery7Cell15Temperature | Lithium battery 7 cell 15 temperature | 锂电池7电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.13 | hw48VDCPowerSupplyLithiumBattery8Cell15Temperature | Lithium battery 8 cell 15 temperature | 锂电池8电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.14 | hw48VDCPowerSupplyLithiumBattery9Cell15Temperature | Lithium battery 9 cell 15 temperature | 锂电池9电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.15 | hw48VDCPowerSupplyLithiumBattery10Cell15Temperature | Lithium battery 10 cell 15 temperature | 锂电池10电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.16 | hw48VDCPowerSupplyLithiumBattery11Cell15Temperature | Lithium battery 11 cell 15 temperature | 锂电池11电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.17 | hw48VDCPowerSupplyLithiumBattery12Cell15Temperature | Lithium battery 12 cell 15 temperature | 锂电池12电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.18 | hw48VDCPowerSupplyLithiumBattery13Cell15Temperature | Lithium battery 13 cell 15 temperature | 锂电池13电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.19 | hw48VDCPowerSupplyLithiumBattery14Cell15Temperature | Lithium battery 14 cell 15 temperature | 锂电池14电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.20 | hw48VDCPowerSupplyLithiumBattery15Cell15Temperature | Lithium battery 15 cell 15 temperature | 锂电池15电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.21 | hw48VDCPowerSupplyLithiumBattery16Cell15Temperature | Lithium battery 16 cell 15 temperature | 锂电池16电芯15温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 15 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.22 | hw48VDCPowerSupplyLithiumBattery1Cell16Temperature | Lithium battery 1 cell 16 temperature | 锂电池1电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.23 | hw48VDCPowerSupplyLithiumBattery2Cell16Temperature | Lithium battery 2 cell 16 temperature | 锂电池2电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.24 | hw48VDCPowerSupplyLithiumBattery3Cell16Temperature | Lithium battery 3 cell 16 temperature | 锂电池3电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.25 | hw48VDCPowerSupplyLithiumBattery4Cell16Temperature | Lithium battery 4 cell 16 temperature | 锂电池4电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.26 | hw48VDCPowerSupplyLithiumBattery5Cell16Temperature | Lithium battery 5 cell 16 temperature | 锂电池5电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.27 | hw48VDCPowerSupplyLithiumBattery6Cell16Temperature | Lithium battery 6 cell 16 temperature | 锂电池6电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.28 | hw48VDCPowerSupplyLithiumBattery7Cell16Temperature | Lithium battery 7 cell 16 temperature | 锂电池7电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.29 | hw48VDCPowerSupplyLithiumBattery8Cell16Temperature | Lithium battery 8 cell 16 temperature | 锂电池8电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.30 | hw48VDCPowerSupplyLithiumBattery9Cell16Temperature | Lithium battery 9 cell 16 temperature | 锂电池9电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.31 | hw48VDCPowerSupplyLithiumBattery10Cell16Temperature | Lithium battery 10 cell 16 temperature | 锂电池10电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.32 | hw48VDCPowerSupplyLithiumBattery11Cell16Temperature | Lithium battery 11 cell 16 temperature | 锂电池11电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.33 | hw48VDCPowerSupplyLithiumBattery12Cell16Temperature | Lithium battery 12 cell 16 temperature | 锂电池12电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.34 | hw48VDCPowerSupplyLithiumBattery13Cell16Temperature | Lithium battery 13 cell 16 temperature | 锂电池13电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.35 | hw48VDCPowerSupplyLithiumBattery14Cell16Temperature | Lithium battery 14 cell 16 temperature | 锂电池14电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.36 | hw48VDCPowerSupplyLithiumBattery15Cell16Temperature | Lithium battery 15 cell 16 temperature | 锂电池15电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.37 | hw48VDCPowerSupplyLithiumBattery16Cell16Temperature | Lithium battery 16 cell 16 temperature | 锂电池16电芯16温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 16 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.38 | hw48VDCPowerSupplyLithiumBattery1Cell17Temperature | Lithium battery 1 cell 17 temperature | 锂电池1电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.39 | hw48VDCPowerSupplyLithiumBattery2Cell17Temperature | Lithium battery 2 cell 17 temperature | 锂电池2电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.40 | hw48VDCPowerSupplyLithiumBattery3Cell17Temperature | Lithium battery 3 cell 17 temperature | 锂电池3电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.41 | hw48VDCPowerSupplyLithiumBattery4Cell17Temperature | Lithium battery 4 cell 17 temperature | 锂电池4电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.42 | hw48VDCPowerSupplyLithiumBattery5Cell17Temperature | Lithium battery 5 cell 17 temperature | 锂电池5电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.43 | hw48VDCPowerSupplyLithiumBattery6Cell17Temperature | Lithium battery 6 cell 17 temperature | 锂电池6电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.44 | hw48VDCPowerSupplyLithiumBattery7Cell17Temperature | Lithium battery 7 cell 17 temperature | 锂电池7电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.45 | hw48VDCPowerSupplyLithiumBattery8Cell17Temperature | Lithium battery 8 cell 17 temperature | 锂电池8电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.46 | hw48VDCPowerSupplyLithiumBattery9Cell17Temperature | Lithium battery 9 cell 17 temperature | 锂电池9电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.47 | hw48VDCPowerSupplyLithiumBattery10Cell17Temperature | Lithium battery 10 cell 17 temperature | 锂电池10电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.48 | hw48VDCPowerSupplyLithiumBattery11Cell17Temperature | Lithium battery 11 cell 17 temperature | 锂电池11电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.49 | hw48VDCPowerSupplyLithiumBattery12Cell17Temperature | Lithium battery 12 cell 17 temperature | 锂电池12电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.50 | hw48VDCPowerSupplyLithiumBattery13Cell17Temperature | Lithium battery 13 cell 17 temperature | 锂电池13电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.51 | hw48VDCPowerSupplyLithiumBattery14Cell17Temperature | Lithium battery 14 cell 17 temperature | 锂电池14电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.52 | hw48VDCPowerSupplyLithiumBattery15Cell17Temperature | Lithium battery 15 cell 17 temperature | 锂电池15电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.53 | hw48VDCPowerSupplyLithiumBattery16Cell17Temperature | Lithium battery 16 cell 17 temperature | 锂电池16电芯17温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 17 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.54 | hw48VDCPowerSupplyLithiumBattery1Cell18Temperature | Lithium battery 1 cell 18 temperature | 锂电池1电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.55 | hw48VDCPowerSupplyLithiumBattery2Cell18Temperature | Lithium battery 2 cell 18 temperature | 锂电池2电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.56 | hw48VDCPowerSupplyLithiumBattery3Cell18Temperature | Lithium battery 3 cell 18 temperature | 锂电池3电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.57 | hw48VDCPowerSupplyLithiumBattery4Cell18Temperature | Lithium battery 4 cell 18 temperature | 锂电池4电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.58 | hw48VDCPowerSupplyLithiumBattery5Cell18Temperature | Lithium battery 5 cell 18 temperature | 锂电池5电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.59 | hw48VDCPowerSupplyLithiumBattery6Cell18Temperature | Lithium battery 6 cell 18 temperature | 锂电池6电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.60 | hw48VDCPowerSupplyLithiumBattery7Cell18Temperature | Lithium battery 7 cell 18 temperature | 锂电池7电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.61 | hw48VDCPowerSupplyLithiumBattery8Cell18Temperature | Lithium battery 8 cell 18 temperature | 锂电池8电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.62 | hw48VDCPowerSupplyLithiumBattery9Cell18Temperature | Lithium battery 9 cell 18 temperature | 锂电池9电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.63 | hw48VDCPowerSupplyLithiumBattery10Cell18Temperature | Lithium battery 10 cell 18 temperature | 锂电池10电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.64 | hw48VDCPowerSupplyLithiumBattery11Cell18Temperature | Lithium battery 11 cell 18 temperature | 锂电池11电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.65 | hw48VDCPowerSupplyLithiumBattery12Cell18Temperature | Lithium battery 12 cell 18 temperature | 锂电池12电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.66 | hw48VDCPowerSupplyLithiumBattery13Cell18Temperature | Lithium battery 13 cell 18 temperature | 锂电池13电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.67 | hw48VDCPowerSupplyLithiumBattery14Cell18Temperature | Lithium battery 14 cell 18 temperature | 锂电池14电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.68 | hw48VDCPowerSupplyLithiumBattery15Cell18Temperature | Lithium battery 15 cell 18 temperature | 锂电池15电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.69 | hw48VDCPowerSupplyLithiumBattery16Cell18Temperature | Lithium battery 16 cell 18 temperature | 锂电池16电芯18温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 18 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.70 | hw48VDCPowerSupplyLithiumBattery1Cell19Temperature | Lithium battery 1 cell 19 temperature | 锂电池1电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.71 | hw48VDCPowerSupplyLithiumBattery2Cell19Temperature | Lithium battery 2 cell 19 temperature | 锂电池2电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.72 | hw48VDCPowerSupplyLithiumBattery3Cell19Temperature | Lithium battery 3 cell 19 temperature | 锂电池3电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.73 | hw48VDCPowerSupplyLithiumBattery4Cell19Temperature | Lithium battery 4 cell 19 temperature | 锂电池4电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.74 | hw48VDCPowerSupplyLithiumBattery5Cell19Temperature | Lithium battery 5 cell 19 temperature | 锂电池5电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.75 | hw48VDCPowerSupplyLithiumBattery6Cell19Temperature | Lithium battery 6 cell 19 temperature | 锂电池6电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.76 | hw48VDCPowerSupplyLithiumBattery7Cell19Temperature | Lithium battery 7 cell 19 temperature | 锂电池7电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.77 | hw48VDCPowerSupplyLithiumBattery8Cell19Temperature | Lithium battery 8 cell 19 temperature | 锂电池8电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.78 | hw48VDCPowerSupplyLithiumBattery9Cell19Temperature | Lithium battery 9 cell 19 temperature | 锂电池9电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.79 | hw48VDCPowerSupplyLithiumBattery10Cell19Temperature | Lithium battery 10 cell 19 temperature | 锂电池10电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.80 | hw48VDCPowerSupplyLithiumBattery11Cell19Temperature | Lithium battery 11 cell 19 temperature | 锂电池11电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.81 | hw48VDCPowerSupplyLithiumBattery12Cell19Temperature | Lithium battery 12 cell 19 temperature | 锂电池12电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.82 | hw48VDCPowerSupplyLithiumBattery13Cell19Temperature | Lithium battery 13 cell 19 temperature | 锂电池13电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.83 | hw48VDCPowerSupplyLithiumBattery14Cell19Temperature | Lithium battery 14 cell 19 temperature | 锂电池14电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.84 | hw48VDCPowerSupplyLithiumBattery15Cell19Temperature | Lithium battery 15 cell 19 temperature | 锂电池15电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.85 | hw48VDCPowerSupplyLithiumBattery16Cell19Temperature | Lithium battery 16 cell 19 temperature | 锂电池16电芯19温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 19 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.86 | hw48VDCPowerSupplyLithiumBattery1Cell20Temperature | Lithium battery 1 cell 20 temperature | 锂电池1电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 1 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.87 | hw48VDCPowerSupplyLithiumBattery2Cell20Temperature | Lithium battery 2 cell 20 temperature | 锂电池2电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 2 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.88 | hw48VDCPowerSupplyLithiumBattery3Cell20Temperature | Lithium battery 3 cell 20 temperature | 锂电池3电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 3 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.89 | hw48VDCPowerSupplyLithiumBattery4Cell20Temperature | Lithium battery 4 cell 20 temperature | 锂电池4电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 4 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.90 | hw48VDCPowerSupplyLithiumBattery5Cell20Temperature | Lithium battery 5 cell 20 temperature | 锂电池5电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 5 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.91 | hw48VDCPowerSupplyLithiumBattery6Cell20Temperature | Lithium battery 6 cell 20 temperature | 锂电池6电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 6 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.92 | hw48VDCPowerSupplyLithiumBattery7Cell20Temperature | Lithium battery 7 cell 20 temperature | 锂电池7电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 7 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.93 | hw48VDCPowerSupplyLithiumBattery8Cell20Temperature | Lithium battery 8 cell 20 temperature | 锂电池8电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 8 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.94 | hw48VDCPowerSupplyLithiumBattery9Cell20Temperature | Lithium battery 9 cell 20 temperature | 锂电池9电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 9 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.95 | hw48VDCPowerSupplyLithiumBattery10Cell20Temperature | Lithium battery 10 cell 20 temperature | 锂电池10电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 10 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.96 | hw48VDCPowerSupplyLithiumBattery11Cell20Temperature | Lithium battery 11 cell 20 temperature | 锂电池11电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 11 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.97 | hw48VDCPowerSupplyLithiumBattery12Cell20Temperature | Lithium battery 12 cell 20 temperature | 锂电池12电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 12 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.98 | hw48VDCPowerSupplyLithiumBattery13Cell20Temperature | Lithium battery 13 cell 20 temperature | 锂电池13电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 13 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.99 | hw48VDCPowerSupplyLithiumBattery14Cell20Temperature | Lithium battery 14 cell 20 temperature | 锂电池14电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 14 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.100 | hw48VDCPowerSupplyLithiumBattery15Cell20Temperature | Lithium battery 15 cell 20 temperature | 锂电池15电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 15 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.101 | hw48VDCPowerSupplyLithiumBattery16Cell20Temperature | Lithium battery 16 cell 20 temperature | 锂电池16电芯20温度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Lithium battery 16 cell 20 temperature of the device config table for the 48 V DC Power Supply.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.102 | hw48VDCPowerSupplyLithiumBattery1Cell1Voltage | Lithium battery 1 cell 1 voltage | 锂电池1电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.103 | hw48VDCPowerSupplyLithiumBattery2Cell1Voltage | Lithium battery 2 cell 1 voltage | 锂电池2电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.104 | hw48VDCPowerSupplyLithiumBattery3Cell1Voltage | Lithium battery 3 cell 1 voltage | 锂电池3电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.105 | hw48VDCPowerSupplyLithiumBattery4Cell1Voltage | Lithium battery 4 cell 1 voltage | 锂电池4电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.106 | hw48VDCPowerSupplyLithiumBattery5Cell1Voltage | Lithium battery 5 cell 1 voltage | 锂电池5电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.107 | hw48VDCPowerSupplyLithiumBattery6Cell1Voltage | Lithium battery 6 cell 1 voltage | 锂电池6电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.108 | hw48VDCPowerSupplyLithiumBattery7Cell1Voltage | Lithium battery 7 cell 1 voltage | 锂电池7电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.109 | hw48VDCPowerSupplyLithiumBattery8Cell1Voltage | Lithium battery 8 cell 1 voltage | 锂电池8电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.110 | hw48VDCPowerSupplyLithiumBattery9Cell1Voltage | Lithium battery 9 cell 1 voltage | 锂电池9电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.111 | hw48VDCPowerSupplyLithiumBattery10Cell1Voltage | Lithium battery 10 cell 1 voltage | 锂电池10电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.112 | hw48VDCPowerSupplyLithiumBattery11Cell1Voltage | Lithium battery 11 cell 1 voltage | 锂电池11电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.113 | hw48VDCPowerSupplyLithiumBattery12Cell1Voltage | Lithium battery 12 cell 1 voltage | 锂电池12电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.114 | hw48VDCPowerSupplyLithiumBattery13Cell1Voltage | Lithium battery 13 cell 1 voltage | 锂电池13电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.115 | hw48VDCPowerSupplyLithiumBattery14Cell1Voltage | Lithium battery 14 cell 1 voltage | 锂电池14电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.116 | hw48VDCPowerSupplyLithiumBattery15Cell1Voltage | Lithium battery 15 cell 1 voltage | 锂电池15电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.117 | hw48VDCPowerSupplyLithiumBattery16Cell1Voltage | Lithium battery 16 cell 1 voltage | 锂电池16电芯1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 1 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.118 | hw48VDCPowerSupplyLithiumBattery1Cell2Voltage | Lithium battery 1 cell 2 voltage | 锂电池1电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.119 | hw48VDCPowerSupplyLithiumBattery2Cell2Voltage | Lithium battery 2 cell 2 voltage | 锂电池2电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.120 | hw48VDCPowerSupplyLithiumBattery3Cell2Voltage | Lithium battery 3 cell 2 voltage | 锂电池3电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.121 | hw48VDCPowerSupplyLithiumBattery4Cell2Voltage | Lithium battery 4 cell 2 voltage | 锂电池4电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.122 | hw48VDCPowerSupplyLithiumBattery5Cell2Voltage | Lithium battery 5 cell 2 voltage | 锂电池5电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.123 | hw48VDCPowerSupplyLithiumBattery6Cell2Voltage | Lithium battery 6 cell 2 voltage | 锂电池6电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.124 | hw48VDCPowerSupplyLithiumBattery7Cell2Voltage | Lithium battery 7 cell 2 voltage | 锂电池7电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.125 | hw48VDCPowerSupplyLithiumBattery8Cell2Voltage | Lithium battery 8 cell 2 voltage | 锂电池8电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.126 | hw48VDCPowerSupplyLithiumBattery9Cell2Voltage | Lithium battery 9 cell 2 voltage | 锂电池9电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.127 | hw48VDCPowerSupplyLithiumBattery10Cell2Voltage | Lithium battery 10 cell 2 voltage | 锂电池10电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.128 | hw48VDCPowerSupplyLithiumBattery11Cell2Voltage | Lithium battery 11 cell 2 voltage | 锂电池11电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.129 | hw48VDCPowerSupplyLithiumBattery12Cell2Voltage | Lithium battery 12 cell 2 voltage | 锂电池12电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.130 | hw48VDCPowerSupplyLithiumBattery13Cell2Voltage | Lithium battery 13 cell 2 voltage | 锂电池13电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.131 | hw48VDCPowerSupplyLithiumBattery14Cell2Voltage | Lithium battery 14 cell 2 voltage | 锂电池14电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.132 | hw48VDCPowerSupplyLithiumBattery15Cell2Voltage | Lithium battery 15 cell 2 voltage | 锂电池15电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.133 | hw48VDCPowerSupplyLithiumBattery16Cell2Voltage | Lithium battery 16 cell 2 voltage | 锂电池16电芯2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 2 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.134 | hw48VDCPowerSupplyLithiumBattery1Cell3Voltage | Lithium battery 1 cell 3 voltage | 锂电池1电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.135 | hw48VDCPowerSupplyLithiumBattery2Cell3Voltage | Lithium battery 2 cell 3 voltage | 锂电池2电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.136 | hw48VDCPowerSupplyLithiumBattery3Cell3Voltage | Lithium battery 3 cell 3 voltage | 锂电池3电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.137 | hw48VDCPowerSupplyLithiumBattery4Cell3Voltage | Lithium battery 4 cell 3 voltage | 锂电池4电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.138 | hw48VDCPowerSupplyLithiumBattery5Cell3Voltage | Lithium battery 5 cell 3 voltage | 锂电池5电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.139 | hw48VDCPowerSupplyLithiumBattery6Cell3Voltage | Lithium battery 6 cell 3 voltage | 锂电池6电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.140 | hw48VDCPowerSupplyLithiumBattery7Cell3Voltage | Lithium battery 7 cell 3 voltage | 锂电池7电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.141 | hw48VDCPowerSupplyLithiumBattery8Cell3Voltage | Lithium battery 8 cell 3 voltage | 锂电池8电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.142 | hw48VDCPowerSupplyLithiumBattery9Cell3Voltage | Lithium battery 9 cell 3 voltage | 锂电池9电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.143 | hw48VDCPowerSupplyLithiumBattery10Cell3Voltage | Lithium battery 10 cell 3 voltage | 锂电池10电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.144 | hw48VDCPowerSupplyLithiumBattery11Cell3Voltage | Lithium battery 11 cell 3 voltage | 锂电池11电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.145 | hw48VDCPowerSupplyLithiumBattery12Cell3Voltage | Lithium battery 12 cell 3 voltage | 锂电池12电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.146 | hw48VDCPowerSupplyLithiumBattery13Cell3Voltage | Lithium battery 13 cell 3 voltage | 锂电池13电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.147 | hw48VDCPowerSupplyLithiumBattery14Cell3Voltage | Lithium battery 14 cell 3 voltage | 锂电池14电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.148 | hw48VDCPowerSupplyLithiumBattery15Cell3Voltage | Lithium battery 15 cell 3 voltage | 锂电池15电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.149 | hw48VDCPowerSupplyLithiumBattery16Cell3Voltage | Lithium battery 16 cell 3 voltage | 锂电池16电芯3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 3 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.150 | hw48VDCPowerSupplyLithiumBattery1Cell4Voltage | Lithium battery 1 cell 4 voltage | 锂电池1电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.151 | hw48VDCPowerSupplyLithiumBattery2Cell4Voltage | Lithium battery 2 cell 4 voltage | 锂电池2电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.152 | hw48VDCPowerSupplyLithiumBattery3Cell4Voltage | Lithium battery 3 cell 4 voltage | 锂电池3电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.153 | hw48VDCPowerSupplyLithiumBattery4Cell4Voltage | Lithium battery 4 cell 4 voltage | 锂电池4电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.154 | hw48VDCPowerSupplyLithiumBattery5Cell4Voltage | Lithium battery 5 cell 4 voltage | 锂电池5电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.155 | hw48VDCPowerSupplyLithiumBattery6Cell4Voltage | Lithium battery 6 cell 4 voltage | 锂电池6电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.156 | hw48VDCPowerSupplyLithiumBattery7Cell4Voltage | Lithium battery 7 cell 4 voltage | 锂电池7电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.157 | hw48VDCPowerSupplyLithiumBattery8Cell4Voltage | Lithium battery 8 cell 4 voltage | 锂电池8电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.158 | hw48VDCPowerSupplyLithiumBattery9Cell4Voltage | Lithium battery 9 cell 4 voltage | 锂电池9电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.159 | hw48VDCPowerSupplyLithiumBattery10Cell4Voltage | Lithium battery 10 cell 4 voltage | 锂电池10电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.160 | hw48VDCPowerSupplyLithiumBattery11Cell4Voltage | Lithium battery 11 cell 4 voltage | 锂电池11电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.161 | hw48VDCPowerSupplyLithiumBattery12Cell4Voltage | Lithium battery 12 cell 4 voltage | 锂电池12电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.162 | hw48VDCPowerSupplyLithiumBattery13Cell4Voltage | Lithium battery 13 cell 4 voltage | 锂电池13电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.163 | hw48VDCPowerSupplyLithiumBattery14Cell4Voltage | Lithium battery 14 cell 4 voltage | 锂电池14电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.164 | hw48VDCPowerSupplyLithiumBattery15Cell4Voltage | Lithium battery 15 cell 4 voltage | 锂电池15电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.165 | hw48VDCPowerSupplyLithiumBattery16Cell4Voltage | Lithium battery 16 cell 4 voltage | 锂电池16电芯4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 4 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.166 | hw48VDCPowerSupplyLithiumBattery1Cell5Voltage | Lithium battery 1 cell 5 voltage | 锂电池1电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.167 | hw48VDCPowerSupplyLithiumBattery2Cell5Voltage | Lithium battery 2 cell 5 voltage | 锂电池2电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.168 | hw48VDCPowerSupplyLithiumBattery3Cell5Voltage | Lithium battery 3 cell 5 voltage | 锂电池3电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.169 | hw48VDCPowerSupplyLithiumBattery4Cell5Voltage | Lithium battery 4 cell 5 voltage | 锂电池4电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.170 | hw48VDCPowerSupplyLithiumBattery5Cell5Voltage | Lithium battery 5 cell 5 voltage | 锂电池5电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.171 | hw48VDCPowerSupplyLithiumBattery6Cell5Voltage | Lithium battery 6 cell 5 voltage | 锂电池6电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.172 | hw48VDCPowerSupplyLithiumBattery7Cell5Voltage | Lithium battery 7 cell 5 voltage | 锂电池7电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.173 | hw48VDCPowerSupplyLithiumBattery8Cell5Voltage | Lithium battery 8 cell 5 voltage | 锂电池8电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.174 | hw48VDCPowerSupplyLithiumBattery9Cell5Voltage | Lithium battery 9 cell 5 voltage | 锂电池9电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.175 | hw48VDCPowerSupplyLithiumBattery10Cell5Voltage | Lithium battery 10 cell 5 voltage | 锂电池10电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.176 | hw48VDCPowerSupplyLithiumBattery11Cell5Voltage | Lithium battery 11 cell 5 voltage | 锂电池11电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.177 | hw48VDCPowerSupplyLithiumBattery12Cell5Voltage | Lithium battery 12 cell 5 voltage | 锂电池12电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.178 | hw48VDCPowerSupplyLithiumBattery13Cell5Voltage | Lithium battery 13 cell 5 voltage | 锂电池13电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.179 | hw48VDCPowerSupplyLithiumBattery14Cell5Voltage | Lithium battery 14 cell 5 voltage | 锂电池14电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.180 | hw48VDCPowerSupplyLithiumBattery15Cell5Voltage | Lithium battery 15 cell 5 voltage | 锂电池15电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.181 | hw48VDCPowerSupplyLithiumBattery16Cell5Voltage | Lithium battery 16 cell 5 voltage | 锂电池16电芯5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 5 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.182 | hw48VDCPowerSupplyLithiumBattery1Cell6Voltage | Lithium battery 1 cell 6 voltage | 锂电池1电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.183 | hw48VDCPowerSupplyLithiumBattery2Cell6Voltage | Lithium battery 2 cell 6 voltage | 锂电池2电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.184 | hw48VDCPowerSupplyLithiumBattery3Cell6Voltage | Lithium battery 3 cell 6 voltage | 锂电池3电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.185 | hw48VDCPowerSupplyLithiumBattery4Cell6Voltage | Lithium battery 4 cell 6 voltage | 锂电池4电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.186 | hw48VDCPowerSupplyLithiumBattery5Cell6Voltage | Lithium battery 5 cell 6 voltage | 锂电池5电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.187 | hw48VDCPowerSupplyLithiumBattery6Cell6Voltage | Lithium battery 6 cell 6 voltage | 锂电池6电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.188 | hw48VDCPowerSupplyLithiumBattery7Cell6Voltage | Lithium battery 7 cell 6 voltage | 锂电池7电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.189 | hw48VDCPowerSupplyLithiumBattery8Cell6Voltage | Lithium battery 8 cell 6 voltage | 锂电池8电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.190 | hw48VDCPowerSupplyLithiumBattery9Cell6Voltage | Lithium battery 9 cell 6 voltage | 锂电池9电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.191 | hw48VDCPowerSupplyLithiumBattery10Cell6Voltage | Lithium battery 10 cell 6 voltage | 锂电池10电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.192 | hw48VDCPowerSupplyLithiumBattery11Cell6Voltage | Lithium battery 11 cell 6 voltage | 锂电池11电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.193 | hw48VDCPowerSupplyLithiumBattery12Cell6Voltage | Lithium battery 12 cell 6 voltage | 锂电池12电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.194 | hw48VDCPowerSupplyLithiumBattery13Cell6Voltage | Lithium battery 13 cell 6 voltage | 锂电池13电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.195 | hw48VDCPowerSupplyLithiumBattery14Cell6Voltage | Lithium battery 14 cell 6 voltage | 锂电池14电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.196 | hw48VDCPowerSupplyLithiumBattery15Cell6Voltage | Lithium battery 15 cell 6 voltage | 锂电池15电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.197 | hw48VDCPowerSupplyLithiumBattery16Cell6Voltage | Lithium battery 16 cell 6 voltage | 锂电池16电芯6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 6 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.198 | hw48VDCPowerSupplyLithiumBattery1Cell7Voltage | Lithium battery 1 cell 7 voltage | 锂电池1电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.199 | hw48VDCPowerSupplyLithiumBattery2Cell7Voltage | Lithium battery 2 cell 7 voltage | 锂电池2电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.200 | hw48VDCPowerSupplyLithiumBattery3Cell7Voltage | Lithium battery 3 cell 7 voltage | 锂电池3电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.201 | hw48VDCPowerSupplyLithiumBattery4Cell7Voltage | Lithium battery 4 cell 7 voltage | 锂电池4电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.202 | hw48VDCPowerSupplyLithiumBattery5Cell7Voltage | Lithium battery 5 cell 7 voltage | 锂电池5电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.203 | hw48VDCPowerSupplyLithiumBattery6Cell7Voltage | Lithium battery 6 cell 7 voltage | 锂电池6电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.204 | hw48VDCPowerSupplyLithiumBattery7Cell7Voltage | Lithium battery 7 cell 7 voltage | 锂电池7电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.205 | hw48VDCPowerSupplyLithiumBattery8Cell7Voltage | Lithium battery 8 cell 7 voltage | 锂电池8电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.206 | hw48VDCPowerSupplyLithiumBattery9Cell7Voltage | Lithium battery 9 cell 7 voltage | 锂电池9电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.207 | hw48VDCPowerSupplyLithiumBattery10Cell7Voltage | Lithium battery 10 cell 7 voltage | 锂电池10电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.208 | hw48VDCPowerSupplyLithiumBattery11Cell7Voltage | Lithium battery 11 cell 7 voltage | 锂电池11电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.209 | hw48VDCPowerSupplyLithiumBattery12Cell7Voltage | Lithium battery 12 cell 7 voltage | 锂电池12电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.210 | hw48VDCPowerSupplyLithiumBattery13Cell7Voltage | Lithium battery 13 cell 7 voltage | 锂电池13电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.211 | hw48VDCPowerSupplyLithiumBattery14Cell7Voltage | Lithium battery 14 cell 7 voltage | 锂电池14电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.212 | hw48VDCPowerSupplyLithiumBattery15Cell7Voltage | Lithium battery 15 cell 7 voltage | 锂电池15电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.213 | hw48VDCPowerSupplyLithiumBattery16Cell7Voltage | Lithium battery 16 cell 7 voltage | 锂电池16电芯7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 7 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.214 | hw48VDCPowerSupplyLithiumBattery1Cell8Voltage | Lithium battery 1 cell 8 voltage | 锂电池1电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.215 | hw48VDCPowerSupplyLithiumBattery2Cell8Voltage | Lithium battery 2 cell 8 voltage | 锂电池2电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.216 | hw48VDCPowerSupplyLithiumBattery3Cell8Voltage | Lithium battery 3 cell 8 voltage | 锂电池3电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.217 | hw48VDCPowerSupplyLithiumBattery4Cell8Voltage | Lithium battery 4 cell 8 voltage | 锂电池4电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.218 | hw48VDCPowerSupplyLithiumBattery5Cell8Voltage | Lithium battery 5 cell 8 voltage | 锂电池5电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.219 | hw48VDCPowerSupplyLithiumBattery6Cell8Voltage | Lithium battery 6 cell 8 voltage | 锂电池6电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.220 | hw48VDCPowerSupplyLithiumBattery7Cell8Voltage | Lithium battery 7 cell 8 voltage | 锂电池7电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.221 | hw48VDCPowerSupplyLithiumBattery8Cell8Voltage | Lithium battery 8 cell 8 voltage | 锂电池8电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.222 | hw48VDCPowerSupplyLithiumBattery9Cell8Voltage | Lithium battery 9 cell 8 voltage | 锂电池9电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.223 | hw48VDCPowerSupplyLithiumBattery10Cell8Voltage | Lithium battery 10 cell 8 voltage | 锂电池10电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.224 | hw48VDCPowerSupplyLithiumBattery11Cell8Voltage | Lithium battery 11 cell 8 voltage | 锂电池11电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.225 | hw48VDCPowerSupplyLithiumBattery12Cell8Voltage | Lithium battery 12 cell 8 voltage | 锂电池12电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.226 | hw48VDCPowerSupplyLithiumBattery13Cell8Voltage | Lithium battery 13 cell 8 voltage | 锂电池13电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.227 | hw48VDCPowerSupplyLithiumBattery14Cell8Voltage | Lithium battery 14 cell 8 voltage | 锂电池14电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.228 | hw48VDCPowerSupplyLithiumBattery15Cell8Voltage | Lithium battery 15 cell 8 voltage | 锂电池15电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.229 | hw48VDCPowerSupplyLithiumBattery16Cell8Voltage | Lithium battery 16 cell 8 voltage | 锂电池16电芯8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 8 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.230 | hw48VDCPowerSupplyLithiumBattery1Cell9Voltage | Lithium battery 1 cell 9 voltage | 锂电池1电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.231 | hw48VDCPowerSupplyLithiumBattery2Cell9Voltage | Lithium battery 2 cell 9 voltage | 锂电池2电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.232 | hw48VDCPowerSupplyLithiumBattery3Cell9Voltage | Lithium battery 3 cell 9 voltage | 锂电池3电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.233 | hw48VDCPowerSupplyLithiumBattery4Cell9Voltage | Lithium battery 4 cell 9 voltage | 锂电池4电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.234 | hw48VDCPowerSupplyLithiumBattery5Cell9Voltage | Lithium battery 5 cell 9 voltage | 锂电池5电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.235 | hw48VDCPowerSupplyLithiumBattery6Cell9Voltage | Lithium battery 6 cell 9 voltage | 锂电池6电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.236 | hw48VDCPowerSupplyLithiumBattery7Cell9Voltage | Lithium battery 7 cell 9 voltage | 锂电池7电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.237 | hw48VDCPowerSupplyLithiumBattery8Cell9Voltage | Lithium battery 8 cell 9 voltage | 锂电池8电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.238 | hw48VDCPowerSupplyLithiumBattery9Cell9Voltage | Lithium battery 9 cell 9 voltage | 锂电池9电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.239 | hw48VDCPowerSupplyLithiumBattery10Cell9Voltage | Lithium battery 10 cell 9 voltage | 锂电池10电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.240 | hw48VDCPowerSupplyLithiumBattery11Cell9Voltage | Lithium battery 11 cell 9 voltage | 锂电池11电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.241 | hw48VDCPowerSupplyLithiumBattery12Cell9Voltage | Lithium battery 12 cell 9 voltage | 锂电池12电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.242 | hw48VDCPowerSupplyLithiumBattery13Cell9Voltage | Lithium battery 13 cell 9 voltage | 锂电池13电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.243 | hw48VDCPowerSupplyLithiumBattery14Cell9Voltage | Lithium battery 14 cell 9 voltage | 锂电池14电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.244 | hw48VDCPowerSupplyLithiumBattery15Cell9Voltage | Lithium battery 15 cell 9 voltage | 锂电池15电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.245 | hw48VDCPowerSupplyLithiumBattery16Cell9Voltage | Lithium battery 16 cell 9 voltage | 锂电池16电芯9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 9 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.246 | hw48VDCPowerSupplyLithiumBattery1Cell10Voltage | Lithium battery 1 cell 10 voltage | 锂电池1电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.247 | hw48VDCPowerSupplyLithiumBattery2Cell10Voltage | Lithium battery 2 cell 10 voltage | 锂电池2电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.248 | hw48VDCPowerSupplyLithiumBattery3Cell10Voltage | Lithium battery 3 cell 10 voltage | 锂电池3电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.249 | hw48VDCPowerSupplyLithiumBattery4Cell10Voltage | Lithium battery 4 cell 10 voltage | 锂电池4电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.250 | hw48VDCPowerSupplyLithiumBattery5Cell10Voltage | Lithium battery 5 cell 10 voltage | 锂电池5电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.251 | hw48VDCPowerSupplyLithiumBattery6Cell10Voltage | Lithium battery 6 cell 10 voltage | 锂电池6电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.252 | hw48VDCPowerSupplyLithiumBattery7Cell10Voltage | Lithium battery 7 cell 10 voltage | 锂电池7电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.253 | hw48VDCPowerSupplyLithiumBattery8Cell10Voltage | Lithium battery 8 cell 10 voltage | 锂电池8电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.254 | hw48VDCPowerSupplyLithiumBattery9Cell10Voltage | Lithium battery 9 cell 10 voltage | 锂电池9电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.255 | hw48VDCPowerSupplyLithiumBattery10Cell10Voltage | Lithium battery 10 cell 10 voltage | 锂电池10电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.256 | hw48VDCPowerSupplyLithiumBattery11Cell10Voltage | Lithium battery 11 cell 10 voltage | 锂电池11电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.257 | hw48VDCPowerSupplyLithiumBattery12Cell10Voltage | Lithium battery 12 cell 10 voltage | 锂电池12电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.258 | hw48VDCPowerSupplyLithiumBattery13Cell10Voltage | Lithium battery 13 cell 10 voltage | 锂电池13电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.259 | hw48VDCPowerSupplyLithiumBattery14Cell10Voltage | Lithium battery 14 cell 10 voltage | 锂电池14电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.260 | hw48VDCPowerSupplyLithiumBattery15Cell10Voltage | Lithium battery 15 cell 10 voltage | 锂电池15电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.261 | hw48VDCPowerSupplyLithiumBattery16Cell10Voltage | Lithium battery 16 cell 10 voltage | 锂电池16电芯10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 10 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.262 | hw48VDCPowerSupplyLithiumBattery1Cell11Voltage | Lithium battery 1 cell 11 voltage | 锂电池1电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.263 | hw48VDCPowerSupplyLithiumBattery2Cell11Voltage | Lithium battery 2 cell 11 voltage | 锂电池2电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.264 | hw48VDCPowerSupplyLithiumBattery3Cell11Voltage | Lithium battery 3 cell 11 voltage | 锂电池3电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.265 | hw48VDCPowerSupplyLithiumBattery4Cell11Voltage | Lithium battery 4 cell 11 voltage | 锂电池4电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.266 | hw48VDCPowerSupplyLithiumBattery5Cell11Voltage | Lithium battery 5 cell 11 voltage | 锂电池5电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.267 | hw48VDCPowerSupplyLithiumBattery6Cell11Voltage | Lithium battery 6 cell 11 voltage | 锂电池6电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.268 | hw48VDCPowerSupplyLithiumBattery7Cell11Voltage | Lithium battery 7 cell 11 voltage | 锂电池7电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.269 | hw48VDCPowerSupplyLithiumBattery8Cell11Voltage | Lithium battery 8 cell 11 voltage | 锂电池8电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.270 | hw48VDCPowerSupplyLithiumBattery9Cell11Voltage | Lithium battery 9 cell 11 voltage | 锂电池9电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.271 | hw48VDCPowerSupplyLithiumBattery10Cell11Voltage | Lithium battery 10 cell 11 voltage | 锂电池10电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.272 | hw48VDCPowerSupplyLithiumBattery11Cell11Voltage | Lithium battery 11 cell 11 voltage | 锂电池11电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.273 | hw48VDCPowerSupplyLithiumBattery12Cell11Voltage | Lithium battery 12 cell 11 voltage | 锂电池12电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.274 | hw48VDCPowerSupplyLithiumBattery13Cell11Voltage | Lithium battery 13 cell 11 voltage | 锂电池13电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.275 | hw48VDCPowerSupplyLithiumBattery14Cell11Voltage | Lithium battery 14 cell 11 voltage | 锂电池14电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.276 | hw48VDCPowerSupplyLithiumBattery15Cell11Voltage | Lithium battery 15 cell 11 voltage | 锂电池15电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.277 | hw48VDCPowerSupplyLithiumBattery16Cell11Voltage | Lithium battery 16 cell 11 voltage | 锂电池16电芯11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 11 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.278 | hw48VDCPowerSupplyLithiumBattery1Cell12Voltage | Lithium battery 1 cell 12 voltage | 锂电池1电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.279 | hw48VDCPowerSupplyLithiumBattery2Cell12Voltage | Lithium battery 2 cell 12 voltage | 锂电池2电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.280 | hw48VDCPowerSupplyLithiumBattery3Cell12Voltage | Lithium battery 3 cell 12 voltage | 锂电池3电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.281 | hw48VDCPowerSupplyLithiumBattery4Cell12Voltage | Lithium battery 4 cell 12 voltage | 锂电池4电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.282 | hw48VDCPowerSupplyLithiumBattery5Cell12Voltage | Lithium battery 5 cell 12 voltage | 锂电池5电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.283 | hw48VDCPowerSupplyLithiumBattery6Cell12Voltage | Lithium battery 6 cell 12 voltage | 锂电池6电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.284 | hw48VDCPowerSupplyLithiumBattery7Cell12Voltage | Lithium battery 7 cell 12 voltage | 锂电池7电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.285 | hw48VDCPowerSupplyLithiumBattery8Cell12Voltage | Lithium battery 8 cell 12 voltage | 锂电池8电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.286 | hw48VDCPowerSupplyLithiumBattery9Cell12Voltage | Lithium battery 9 cell 12 voltage | 锂电池9电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.287 | hw48VDCPowerSupplyLithiumBattery10Cell12Voltage | Lithium battery 10 cell 12 voltage | 锂电池10电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.288 | hw48VDCPowerSupplyLithiumBattery11Cell12Voltage | Lithium battery 11 cell 12 voltage | 锂电池11电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.289 | hw48VDCPowerSupplyLithiumBattery12Cell12Voltage | Lithium battery 12 cell 12 voltage | 锂电池12电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.290 | hw48VDCPowerSupplyLithiumBattery13Cell12Voltage | Lithium battery 13 cell 12 voltage | 锂电池13电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.291 | hw48VDCPowerSupplyLithiumBattery14Cell12Voltage | Lithium battery 14 cell 12 voltage | 锂电池14电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.292 | hw48VDCPowerSupplyLithiumBattery15Cell12Voltage | Lithium battery 15 cell 12 voltage | 锂电池15电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.293 | hw48VDCPowerSupplyLithiumBattery16Cell12Voltage | Lithium battery 16 cell 12 voltage | 锂电池16电芯12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 12 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.294 | hw48VDCPowerSupplyLithiumBattery1Cell13Voltage | Lithium battery 1 cell 13 voltage | 锂电池1电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.295 | hw48VDCPowerSupplyLithiumBattery2Cell13Voltage | Lithium battery 2 cell 13 voltage | 锂电池2电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.296 | hw48VDCPowerSupplyLithiumBattery3Cell13Voltage | Lithium battery 3 cell 13 voltage | 锂电池3电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.297 | hw48VDCPowerSupplyLithiumBattery4Cell13Voltage | Lithium battery 4 cell 13 voltage | 锂电池4电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.298 | hw48VDCPowerSupplyLithiumBattery5Cell13Voltage | Lithium battery 5 cell 13 voltage | 锂电池5电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.299 | hw48VDCPowerSupplyLithiumBattery6Cell13Voltage | Lithium battery 6 cell 13 voltage | 锂电池6电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.3.1.300 | hw48VDCPowerSupplyRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.4 | hw48VDCPowerSupplyRunning3Table | / | / |  |  | / | / | The running table of 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.1 | hw48VDCPowerSupplyRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.2 | hw48VDCPowerSupplyLithiumBattery7Cell13Voltage | Lithium battery 7 cell 13 voltage | 锂电池7电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.3 | hw48VDCPowerSupplyLithiumBattery8Cell13Voltage | Lithium battery 8 cell 13 voltage | 锂电池8电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.4 | hw48VDCPowerSupplyLithiumBattery9Cell13Voltage | Lithium battery 9 cell 13 voltage | 锂电池9电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.5 | hw48VDCPowerSupplyLithiumBattery10Cell13Voltage | Lithium battery 10 cell 13 voltage | 锂电池10电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.6 | hw48VDCPowerSupplyLithiumBattery11Cell13Voltage | Lithium battery 11 cell 13 voltage | 锂电池11电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.7 | hw48VDCPowerSupplyLithiumBattery12Cell13Voltage | Lithium battery 12 cell 13 voltage | 锂电池12电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.8 | hw48VDCPowerSupplyLithiumBattery13Cell13Voltage | Lithium battery 13 cell 13 voltage | 锂电池13电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.9 | hw48VDCPowerSupplyLithiumBattery14Cell13Voltage | Lithium battery 14 cell 13 voltage | 锂电池14电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.10 | hw48VDCPowerSupplyLithiumBattery15Cell13Voltage | Lithium battery 15 cell 13 voltage | 锂电池15电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.11 | hw48VDCPowerSupplyLithiumBattery16Cell13Voltage | Lithium battery 16 cell 13 voltage | 锂电池16电芯13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 13 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.12 | hw48VDCPowerSupplyLithiumBattery1Cell14Voltage | Lithium battery 1 cell 14 voltage | 锂电池1电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.13 | hw48VDCPowerSupplyLithiumBattery2Cell14Voltage | Lithium battery 2 cell 14 voltage | 锂电池2电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.14 | hw48VDCPowerSupplyLithiumBattery3Cell14Voltage | Lithium battery 3 cell 14 voltage | 锂电池3电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.15 | hw48VDCPowerSupplyLithiumBattery4Cell14Voltage | Lithium battery 4 cell 14 voltage | 锂电池4电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.16 | hw48VDCPowerSupplyLithiumBattery5Cell14Voltage | Lithium battery 5 cell 14 voltage | 锂电池5电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.17 | hw48VDCPowerSupplyLithiumBattery6Cell14Voltage | Lithium battery 6 cell 14 voltage | 锂电池6电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.18 | hw48VDCPowerSupplyLithiumBattery7Cell14Voltage | Lithium battery 7 cell 14 voltage | 锂电池7电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.19 | hw48VDCPowerSupplyLithiumBattery8Cell14Voltage | Lithium battery 8 cell 14 voltage | 锂电池8电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.20 | hw48VDCPowerSupplyLithiumBattery9Cell14Voltage | Lithium battery 9 cell 14 voltage | 锂电池9电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.21 | hw48VDCPowerSupplyLithiumBattery10Cell14Voltage | Lithium battery 10 cell 14 voltage | 锂电池10电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.22 | hw48VDCPowerSupplyLithiumBattery11Cell14Voltage | Lithium battery 11 cell 14 voltage | 锂电池11电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.23 | hw48VDCPowerSupplyLithiumBattery12Cell14Voltage | Lithium battery 12 cell 14 voltage | 锂电池12电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.24 | hw48VDCPowerSupplyLithiumBattery13Cell14Voltage | Lithium battery 13 cell 14 voltage | 锂电池13电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.25 | hw48VDCPowerSupplyLithiumBattery14Cell14Voltage | Lithium battery 14 cell 14 voltage | 锂电池14电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.26 | hw48VDCPowerSupplyLithiumBattery15Cell14Voltage | Lithium battery 15 cell 14 voltage | 锂电池15电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.27 | hw48VDCPowerSupplyLithiumBattery16Cell14Voltage | Lithium battery 16 cell 14 voltage | 锂电池16电芯14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 14 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.28 | hw48VDCPowerSupplyLithiumBattery1Cell15Voltage | Lithium battery 1 cell 15 voltage | 锂电池1电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.29 | hw48VDCPowerSupplyLithiumBattery2Cell15Voltage | Lithium battery 2 cell 15 voltage | 锂电池2电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.30 | hw48VDCPowerSupplyLithiumBattery3Cell15Voltage | Lithium battery 3 cell 15 voltage | 锂电池3电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.31 | hw48VDCPowerSupplyLithiumBattery4Cell15Voltage | Lithium battery 4 cell 15 voltage | 锂电池4电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.32 | hw48VDCPowerSupplyLithiumBattery5Cell15Voltage | Lithium battery 5 cell 15 voltage | 锂电池5电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.33 | hw48VDCPowerSupplyLithiumBattery6Cell15Voltage | Lithium battery 6 cell 15 voltage | 锂电池6电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.34 | hw48VDCPowerSupplyLithiumBattery7Cell15Voltage | Lithium battery 7 cell 15 voltage | 锂电池7电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.35 | hw48VDCPowerSupplyLithiumBattery8Cell15Voltage | Lithium battery 8 cell 15 voltage | 锂电池8电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.36 | hw48VDCPowerSupplyLithiumBattery9Cell15Voltage | Lithium battery 9 cell 15 voltage | 锂电池9电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.37 | hw48VDCPowerSupplyLithiumBattery10Cell15Voltage | Lithium battery 10 cell 15 voltage | 锂电池10电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.38 | hw48VDCPowerSupplyLithiumBattery11Cell15Voltage | Lithium battery 11 cell 15 voltage | 锂电池11电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.39 | hw48VDCPowerSupplyLithiumBattery12Cell15Voltage | Lithium battery 12 cell 15 voltage | 锂电池12电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.40 | hw48VDCPowerSupplyLithiumBattery13Cell15Voltage | Lithium battery 13 cell 15 voltage | 锂电池13电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.41 | hw48VDCPowerSupplyLithiumBattery14Cell15Voltage | Lithium battery 14 cell 15 voltage | 锂电池14电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.42 | hw48VDCPowerSupplyLithiumBattery15Cell15Voltage | Lithium battery 15 cell 15 voltage | 锂电池15电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.43 | hw48VDCPowerSupplyLithiumBattery16Cell15Voltage | Lithium battery 16 cell 15 voltage | 锂电池16电芯15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 15 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.44 | hw48VDCPowerSupplyLithiumBattery1Cell16Voltage | Lithium battery 1 cell 16 voltage | 锂电池1电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.45 | hw48VDCPowerSupplyLithiumBattery2Cell16Voltage | Lithium battery 2 cell 16 voltage | 锂电池2电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.46 | hw48VDCPowerSupplyLithiumBattery3Cell16Voltage | Lithium battery 3 cell 16 voltage | 锂电池3电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.47 | hw48VDCPowerSupplyLithiumBattery4Cell16Voltage | Lithium battery 4 cell 16 voltage | 锂电池4电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.48 | hw48VDCPowerSupplyLithiumBattery5Cell16Voltage | Lithium battery 5 cell 16 voltage | 锂电池5电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.49 | hw48VDCPowerSupplyLithiumBattery6Cell16Voltage | Lithium battery 6 cell 16 voltage | 锂电池6电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.50 | hw48VDCPowerSupplyLithiumBattery7Cell16Voltage | Lithium battery 7 cell 16 voltage | 锂电池7电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.51 | hw48VDCPowerSupplyLithiumBattery8Cell16Voltage | Lithium battery 8 cell 16 voltage | 锂电池8电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.52 | hw48VDCPowerSupplyLithiumBattery9Cell16Voltage | Lithium battery 9 cell 16 voltage | 锂电池9电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.53 | hw48VDCPowerSupplyLithiumBattery10Cell16Voltage | Lithium battery 10 cell 16 voltage | 锂电池10电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.54 | hw48VDCPowerSupplyLithiumBattery11Cell16Voltage | Lithium battery 11 cell 16 voltage | 锂电池11电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.55 | hw48VDCPowerSupplyLithiumBattery12Cell16Voltage | Lithium battery 12 cell 16 voltage | 锂电池12电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.56 | hw48VDCPowerSupplyLithiumBattery13Cell16Voltage | Lithium battery 13 cell 16 voltage | 锂电池13电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.57 | hw48VDCPowerSupplyLithiumBattery14Cell16Voltage | Lithium battery 14 cell 16 voltage | 锂电池14电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.58 | hw48VDCPowerSupplyLithiumBattery15Cell16Voltage | Lithium battery 15 cell 16 voltage | 锂电池15电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.59 | hw48VDCPowerSupplyLithiumBattery16Cell16Voltage | Lithium battery 16 cell 16 voltage | 锂电池16电芯16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 16 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.60 | hw48VDCPowerSupplyLithiumBattery1Cell17Voltage | Lithium battery 1 cell 17 voltage | 锂电池1电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.61 | hw48VDCPowerSupplyLithiumBattery2Cell17Voltage | Lithium battery 2 cell 17 voltage | 锂电池2电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.62 | hw48VDCPowerSupplyLithiumBattery3Cell17Voltage | Lithium battery 3 cell 17 voltage | 锂电池3电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.63 | hw48VDCPowerSupplyLithiumBattery4Cell17Voltage | Lithium battery 4 cell 17 voltage | 锂电池4电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.64 | hw48VDCPowerSupplyLithiumBattery5Cell17Voltage | Lithium battery 5 cell 17 voltage | 锂电池5电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.65 | hw48VDCPowerSupplyLithiumBattery6Cell17Voltage | Lithium battery 6 cell 17 voltage | 锂电池6电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.66 | hw48VDCPowerSupplyLithiumBattery7Cell17Voltage | Lithium battery 7 cell 17 voltage | 锂电池7电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.67 | hw48VDCPowerSupplyLithiumBattery8Cell17Voltage | Lithium battery 8 cell 17 voltage | 锂电池8电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.68 | hw48VDCPowerSupplyLithiumBattery9Cell17Voltage | Lithium battery 9 cell 17 voltage | 锂电池9电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.69 | hw48VDCPowerSupplyLithiumBattery10Cell17Voltage | Lithium battery 10 cell 17 voltage | 锂电池10电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.70 | hw48VDCPowerSupplyLithiumBattery11Cell17Voltage | Lithium battery 11 cell 17 voltage | 锂电池11电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.71 | hw48VDCPowerSupplyLithiumBattery12Cell17Voltage | Lithium battery 12 cell 17 voltage | 锂电池12电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.72 | hw48VDCPowerSupplyLithiumBattery13Cell17Voltage | Lithium battery 13 cell 17 voltage | 锂电池13电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.73 | hw48VDCPowerSupplyLithiumBattery14Cell17Voltage | Lithium battery 14 cell 17 voltage | 锂电池14电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.74 | hw48VDCPowerSupplyLithiumBattery15Cell17Voltage | Lithium battery 15 cell 17 voltage | 锂电池15电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.75 | hw48VDCPowerSupplyLithiumBattery16Cell17Voltage | Lithium battery 16 cell 17 voltage | 锂电池16电芯17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 17 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.76 | hw48VDCPowerSupplyLithiumBattery1Cell18Voltage | Lithium battery 1 cell 18 voltage | 锂电池1电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.77 | hw48VDCPowerSupplyLithiumBattery2Cell18Voltage | Lithium battery 2 cell 18 voltage | 锂电池2电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.78 | hw48VDCPowerSupplyLithiumBattery3Cell18Voltage | Lithium battery 3 cell 18 voltage | 锂电池3电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.79 | hw48VDCPowerSupplyLithiumBattery4Cell18Voltage | Lithium battery 4 cell 18 voltage | 锂电池4电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.80 | hw48VDCPowerSupplyLithiumBattery5Cell18Voltage | Lithium battery 5 cell 18 voltage | 锂电池5电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.81 | hw48VDCPowerSupplyLithiumBattery6Cell18Voltage | Lithium battery 6 cell 18 voltage | 锂电池6电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.82 | hw48VDCPowerSupplyLithiumBattery7Cell18Voltage | Lithium battery 7 cell 18 voltage | 锂电池7电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.83 | hw48VDCPowerSupplyLithiumBattery8Cell18Voltage | Lithium battery 8 cell 18 voltage | 锂电池8电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.84 | hw48VDCPowerSupplyLithiumBattery9Cell18Voltage | Lithium battery 9 cell 18 voltage | 锂电池9电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.85 | hw48VDCPowerSupplyLithiumBattery10Cell18Voltage | Lithium battery 10 cell 18 voltage | 锂电池10电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.86 | hw48VDCPowerSupplyLithiumBattery11Cell18Voltage | Lithium battery 11 cell 18 voltage | 锂电池11电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.87 | hw48VDCPowerSupplyLithiumBattery12Cell18Voltage | Lithium battery 12 cell 18 voltage | 锂电池12电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.88 | hw48VDCPowerSupplyLithiumBattery13Cell18Voltage | Lithium battery 13 cell 18 voltage | 锂电池13电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.89 | hw48VDCPowerSupplyLithiumBattery14Cell18Voltage | Lithium battery 14 cell 18 voltage | 锂电池14电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.90 | hw48VDCPowerSupplyLithiumBattery15Cell18Voltage | Lithium battery 15 cell 18 voltage | 锂电池15电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.91 | hw48VDCPowerSupplyLithiumBattery16Cell18Voltage | Lithium battery 16 cell 18 voltage | 锂电池16电芯18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 18 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.92 | hw48VDCPowerSupplyLithiumBattery1Cell19Voltage | Lithium battery 1 cell 19 voltage | 锂电池1电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.93 | hw48VDCPowerSupplyLithiumBattery2Cell19Voltage | Lithium battery 2 cell 19 voltage | 锂电池2电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.94 | hw48VDCPowerSupplyLithiumBattery3Cell19Voltage | Lithium battery 3 cell 19 voltage | 锂电池3电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.95 | hw48VDCPowerSupplyLithiumBattery4Cell19Voltage | Lithium battery 4 cell 19 voltage | 锂电池4电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.96 | hw48VDCPowerSupplyLithiumBattery5Cell19Voltage | Lithium battery 5 cell 19 voltage | 锂电池5电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.97 | hw48VDCPowerSupplyLithiumBattery6Cell19Voltage | Lithium battery 6 cell 19 voltage | 锂电池6电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.98 | hw48VDCPowerSupplyLithiumBattery7Cell19Voltage | Lithium battery 7 cell 19 voltage | 锂电池7电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.99 | hw48VDCPowerSupplyLithiumBattery8Cell19Voltage | Lithium battery 8 cell 19 voltage | 锂电池8电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.100 | hw48VDCPowerSupplyLithiumBattery9Cell19Voltage | Lithium battery 9 cell 19 voltage | 锂电池9电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.101 | hw48VDCPowerSupplyLithiumBattery10Cell19Voltage | Lithium battery 10 cell 19 voltage | 锂电池10电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.102 | hw48VDCPowerSupplyLithiumBattery11Cell19Voltage | Lithium battery 11 cell 19 voltage | 锂电池11电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.103 | hw48VDCPowerSupplyLithiumBattery12Cell19Voltage | Lithium battery 12 cell 19 voltage | 锂电池12电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.104 | hw48VDCPowerSupplyLithiumBattery13Cell19Voltage | Lithium battery 13 cell 19 voltage | 锂电池13电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.105 | hw48VDCPowerSupplyLithiumBattery14Cell19Voltage | Lithium battery 14 cell 19 voltage | 锂电池14电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.106 | hw48VDCPowerSupplyLithiumBattery15Cell19Voltage | Lithium battery 15 cell 19 voltage | 锂电池15电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.107 | hw48VDCPowerSupplyLithiumBattery16Cell19Voltage | Lithium battery 16 cell 19 voltage | 锂电池16电芯19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 19 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.108 | hw48VDCPowerSupplyLithiumBattery1Cell20Voltage | Lithium battery 1 cell 20 voltage | 锂电池1电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 1 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.109 | hw48VDCPowerSupplyLithiumBattery2Cell20Voltage | Lithium battery 2 cell 20 voltage | 锂电池2电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 2 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.110 | hw48VDCPowerSupplyLithiumBattery3Cell20Voltage | Lithium battery 3 cell 20 voltage | 锂电池3电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 3 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.111 | hw48VDCPowerSupplyLithiumBattery4Cell20Voltage | Lithium battery 4 cell 20 voltage | 锂电池4电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 4 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.112 | hw48VDCPowerSupplyLithiumBattery5Cell20Voltage | Lithium battery 5 cell 20 voltage | 锂电池5电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 5 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.113 | hw48VDCPowerSupplyLithiumBattery6Cell20Voltage | Lithium battery 6 cell 20 voltage | 锂电池6电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 6 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.114 | hw48VDCPowerSupplyLithiumBattery7Cell20Voltage | Lithium battery 7 cell 20 voltage | 锂电池7电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 7 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.115 | hw48VDCPowerSupplyLithiumBattery8Cell20Voltage | Lithium battery 8 cell 20 voltage | 锂电池8电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 8 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.116 | hw48VDCPowerSupplyLithiumBattery9Cell20Voltage | Lithium battery 9 cell 20 voltage | 锂电池9电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 9 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.117 | hw48VDCPowerSupplyLithiumBattery10Cell20Voltage | Lithium battery 10 cell 20 voltage | 锂电池10电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 10 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.118 | hw48VDCPowerSupplyLithiumBattery11Cell20Voltage | Lithium battery 11 cell 20 voltage | 锂电池11电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 11 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.119 | hw48VDCPowerSupplyLithiumBattery12Cell20Voltage | Lithium battery 12 cell 20 voltage | 锂电池12电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 12 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.120 | hw48VDCPowerSupplyLithiumBattery13Cell20Voltage | Lithium battery 13 cell 20 voltage | 锂电池13电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 13 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.121 | hw48VDCPowerSupplyLithiumBattery14Cell20Voltage | Lithium battery 14 cell 20 voltage | 锂电池14电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 14 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.122 | hw48VDCPowerSupplyLithiumBattery15Cell20Voltage | Lithium battery 15 cell 20 voltage | 锂电池15电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 15 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.123 | hw48VDCPowerSupplyLithiumBattery16Cell20Voltage | Lithium battery 16 cell 20 voltage | 锂电池16电芯20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Lithium battery 16 cell 20 voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.4.1.300 | hw48VDCPowerSupplyRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.5 | hw48VDCPowerSupplyConfig4Table | / | / |  |  | / | / | The config table of 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.1 | hw48VDCPowerSupplyConfig4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.2 | hw48VDCPowerSupplyLlvd1DisconnectMode | LLVD1 disconnect mode | LLVD1下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | LLVD1 disconnect mode of the device config table for the 48 V DC Power Supply. Value 1 indicate voltage mode Value 2 indicate time mode Value 3 indicate capacity mode
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.3 | hw48VDCPowerSupplyLlvd1DisconnectTime | LLVD1 disconnect time | LLVD1下电时间 | 1-Read_Write | 读写 | 5..1000 | 5..1000 | LLVD1 disconnect time of the device config table for the 48 V DC Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.4 | hw48VDCPowerSupplyLlvd1DisconnectCapacity | LLVD1 disconnect capacity | LLVD1下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | LLVD1 disconnect capacity of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.5 | hw48VDCPowerSupplyLlvd1HighTempDisconnectEnable | LLVD1 high temp disconnect enable | LLVD1高温下电使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD1 high temp disconnect enable of the device config table for the 48 V DC Power Supply. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.6 | hw48VDCPowerSupplyLlvd1HighTempDisconnectTemperature | LLVD1 high temp disconnect temperature | LLVD1高温下电温度 | 1-Read_Write | 读写 | 250..800 | 250..800 | LLVD1 high temp disconnect temperature of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.7 | hw48VDCPowerSupplyLlvd2DisconnectMode | LLVD2 disconnect mode | LLVD2下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | LLVD2 disconnect mode of the device config table for the 48 V DC Power Supply. Value 1 indicate voltageMode Value 2 indicate timeMode Value 3 indicate capacityMode
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.8 | hw48VDCPowerSupplyLlvd2DisconnectTime | LLVD2 disconnect time | LLVD2下电时间 | 1-Read_Write | 读写 | 5..1000 | 5..1000 | LLVD2 disconnect time of the device config table for the 48 V DC Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.9 | hw48VDCPowerSupplyLlvd2DisconnectCapacity | LLVD2 disconnect capacity | LLVD2下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | LLVD2 disconnect capacity of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.10 | hw48VDCPowerSupplyLlvd2HighTempDisconnectEnable | LLVD2 high temp disconnect enable | LLVD2高温下电使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD2 high temp disconnect enable of the device config table for the 48 V DC Power Supply. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.11 | hw48VDCPowerSupplyLlvd2HighTempDisconnectTemperature | LLVD2 high temp disconnect temperature | LLVD2高温下电温度 | 1-Read_Write | 读写 | 250..800 | 250..800 | LLVD2 high temp disconnect temperature of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.12 | hw48VDCPowerSupplyLlvd3Enable | LLVD3 enable | LLVD3使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | LLVD3 enable of the device config table for the 48 V DC Power Supply. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.13 | hw48VDCPowerSupplyLlvd3DisconnectVoltage | LLVD3 disconnect voltage | LLVD3下电电压 | 1-Read_Write | 读写 | 360..560 | 360..560 | LLVD3 disconnect voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.14 | hw48VDCPowerSupplyLlvd3ConnectionVoltage | LLVD3 connection voltage | LLVD3上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | LLVD3 connection voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.15 | hw48VDCPowerSupplyLlvd3DisconnectMode | LLVD3 disconnect mode | LLVD3下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | LLVD3 disconnect mode of the device config table for the 48 V DC Power Supply. Value 1 indicate voltageMode Value 2 indicate timeMode Value 3 indicate capacityMode
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.16 | hw48VDCPowerSupplyLlvd3DisconnectTime | LLVD3 disconnect Time | LLVD3下电时间 | 1-Read_Write | 读写 | 5..1000 | 5..1000 | LLVD3 disconnect Time of the device config table for the 48 V DC Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.17 | hw48VDCPowerSupplyLlvd3DisconnectCapacity | LLVD3 disconnect capacity | LLVD3下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | LLVD3 disconnect capacity of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.18 | hw48VDCPowerSupplyLlvd3HighTempDisconnectEnable | LLVD3 high temp disconnect enable | LLVD3高温下电使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD3 high temp disconnect enable of the device config table for the 48 V DC Power Supply. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.19 | hw48VDCPowerSupplyLlvd3HighTempDisconnectTemperature | LLVD3 high temp disconnect temperature | LLVD3高温下电温度 | 1-Read_Write | 读写 | 250..800 | 250..800 | LLVD3 high temp disconnect temperature of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.20 | hw48VDCPowerSupplyLlvd4Enable | LLVD4 enable | LLVD4使能 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | LLVD4 enable of the device config table for the 48 V DC Power Supply. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.21 | hw48VDCPowerSupplyLlvd4DisconnectVoltage | LLVD4 disconnect voltage | LLVD4下电电压 | 1-Read_Write | 读写 | 360..560 | 360..560 | LLVD4 disconnect voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.22 | hw48VDCPowerSupplyLlvd4ConnectionVoltage | LLVD4 connection voltage | LLVD4上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | LLVD4 connection voltage of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.23 | hw48VDCPowerSupplyLlvd4DisconnectMode | LLVD4 disconnect mode | LLVD4下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | LLVD4 disconnect mode of the device config table for the 48 V DC Power Supply. Value 1 indicate voltageMode Value 2 indicate timeMode Value 3 indicate capacityMode
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.24 | hw48VDCPowerSupplyLlvd4DisconnectTime | LLVD4 disconnect time | LLVD4下电时间 | 1-Read_Write | 读写 | 5..1000 | 5..1000 | LLVD4 disconnect time of the device config table for the 48 V DC Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.25 | hw48VDCPowerSupplyLlvd4DisconnectCapacity | LLVD4 disconnect capacity | LLVD4下电容量 | 1-Read_Write | 读写 | 0..990 | 0..990 | LLVD4 disconnect capacity of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.26 | hw48VDCPowerSupplyLlvd4HighTempDisconnectEnable | LLVD4 high temp disconnect enable | LLVD4高温下电使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD4 high temp disconnect enable of the device config table for the 48 V DC Power Supply. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.27 | hw48VDCPowerSupplyLlvd4HighTempDisconnectTemperature | LLVD4 high temp disconnect temperature | LLVD4高温下电温度 | 1-Read_Write | 读写 | 250..800 | 250..800 | LLVD4 high temp disconnect temperature of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.28 | hw48VDCPowerSupplyAcOvervoltageThreshold2 | AC overvoltage threshold 2 | 交流过压2告警点 | 1-Read_Write | 读写 | 242..300 | 242..300 | AC overvoltage threshold 2 of the device config table for the 48 V DC Power Supply.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.29 | hw48VDCPowerSupplyAcUndervoltageThreshold2 | AC undervoltage threshold 2 | 交流欠压2告警点 | 1-Read_Write | 读写 | 60..198 | 60..198 | AC undervoltage threshold 2 of the device config table for the 48 V DC Power Supply.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.30 | hw48VDCPowerSupplyAcHighFrequencyThreshold2 | AC high frequency threshold 2 | 交流频率过高2告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | AC high frequency threshold 2 of the device config table for the 48 V DC Power Supply.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.31 | hw48VDCPowerSupplyAcLowFrequencyThreshold2 | AC low frequency threshold 2 | 交流频率过低2告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | AC low frequency threshold 2 of the device config table for the 48 V DC Power Supply.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.32 | hw48VDCPowerSupplyBlvdDisconnectMode | BLVD disconnect mode | BLVD下电模式 | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | [电压模式=1]/[时间模式=2]/[容量模式=3] | BLVD disconnect mode of the device config table for the 48 V DC Power Supply. Value 1 indicate voltageMode Value 2 indicate timeMode Value 3 indicate capacityMode
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.33 | hw48VDCPowerSupplyBlvdDisconnectTime | BLVD disconnect time | BLVD下电时间 | 1-Read_Write | 读写 | 5..12000 | 5..12000 | BLVD disconnect time of the device config table for the 48 V DC Power Supply.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.34 | hw48VDCPowerSupplyBlvdDisconnectCapacity | BLVD disconnect capacity | BLVD下电容量 | 1-Read_Write | 读写 | 0..99 | 0..99 | BLVD disconnect capacity of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.35 | hw48VDCPowerSupplyIntelligentAirConditionerWorkTemperature | Intelligent air conditioner work temperature | 智能空调工作温度 | 1-Read_Write | 读写 | 380..500 | 380..500 | Intelligent air conditioner work temperature of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.36 | hw48VDCPowerSupplyIntelligentAirConditionerStopTemperature | Intelligent air conditioner stop temperature | 智能空调停止温度 | 1-Read_Write | 读写 | 330..450 | 330..450 | Intelligent air conditioner stop temperature of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.37 | hw48VDCPowerSupplyAorCAirConditionerWorkTemperature | A/C air conditioner work temperature | 空调工作温度 | 1-Read_Write | 读写 | 380..500 | 380..500 | A/C air conditioner work temperature of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.38 | hw48VDCPowerSupplyAorCAirConditionerStopTemperature | A/C air conditioner stop temperature | A/C空调停止温度 | 1-Read_Write | 读写 | 330..450 | 330..450 | A/C air conditioner stop temperature of the device config table for the 48 V DC Power Supply.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.39 | hw48VDCPowerSupplyNumberOfAcbCabinets | Number of ACB cabinets | ACB机柜数量 | 1-Read_Write | 读写 | 1..10 | 1..10 | Number of ACB cabinets of the device config table for the 48 V DC Power Supply.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.40 | hw48VDCPowerSupplyFanSpeedRatio | Fan speed ratio | 风扇转速比 | 1-Read_Write | 读写 | 0..100 | 0..100 | Fan speed ratio of the device config table for the 48 V DC Power Supply.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.41 | hw48VDCPowerSupplyDoorSensor | Door sensor | 门磁传感器 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Door sensor of the device config table for the 48 V DC Power Supply. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.42 | hw48VDCPowerSupplySetDCUltraHighVoltage | DC ultra high voltage | 直流过过压告警点 | 1-Read_Write | 读写 | 530..600 | 530..600 | 48 V DC Power Supply Set DC ultra high voltage. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.43 | hw48VDCPowerSupplySetDCUltraLowVoltage | DC ultra low voltage | 直流欠欠压告警点 | 1-Read_Write | 读写 | 360..560 | 360..560 | 48 V DC Power Supply Set DC ultra low voltage. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.28.5.1.300 | hw48VDCPowerSupplyConfig4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of 48 V DC Power Supply.

## YaDa DC Meter
雅达直流电表
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.29 | DCMeter | YaDa DC Meter | 雅达直流电表 | / | / | / | / | The DC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.29.1 | hwDCMeterRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.1 | hwDCMeterRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.2 | hwDCMeterCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Comm Status of the device config table for the DCMeter. value 1 indicates normal. value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.3 | hwDCMeterComNumber | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Dcm Samp Com Number.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.4 | hwDCMeterModbusAddr | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Dcm Samp Modbus Addr.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.5 | hwDCMeterDcVoltage | Voltage | 电压 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Dcm Samp Dc Voltage. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.6 | hwDCMeterDcCurrent | Current | 电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Dcm Samp Dc Current. Multiple:10000. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.7 | hwDCMeterDcPower | Power | 功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Dcm Samp Dc Power. Multiple:10000. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.8 | hwDCMeterDcEnergy | Energy | 电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Dcm Samp Dc Energy. Multiple:100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.9 | hwDCMeterLightningProtectionStatus | / | / | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | / | Dcm Samp Lightning Protection Status. value 1 indicates normal. value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.10 | hwDCMeterQf1Status | QF1 status | QF1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf1 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.11 | hwDCMeterQf2Status | QF2 status | QF2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf2 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.12 | hwDCMeterQf3Status | QF3 status | QF3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf3 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.13 | hwDCMeterQf4Status | QF4 status | QF4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf4 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.14 | hwDCMeterQf5Status | QF5 status | QF5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf5 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.15 | hwDCMeterQf6Status | QF6 status | QF6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf6 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.16 | hwDCMeterQf7Status | QF7 status | QF7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf7 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.17 | hwDCMeterQf8Status | QF8 status | QF8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf8 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.18 | hwDCMeterQf9Status | QF9 status | QF9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf9 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.19 | hwDCMeterQf10Status | QF10 status | QF10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf10 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.20 | hwDCMeterQf11Status | QF11 status | QF11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf11 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.21 | hwDCMeterQf12Status | QF12 status | QF12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf12 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.22 | hwDCMeterQf13Status | QF13 status | QF13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf13 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.23 | hwDCMeterQf14Status | QF14 status | QF14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf14 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.24 | hwDCMeterQf15Status | QF15 status | QF15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf15 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.25 | hwDCMeterQf16Status | QF16 status | QF16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf16 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.26 | hwDCMeterQf17Status | QF17 status | QF17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf17 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.27 | hwDCMeterQf18Status | QF18 status | QF18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf18 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.28 | hwDCMeterQf19Status | QF19 status | QF19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf19 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.29 | hwDCMeterQf20Status | QF20 status | QF20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf20 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.30 | hwDCMeterQf21Status | QF21 status | QF21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf21 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.31 | hwDCMeterQf22Status | QF22 status | QF22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf22 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.32 | hwDCMeterQf23Status | QF23 status | QF23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf23 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.33 | hwDCMeterQf24Status | QF24 status | QF24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf24 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.34 | hwDCMeterQf25Status | QF25 status | QF25开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf25 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.35 | hwDCMeterQf26Status | QF26 status | QF26开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf26 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.36 | hwDCMeterQf27Status | QF27 status | QF27开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf27 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.37 | hwDCMeterQf28Status | QF28 status | QF28开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf28 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.38 | hwDCMeterQf29Status | QF29 status | QF29开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf29 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.39 | hwDCMeterQf30Status | QF30 status | QF30开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf30 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.40 | hwDCMeterQf31Status | QF31 status | QF31开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf31 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.41 | hwDCMeterQf32Status | QF32 status | QF32开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf32 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.42 | hwDCMeterQf33Status | QF33 status | QF33开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf33 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.43 | hwDCMeterQf34Status | QF34 status | QF34开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf34 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.44 | hwDCMeterQf35Status | QF35 status | QF35开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf35 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.45 | hwDCMeterQf36Status | QF36 status | QF36开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf36 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.46 | hwDCMeterQf37Status | QF37 status | QF37开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf37 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.47 | hwDCMeterQf38Status | QF38 status | QF38开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf38 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.48 | hwDCMeterQf39Status | QF39 status | QF39开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf39 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.49 | hwDCMeterQf40Status | QF40 status | QF40开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf40 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.50 | hwDCMeterQf41Status | QF41 status | QF41开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf41 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.51 | hwDCMeterQf42Status | QF42 status | QF42开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf42 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.52 | hwDCMeterQf43Status | QF43 status | QF43开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf43 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.53 | hwDCMeterQf44Status | QF44 status | QF44开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf44 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.54 | hwDCMeterQf45Status | QF45 status | QF45开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf45 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.55 | hwDCMeterQf46Status | QF46 status | QF46开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf46 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.56 | hwDCMeterQf47Status | QF47 status | QF47开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf47 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.57 | hwDCMeterQf48Status | QF48 status | QF48开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf48 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.58 | hwDCMeterQf49Status | QF49 status | QF49开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf49 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.59 | hwDCMeterQf50Status | QF50 status | QF50开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf50 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.60 | hwDCMeterQf51Status | QF51 status | QF51开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf51 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.61 | hwDCMeterQf52Status | QF52 status | QF52开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf52 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.62 | hwDCMeterQf53Status | QF53 status | QF53开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf53 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.63 | hwDCMeterQf54Status | QF54 status | QF54开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf54 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.64 | hwDCMeterQf55Status | QF55 status | QF55开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf55 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.65 | hwDCMeterQf56Status | QF56 status | QF56开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf56 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.66 | hwDCMeterQf57Status | QF57 status | QF57开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf57 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.67 | hwDCMeterQf58Status | QF58 status | QF58开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf58 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.68 | hwDCMeterQf59Status | QF59 status | QF59开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf59 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.69 | hwDCMeterQf60Status | QF60 status | QF60开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Dcm Samp Qf60 Status. value 1 indicates Open. value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.70 | hwDCMeterVirSysDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Vir Sys Device Name.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.71 | hwDCMeterSetQfNum | Branch circuit breaker quantity | 支路开关数量 | 1-Read_Write | 读写 | 1..60 | 1..60 | Dcm Set Qf Num.
1.3.6.1.4.1.2011.6.178.1.1.29.1.1.100 | hwDCMeterRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running and config table for the hwDCMeter.

## PD510 Meter
PD510电表
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.30 | ACMeter | PD510 Meter | PD510电表 | / | / | / | / | The AC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.30.1 | hwACMeterRunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.1 | hwACMeterRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the ACMeter.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.2 | hwACMeterCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Comm Status of the device config table for the ACMeter: value 1 indicates normal. value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.3 | hwACMeterComNumber | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | PD510 Samp Com Number.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.4 | hwACMeterModbusAddr | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | PD510 Samp Modbus Addr.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.5 | hwACMeterVolWiringtype | Voltage wiring | 电压接线方式 | 0-Read_Only | 只读 | threeln(1), twoln(2), twoll(3), unknown(255) | [3LN=1]/[2LN=2]/[2LL=3] | PD510 Samp Vol Wiring type. value 1 indicates 3LN. value 2 indicates 2LN. value 3 indicates 2LL.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.6 | hwACMeterCurrWiringType | Current wiring | 电流接线方式 | 0-Read_Only | 只读 | threect(1), twoct(2), onect(3), unknown(255) | [3CT=1]/[2CT=2]/[1CT=3] | PD510 Samp Curr Wiring Type. value 1 indicates 3CT. value 2 indicates 2CT. value 3 indicates 1CT.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.7 | hwACMeterLoadType | Load property | 负载性质 | 0-Read_Only | 只读 | resistive(1), inductive(2), capacitive(3), unknown(255) | [阻性=1]/[感性=2]/[容性=3] | PD510 Samp Load Type. value 1 indicates Resistive. value 2 indicates Inductive. value 3 indicates Capacitive.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.8 | hwACMeterVolUnsymmetry | Voltage asymmetry | 电压不对称度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | PD510 Samp Vol Unsymmetry. Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.9 | hwACMeterCurrUnsymmetry | Current asymmetry | 电流不对称度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | PD510 Samp Curr Unsymmetry. Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.10 | hwACMeterRunTime | Meter running time | 仪表运行时间 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Run Time. Multiple:10. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.11 | hwACMeterFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | PD510 Samp Frequency. Multiple:100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.12 | hwACMeterPhaseVolV1 | Phase voltage V1 | 相电压V1 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | PD510 Samp Phase Vol V1. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.13 | hwACMeterPhaseVolV2 | Phase voltage V2 | 相电压V2 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | PD510 Samp Phase Vol V2. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.14 | hwACMeterPhaseVolV3 | Phase voltage V3 | 相电压V3 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | PD510 Samp Phase Vol V3. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.15 | hwACMeterPhaseVolAvg | Average phase voltage (Vvavg) | 相电压均值Vvavg | 0-Read_Only | 只读 | 0..5000 | 0..5000 | PD510 Samp Phase Vol Avg. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.16 | hwACMeterLineVolV12 | Line voltage V12 | 线电压V12 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | PD510 Samp Line Vol V12. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.17 | hwACMeterLineVolV23 | Line voltage V23 | 线电压V23 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | PD510 Samp Line Vol V23. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.18 | hwACMeterLineVolV31 | Line voltage V31 | 线电压V31 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | PD510 Samp Line Vol V31. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.19 | hwACMeterLineVolAvg | Average line voltage (Vlavg) | 线电压均值Vlavg | 0-Read_Only | 只读 | 0..6000 | 0..6000 | PD510 Samp Line Vol Avg. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.20 | hwACMeterPhaseCurrI1 | Phase (line) current I1 | 相(线)电流I1 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Phase Curr I1. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.21 | hwACMeterPhaseCurrI2 | Phase (line) current I2 | 相(线)电流I2 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Phase Curr I2. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.22 | hwACMeterPhaseCurrI3 | Phase (line) current I3 | 相(线)电流I3 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Phase Curr I3. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.23 | hwACMeterPhaseCurrAvg | Three phase average current (Iavg) | 三相电流均值Iavg | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Phase Curr Avg. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.24 | hwACMeterMiddleLineCurr | Neutral line current in | 中线电流In | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Middle Line Curr. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.25 | hwACMeterPhaseActivePowerP1 | Phase active power P1 | 分相有功功率P1 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | PD510 Samp Phase Active Power P1. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.26 | hwACMeterPhaseActivePowerP2 | Phase active power P2 | 分相有功功率P2 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | PD510 Samp Phase Active Power P2. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.27 | hwACMeterPhaseActivePowerP3 | Phase active power P3 | 分相有功功率P3 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | PD510 Samp Phase Active Power P3. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.28 | hwACMeterSysActivePower | System active power (Psum) | 系统有功功率Psum | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | PD510 Samp Sys Active Power. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.29 | hwACMeterPhaseReactivePowerQ1 | Phase reactive power Q1 | 分相无功功率Q1 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | PD510 Samp Phase Reactive Power Q1. Multiple:10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.30 | hwACMeterPhaseReactivePowerQ2 | Phase reactive power Q2 | 分相无功功率Q2 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | PD510 Samp Phase Reactive Power Q2. Multiple:10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.31 | hwACMeterPhaseReactivePowerQ3 | Phase reactive power Q3 | 分相无功功率Q3 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | PD510 Samp Phase Reactive Power Q3. Multiple:10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.32 | hwACMeterSysReactivePower | System reactive power (Qsum) | 系统无功功率Qsum | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | PD510 Samp Sys Reactive Power. Multiple:10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.33 | hwACMeterPhaseApparentPowerS1 | Phase apparent power S1 | 分相视在功率S1 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Phase Apparent Power S1. Multiple:10. SigUnitInfo:VA
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.34 | hwACMeterPhaseApparentPowerS2 | Phase apparent power S2 | 分相视在功率S2 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Phase Apparent Power S2. Multiple:10. SigUnitInfo:VA
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.35 | hwACMeterPhaseApparentPowerS3 | Phase apparent power S3 | 分相视在功率S3 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Phase Apparent Power S3. Multiple:10. SigUnitInfo:VA
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.36 | hwACMeterSysApparentPower | System apparent power (Ssum) | 系统视在功率Ssum | 0-Read_Only | 只读 | 0..655350 | 0..655350 | PD510 Samp Sys Apparent Power. Multiple:10. SigUnitInfo:VA
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.37 | hwACMeterPhasePowerFactorPf1 | Phase power factor PF1 | 分相功率因数PF1 | 0-Read_Only | 只读 | -100..100 | -100..100 | PD510 Samp Phase Power Factor Pf1. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.38 | hwACMeterPhasePowerFactorPf2 | Phase power factor PF2 | 分相功率因数PF2 | 0-Read_Only | 只读 | -100..100 | -100..100 | PD510 Samp Phase Power Factor Pf2. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.39 | hwACMeterPhasePowerFactorPf3 | Phase power factor PF3 | 分相功率因数PF3 | 0-Read_Only | 只读 | -100..100 | -100..100 | PD510 Samp Phase Power Factor Pf3. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.40 | hwACMeterSysPowerFactor | System power factor PF | 系统功率因数PF | 0-Read_Only | 只读 | -100..100 | -100..100 | PD510 Samp Sys Power Factor. Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.41 | hwACMeterInputActiveEnergy | Input active electric energy | 输入有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Input Active Energy. Multiple:10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.42 | hwACMeterOutputActiveEnergy | Output active electric energy | 输出有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Output Active Energy. Multiple:10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.43 | hwACMeterInductiveReactiveEnergy | Inductive reactive electric energy | 感性无功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Inductive Reactive Energy. Multiple:10. SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.44 | hwACMeterCapacitiveReactiveEnergy | Capacitive reactive electric energy | 容性无功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Capacitive Reactive Energy. Multiple:10. SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.45 | hwACMeterTotalActiveEnergy | Total electric energy | 总有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Total Active Energy. Multiple:10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.46 | hwACMeterNetActiveEnergy | Net active electric energy | 净有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Net Active Energy. Multiple:10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.47 | hwACMeterTotalReactiveEnergy | Total reactive electric energy | 总无功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Total Reactive Energy. Multiple:10. SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.48 | hwACMeterNetReactiveEnergy | Net reactive electric energy | 净无功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Net Reactive Energy. Multiple:10. SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.49 | hwACMeterApparentEnergy | Apparent electric energy | 视在电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PD510 Samp Apparent Energy. Multiple:10. SigUnitInfo:kVAh
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.50 | hwACMeterSetFreqHigher | High frequency alarm threshold | 频率过高告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | PD510 Set Freq Higher. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.51 | hwACMeterSetFreqLower | Low frequency alarm threshold | 频率过低告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | PD510 Set Freq Lower. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.52 | hwACMeterSetPhaseVoltOV | Phase overvoltage alarm threshold | 相电压过压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | PD510 Set Phase Volt OV. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.53 | hwACMeterSetPhaseVoltUN | Phase undervoltage alarm threshold | 相电压欠压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | PD510 Set Phase Volt UN. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.54 | hwACMeterSetLineVoltOV | Line overvoltage alarm threshold | 线电压过压告警点 | 1-Read_Write | 读写 | 500..6000 | 500..6000 | PD510 Set Line Volt OV. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.55 | hwACMeterSetLineVoltUN | Line undervoltage alarm threshold | 线电压欠压告警点 | 1-Read_Write | 读写 | 500..6000 | 500..6000 | PD510 Set Line Volt UN. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.56 | hwACMeterDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | PD510 Device Name.
1.3.6.1.4.1.2011.6.178.1.1.30.1.1.100 | hwACMeterRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running and config table for the hwDCMeter.

## PowerModule
电源模块
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.31 | PowerModule |  |  | / | / | / | / | The Power Module Equipment.
1.3.6.1.4.1.2011.6.178.1.1.31.1 | hwPowerModuleRunningTable | / | / |  |  | / | / | The running and config table of Huawei Power Module.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.1 | hwPowerModuleRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the Power Module.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.2 | hwPowerModuleStatus | / | / | 0-Read_Only | 只读 | notdetected(1), detected(2), unknown(255) | / | Status of the device running table for the Power Module. value 1 indicates Not detected. value 2 indicates Detected.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.3 | hwPowerModuleSlot | / | / | 0-Read_Only | 只读 | 1..13 | / | Slot of the device running table for the Power Module.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.4 | hwPowerModuleRunningStatus | / | / | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | / | Running status of the device running table for the Power Module. value 1 indicates On. value 2 indicates Off.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.5 | hwPowerModuleTotalRunTime | / | / | 0-Read_Only | 只读 | 0..4294967295 | / | Total run time of the device running table for the Power Module.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.6 | hwPowerModuleDcOutputPower | / | / | 0-Read_Only | 只读 | 0..2147483647 | / | Dc output power of the device running table for the Power Module. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.7 | hwPowerModuleDcOutputVoltServeyValue | / | / | 0-Read_Only | 只读 | 0..2147483647 | / | Dc output volt servey value of the device running table for the Power Module. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.8 | hwPowerModuleShowOutputCurrent | / | / | 0-Read_Only | 只读 | 0..2147483647 | / | Show output current of the device running table for the Power Module. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.9 | hwPowerModuleInnerTemp | / | / | 0-Read_Only | 只读 | 0..2147483647 | / | Inner temp of the device running table for the Power Module. Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.10 | hwPowerModuleESN | / | / | 0-Read_Only | 只读 | 0..31 | / | ESN of the device running table for the Power Module.
1.3.6.1.4.1.2011.6.178.1.1.31.1.1.100 | hwPowerModuleRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running and config table for the Power Module.

## LF DC Meter
LF直流电表
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.33 | LFDCMeter | LF DC Meter | LF直流电表 | / | / | / | / | The Lang Fang DC Meter Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.33.1 | hwLFDCMeterRunningTable | / | / |  |  | / | / | The running and config table of Huawei Lang Fang DC Meter Meter.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.1 | hwLFDCMeterRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.2 | hwLFDCMeterCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Lang Fang DC Meter comm status: Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.3 | hwLFDCMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 0..8 | 0..8 | Lang Fang DC Meter Meter Port No.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.4 | hwLFDCMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Lang Fang DC Meter Meter Modbus Address.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.5 | hwLFDCMeterInputVoltage | Input voltage | 输入电压 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter Input Voltage. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.6 | hwLFDCMeterInputCurrent | Input current | 输入电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter Input Current. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.7 | hwLFDCMeterInputPower | Input power | 输入功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter Input Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.8 | hwLFDCMeterInputElectricEnergy | Input electric energy | 输入电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter Input Electric Energy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.9 | hwLFDCMeterLightningProtectionStatus | SPD status | 防雷状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [正常=1]/[故障=2] | Lang Fang DC Meter Meter SPD Status. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.10 | hwLFDCMeterMainSwitchStatus | Main switch status | 主开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC Meter Meter MainSwitchStatus. Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.11 | hwLFDCMeterQF1OutputCurrent | QF1 output current | QF1输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF1OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.12 | hwLFDCMeterQF2OutputCurrent | QF2 output current | QF2输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF2OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.13 | hwLFDCMeterQF3OutputCurrent | QF3 output current | QF3输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF3OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.14 | hwLFDCMeterQF4OutputCurrent | QF4 output current | QF4输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF4OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.15 | hwLFDCMeterQF5OutputCurrent | QF5 output current | QF5输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF5OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.16 | hwLFDCMeterQF6OutputCurrent | QF6 output current | QF6输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF6OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.17 | hwLFDCMeterQF7OutputCurrent | QF7 output current | QF7输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF7OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.18 | hwLFDCMeterQF8OutputCurrent | QF8 output current | QF8输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF8OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.19 | hwLFDCMeterQF9OutputCurrent | QF9 output current | QF9输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF9OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.20 | hwLFDCMeterQF10OutputCurrent | QF10 output current | QF10输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF10OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.21 | hwLFDCMeterQF11OutputCurrent | QF11 output current | QF11输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF11OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.22 | hwLFDCMeterQF12OutputCurrent | QF12 output current | QF12输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF12OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.23 | hwLFDCMeterQF13OutputCurrent | QF13 output current | QF13输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF13OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.24 | hwLFDCMeterQF14OutputCurrent | QF14 output current | QF14输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF14OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.25 | hwLFDCMeterQF15OutputCurrent | QF15 output current | QF15输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF15OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.26 | hwLFDCMeterQF16OutputCurrent | QF16 output current | QF16输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF16OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.27 | hwLFDCMeterQF17OutputCurrent | QF17 output current | QF17输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF17OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.28 | hwLFDCMeterQF18OutputCurrent | QF18 output current | QF18输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF18OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.29 | hwLFDCMeterQF19OutputCurrent | QF19 output current | QF19输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF19OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.30 | hwLFDCMeterQF20OutputCurrent | QF20 output current | QF20输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF20OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.31 | hwLFDCMeterQF21OutputCurrent | QF21 output current | QF21输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF21OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.32 | hwLFDCMeterQF22OutputCurrent | QF22 output current | QF22输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF22OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.33 | hwLFDCMeterQF23OutputCurrent | QF23 output current | QF23输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF23OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.34 | hwLFDCMeterQF24OutputCurrent | QF24 output current | QF24输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF24OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.35 | hwLFDCMeterQF25OutputCurrent | QF25 output current | QF25输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF25OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.36 | hwLFDCMeterQF26OutputCurrent | QF26 output current | QF26输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF26OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.37 | hwLFDCMeterQF27OutputCurrent | QF27 output current | QF27输出电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF27OutputCurrent. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.38 | hwLFDCMeterQF1Power | QF1 power | QF1功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF1Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.39 | hwLFDCMeterQF2Power | QF2 power | QF2功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF2Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.40 | hwLFDCMeterQF3Power | QF3 power | QF3功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF3Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.41 | hwLFDCMeterQF4Power | QF4 power | QF4功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF4Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.42 | hwLFDCMeterQF5Power | QF5 power | QF5功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF5Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.43 | hwLFDCMeterQF6Power | QF6 power | QF6功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF6Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.44 | hwLFDCMeterQF7Power | QF7 power | QF7功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF7Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.45 | hwLFDCMeterQF8Power | QF8 power | QF8功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF8Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.46 | hwLFDCMeterQF9Power | QF9 power | QF9功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF9Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.47 | hwLFDCMeterQF10Power | QF10 power | QF10功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF10Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.48 | hwLFDCMeterQF11Power | QF11 power | QF11功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF11Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.49 | hwLFDCMeterQF12Power | QF12 power | QF12功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF12Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.50 | hwLFDCMeterQF13Power | QF13 power | QF13功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF13Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.51 | hwLFDCMeterQF14Power | QF14 power | QF14功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF14Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.52 | hwLFDCMeterQF15Power | QF15 power | QF15功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF15Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.53 | hwLFDCMeterQF16Power | QF16 power | QF16功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF16Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.54 | hwLFDCMeterQF17Power | QF17 power | QF17功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF17Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.55 | hwLFDCMeterQF18Power | QF18 power | QF18功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF18Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.56 | hwLFDCMeterQF19Power | QF19 power | QF19功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF19Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.57 | hwLFDCMeterQF20Power | QF20 power | QF20功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF20Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.58 | hwLFDCMeterQF21Power | QF21 power | QF21功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF21Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.59 | hwLFDCMeterQF22Power | QF22 power | QF22功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF22Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.60 | hwLFDCMeterQF23Power | QF23 power | QF23功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF23Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.61 | hwLFDCMeterQF24Power | QF24 power | QF24功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF24Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.62 | hwLFDCMeterQF25Power | QF25 power | QF25功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF25Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.63 | hwLFDCMeterQF26Power | QF26 power | QF26功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF26Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.64 | hwLFDCMeterQF27Power | QF27 power | QF27功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF27Power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.65 | hwLFDCMeterQF1ElectricEnergy | QF1 electric energy | QF1电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF1ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.66 | hwLFDCMeterQF2ElectricEnergy | QF2 electric energy | QF2电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF2ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.67 | hwLFDCMeterQF3ElectricEnergy | QF3 electric energy | QF3电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF3ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.68 | hwLFDCMeterQF4ElectricEnergy | QF4 electric energy | QF4电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF4ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.69 | hwLFDCMeterQF5ElectricEnergy | QF5 electric energy | QF5电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF5ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.70 | hwLFDCMeterQF6ElectricEnergy | QF6 electric energy | QF6电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF6ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.71 | hwLFDCMeterQF7ElectricEnergy | QF7 electric energy | QF7电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF7ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.72 | hwLFDCMeterQF8ElectricEnergy | QF8 electric energy | QF8电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF8ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.73 | hwLFDCMeterQF9ElectricEnergy | QF9 electric energy | QF9电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF9ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.74 | hwLFDCMeterQF10ElectricEnergy | QF10 electric energy | QF10电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF10ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.75 | hwLFDCMeterQF11ElectricEnergy | QF11 electric energy | QF11电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF11ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.76 | hwLFDCMeterQF12ElectricEnergy | QF12 electric energy | QF12电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF12ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.77 | hwLFDCMeterQF13ElectricEnergy | QF13 electric energy | QF13电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF13ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.78 | hwLFDCMeterQF14ElectricEnergy | QF14 electric energy | QF14电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF14ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.79 | hwLFDCMeterQF15ElectricEnergy | QF15 electric energy | QF15电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF15ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.80 | hwLFDCMeterQF16ElectricEnergy | QF16 electric energy | QF16电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF16ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.81 | hwLFDCMeterQF17ElectricEnergy | QF17 electric energy | QF17电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF17ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.82 | hwLFDCMeterQF18ElectricEnergy | QF18 electric energy | QF18电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF18ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.83 | hwLFDCMeterQF19ElectricEnergy | QF19 electric energy | QF19电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF19ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.84 | hwLFDCMeterQF20ElectricEnergy | QF20 electric energy | QF20电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF20ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.85 | hwLFDCMeterQF21ElectricEnergy | QF21 electric energy | QF21电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF21ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.86 | hwLFDCMeterQF22ElectricEnergy | QF22 electric energy | QF22电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF22ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.87 | hwLFDCMeterQF23ElectricEnergy | QF23 electric energy | QF23电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF23ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.88 | hwLFDCMeterQF24ElectricEnergy | QF24 electric energy | QF24电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF24ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.89 | hwLFDCMeterQF25ElectricEnergy | QF25 electric energy | QF25电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF25ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.90 | hwLFDCMeterQF26ElectricEnergy | QF26 electric energy | QF26电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF26ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.91 | hwLFDCMeterQF27ElectricEnergy | QF27 electric energy | QF27电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Lang Fang DC Meter Meter QF27ElectricEnergy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.92 | hwLFDCMeterQF1SwitchStatus | QF1 switch status | QF1开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF1 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.93 | hwLFDCMeterQF2SwitchStatus | QF2 switch status | QF2开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF2 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.94 | hwLFDCMeterQF3SwitchStatus | QF3 switch status | QF3开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF3 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.95 | hwLFDCMeterQF4SwitchStatus | QF4 switch status | QF4开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF4 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.96 | hwLFDCMeterQF5SwitchStatus | QF5 switch status | QF5开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF5 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.97 | hwLFDCMeterQF6SwitchStatus | QF6 switch status | QF6开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF6 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.98 | hwLFDCMeterQF7SwitchStatus | QF7 switch status | QF7开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF7 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.99 | hwLFDCMeterQF8SwitchStatus | QF8 switch status | QF8开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF8 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.100 | hwLFDCMeterQF9SwitchStatus | QF9 switch status | QF9开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF9 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.101 | hwLFDCMeterQF10SwitchStatus | QF10 switch status | QF10开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF10 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.102 | hwLFDCMeterQF11SwitchStatus | QF11 switch status | QF11开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF11 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.103 | hwLFDCMeterQF12SwitchStatus | QF12 switch status | QF12开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF12 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.104 | hwLFDCMeterQF13SwitchStatus | QF13 switch status | QF13开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF13 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.105 | hwLFDCMeterQF14SwitchStatus | QF14 switch status | QF14开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF14 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.106 | hwLFDCMeterQF15SwitchStatus | QF15 switch status | QF15开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF15 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.107 | hwLFDCMeterQF16SwitchStatus | QF16 switch status | QF16开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF16 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.108 | hwLFDCMeterQF17SwitchStatus | QF17 switch status | QF17开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF17 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.109 | hwLFDCMeterQF18SwitchStatus | QF18 switch status | QF18开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF18 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.110 | hwLFDCMeterQF19SwitchStatus | QF19 switch status | QF19开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF19 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.111 | hwLFDCMeterQF20SwitchStatus | QF20 switch status | QF20开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF20 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.112 | hwLFDCMeterQF21SwitchStatus | QF21 switch status | QF21开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF21 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.113 | hwLFDCMeterQF22SwitchStatus | QF22 switch status | QF22开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF22 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.114 | hwLFDCMeterQF23SwitchStatus | QF23 switch status | QF23开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF23 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.115 | hwLFDCMeterQF24SwitchStatus | QF24 switch status | QF24开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF24 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.116 | hwLFDCMeterQF25SwitchStatus | QF25 switch status | QF25开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF25Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.117 | hwLFDCMeterQF26SwitchStatus | QF26 switch status | QF26开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF26 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.118 | hwLFDCMeterQF27SwitchStatus | QF27 switch status | QF27开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Lang Fang DC MeterMeter QF27 Switch Status: Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.119 | hwLFDCMeterDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The device name of Lang Fang DC Meter Meter.
1.3.6.1.4.1.2011.6.178.1.1.33.1.1.150 | hwLFDCMeterRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Lang Fang DC Meter Meter.

## Infrared Remote Control Module
红外遥控模块
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.34 | InfraredRemoteControlModule | Infrared Remote Control Module | 红外遥控模块 | / | / | / | / | The Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1 | hwInfraredRemoteControlModuleRunningandConfigTable | / | / |  |  | / | / | The running table of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.1 | hwInfraredRemoteControlModuleRunningandConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.2 | hwInfraredRemoteControlModuleCommState | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Communication Status of Infrared Remote Control Module: Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.3 | hwInfraredRemoteControlModuleCommPort | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The Comm Port of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.4 | hwInfraredRemoteControlModuleModbusAddr | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Modbus Addr of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.5 | hwInfraredRemoteControlModuleControlState | Running status | 运行状态 | 0-Read_Only | 只读 | controlstatus(1), learningstatus(2), unknown(255) | [控制状态=1]/[学习状态=2] | The Control Status of Infrared Remote Control Module: Value 1 indicates Control status. Value 2 indicates Learning status.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.6 | hwInfraredRemoteControlModuleLearnState | Learning status | 学习状态 | 0-Read_Only | 只读 | learning(1), learningsucceeded(2), learningfailed(3), unknown(255) | [正在学习=1]/[学习成功=2]/[学习失败=3] | The Learn Status of Infrared Remote Control Module: Value 1 indicates Learning. Value 2 indicates Learning succeeded. Value 3 indicates Learning failed.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.7 | hwInfraredRemoteControlModuleCtrlOnCode | Air conditioner startup | 空调开机 | 1-Read_Write | 读写 | yes(2), unknown(255) | [是=1] | The Ctrl On Code of Infrared Remote Control Module.: Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.8 | hwInfraredRemoteControlModuleEquipmentOrdinate | Device ordinate | 设备纵坐标 | 0-Read_Only | 只读 | 0..13 | 0..13 | The Equipment Ordinate of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.9 | hwInfraredRemoteControlModuleEquipmentHorizontal | Device horizontal | 设备横坐标 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Equipment Horizontal of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.10 | hwInfraredRemoteControlModuleOriginZ | Original coordinate Z | 起始坐标Z | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The OriginZ of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.11 | hwInfraredRemoteControlModuleEquipLength | Device length | 设备长度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Equip Length of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.12 | hwInfraredRemoteControlModuleEquipWidth | Device width | 设备宽度 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Equip Width of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.13 | hwInfraredRemoteControlModuleIsLayoutEquip | Layout type | 布局类型 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Is Layout Equip of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.14 | hwInfraredRemoteControlModuleIsSmartEquip | Smart device or not | 是否为智能设备 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Is Smart Equip of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.15 | hwInfraredRemoteControlModuleManualaddEquip | Manually add device | 手动添加子设备 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Manualadd Equip of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.16 | hwInfraredRemoteControlModuleDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The Device Name of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.17 | hwInfraredRemoteControlModulePictureName | Picture name | 图片名称 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Picture Name of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.18 | hwInfraredRemoteControlModulePositionAttribute | Position attribute | 位置属性 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Position Attribute of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.19 | hwInfraredRemoteControlModuleEquipIntroduction | Device introduction | 设备简介 | 0-Read_Only | 只读 | 0..1024 | 0..1024 | The Equip Introduction of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.20 | hwInfraredRemoteControlModuleParentDeviceDevId | Father equip ID | 父设备ID | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Parent Device DevId of Infrared Remote Control Module.
1.3.6.1.4.1.2011.6.178.1.1.34.1.1.100 | hwInfraredRemoteControlModuleRunningandConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running row status of Infrared Remote Control Module.

## PMAC615
PMAC615
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.35 | UniphaseSmartMeter615 | PMAC615 | PMAC615 | / | / | / | / | The Uniphase Smart Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.35.1 | hwUniphaseSmartMeter615RunningAndConfigTable | / | / |  |  | / | / | The running and config table of Uniphase Smart Meter 615.
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.1 | hwUniphaseSmartMeter615RunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the Uniphase Smart Meter 615.
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.2 | hwUniphaseSmartMeter615CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Communication Status of Uniphase Smart Meter 615: Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.3 | hwUniphaseSmartMeter615PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 0..8 | 0..8 | The Port No. of Uniphase Smart Meter 615.
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.4 | hwUniphaseSmartMeter615ModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Modbus Address of Uniphase Smart Meter 615.
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.5 | hwUniphaseSmartMeter615Current | Current | 电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Current of Uniphase Smart Meter 615. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.6 | hwUniphaseSmartMeter615Voltage | Voltage | 电压 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Voltage of Uniphase Smart Meter 615. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.7 | hwUniphaseSmartMeter615ValidPower | Active power | 有功功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Valid Power of Uniphase Smart Meter 615. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.8 | hwUniphaseSmartMeter615InvalidPower | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Invalid Power of Uniphase Smart Meter 615. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.9 | hwUniphaseSmartMeter615PowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Power Factor of Uniphase Smart Meter 615. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.10 | hwUniphaseSmartMeter615Frequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Frequency of Uniphase Smart Meter 615. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.13 | hwUniphaseSmartMeter615AllEnergy | Total active electricity | 总有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The All Energy of Uniphase Smart Meter 615. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.14 | hwUniphaseSmartMeter615InputEnergy | Input active electricity | 输入有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Input Energy of Uniphase Smart Meter 615. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.15 | hwUniphaseSmartMeter615OutputEnergy | Output active electricity | 输出有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Output Energy of Uniphase Smart Meter 615. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.16 | hwUniphaseSmartMeter615SetFreqHigher | High frequency alarm threshold | 频率过高告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | Set Uniphase Smart Meter 615 Freq Higher. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.17 | hwUniphaseSmartMeter615SetFreqLower | Low frequency alarm threshold | 频率过低告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | Set Uniphase Smart Meter 615 Freq Lower. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.18 | hwUniphaseSmartMeter615SetVoltOver | Overvoltage alarm threshold | 电压过压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | Set Uniphase Smart Meter 615 Volt Over. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.19 | hwUniphaseSmartMeter615SetVoltDeficiency | Undervoltage alarm threshold | 电压欠压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | Set Uniphase Smart Meter 615 Volt Deficiency. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.31 | hwUniphaseSmartMeter615DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The Device Name of Uniphase Smart Meter 615.
1.3.6.1.4.1.2011.6.178.1.1.35.1.1.50 | hwUniphaseSmartMeter615RunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running and config table for the Uniphase Smart Meter.

## PMAC625
PMAC625
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.36 | UniphaseSmartMeter625 | PMAC625 | PMAC625 | / | / | / | / | The Uniphase Smart Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.36.1 | hwUniphaseSmartMeter625RunningAndConfigTable | / | / |  |  | / | / | The running and config table of Uniphase Smart Meter 625.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.1 | hwUniphaseSmartMeter625RunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the Uniphase Smart Meter 625.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.2 | hwUniphaseSmartMeter625CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The CommunicationStatus of the Uniphase Smart Meter 625: Value 1 indicates commok. Value 2 indicates commfail.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.3 | hwUniphaseSmartMeter625PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 0..8 | 0..8 | The PortNo. of the Uniphase Smart Meter 625.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.4 | hwUniphaseSmartMeter625ModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The ModbusAddress of the Uniphase Smart Meter 625.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.5 | hwUniphaseSmartMeter625PhaseVoltA | Phase A voltage | A相电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The PhaseVoltA of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.6 | hwUniphaseSmartMeter625PhaseVoltB | Phase B voltage | B相电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The PhaseVoltB of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.7 | hwUniphaseSmartMeter625PhaseVoltC | Phase C voltage | C相电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The PhaseVoltC of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.8 | hwUniphaseSmartMeter625LineVoltAB | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The LineVoltAB of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.9 | hwUniphaseSmartMeter625LineVoltBC | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The LineVoltBC of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.10 | hwUniphaseSmartMeter625LineVoltCA | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The LineVoltCA of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.11 | hwUniphaseSmartMeter625PhaseCurA | Phase A current | A相电流 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | The PhaseCurA of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.12 | hwUniphaseSmartMeter625PhaseCurB | Phase B current | B相电流 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | The PhaseCurA of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.13 | hwUniphaseSmartMeter625PhaseCurC | Phase C current | C相电流 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | The PhaseCurA of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.14 | hwUniphaseSmartMeter625ZeroSeqCur | Zero sequence current | 零序电流 | 0-Read_Only | 只读 | 0..6000 | 0..6000 | The ZeroSeqCur of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.15 | hwUniphaseSmartMeter625SumPowerValid | Total active power | 有功功率总和 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The SumPowerValid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.16 | hwUniphaseSmartMeter625SumPowerInvalid | Total reactive power | 无功功率总和 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The SumPowerInvalid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.17 | hwUniphaseSmartMeter625FactorSumPower | Total power factor | 功率因数总和 | 0-Read_Only | 只读 | -100..100 | -100..100 | The FactorSumPower of the Uniphase Smart Meter 625. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.18 | hwUniphaseSmartMeter625PhaseAPowerValid | Phase A active power | A相有功功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The PhaseAPowerValid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.19 | hwUniphaseSmartMeter625PhaseBPowerValid | Phase B active power | B相有功功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The PhaseBPowerValid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.20 | hwUniphaseSmartMeter625PhaseCPowerValid | Phase C active power | C相有功功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The PhaseCPowerValid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.21 | hwUniphaseSmartMeter625PhaseAPowerInvalid | Phase A reactive power | A相无功功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The PhaseAPowerInvalid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.22 | hwUniphaseSmartMeter625PhaseBPowerInvalid | Phase B reactive power | B相无功功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The PhaseBPowerInvalid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.23 | hwUniphaseSmartMeter625PhaseCPowerInvalid | Phase C reactive power | C相无功功率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The PhaseCPowerInvalid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.24 | hwUniphaseSmartMeter625FactorPhaseAPower | Phase A power factor | A相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The FactorPhaseAPower of the Uniphase Smart Meter 625. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.25 | hwUniphaseSmartMeter625FactorPhaseBPower | Phase B power factor | B相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The FactorPhaseBPower of the Uniphase Smart Meter 625. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.26 | hwUniphaseSmartMeter625FactorPhaseCPower | Phase C power factor | C相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The FactorPhaseCPower of the Uniphase Smart Meter 625. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.27 | hwUniphaseSmartMeter625Frequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Frequency of the Uniphase Smart Meter 625. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.28 | hwUniphaseSmartMeter625EnergySumValid | Total active electricity | 有功电度总和 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The EnergySumValid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.29 | hwUniphaseSmartMeter625EnergySumInvalid | Total reactive electricity | 无功电度总和 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The EnergySumInvalid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.30 | hwUniphaseSmartMeter625EnergyInputValid | Input active electricity | 输入有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The EnergyInputValid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.31 | hwUniphaseSmartMeter625EnergyOutputValid | Output active electricity | 输出有功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The EnergyOutputValid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.32 | hwUniphaseSmartMeter625EnergyInputInvalid | Input reactive electricity | 输入无功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The EnergyInputInvalid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.33 | hwUniphaseSmartMeter625EnergyOutputInvalid | Output reactive electricity | 输出无功电度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The EnergyOutputInvalid of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.36 | hwUniphaseSmartMeter625SetFreqHigher | High frequency alarm threshold | 频率过高告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | Set Freq Higher Comm Addr of the Uniphase Smart Meter 625. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.37 | hwUniphaseSmartMeter625SetFreqLower | Low frequency alarm threshold | 频率过低告警点 | 1-Read_Write | 读写 | 40..70 | 40..70 | Set Freq Lower of the Uniphase Smart Meter 625. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.38 | hwUniphaseSmartMeter625SetPhaseVoltOver | Phase overvoltage alarm threshold | 相电压过压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | Set Phase Volt Over of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.39 | hwUniphaseSmartMeter625SetPhaseVoltDeficiency | Phase undervoltage alarm threshold | 相电压欠压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | Set Phase Volt Deficiency of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.40 | hwUniphaseSmartMeter625SetLineVoltOver | Line overvoltage alarm threshold | 线电压过压告警点 | 1-Read_Write | 读写 | 500..6000 | 500..6000 | Set Line Volt Over of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.41 | hwUniphaseSmartMeter625SetLineVoltDeficiency | Line undervoltage alarm threshold | 线电压欠压告警点 | 1-Read_Write | 读写 | 500..6000 | 500..6000 | Line Volt Deficiency of the Uniphase Smart Meter 625. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.55 | hwUniphaseSmartMeter625DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The Device Name of the Uniphase Smart Meter 625.
1.3.6.1.4.1.2011.6.178.1.1.36.1.1.100 | hwUniphaseSmartMeter625RunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running and config table for the Uniphase Smart Meter.

## Power Distribution Unit
分接单元
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.37 | PowerDistributionUnit | Power Distribution Unit | 分接单元 | / | / | / | / | The General Input Unit Equipment.
1.3.6.1.4.1.2011.6.178.1.1.37.1 | hwPowerDistributionUnitRunningAndConfig1Table | / | / |  |  | / | / | The running and config table of Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.1 | hwPowerDistributionUnitRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.2 | hwPowerDistributionUnitCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Comm Status of the Power Distribution Unit: value 1 indicates normal. value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.3 | hwPowerDistributionUnitESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of power distribution unit.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.4 | hwPowerDistributionUnitSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of power distribution unit.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.5 | hwPowerDistributionUnitHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of power distribution unit.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.6 | hwPowerDistributionUnitPOE1PowerSwitchStatus | POE1 power switch status | POE1 电源开关状态 | 0-Read_Only | 只读 | powerOn(1), powerOff(2), unknown(255) | [供电=1]/[断电=2] | POE1 power switch status of power distribution unit: value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.7 | hwPowerDistributionUnitPOE2PowerSwitchStatus | POE2 power switch status | POE2 电源开关状态 | 0-Read_Only | 只读 | powerOn(1), powerOff(2), unknown(255) | [供电=1]/[断电=2] | POE2 power switch status of power distribution unit: value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.8 | hwPowerDistributionUnitPOE3PowerSwitchStatus | POE3 power switch status | POE3 电源开关状态 | 0-Read_Only | 只读 | powerOn(1), powerOff(2), unknown(255) | [供电=1]/[断电=2] | POE3 power switch status of power distribution unit: value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.9 | hwPowerDistributionUnitPOE4PowerSwitchStatus | POE4 power switch status | POE4 电源开关状态 | 0-Read_Only | 只读 | powerOn(1), powerOff(2), unknown(255) | [供电=1]/[断电=2] | POE4 power switch status of power distribution unit: value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.10 | hwPowerDistributionUnitPOE1ConnectionStatus | POE1 connection status | POE1 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | POE1 connection status of power distribution unit: value 1 indicates link. Value 2 indicates nonlink.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.11 | hwPowerDistributionUnitPOE2ConnectionStatus | POE2 connection status | POE2 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | POE2 connection status of power distribution unit: value 1 indicates link. Value 2 indicates nonlink.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.12 | hwPowerDistributionUnitPOE3ConnectionStatus | POE3 connection status | POE3 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | POE3 connection status of power distribution unit: value 1 indicates link. Value 2 indicates nonlink.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.13 | hwPowerDistributionUnitPOE4ConnectionStatus | POE4 connection status | POE4 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | POE4 connection status of power distribution unit: value 1 indicates link. Value 2 indicates nonlink.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.14 | hwPowerDistributionUnitFE1ConnectionStatus | FE1 connection status | FE1 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | FE1 connection status of power distribution unit: value 1 indicates link. Value 2 indicates nonlink.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.15 | hwPowerDistributionUnitFE2ConnectionStatus | FE2 connection status | FE2 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | FE2 connection status of power distribution unit: value 1 indicates link. Value 2 indicates nonlink.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.16 | hwPowerDistributionUnitBranch1SwitchStatus | QF1 Switch status(L1) | QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | Branch 1 switch status of power distribution unit: value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.18 | hwPowerDistributionUnitBranch1OutputCurrent | QF1 Output current(L1) | QF1 输出电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Branch 1 output current of power distribution unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.19 | hwPowerDistributionUnitBranch1OutputActivePower | QF1 Output active power(L1) | QF1 输出有功功率(L1) | 0-Read_Only | 只读 | -400..400 | -400..400 | Branch 1 output active power of power distribution unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.22 | hwPowerDistributionUnitBranch1OutputActiveElectricity | QF1 Output active electricity(L1) | QF1 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Branch 1 output active electricity of power distribution unit. Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.23 | hwPowerDistributionUnitBranch1OutputLoadPercentage | QF1 Output load percentage(L1) | QF1 输出负载率(L1) | 0-Read_Only | 只读 | 0..500 | 0..500 | Branch 1 output load percentage of power distribution unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.24 | hwPowerDistributionUnitBranch1Temperature | QF1 Temperature(L1) | QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Branch 1 temperature of power distribution unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.26 | hwPowerDistributionUnitBranch2SwitchStatus | QF2 Switch status(L2) | QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | Branch 2 switch status of power distribution unit: value 1 indicates open. value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.28 | hwPowerDistributionUnitBranch2OutputCurrent | QF2 Output current(L2) | QF2 输出电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Branch 2 output current of power distribution unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.29 | hwPowerDistributionUnitBranch2OutputActivePower | QF2 Output active power(L2) | QF2 输出有功功率(L2) | 0-Read_Only | 只读 | -400..400 | -400..400 | Branch 2 output active power of power distribution unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.32 | hwPowerDistributionUnitBranch2OutputActiveElectricity | QF2 Output active electricity(L2) | QF2 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Branch 2 output active electricity of power distribution unit. Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.33 | hwPowerDistributionUnitBranch2OutputLoadPercentage | QF2 Output load percentage(L2) | QF2 输出负载率(L2) | 0-Read_Only | 只读 | 0..500 | 0..500 | Branch 2 output load percentage of power distribution unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.34 | hwPowerDistributionUnitBranch2Temperature | QF2 Temperature(L2) | QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Branch 2 temperature of power distribution unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.36 | hwPowerDistributionUnitBranch3SwitchStatus | QF3 Switch status(L3) | QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | Branch 3 switch status of power distribution unit: value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.38 | hwPowerDistributionUnitBranch3OutputCurrent | QF3 Output current(L3) | QF3 输出电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Branch 3 output current of power distribution unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.39 | hwPowerDistributionUnitBranch3OutputActivePower | QF3 Output active power(L3) | QF3 输出有功功率(L3) | 0-Read_Only | 只读 | -400..400 | -400..400 | Branch 3 output active power of power distribution unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.42 | hwPowerDistributionUnitBranch3OutputActiveElectricity | QF3 Output active electricity(L3) | QF3 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Branch 3 output active electricity of power distribution unit. Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.43 | hwPowerDistributionUnitBranch3OutputLoadPercentage | QF3 Output load percentage(L3) | QF3 输出负载率(L3) | 0-Read_Only | 只读 | 0..500 | 0..500 | Branch 3 output load percentage of power distribution unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.44 | hwPowerDistributionUnitBranch3Temperature | QF3 Temperature(L3) | QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Branch 3 temperature of power distribution unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.46 | hwPowerDistributionUnitBranch4SwitchStatus | QF4 Switch status(L1) | QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | Branch 4 switch status of power distribution unit: value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.48 | hwPowerDistributionUnitBranch4OutputCurrent | QF4 Output current(L1) | QF4 输出电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Branch 4 output current of power distribution unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.49 | hwPowerDistributionUnitBranch4OutputActivePower | QF4 Output active power(L1) | QF4 输出有功功率(L1) | 0-Read_Only | 只读 | -400..400 | -400..400 | Branch 4 output active power of power distribution unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.52 | hwPowerDistributionUnitBranch4OutputActiveElectricity | QF4 Output active electricity(L1) | QF4 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Branch 4 output active electricity of power distribution unit. Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.53 | hwPowerDistributionUnitBranch4OutputLoadPercentage | QF4 Output load percentage(L1) | QF4 输出负载率(L1) | 0-Read_Only | 只读 | 0..500 | 0..500 | Branch 4 output load percentage of power distribution unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.54 | hwPowerDistributionUnitBranch4Temperature | QF4 Temperature(L1) | QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Branch 4 temperature of power distribution unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.56 | hwPowerDistributionUnitBranch5SwitchStatus | QF5 Switch status(L2) | QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | Branch 5 switch status of power distribution unit: value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.58 | hwPowerDistributionUnitBranch5OutputCurrent | QF5 Output current(L2) | QF5 输出电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Branch 5 output current of power distribution unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.59 | hwPowerDistributionUnitBranch5OutputActivePower | QF5 Output active power(L2) | QF5 输出有功功率(L2) | 0-Read_Only | 只读 | -400..400 | -400..400 | Branch 5 output active power of power distribution unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.62 | hwPowerDistributionUnitBranch5OutputActiveElectricity | QF5 Output active electricity(L2) | QF5 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Branch 5 output active electricity of power distribution unit. Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.63 | hwPowerDistributionUnitBranch5OutputLoadPercentage | QF5 Output load percentage(L2) | QF5 输出负载率(L2) | 0-Read_Only | 只读 | 0..500 | 0..500 | Branch 5 output load percentage of power distribution unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.64 | hwPowerDistributionUnitBranch5Temperature | QF5 Temperature(L2) | QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Branch 5 temperature of power distribution unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.66 | hwPowerDistributionUnitBranch6SwitchStatus | QF6 Switch status(L3) | QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | Branch 6 switch status of power distribution unit: value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.68 | hwPowerDistributionUnitBranch6OutputCurrent | QF6 Output current(L3) | QF6 输出电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Branch 6 output current of power distribution unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.69 | hwPowerDistributionUnitBranch6OutputActivePower | QF6 Output active power(L3) | QF6 输出有功功率(L3) | 0-Read_Only | 只读 | -400..400 | -400..400 | Branch 6 output active power of power distribution unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.72 | hwPowerDistributionUnitBranch6OutputActiveElectricity | QF6 Output active electricity(L3) | QF6 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Branch 6 output active electricity of power distribution unit. Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.73 | hwPowerDistributionUnitBranch6OutputLoadPercentage | QF6 Output load percentage(L3) | QF6 输出负载率(L3) | 0-Read_Only | 只读 | 0..500 | 0..500 | Branch 6 output load percentage of power distribution unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.74 | hwPowerDistributionUnitBranch6Temperature | QF6 Temperature(L3) | QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Branch 6 temperature of power distribution unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.80 | hwPowerDistributionUnitDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device name of power distribution unit.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.81 | hwPowerDistributionUnitBranch1RatedCurrent | QF1 Rated current(L1) | QF1 额定电流(L1) | 1-Read_Write | 读写 | 0..100 | 0..100 | Branch 1 rated current of power distribution unit. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.82 | hwPowerDistributionUnitBranch2RatedCurrent | QF2 Rated current(L2) | QF2 额定电流(L2) | 1-Read_Write | 读写 | 0..100 | 0..100 | Branch 2 rated current of power distribution unit. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.83 | hwPowerDistributionUnitBranch3RatedCurrent | QF3 Rated current(L3) | QF3 额定电流(L3) | 1-Read_Write | 读写 | 0..100 | 0..100 | Branch 3 rated current of power distribution unit. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.84 | hwPowerDistributionUnitBranch4RatedCurrent | QF4 Rated current(L1) | QF4 额定电流(L1) | 1-Read_Write | 读写 | 0..100 | 0..100 | Branch 4 rated current of power distribution unit. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.85 | hwPowerDistributionUnitBranch5RatedCurrent | QF5 Rated current(L2) | QF5 额定电流(L2) | 1-Read_Write | 读写 | 0..100 | 0..100 | Branch 5 rated current of power distribution unit. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.86 | hwPowerDistributionUnitBranch6RatedCurrent | QF6 Rated current(L3) | QF6 额定电流(L3) | 1-Read_Write | 读写 | 0..100 | 0..100 | Branch 6 rated current of power distribution unit. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.87 | hwPowerDistributionUnitClearEnergyYieldData | Clear energy yield data (affecting PUE) | 清除电能数据(会影响PUE计算) | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear energy yield data of power distribution unit: value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.88 | hwPowerDistributionUnitBranchCurrentShockProtection | Branch current shock protection | 支路电流冲击保护 | 1-Read_Write | 读写 | 100..500 | 100..500 | Branch Current Shock Protection of the Uniphase Power Distribution Unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.89 | hwPowerDistributionUnitBranch1Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Branch 1 name of Power Distribution.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.90 | hwPowerDistributionUnitBranch2Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Branch 2 name of Power Distribution.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.91 | hwPowerDistributionUnitBranch3Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Branch 3 name of Power Distribution.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.92 | hwPowerDistributionUnitBranch4Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Branch 4 name of Power Distribution.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.93 | hwPowerDistributionUnitBranch5Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Branch 5 name of Power Distribution.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.94 | hwPowerDistributionUnitBranch6Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Branch 6 name of Power Distribution.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.95 | hwPowerDistributionUnitBranch1CollectionDisplayFlag | QF1 collection display flag(L1) | QF1 采集显示标志(L1) | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch1 collection display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.96 | hwPowerDistributionUnitBranch2CollectionDisplayFlag | QF2 collection display flag(L2) | QF2 采集显示标志(L2) | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch2 collection display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.97 | hwPowerDistributionUnitBranch3CollectionDisplayFlag | QF3 collection display flag(L3) | QF3 采集显示标志(L3) | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch3 collection display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.98 | hwPowerDistributionUnitBranch4CollectionDisplayFlag | QF4 collection display flag(L1) | QF4 采集显示标志(L1) | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch4 collection display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.99 | hwPowerDistributionUnitBranch5CollectionDisplayFlag | QF5 collection display flag(L2) | QF5 采集显示标志(L2) | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch5 collection display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.100 | hwPowerDistributionUnitBranch6CollectionDisplayFlag | QF6 collection display flag(L3) | QF6 采集显示标志(L3) | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch6 collection display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.101 | hwPowerDistributionUnitBranch1SettingDisplayFlag | Branch 1 setting display flag | QF1设置显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch1 setting display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.102 | hwPowerDistributionUnitBranch2SettingDisplayFlag | Branch 2 setting display flag | QF2设置显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch2 setting display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.103 | hwPowerDistributionUnitBranch3SettingDisplayFlag | Branch 3 setting display flag | QF3设置显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch3 setting display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.104 | hwPowerDistributionUnitBranch4SettingDisplayFlag | Branch 4 setting display flag | QF4设置显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch4 setting display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.105 | hwPowerDistributionUnitBranch5SettingDisplayFlag | Branch 5 setting display flag | QF5设置显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch5 setting display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.106 | hwPowerDistributionUnitBranch6SettingDisplayFlag | Branch 6 setting display flag | QF6设置显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | Branch6 setting display flag.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.107 | hwPowerDistributionUnitBranch1CircuitBreakerInUse | QF1 Branch circuit breaker in use(L1) | QF1 支路空开使用状态(L1) | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Branch Circuit Breaker InUse(QF1): value 1 indicates enable, value 2 indicates disable,
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.108 | hwPowerDistributionUnitBranch2CircuitBreakerInUse | QF2 Branch circuit breaker in use(L2) | QF2 支路空开使用状态(L2) | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Branch Circuit Breaker InUse(QF2): value 1 indicates enable, value 2 indicates disable,
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.109 | hwPowerDistributionUnitBranch3CircuitBreakerInUse | QF3 Branch circuit breaker in use(L3) | QF3 支路空开使用状态(L3) | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Branch Circuit Breaker InUse(QF3): value 1 indicates enable, value 2 indicates disable,
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.110 | hwPowerDistributionUnitBranch4CircuitBreakerInUse | QF4 Branch circuit breaker in use(L1) | QF4 支路空开使用状态(L1) | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Branch Circuit Breaker InUse(QF4): value 1 indicates enable, value 2 indicates disable,
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.111 | hwPowerDistributionUnitBranch5CircuitBreakerInUse | QF5 Branch circuit breaker in use(L2) | QF5 支路空开使用状态(L2) | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Branch Circuit Breaker InUse(QF5): value 1 indicates enable, value 2 indicates disable,
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.112 | hwPowerDistributionUnitBranch6CircuitBreakerInUse | QF6 Branch circuit breaker in use(L3) | QF6 支路空开使用状态(L3) | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Branch Circuit Breaker InUse(QF6): value 1 indicates enable, value 2 indicates disable,
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.113 | hwPowerDistributionUnitMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | Mac address of Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.1.1.125 | hwPowerDistributionUnitRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.2 | hwPowerDistributionUnitRunningAndConfig2Table | / | / |  |  | / | / | The running and config table of Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.1 | hwPowerDistributionUnitRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.2 | hwPowerDistributionUnitElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | Elabel of power distribution unit.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.3 | hwPowerDistributionUnitConfigureNTConbranch | Configure NTC on branch | 支路是否配置NTC | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Configure NTC on branch: value 1 indicates no, value 2 indicates yes,
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.4 | hwPowerDistributionUnitL1busbartemperature | L1 busbar temperature | L1母排温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | The L1 busbar temperature of the Power Distribution Unit.Multiple:100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.5 | hwPowerDistributionUnitL2busbartemperature | L2 busbar temperature | L2母排温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | The L2 busbar temperature of the Power Distribution Unit.Multiple:100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.6 | hwPowerDistributionUnitL3busbartemperature | L3 busbar temperature | L3母排温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | The L3 busbar temperature of the Power Distribution Unit.Multiple:100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.7 | hwPowerDistributionUnitNbusbartemperature | N busbar temperature | N母排温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | The N busbar temperature of the Power Distribution Unit.Multiple:100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.8 | hwPowerDistributionUnitUpperloadcurthres | Upper load current threshold | 负载电流高阈值 | 1-Read_Write | 读写 | 80..99 | 80..99 | The Upper load cur thres of the Power Distribution Unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.9 | hwPowerDistributionUnitLowerloadcurthres | Lower load current threshold | 负载电流低阈值 | 1-Read_Write | 读写 | 60..79 | 60..79 | The Lower load cur thres of the Power Distribution Unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.10 | hwPowerDistributionUnitBranchnumber | Branch number | 支路数目 | 0-Read_Only | 只读 | 0..6 | 0..6 | The Branch number of the Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.11 | hwPowerDistributionUnitPredictedL1BranchBusbarTemperature | Predicted L1 branch busbar temperature | 支路L1母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L1 branch busbar temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.12 | hwPowerDistributionUnitPredictedL2BranchBusbarTemperature | Predicted L2 branch busbar temperature | 支路L2母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L2 branch busbar temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.13 | hwPowerDistributionUnitPredictedL3BranchBusbarTemperature | Predicted L3 branch busbar temperature | 支路L3母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L3 branch busbar temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.14 | hwPowerDistributionUnitAmbientTemperature | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Ambient temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.15 | hwPowerDistributionUnitNumberOfDetectionPoints | Number of detection points | 检测点数目 | 1-Read_Write | 读写 | 0..6 | 0..6 | Number of detection points of the device config table for the Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.16 | hwPowerDistributionUnitTemperatureWarningThreshold | Temperature warning threshold | 温度预警阈值 | 1-Read_Write | 读写 | 10..30 | 10..30 | Temperature warning threshold of the device config table for the Power Distribution Unit.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.17 | hwPowerDistributionUnitTemperaturePredictionEnabledStatus | Temperature prediction enabled status | 温度预测使能状态 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Temperature prediction enabled status of the device config table for the Power Distribution Unit. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.37.2.1.100 | hwPowerDistributionUnitRunningAndConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.3 | hwPowerDistributionUnitRunningAndConfig3Table | / | / |  |  | / | / | The running table of Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.1 | hwPowerDistributionUnitRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.2 | hwPowerDistributionUnitAmmeterSoftwareVersion | Ammeter software version | 电表软件版本 | 0-Read_Only | 只读 | 0..20 | 0..20 | Ammeter software version of the device config table for the Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.3 | hwPowerDistributionUnitNode1Temperature | Node1 temperature | 节点1温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node1 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.4 | hwPowerDistributionUnitNode2Temperature | Node2 temperature | 节点2温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node2 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.5 | hwPowerDistributionUnitNode3Temperature | Node3 temperature | 节点3温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node3 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.6 | hwPowerDistributionUnitNode4Temperature | Node4 temperature | 节点4温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node4 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.7 | hwPowerDistributionUnitNode5Temperature | Node5 temperature | 节点5温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node5 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.8 | hwPowerDistributionUnitNode6Temperature | Node6 temperature | 节点6温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node6 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.9 | hwPowerDistributionUnitNode7Temperature | Node7 temperature | 节点7温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node7 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.10 | hwPowerDistributionUnitNode8Temperature | Node8 temperature | 节点8温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node8 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.11 | hwPowerDistributionUnitNode9Temperature | Node9 temperature | 节点9温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node9 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.12 | hwPowerDistributionUnitNode10Temperature | Node10 temperature | 节点10温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node10 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.13 | hwPowerDistributionUnitNode11Temperature | Node11 temperature | 节点11温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node11 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.14 | hwPowerDistributionUnitNode12Temperature | Node12 temperature | 节点12温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Node12 temperature of the device config table for the Power Distribution Unit.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.15 | hwPowerDistributionUnitOverload | Overload | 负载过载 | 1-Read_Write | 读写 | 100..120 | 100..120 | Overload of the device config table for the Power Distribution Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.37.3.1.300 | hwPowerDistributionUnitConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Power Distribution Unit.

## General Input Unit
始端单元
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.38 | GeneralInputUnit | General Input Unit | 始端单元 | / | / | / | / | The General Input Unit Equipment.
1.3.6.1.4.1.2011.6.178.1.1.38.1 | hwGeneralInputUnitRunningAndConfigTable | / | / |  |  | / | / | The running and config table of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.1 | hwGeneralInputUnitRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.2 | hwGeneralInputUnitCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Comm Status of the General Input Unit: value 1 indicates normal. value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.3 | hwGeneralInputUnitESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.4 | hwGeneralInputUnitSoftwareversion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.5 | hwGeneralInputUnitHardwareversion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.6 | hwGeneralInputUnitPOE1PowerSwitchStatus | POE1 power switch status | POE1 电源开关状态 | 0-Read_Only | 只读 | powerOn(1), powerOff(2), unknown(255) | [供电=1]/[断电=2] | POE1 power switch status of General Input Unit: value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.7 | hwGeneralInputUnitPOE2PowerSwitchStatus | POE2 power switch status | POE2 电源开关状态 | 0-Read_Only | 只读 | powerOn(1), powerOff(2), unknown(255) | [供电=1]/[断电=2] | POE2 power switch status of General Input Unit: value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.8 | hwGeneralInputUnitPOE3PowerSwitchStatus | POE3 power switch status | POE3 电源开关状态 | 0-Read_Only | 只读 | powerOn(1), powerOff(2), unknown(255) | [供电=1]/[断电=2] | POE3 power switch status of General Input Unit: value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.9 | hwGeneralInputUnitPOE4PowerSwitchStatus | POE4 power switch status | POE4 电源开关状态 | 0-Read_Only | 只读 | powerOn(1), powerOff(2), unknown(255) | [供电=1]/[断电=2] | POE4 power switch status of General Input Unit: value 1 indicates power on. Value 2 indicates power off.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.10 | hwGeneralInputUnitPOE1ConnectionStatus | POE1 connection status | POE1 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | POE1 connection status of General Input Unit: value 1 indicates link. Value 2 indicates unlink.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.11 | hwGeneralInputUnitPOE2ConnectionStatus | POE2 connection status | POE2 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | POE2 connection status of General Input Unit: value 1 indicates link. Value 2 indicates unlink.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.12 | hwGeneralInputUnitPOE3ConnectionStatus | POE3 connection status | POE3 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | POE3 connection status of General Input Unit: value 1 indicates link. Value 2 indicates unlink.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.13 | hwGeneralInputUnitPOE4ConnectionStatus | POE4 connection status | POE4 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | POE4 connection status of General Input Unit: value 1 indicates link. Value 2 indicates unlink.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.14 | hwGeneralInputUnitFE1ConnectionStatus | FE1 connection status | FE1 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | FE1 connection status of General Input Unit: value 1 indicates link. Value 2 indicates unlink.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.15 | hwGeneralInputUnitFE2ConnectionStatus | FE2 connection status | FE2 连接状态 | 0-Read_Only | 只读 | link(1), nonLink(2), unknown(255) | [连接=1]/[空闲=2] | FE2 connection status of General Input Unit: value 1 indicates link. Value 2 indicates unlink.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.16 | hwGeneralInputUnitL1InputVoltage | L1 input voltage | L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 input voltage of General Input Unit. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.17 | hwGeneralInputUnitL2InputVoltage | L2 input voltage | L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 input voltage of General Input Unit. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.18 | hwGeneralInputUnitL3InputVoltage | L3 input voltage | L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 input voltage of General Input Unit. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.19 | hwGeneralInputUnitL1L2InputLineVoltage | L1-L2 input line voltage | L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1-L2 input line voltage of General Input Unit. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.20 | hwGeneralInputUnitL2L3InputLineVoltage | L2-L3 input line voltage | L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2-L3 input line voltage of General Input Unit. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.21 | hwGeneralInputUnitL3L1InputLineVoltage | L3-L1 input line voltage | L1-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3-L1input line voltage of General Input Unit. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.22 | hwGeneralInputUnitL1InputCurrent | L1 input current | L1输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | L1 input current of General Input Unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.23 | hwGeneralInputUnitL2InputCurrent | L2 input current | L2输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | L2 input current of General Input Unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.24 | hwGeneralInputUnitL3InputCurrent | L3 input current | L3输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | L3 input current of General Input Unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.25 | hwGeneralInputUnitInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input frequency of General Input Unit. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.26 | hwGeneralInputUnitL1InputActivePower | L1 input active power | L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L1 input active power of General Input Unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.27 | hwGeneralInputUnitL2InputActivePower | L2 input active power | L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L2 input active power of General Input Unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.28 | hwGeneralInputUnitL3InputActivePower | L3 input active power | L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L3 input active power of General Input Unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.29 | hwGeneralInputUnitL1InputApparentPower | L1 input apparent power | L1输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L1 input apparent power of General Input Unit. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.30 | hwGeneralInputUnitL2InputApparentPower | L2 input apparent power | L2输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L2 input apparent power of General Input Unit. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.31 | hwGeneralInputUnitL3InputApparentPower | L3 input apparent power | L3输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L3 input apparent power of General Input Unit. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.32 | hwGeneralInputUnitL1InputReactivePower | L1 input reactive power | L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L1 input reactive power of General Input Unit. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.33 | hwGeneralInputUnitL2InputReactivePower | L2 input reactive power | L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L2 input reactive power of General Input Unit. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.34 | hwGeneralInputUnitL3InputReactivePower | L3 input reactive power | L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | L3 input reactive power of General Input Unit. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.35 | hwGeneralInputUnitL1InputPowerFactor | L1 input power factor | L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L1 input power factor of General Input Unit. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.36 | hwGeneralInputUnitL2InputPowerFactor | L2 input power factor | L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L2 input power factor of General Input Unit. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.37 | hwGeneralInputUnitL3InputPowerFactor | L3 input power factor | L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L3 input power factor of General Input Unit. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.38 | hwGeneralInputUnitInputActiveElectricity | Input active electricity | 输入有功电能 | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Input active electricity of General Input Unit. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.39 | hwGeneralInputUnitL1InputPowerLoadPercentage | L1 input power load percentage | L1输入电源负载率 | 0-Read_Only | 只读 | 0..500 | 0..500 | L1 input power load percentage of General Input Unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.40 | hwGeneralInputUnitL2InputPowerLoadPercentage | L2 input power load percentage | L2输入电源负载率 | 0-Read_Only | 只读 | 0..500 | 0..500 | L2 input power load percentage of General Input Unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.41 | hwGeneralInputUnitL3InputPowerLoadPercentage | L3 input power load percentage | L3输入电源负载率 | 0-Read_Only | 只读 | 0..500 | 0..500 | L3 input power load percentage of General Input Unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.42 | hwGeneralInputUnitInputNeutralWireCurrent | Input neutral wire current | 输入N线电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Input neutral wire current of General Input Unit. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.43 | hwGeneralInputUnitL1THDu | L1 THDu | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | L1 THDu of General Input Unit. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.44 | hwGeneralInputUnitL2THDu | L2 THDu | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | L2 THDu of General Input Unit. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.45 | hwGeneralInputUnitL3THDu | L3 THDu | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | L3 THDu of General Input Unit. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.46 | hwGeneralInputUnitL1THDi | L1 THDi | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | L1 THDi of General Input Unit. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.47 | hwGeneralInputUnitL2THDi | L2 THDi | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | L2 THDi of General Input Unit. Multiple 100.. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.48 | hwGeneralInputUnitL3THDi | L3 THDi | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | L3 THDi of General Input Unit. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.49 | hwGeneralInputUnitTotalInputActivePower | Total input active power | 总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Total input active power of General Input Unit. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.50 | hwGeneralInputUnitTotalInputApparentPower | Total input apparent power | 总输入视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Total input apparent power of General Input Unit. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.51 | hwGeneralInputUnitTotalInputReActivePower | Total input reactive power | 总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Total input reactive power of General Input Unit. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.52 | hwGeneralInputUnitInputNPEVoltage | Input N-PE voltage | 输入N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input N-PE voltage of General Input Unit. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.53 | hwGeneralInputUnitL1BusbarTemperature | L1 busbar temperature | L1母排温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | L1 busbar temperature of General Input Unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.54 | hwGeneralInputUnitL2BusbarTemperature | L2 busbar temperature | L2母排温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | L2 busbar temperature of General Input Unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.55 | hwGeneralInputUnitL3BusbarTemperature | L3 busbar temperature | L3母排温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | L3 busbar temperature of General Input Unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.56 | hwGeneralInputUnitNBusbarTemperature | N busbar temperature | N母排温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | N busbar temperature of General Input Unit. Multiple 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.57 | hwGeneralInputUnitElectricInformation | / | / | 0-Read_Only | 只读 | 0..4294967295 | / | Electric Information of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.58 | hwGeneralInputUnitDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device name of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.59 | hwGeneralInputUnitRatedSystemFrequency | Rated system frequency | 系统额定频率 | 1-Read_Write | 读写 | 45..65 | 45..65 | Rated system frequency of General Input Unit. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.60 | hwGeneralInputUnitRatedSystemVoltage | Rated system voltage | 系统额定电压 | 1-Read_Write | 读写 | 100..480 | 100..480 | Rated system voltage of General Input Unit. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.61 | hwGeneralInputUnitRatedSystemCurrent | Rated system current | 系统额定电流 | 1-Read_Write | 读写 | 100..630 | 100..630 | Rated system current of General Input Unit. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.62 | hwGeneralInputUnitSystemCTRatio | System CT ratio | 系统电流CT变比 | 1-Read_Write | 读写 | 100..800 | 100..800 | System CT ratio of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.64 | hwGeneralInputUnitClearEnergyYieldData | Clear energy yield data (affecting PUE) | 清除电能数据(会影响PUE计算) | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear energy yield data of General Input Unit: value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.65 | hwGeneralInputUnitMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | Mac address of Power General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.66 | hwGeneralInputUnitElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | Elabel of Power General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.1.1.100 | hwGeneralInputUnitRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase Power Distribution Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.2 | hwGeneralInputUnitRunning1Table | / | / |  |  | / | / | The running and config table of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.1 | hwGeneralInputUnitRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.2 | hwGeneralInputUnitSwitchStatus | Mains input switch status | 主路输入开关状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | The Switch of the General Input Unit: value 1 indicates open. value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.3 | hwGeneralInputUnitSpdSwitchStatus | Mains SPD switch status | 主路防雷开关状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | The Spd Switch of the General Input Unit: value 1 indicates open. value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.4 | hwGeneralInputUnitTrippingStatus | Main road trip status | 主路脱扣状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | The Tripping Status of the General Input Unit: value 1 indicates open. value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.5 | hwGeneralInputUnitUpperloadcurthres | Upper load current threshold | 负载电流高阈值 | 1-Read_Write | 读写 | 80..99 | 80..99 | Rated system frequency of General Input Unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.6 | hwGeneralInputUnitLowerloadcurthres | Lower load current threshold | 负载电流低阈值 | 1-Read_Write | 读写 | 60..79 | 60..79 | Rated system frequency of General Input Unit. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.7 | hwGeneralInputUnitPredictedL1BusbarTemperature | Predicted L1 busbar temperature | L1母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L1 busbar temperature of the device config table for the General Input Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.8 | hwGeneralInputUnitPredictedL2BusbarTemperature | Predicted L2 busbar temperature | L2母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L2 busbar temperature of the device config table for the General Input Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.9 | hwGeneralInputUnitPredictedL3BusbarTemperature | Predicted L3 busbar temperature | L3母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L3 busbar temperature of the device config table for the General Input Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.10 | hwGeneralInputUnitAmbientTemperature | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -4000..32767 | -4000..32767 | Ambient temperature of the device config table for the General Input Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.11 | hwGeneralInputUnitNumberOfDetectionPoints | Number of detection points | 检测点数目 | 1-Read_Write | 读写 | 0..6 | 0..6 | Number of detection points of the device config table for the General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.12 | hwGeneralInputUnitTemperatureWarningThreshold | Temperature warning threshold | 温度预警阈值 | 1-Read_Write | 读写 | 10..30 | 10..30 | Temperature warning threshold of the device config table for the General Input Unit.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.13 | hwGeneralInputUnitTemperaturePredictionEnabledStatus | Temperature prediction enabled status | 温度预测使能状态 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Temperature prediction enabled status of the device config table for the General Input Unit. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.7 | hwGeneralInputUnitPredictedL1BusbarTemperature | Predicted L1 busbar temperature | L1母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L1 busbar temperature of the device config table for the General Input Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.8 | hwGeneralInputUnitPredictedL2BusbarTemperature | Predicted L2 busbar temperature | L2母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L2 busbar temperature of the device config table for the General Input Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.9 | hwGeneralInputUnitPredictedL3BusbarTemperature | Predicted L3 busbar temperature | L3母排预测温度 | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Predicted L3 busbar temperature of the device config table for the General Input Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.10 | hwGeneralInputUnitAmbientTemperature | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -4000..32767 | -4000..32767 | Ambient temperature of the device config table for the General Input Unit.Multiple:100.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.11 | hwGeneralInputUnitNumberOfDetectionPoints | Number of detection points | 检测点数目 | 1-Read_Write | 读写 | 0..6 | 0..6 | Number of detection points of the device config table for the General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.12 | hwGeneralInputUnitTemperatureWarningThreshold | Temperature warning threshold | 温度预警阈值 | 1-Read_Write | 读写 | 10..30 | 10..30 | Temperature warning threshold of the device config table for the General Input Unit.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.13 | hwGeneralInputUnitTemperaturePredictionEnabledStatus | Temperature prediction enabled status | 温度预测使能状态 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Temperature prediction enabled status of the device config table for the General Input Unit. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.21 | hwGeneralInputUnitThreePhaseLoadImbalance | Three-phase load imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..50 | 0..50 | Three-phase load imbalance of the device config table for the General Input Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.38.2.1.100 | hwGeneralInputUnitRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running and config row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.38.3 | hwGeneralInputUnitRunning2Table | / | / |  |  | / | / | The running table of General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.1 | hwGeneralInputUnitRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.2 | hwGeneralInputUnitAmmeterSoftwareVersion | Ammeter software version | 电表软件版本 | 0-Read_Only | 只读 | 0..20 | 0..20 | Ammeter software version of the device config table for the General Input Unit.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.3 | hwGeneralInputUnitSystemDefectVoltSet | System defect volt set | 系统缺相电压 | 1-Read_Write | 读写 | 0..60 | 0..60 | System defect volt set of the device config table for the General Input Unit.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.4 | hwGeneralInputUnitVoltageHarmonicAlarm | Voltage harmonic alarm | 电压谐波告警 | 1-Read_Write | 读写 | 0..30 | 0..30 | Voltage harmonic alarm of the device config table for the General Input Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.5 | hwGeneralInputUnitCurrentHarmonicAlarm | Current harmonic alarm | 电流谐波告警 | 1-Read_Write | 读写 | 0..30 | 0..30 | Current harmonic alarm of the device config table for the General Input Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.6 | hwGeneralInputUnitSystemOvervoltage | System overvoltage | 系统过压 | 1-Read_Write | 读写 | 105..125 | 105..125 | System overvoltage of the device config table for the General Input Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.7 | hwGeneralInputUnitSystemUndervoltage | System undervoltage | 系统欠压 | 1-Read_Write | 读写 | 75..95 | 75..95 | System undervoltage of the device config table for the General Input Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.8 | hwGeneralInputUnitOverload | Overload | 负载过载 | 1-Read_Write | 读写 | 100..120 | 100..120 | Overload of the device config table for the General Input Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.9 | hwGeneralInputUnitOverfrequency | Overfrequency | 系统频率越限 | 1-Read_Write | 读写 | 10..100 | 10..100 | Overfrequency of the device config table for the General Input Unit.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.10 | hwGeneralInputUnitNPeVoltOverload | N-PE volt overload | 零地电压超限 | 1-Read_Write | 读写 | 3..500 | 3..500 | N-PE volt overload of the device config table for the General Input Unit.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.11 | hwGeneralInputUnitSystemCurrentShockProtection | System current shock protection | 系统电流冲击保护 | 1-Read_Write | 读写 | 100..500 | 100..500 | System current shock protection of the device config table for the General Input Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.38.3.1.300 | hwGeneralInputUnitConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of General Input Unit.

## Water Sensor
水浸传感器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.39 | WaterSensor | Water Sensor | 水浸传感器 | / | / | / | / | The Water Sensor Equipment.
1.3.6.1.4.1.2011.6.178.1.1.39.1 | hwWaterSensorRunningAndConfigTable | / | / |  |  | / | / | The running and config table of Water Sensor.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.1 | hwWaterSensorRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the Water Sensor.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.2 | hwWaterSensorCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of Water Sensor: value 1 indicates normal. value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.3 | hwWaterSensorPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No of Water Sensor
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.4 | hwWaterSensorModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of Water Sensor
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.5 | hwWaterSensorDistanceFromLeakagePoint | Distance from the leakage point | 漏水距离 | 0-Read_Only | 只读 | 0..2000 | 0..2000 | Reveal data of Water Sensor. Multiple 10. SigUnitInfo:m
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.6 | hwWaterSensorDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device name of Water Sensor
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.7 | hwWaterSensorSetSensingCableLength | / | / | 1-Read_Write | 读写 | 0..2000 | / | Set sensing cable length of Water Sensor. Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.8 | hwWaterSensorSetSensingCableResistivity | / | / | 1-Read_Write | 读写 | 0..65534 | / | Set sensing cable resistivity of Water Sensor.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.9 | hwWaterSensorSetUpperLeakageResistanceThreshold | / | / | 1-Read_Write | 读写 | 80..120 | / | Set upper leakage resistance threshold of Water Sensor.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.10 | hwWaterSensorSetLowerLeakageResistanceThreshold | / | / | 1-Read_Write | 读写 | 0..10 | / | Set lower leakage resistance threshold of Water Sensor.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.11 | hwWaterSensorSetConfirmWaterLeakage | / | / | 1-Read_Write | 读写 | yes(1), unknown(255) | / | Set confirm water leakage of Water Sensor. value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.12 | hwWaterSensorLeakageStatus | Leakage status | 漏水状态 | 0-Read_Only | 只读 | normal(1), alarm(2), unknown(255) | [正常=1]/[告警=2] | The water sensor leakage status: value 1 indicates normal. value 2 indicates alarm.
1.3.6.1.4.1.2011.6.178.1.1.39.1.1.50 | hwWaterSensorRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase Water Sensor.

## Virtual System
系统
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.40 | VirtualSystem | System | 系统 | / | / | / | / | Virtual System Equipment.
1.3.6.1.4.1.2011.6.178.1.1.40.1 | hwVirtualSystemConfigTable | / | / | / | / | / | / | The Config table of Virtual System.
1.3.6.1.4.1.2011.6.178.1.1.40.1.1.1 | hwVirtualSystemRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Virtual System.
1.3.6.1.4.1.2011.6.178.1.1.40.1.1.2 | hwVirtualSystemAirconditionernumber | Number of air conditioners in the order | 订单中空调数量 | 1-Read_Write | 读写 | 0..4 | 0..4 | Air conditioner number for the Virtual System.
1.3.6.1.4.1.2011.6.178.1.1.40.1.1.3 | hwVirtualSystemTransformernumber | Number of transformers in the order | 订单中变压器数量 | 1-Read_Write | 读写 | 0..1 | 0..1 | Transformer number for the Virtual System.
1.3.6.1.4.1.2011.6.178.1.1.40.1.1.4 | hwSystemModuleModel | Module model | 微模块造型 | 1-Read_Write | 读写 | NA(1), microModule3(2), microModule5(3), microModule6(4), unknown(255) | [NA=1]/[微模块3.0=2]/[微模块5.0=3]/[微模块6.0=4] | System total power consumption flag of the device config table for the NetCol5000-A025. Value 1 indicate NA Value 2 indicate micro-module3 Value 3 indicate micro-module5 Value 4 indicate micro-module6
1.3.6.1.4.1.2011.6.178.1.1.40.1.1.101 | hwVirtualSystemConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Virtual System.

## NetCol5000-A010
NetCol5000-A010
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.2 | NetCol5000A010 | NetCol5000-A010 | NetCol5000-A010 | / | / | / | / | NetCol Equipments.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1 | hwNetCol5000A010Running1Table | / | / |  |  | / | / | The running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.1 | hwNetCol5000A010Running1Index | / | / | 0-Read_Only | 只读 | / | / | The Index of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.2 | hwNetCol5000A010CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the NetCol5000A010. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.3 | hwNetCol5000A010Mac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.4 | hwNetCol5000A010Esn | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.5 | hwNetCol5000A010SoftwareVersionOfControlBoard | Software version of control board | 控制板软件版本号 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of control board of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.6 | hwNetCol5000A010HardwareVersionOfControlBoard | Hardware version of control board | 控制板硬件版本号 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of control board of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.7 | hwNetCol5000A010AntiCondensationSpeedDropLimitProtection | Anti-condensation speed drop limit protection | 防凝露限降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-condensation speed drop limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.8 | hwNetCol5000A010CompressorTotalRuntime | Compressor total runtime | 压缩机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.9 | hwNetCol5000A010IndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 1 total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.10 | hwNetCol5000A010IndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 2 total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.11 | hwNetCol5000A010IndoorFan3TotalRuntime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 3 total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.12 | hwNetCol5000A010IndoorFan4TotalRuntime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 4 total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.13 | hwNetCol5000A010HumidifierPumpTotalRuntime | Humidifier pump total runtime | 加湿水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier pump total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.14 | hwNetCol5000A010ElectricHeaterTotalRuntime | Electric heater total runtime | 电加热累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Electric heater total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.15 | hwNetCol5000A010DrainPumpTotalRuntime | Drain pump total runtime | 排水水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Drain pump total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.16 | hwNetCol5000A010ReturnAirFilterTotalRuntime | Return air filter total runtime | 回风过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Return air filter total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.17 | hwNetCol5000A010EevTotalRuntime | EEV total runtime | EEV累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EEV total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.18 | hwNetCol5000A010OutdoorFan1TotalRuntime | Outdoor fan 1 total runtime | 室外风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor fan 1 total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.19 | hwNetCol5000A010OnorOffStatusOfAirConditioner | On/Off status of air conditioner | 机组开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | On/Off status of air conditioner of the device config table for the NetCol5000A010. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.20 | hwNetCol5000A010CoolingOutput | Cooling output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Cooling output of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.21 | hwNetCol5000A010IndoorFanOutput | Indoor fan output | 室内风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan output of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.22 | hwNetCol5000A010HumidifyingOutput | Humidifying output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidifying output of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.23 | hwNetCol5000A010HeatingOutput | Heating output | 加热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Heating output of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.24 | hwNetCol5000A010DewPointTemperature | Dew point temperature | 露点温度 | 0-Read_Only | 只读 | -1000..1500 | -1000..1500 | Dew point temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.25 | hwNetCol5000A010SystemFaultShutdownFlag | System fault shutdown flag | 系统故障停机标志 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | System fault shutdown flag of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.26 | hwNetCol5000A010TeamworkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), intelligentteamworkcontrol(2), unknown(255) | [单机=1]/[智能群控=2] | Teamwork status of the device config table for the NetCol5000A010. Value 1 indicate single Value 2 indicate intelligent teamwork control
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.27 | hwNetCol5000A010ActualTotalNumberOfAirConditionersInThisGroup | Actual total number of air conditioners in this group | 本群组实际机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Actual total number of air conditioners in this group of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.28 | hwNetCol5000A010NumberOfActualActiveAirConditionersInThisGroup | Number of actual active air conditioners in this group | 本群组实际运行机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Number of actual active air conditioners in this group of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.29 | hwNetCol5000A010NumberOfActualStandbyAirConditionersInThisGroup | Number of actual standby air conditioners in this group | 本群组实际备机机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Number of actual standby air conditioners in this group of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.30 | hwNetCol5000A010TeamworkTemperature | Teamwork temperature | 群组温度 | 0-Read_Only | 只读 | -990..990 | -990..990 | Teamwork temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.31 | hwNetCol5000A010TeamworkHumidity | Teamwork humidity | 群组湿度 | 0-Read_Only | 只读 | 0..990 | 0..990 | Teamwork humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.32 | hwNetCol5000A010TotalCoolingCapacityDemandForTheGroup | Total cooling capacity demand for the group | 群组总冷量需求 | 0-Read_Only | 只读 | -5000..5000 | -5000..5000 | Total cooling capacity demand for the group of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.33 | hwNetCol5000A010TotalHumidityDemandForTheGroup | Total humidity demand for the group | 群组总湿度需求 | 0-Read_Only | 只读 | -5000..5000 | -5000..5000 | Total humidity demand for the group of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.34 | hwNetCol5000A010PowerVoltage | Power voltage | 电源电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Power voltage of the device config table for the NetCol5000A010.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.35 | hwNetCol5000A010PowerFrequency | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | Power frequency of the device config table for the NetCol5000A010.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.36 | hwNetCol5000A010AuxiliaryPowerVoltage | Auxiliary power voltage | 辅源电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Auxiliary power voltage of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.37 | hwNetCol5000A010PsuInputType | PSU input type | 电源模块输入类型 | 0-Read_Only | 只读 | dc(1), ac(2), unknown(255) | [直流=1]/[交流=2] | PSU input type of the device config table for the NetCol5000A010. Value 1 indicate dc Value 2 indicate ac
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.38 | hwNetCol5000A010PsuInputVoltage | PSU input voltage | 电源模块输入电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | PSU input voltage of the device config table for the NetCol5000A010.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.39 | hwNetCol5000A010PsuInputCurrent | PSU input current | 电源模块输入电流 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | PSU input current of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.40 | hwNetCol5000A010PsuOutputVoltage | PSU output voltage | 电源模块输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | PSU output voltage of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.41 | hwNetCol5000A010PsuOutputCurrent | PSU output current | 电源模块输出电流 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | PSU output current of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.42 | hwNetCol5000A010PsuInputPower | PSU input power | 电源模块输入功率 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | PSU input power of the device config table for the NetCol5000A010.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.43 | hwNetCol5000A010TemperatureAndHumidityControlType | Temperature and humidity control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnAir(1), supplyAir(2), coldAisle(3), hotAisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | Temperature and humidity control type of the device config table for the NetCol5000A010. Value 1 indicate return-air Value 2 indicate supply-air Value 3 indicate cold-aisle Value 4 indicate hot-aisle
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.44 | hwNetCol5000A010CurrentTemperature | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Current temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.45 | hwNetCol5000A010CurrentHumidity | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Current humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.46 | hwNetCol5000A010AverageSupplyAirTemperature | Average supply air temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Average supply air temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.47 | hwNetCol5000A010AverageReturnAirTemperature | Average return air temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Average return air temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.48 | hwNetCol5000A010AverageColdAisleTemperature | Average cold aisle temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Average cold aisle temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.49 | hwNetCol5000A010AverageHotAisleTemperature | Average hot aisle temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Average hot aisle temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.50 | hwNetCol5000A010AverageSupplyAirHumidity | Average supply air humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Average supply air humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.51 | hwNetCol5000A010AverageReturnAirHumidity | Average return air humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Average return air humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.52 | hwNetCol5000A010AverageColdAisleHumidity | Average cold aisle humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Average cold aisle humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.53 | hwNetCol5000A010AverageHotAisleHumidity | Average hot aisle humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Average hot aisle humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.54 | hwNetCol5000A010SupplyAir1Temperature | Supply air 1 temperature | 送风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply air 1 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.55 | hwNetCol5000A010ReturnAir1Temperature | Return air 1 temperature | 回风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return air 1 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.56 | hwNetCol5000A010ColdAisle1Temperature | Cold aisle 1 temperature | 冷通道1温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Cold aisle 1 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.57 | hwNetCol5000A010ColdAisle2Temperature | Cold aisle 2 temperature | 冷通道2温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Cold aisle 2 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.58 | hwNetCol5000A010ColdAisle3Temperature | Cold aisle 3 temperature | 冷通道3温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Cold aisle 3 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.59 | hwNetCol5000A010ColdAisle4Temperature | Cold aisle 4 temperature | 冷通道4温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Cold aisle 4 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.60 | hwNetCol5000A010ColdAisle5Temperature | Cold aisle 5 temperature | 冷通道5温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Cold aisle 5 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.61 | hwNetCol5000A010ColdAisle6Temperature | Cold aisle 6 temperature | 冷通道6温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Cold aisle 6 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.62 | hwNetCol5000A010ColdAisle7Temperature | Cold aisle 7 temperature | 冷通道7温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Cold aisle 7 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.63 | hwNetCol5000A010ColdAisle8Temperature | Cold aisle 8 temperature | 冷通道8温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Cold aisle 8 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.64 | hwNetCol5000A010ColdAisle1Humidity | Cold aisle 1 humidity | 冷通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 1 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.65 | hwNetCol5000A010ColdAisle2Humidity | Cold aisle 2 humidity | 冷通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 2 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.66 | hwNetCol5000A010ColdAisle3Humidity | Cold aisle 3 humidity | 冷通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 3 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.67 | hwNetCol5000A010ColdAisle4Humidity | Cold aisle 4 humidity | 冷通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 4 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.68 | hwNetCol5000A010ColdAisle5Humidity | Cold aisle 5 humidity | 冷通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 5 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.69 | hwNetCol5000A010ColdAisle6Humidity | Cold aisle 6 humidity | 冷通道6湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 6 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.70 | hwNetCol5000A010ColdAisle7Humidity | Cold aisle 7 humidity | 冷通道7湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 7 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.71 | hwNetCol5000A010ColdAisle8Humidity | Cold aisle 8 humidity | 冷通道8湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 8 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.72 | hwNetCol5000A010HotAisle1Temperature | Hot aisle 1 temperature | 热通道1温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Hot aisle 1 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.73 | hwNetCol5000A010HotAisle2Temperature | Hot aisle 2 temperature | 热通道2温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Hot aisle 2 temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.74 | hwNetCol5000A010HotAisle1Humidity | Hot aisle 1 humidity | 热通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 1 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.75 | hwNetCol5000A010HotAisle2Humidity | Hot aisle 2 humidity | 热通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 2 humidity of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.76 | hwNetCol5000A010CompressorRunStatus | Compressor run status | 压缩机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Compressor run status of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.77 | hwNetCol5000A010DehumiditySolenoidControlStat | Dehumidity solenoid control stat | 除湿电磁阀控制状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Dehumidity solenoid control stat of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.78 | hwNetCol5000A010DischargePressure | Discharge pressure | 排气压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | Discharge pressure of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.79 | hwNetCol5000A010SuctionPressure | Suction pressure | 吸气压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | Suction pressure of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.80 | hwNetCol5000A010DischargeTemperature | Discharge temperature | 排气温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Discharge temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.81 | hwNetCol5000A010SuctionTemperature | Suction temperature | 吸气温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Suction temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.82 | hwNetCol5000A010PhaseCurrent | Phase current | 相电流 | 0-Read_Only | 只读 | 0..15000 | 0..15000 | Phase current of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.83 | hwNetCol5000A010LowPressureSwitchStatus | Low pressure switch status | 低压开关状态 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | Low pressure switch status of the device config table for the NetCol5000A010. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.84 | hwNetCol5000A010IndoorFanProtectionStatus | Indoor fan protection status | 室内风机保护状态 | 0-Read_Only | 只读 | no(1), speedrise(2), retain(3), speeddroplimit(4), speeddrop(5), speedriselimit(6), forbidspeeddrop(7), forbidspeedrise(8), unknown(255) | [无=1]/[升转速=2]/[保持=3]/[限降转速=4]/[降转速=5]/[限升转速=6]/[禁降转速=7]/[禁升转速=8] | Indoor fan protection status of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate speed rise Value 3 indicate retain Value 4 indicate speed drop limit Value 5 indicate speed drop Value 6 indicate speed rise limit Value 7 indicate forbid speed drop Value 8 indicate forbid speed rise
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.85 | hwNetCol5000A010EnhancedDehumidityLocked | Enhanced dehumidity locked | 加强除湿锁定 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Enhanced dehumidity locked of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.86 | hwNetCol5000A010CompressorControlState | Compressor control state | 压缩机控制状态 | 0-Read_Only | 只读 | 0..7200 | 0..7200 | Compressor control state of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.87 | hwNetCol5000A010CompressorHeatTapeStatus | Compressor heat tape status | 压缩机加热带状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Compressor heat tape status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.88 | hwNetCol5000A010OilReturnStatus | Oil return status | 回油状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Oil return status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.89 | hwNetCol5000A010HighFrequencyHoldStatus | High frequency hold status | 高频停频状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | High frequency hold status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.90 | hwNetCol5000A010CompressorProtectionStatus | Compressor protection status | 压缩机保护状态 | 0-Read_Only | 只读 | no(1), freqfall(2), retain(3), limitfreqrise(4), freqrise(5), limitfreqfall(6), forbidfreqrise(7), forbidfreqfall(8), unknown(255) | [无=1]/[降频=2]/[保持=3]/[限升频=4]/[升频=5]/[限降频=6]/[禁升频=7]/[禁降频=8] | Compressor protection status of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate freq fall Value 3 indicate retain Value 4 indicate limit freq rise Value 5 indicate freq rise Value 6 indicate limit freq fall Value 7 indicate forbid freq rise Value 8 indicate forbid freq fall
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.91 | hwNetCol5000A010HighDischargePressureFreqRiseLimitProtection | High discharge pressure frequency rise limit protection | 排气高压限升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High discharge pressure frequency rise limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.92 | hwNetCol5000A010HighDischargePressureFrequencyDropProtection | High discharge pressure frequency drop protection | 排气高压降频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High discharge pressure frequency drop protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.93 | hwNetCol5000A010HighDischargeTempFreqRiseLimitProtection | High discharge temperature frequency rise limit protection | 排气高温限升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High discharge temperature frequency rise limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.94 | hwNetCol5000A010HighDischargeTemperatureFrequencyDropProtection | High discharge temperature frequency drop protection | 排气高温降频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High discharge temperature frequency drop protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.95 | hwNetCol5000A010AntiFreezeFrequencyRiseLimitProtection | Anti-freeze frequency rise limit protection | 防冻结限升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-freeze frequency rise limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.96 | hwNetCol5000A010AntiFreezeFrequencyDropProtection | Anti-freeze frequency drop protection | 防冻结降频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-freeze frequency drop protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.97 | hwNetCol5000A010SpeedDropProtectionForHighSuctionPressure | Speed drop protection for high suction pressure | 吸气高压降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Speed drop protection for high suction pressure of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.98 | hwNetCol5000A010SpeedRiseLimitProtectionForHighSuctionPressure | Speed rise limit protection for high suction pressure | 吸气高压限升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Speed rise limit protection for high suction pressure of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.99 | hwNetCol5000A010LowDischargeSuperheatDegFreqRiseLimitProtect | Low discharge superheat degree frequency rise limit protection | 低排气过热度限升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Low discharge superheat degree frequency rise limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.100 | hwNetCol5000A010LowDischargeSuperheatDegFreqDropProtection | Low discharge superheat degree frequency drop protection | 低排气过热度降频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Low discharge superheat degree frequency drop protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.101 | hwNetCol5000A010LowDischargePressureFreqDropLimitProtection | Low discharge pressure frequency drop limit protection | 排气低压限降频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Low discharge pressure frequency drop limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.102 | hwNetCol5000A010LowDischargePressureFrequencyRiseProtection | Low discharge pressure frequency rise protection | 排气低压升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Low discharge pressure frequency rise protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.103 | hwNetCol5000A010HighSuctionPressureFrequencyRiseProtection | High suction pressure frequency rise protection | 吸气高压升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High suction pressure frequency rise protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.104 | hwNetCol5000A010HighSuctionPressureFrequencyDropLimitProtection | High suction pressure frequency drop limit protection | 吸气高压限降频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High suction pressure frequency drop limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.105 | hwNetCol5000A010AntiCondensationFrequencyDropProtection | Anti-condensation frequency drop protection | 防凝露降频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-condensation frequency drop protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.106 | hwNetCol5000A010AntiCondensationFrequencyRiseLimitProtection | Anti-condensation frequency rise limit protection | 防凝露限升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-condensation frequency rise limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.107 | hwNetCol5000A010SupplyAirHighTemperatureFrequencyRiseProtection | Supply air high temperature frequency rise protection | 送风高温升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Supply air high temperature frequency rise protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.108 | hwNetCol5000A010ReturnAirHighTemperatureFrequencyRiseProtection | Return air high temperature frequency rise protection | 回风高温升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Return air high temperature frequency rise protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.109 | hwNetCol5000A010ColdAisleHighTemperatureFrequencyRiseProtection | Cold aisle high temperature frequency rise protection | 冷通道高温升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Cold aisle high temperature frequency rise protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.110 | hwNetCol5000A010HotAisleHighTemperatureFrequencyRiseProtection | Hot aisle high temperature frequency rise protection | 热通道高温升频保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Hot aisle high temperature frequency rise protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.111 | hwNetCol5000A010EnableCompressorManualControl | Enable compressor manual control | 压缩机手动控制使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable compressor manual control of the device config table for the NetCol5000A010. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.112 | hwNetCol5000A010EnableManDehumiditySolenoidControl | Enable man dehumidity solenoid control | 除湿电磁阀手动控制使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable man dehumidity solenoid control of the device config table for the NetCol5000A010. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.113 | hwNetCol5000A010IndoorFan1RunningStatus | Indoor fan 1 running status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 1 running status of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.114 | hwNetCol5000A010IndoorFan2RunningStatus | Indoor fan 2 running status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 2 running status of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.115 | hwNetCol5000A010IndoorFan3RunningStatus | Indoor fan 3 running status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 3 running status of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.116 | hwNetCol5000A010IndoorFan4RunningStatus | Indoor fan 4 running status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 4 running status of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.117 | hwNetCol5000A010IndoorFanControlStatus | Indoor fan control status | 室内风机控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan control status of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.118 | hwNetCol5000A010AntiCondensationSpeedRiseProtection | Anti-condensation speed rise protection | 防凝露升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-condensation speed rise protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.119 | hwNetCol5000A010AntiFreezeSpeedRiseProtection | Anti-freeze speed rise protection | 防冻结升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-freeze speed rise protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.120 | hwNetCol5000A010AntiFreezeSpeedDropLimitProtection | Anti-freeze speed drop limit protection | 防冻结限降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-freeze speed drop limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.121 | hwNetCol5000A010PipeTemperature | Pipe temperature | 气管温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Pipe temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.122 | hwNetCol5000A010FrequencyRiseLimitProtectionForDriveOverheat | Frequency rise limit protection for drive overheat | 驱动过热限升频保护 | 0-Read_Only | 只读 | yes(1), no(2), unknown(255) | [有=1]/[无=2] | Frequency rise limit protection for drive overheat of the device config table for the NetCol5000A010. Value 1 indicate yes Value 2 indicate no
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.123 | hwNetCol5000A010FrequencyDropProtectionForDriveOverheat | Frequency drop protection for drive overheat | 驱动过热降频保护 | 0-Read_Only | 只读 | yes(1), no(2), unknown(255) | [有=1]/[无=2] | Frequency drop protection for drive overheat of the device config table for the NetCol5000A010. Value 2 indicate yes Value 1 indicate no
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.200 | hwNetCol5000A010Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.2.2 | hwNetCol5000A010Config1Table | / | / |  |  | / | / | The config table of NetCol5000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.2.1.1 | hwNetCol5000A010Config1Index | / | / | 0-Read_Only | 只读 | / | / | The index of config table of NetCol5000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.2.1.2 | hwNetCol5000A010CommAddress | / | / | 1-Read_Write | 读写 | 1..255 | / | The communication address of NetCol5000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.2.1.3 | hwNetCol5000A010StartuporShutdownControl | Startup/Shutdown control | 控制开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Startup/Shutdown control of the device config table for the NetCol5000A010. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.10.2.2.1.4 | hwNetCol5000A010DiagnosticMode | Diagnostic mode | 诊断模式 | 1-Read_Write | 读写 | exit(1), enter(2), unknown(255) | [退出=1]/[进入=2] | Diagnostic mode of the device config table for the NetCol5000A010. Value 1 indicate exit Value 2 indicate enter
1.3.6.1.4.1.2011.6.178.1.1.10.2.2.1.5 | hwNetCol5000A010ElecHeaterManualCtrl | / | / | 1-Read_Write | 读写 | open(1), closed(2), unknown(255) | / | Elec heater manual ctrl status. Value 1 indicates open. Value 2 indicates closed.
1.3.6.1.4.1.2011.6.178.1.1.10.2.2.1.6 | hwNetCol5000A010DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of NetCol5000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.2.1.100 | hwNetCol5000A010Config1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of config table NetCol5000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3 | hwNetCol5000A010Config2Table | / | / |  |  | / | / | The config table of NetCol5000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.1 | hwNetCol5000A010Config2Index | / | / | 0-Read_Only | 只读 | / | / | The index of config table of NetCol5000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.2 | hwNetCol5000A010OutdoorFan2TotalRuntime | Outdoor fan 2 total runtime | 室外风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor fan 2 total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.3 | hwNetCol5000A010RemainingCompressorPreheatingTime | Remaining compressor preheating time | 压缩机预热剩余时间 | 0-Read_Only | 只读 | 0..720 | 0..720 | Remaining compressor preheating time of the device config table for the NetCol5000A010.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.4 | hwNetCol5000A010Network | Network | 组网方式 | 1-Read_Write | 读写 | can(1), fe(2), unknown(255) | [CAN组网=1]/[FE组网=2] | Network. Value 1 indicates can. Value 2 indicates fe. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.5 | hwNetCol5000A010WetFilmHumidifierRunningStatus | Wet film humidifier running status | 湿膜加湿运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier running status of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.6 | hwNetCol5000A010DrainPumpRunningStatus | Drain pump running status | 排水水泵运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Drain pump running status of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.7 | hwNetCol5000A010PreheatTimeForEnablingPowerFailurePreheating | / | / | 1-Read_Write | 读写 | 0..1200 | / | Preheat time for enabling power failure preheating.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.8 | hwNetCol5000A010PreheatTimeForDisablingPowerFailurePreheating | / | / | 1-Read_Write | 读写 | 0..1200 | / | Preheat time for disabling power failure preheating.
1.3.6.1.4.1.2011.6.178.1.1.10.2.3.1.100 | hwNetCol5000A010Config2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of config table NetCol5000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4 | hwNetCol5000A010Running2Table | / | / |  |  | / | / | The running table of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.1 | hwNetCol5000A010Running2Index | / | / | 0-Read_Only | 只读 | / | / | The Index of running table of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.2 | hwNetCol5000A010HumidifierTotalRuntime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.3 | hwNetCol5000A010OutdoorFanTotalRuntime | Outdoor fan total runtime | 室外风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor fan total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.4 | hwNetCol5000A010CoolStatus | Cool status | 制冷状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Cool status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.5 | hwNetCol5000A010HeatStatus | Heat status | 加热状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Heat status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.6 | hwNetCol5000A010HumidStatus | Humid status | 加湿状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Humid status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.7 | hwNetCol5000A010DehumidStatus | Dehumid status | 除湿状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Dehumid status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.8 | hwNetCol5000A010UnitOnOffStatus | Teamwork status | 群控运行状态 | 0-Read_Only | 只读 | invalid(1), cool(2), heat(3), dehumid(4), humid(5), coolhumid(6), heatdehumid(7), heathumid(8), cooldehumid(9), unknown(255) | [无效=1]/[制冷=2]/[加热=3]/[除湿=4]/[加湿=5]/[制冷且加湿=6]/[加热且除湿=7]/[加热且加湿=8]/[制冷且除湿=9] | Teamwork status of the device config table for the NetCol5000A010. Value 1 indicate invalid Value 2 indicate cool Value 3 indicate heat Value 4 indicate dehumid Value 5 indicate humid Value 6 indicate cool & humid Value 7 indicate heat & dehumid Value 8 indicate heat & humid Value 9 indicate cool & dehumid
1.3.6.1.4.1.2011.6.178.1.1.10.2.1.1.26 | hwNetCol5000A010TeamworkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), intelligentteamworkcontrol(2), unknown(255) | [单机=1]/[智能群控=2] | Teamwork status of the device config table for the NetCol5000A010. Value 1 indicate single Value 2 indicate intelligent teamwork control
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.9 | hwNetCol5000A010NumberOfAirConditionersInThisGroup | Number of air conditioners in this group | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of air conditioners in this group of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.10 | hwNetCol5000A010NumberOfRunningAirConditionersInThisGroup | Number of running air conditioners in this group | 本群组运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of running air conditioners in this group of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.11 | hwNetCol5000A010MasterAirConditionerOnlineFlag | Master air conditioner online flag | 主机在线标志 | 0-Read_Only | 只读 | offline(1), online(2), unknown(255) | [不在线=1]/[在线=2] | Master air conditioner online flag of the device config table for the NetCol5000A010. Value 1 indicate offline Value 2 indicate online
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.12 | hwNetCol5000A010MasterorSlaveFlag | Master/Slave flag | 主从机标志 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | Master/Slave flag of the device config table for the NetCol5000A010. Value 1 indicate slave Value 2 indicate master
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.13 | hwNetCol5000A010ActiveorStandby | Active/Standby | 运行机备机标志 | 0-Read_Only | 只读 | active(1), standby(2), unknown(255) | [运行机=1]/[备机=2] | Active/Standby of the device config table for the NetCol5000A010. Value 1 indicate active Value 2 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.14 | hwNetCol5000A010IndoorFan5RunStatus | Indoor fan 5 run status | 室内风机5运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 5 run status of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.15 | hwNetCol5000A010IndoorFan6RunStatus | Indoor fan 6 run status | 室内风机6运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 6 run status of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.16 | hwNetCol5000A010EnableIndoorFanManualControl | Enable indoor fan manual control | 室内风机手动控制使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable indoor fan manual control of the device config table for the NetCol5000A010. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.17 | hwNetCol5000A010SpdDecrLmtPrtecForRetnAirOvertemperature | Spd decr lmt prtec for retn-air overtemperature | 回风高温限降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Spd decr lmt prtec for retn-air overtemperature of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.18 | hwNetCol5000A010SpdIncrPrtecForRetnAirOvertemperature | Spd incr prtec for retn-air overtemperature | 回风高温升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Spd incr prtec for retn-air overtemperature of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.19 | hwNetCol5000A010SpdDecrLmtPrtecForSplyAirOvertemperature | Spd decr lmt prtec for sply-air overtemperature | 送风高温限降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Spd decr lmt prtec for sply-air overtemperature of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.20 | hwNetCol5000A010SpdIncrPrtecForSplyAirOvertemperature | Spd incr prtec for sply-air overtemperature | 送风高温升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Spd incr prtec for sply-air overtemperature of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.21 | hwNetCol5000A010SpdDecrLmtPrtecForCAisleOvertemperature | Spd decr lmt prtec for C-aisle overtemperature | 冷通道高温限降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Spd decr lmt prtec for C-aisle overtemperature of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.22 | hwNetCol5000A010SpdIncrPrtecForCAisleOvertemperature | Spd incr prtec for C-aisle overtemperature | 冷通道高温升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Spd incr prtec for C-aisle overtemperature of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.23 | hwNetCol5000A010SpdDecrLmtPrtecForHAisleOvertemperature | Spd decr lmt prtec for H-aisle overtemperature | 热通道高温限降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Spd decr lmt prtec for H-aisle overtemperature of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.24 | hwNetCol5000A010SpdIncrPrtecForHAisleOvertemperature | Spd incr prtec for H-aisle overtemperature | 热通道高温升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Spd incr prtec for H-aisle overtemperature of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.25 | hwNetCol5000A010OutdoorFan1RunningStatus | Outdoor fan 1 running status | 室外风机1运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor fan 1 running status of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.26 | hwNetCol5000A010OutdoorFan2RunningStatus | Outdoor fan 2 running status | 室外风机2运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor fan 2 running status of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.27 | hwNetCol5000A010OutdoorFanRunStatus | Outdoor fan run status | 室外风机运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor fan run status of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.28 | hwNetCol5000A010OutdoorFanSpeedControlStatus | Outdoor fan speed control status | 室外风机转速控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor fan speed control status of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.29 | hwNetCol5000A010EnableOutdoorFanManualControl | Enable outdoor fan manual control | 室外风机手动控制使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable outdoor fan manual control of the device config table for the NetCol5000A010. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.30 | hwNetCol5000A010OutdoorTemperature | Outdoor temperature | 室外温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Outdoor temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.31 | hwNetCol5000A010LowLiquidLevelStatus | Low liquid level status | 低液位状态 | 0-Read_Only | 只读 | nottriggered(1), triggered(2), unknown(255) | [非触发=1]/[触发=2] | Low liquid level status of the device config table for the NetCol5000A010. Value 1 indicate not triggered Value 2 indicate triggered
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.32 | hwNetCol5000A010WaterInletSolenoidValveControlStatus | Water inlet solenoid valve control status | 进水电磁阀控制状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Water inlet solenoid valve control status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.33 | hwNetCol5000A010HumidifierPumpControlStatus | Humidifier pump control status | 加湿水泵控制状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Humidifier pump control status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.34 | hwNetCol5000A010EnableWaterInletSolenoidValveManualControl | Enable water inlet solenoid valve manual control | 进水电磁阀手动控制使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable water inlet solenoid valve manual control of the device config table for the NetCol5000A010. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.35 | hwNetCol5000A010EnableWetFilmHumidifierManualControl | Enable wet film humidifier manual control | 湿膜加湿手动控制使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable wet film humidifier manual control of the device config table for the NetCol5000A010. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.36 | hwNetCol5000A010WetFilmHumidifierControlStatus | Wet film humidifier control status | 湿膜加湿控制状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Wet film humidifier control status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.37 | hwNetCol5000A010ElectricHeaterControlStatus | Electric heater control status | 电加热控制状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Electric heater control status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.38 | hwNetCol5000A010EnableElectricHeaterManualControl | Enable electric heater manual control | 电加热手动控制使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable electric heater manual control of the device config table for the NetCol5000A010. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.39 | hwNetCol5000A010ElectricHeaterRunningStatus | Electric heater running status | 电加热运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Electric heater running status of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.40 | hwNetCol5000A010DrainPumpControlStatus | Drain pump control status | 排水水泵控制状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Drain pump control status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.41 | hwNetCol5000A010LowLiquidLevelDetection | Low liquid level detection | 低液位检测 | 0-Read_Only | 只读 | nottriggered(1), triggered(2), unknown(255) | [非触发=1]/[触发=2] | Low liquid level detection of the device config table for the NetCol5000A010. Value 1 indicate not triggered Value 2 indicate triggered
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.42 | hwNetCol5000A010HighLiquidLevelDetection | High liquid level detection | 高液位检测 | 0-Read_Only | 只读 | nottriggered(1), triggered(2), unknown(255) | [非触发=1]/[触发=2] | High liquid level detection of the device config table for the NetCol5000A010. Value 1 indicate not triggered Value 2 indicate triggered
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.43 | hwNetCol5000A010EevControlStatus | EEV control status | EEV控制状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | EEV control status of the device config table for the NetCol5000A010.SigUnitInfo:step.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.44 | hwNetCol5000A010EevRunningStatus | EEV running status | EEV运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | EEV running status of the device config table for the NetCol5000A010.SigUnitInfo:step.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.45 | hwNetCol5000A010EevSuctionSuperheatDegree | EEV suction superheat degree | EEV吸气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | EEV suction superheat degree of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.46 | hwNetCol5000A010EevDischargeSuperheatDegree | EEV discharge superheat degree | EEV排气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | EEV discharge superheat degree of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.47 | hwNetCol5000A010HighDischargeTempEevOpeningDropLimitProtect | High discharge temp EEV opening drop limit protect | EEV排气高温限降开度保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High discharge temp EEV opening drop limit protect of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.48 | hwNetCol5000A010HighSuctionPressEevOpeningDropProtect | High suction press EEV opening drop protect | EEV吸气高压降开度保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High suction press EEV opening drop protect of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.49 | hwNetCol5000A010HighSuctionPressEevOpeningRiseLimitProtect | High suction press EEV opening rise limit protect | EEV吸气高压限升开度保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | High suction press EEV opening rise limit protect of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.50 | hwNetCol5000A010EevAntiSuctionLiquidReturnProtect | EEV anti-suction liquid return protect | EEV防吸气回液保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | EEV anti-suction liquid return protect of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.51 | hwNetCol5000A010LowDischargeShdEevOpeningDropProtect | Low discharge SHD EEV opening drop protect | EEV低排气过热度降开度保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Low discharge SHD EEV opening drop protect of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.52 | hwNetCol5000A010LowDischargeShdEevOpeningRiseLimitProtect | Low discharge SHD EEV opening rise limit protect | EEV低排气过热度限升开度保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Low discharge SHD EEV opening rise limit protect of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.53 | hwNetCol5000A010EevProtectionStatus | EEV protection status | EEV保护状态 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | EEV protection status of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.54 | hwNetCol5000A010CondensationTemperature | Condensation temperature | 冷凝温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Condensation temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.55 | hwNetCol5000A010ManClearAirFilterBlockedAlm | Man clear air filter blocked alm | 过滤网堵告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear air filter blocked alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.56 | hwNetCol5000A010ReturnAirHighTemperatureAlarmThreshold | Return air high temperature alarm threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Return air high temperature alarm threshold of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.57 | hwNetCol5000A010ReturnAirLowTemperatureAlarmThreshold | Return air low temperature alarm threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Return air low temperature alarm threshold of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.58 | hwNetCol5000A010SupplyAirHighTemperatureAlarmThreshold | Supply air high temperature alarm threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Supply air high temperature alarm threshold of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.59 | hwNetCol5000A010SupplyAirLowTemperatureAlarmThreshold | Supply air low temperature alarm threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | Supply air low temperature alarm threshold of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.60 | hwNetCol5000A010ColdAisleHighTemperatureAlarmThreshold | Cold aisle high temperature alarm threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Cold aisle high temperature alarm threshold of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.61 | hwNetCol5000A010HotAisleHighTemperatureAlarmThreshold | Hot aisle high temperature alarm threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Hot aisle high temperature alarm threshold of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.62 | hwNetCol5000A010TemperatureProportionalBand | Temperature proportional band | 温度比例带 | 1-Read_Write | 读写 | 10..60 | 10..60 | Temperature proportional band of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.63 | hwNetCol5000A010TemperatureDeadband | Temperature deadband | 温度死区 | 1-Read_Write | 读写 | 0..20 | 0..20 | Temperature deadband of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.64 | hwNetCol5000A010ColdAisle1TemperatureCalibrationValue | Cold aisle 1 temperature calibration value | 冷通道1温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Cold aisle 1 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.65 | hwNetCol5000A010ColdAisle2TemperatureCalibrationValue | Cold aisle 2 temperature calibration value | 冷通道2温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Cold aisle 2 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.66 | hwNetCol5000A010ColdAisle3TemperatureCalibrationValue | Cold aisle 3 temperature calibration value | 冷通道3温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Cold aisle 3 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.67 | hwNetCol5000A010ColdAisle4TemperatureCalibrationValue | Cold aisle 4 temperature calibration value | 冷通道4温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Cold aisle 4 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.68 | hwNetCol5000A010ColdAisle5TemperatureCalibrationValue | Cold aisle 5 temperature calibration value | 冷通道5温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Cold aisle 5 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.69 | hwNetCol5000A010ColdAisle6TempCalibrationValue | Cold aisle 6 temp calibration value | 冷通道6温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Cold aisle 6 temp calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.70 | hwNetCol5000A010ColdAisle7TempCalibrationValue | Cold aisle 7 temp calibration value | 冷通道7温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Cold aisle 7 temp calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.71 | hwNetCol5000A010ColdAisle8TempCalibrationValue | Cold aisle 8 temp calibration value | 冷通道8温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Cold aisle 8 temp calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.72 | hwNetCol5000A010HotAisle1TemperatureCalibrationValue | Hot aisle 1 temperature calibration value | 热通道1温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Hot aisle 1 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.73 | hwNetCol5000A010HotAisle2TemperatureCalibrationValue | Hot aisle 2 temperature calibration value | 热通道2温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Hot aisle 2 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.74 | hwNetCol5000A010ReturnAir1TemperatureCalibrationValue | Return air 1 temperature calibration value | 回风1温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Return air 1 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.75 | hwNetCol5000A010SupplyAir1TemperatureCalibrationValue | Supply air 1 temperature calibration value | 送风1温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Supply air 1 temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.76 | hwNetCol5000A010EnhDehumidityLockedManualClear | Enh dehumidity locked manual clear | 加强除湿锁定手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Enh dehumidity locked manual clear of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.77 | hwNetCol5000A010LowDischargeSuperheatDegForFreqRiseLimit | Low discharge superheat degree for frequency rise limit | 低排气过热度限升频过热度 | 1-Read_Write | 读写 | -1000..1000 | -1000..1000 | Low discharge superheat degree for frequency rise limit of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.78 | hwNetCol5000A010LowDischargeSuperheatDegreeForFrequencyDrop | Low discharge superheat degree for frequency drop | 低排气过热度降频过热度 | 1-Read_Write | 读写 | -1000..1000 | -1000..1000 | Low discharge superheat degree for frequency drop of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.79 | hwNetCol5000A010LowDshdProtectHyst | Low DSHD protect hyst | 低排气过热度保护回差 | 1-Read_Write | 读写 | -1000..1000 | -1000..1000 | Low DSHD protect hyst of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.80 | hwNetCol5000A010LowDshdProtectDelay | Low DSHD protect delay | 低排气过热度保护延时 | 1-Read_Write | 读写 | 0..1200 | 0..1200 | Low DSHD protect delay of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.81 | hwNetCol5000A010LowDshdStartShieldTime | Low DSHD start shield time | 低排气过热度保护启动屏蔽时间 | 1-Read_Write | 读写 | 0..1200 | 0..1200 | Low DSHD start shield time of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.82 | hwNetCol5000A010AntiCondensationFreqDropTempDiff | Anti-condensation frequency drop temperature difference | 防凝露降频温差 | 1-Read_Write | 读写 | -100..50 | -100..50 | Anti-condensation frequency drop temperature difference of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.83 | hwNetCol5000A010AntiCondensationFreqRiseLimitTempDiff | Anti-condensation frequency rise limit temperature difference | 防凝露限升频温差 | 1-Read_Write | 读写 | -100..50 | -100..50 | Anti-condensation frequency rise limit temperature difference of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.84 | hwNetCol5000A010CompressorDischargeTemperatureCalibrationValue | Compressor discharge temperature calibration value | 压缩机排气温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Compressor discharge temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.85 | hwNetCol5000A010CompressorSuctionTemperatureCalibrationValue | Compressor suction temperature calibration value | 压缩机吸气温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Compressor suction temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.86 | hwNetCol5000A010ManClearCompressorDischargeHtLockAlm | Man clear compressor discharge HT lock alm | 压缩机排气高温锁定告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear compressor discharge HT lock alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.87 | hwNetCol5000A010ManClearCompressorHpSwitchLockAlm | Man clear compressor HP switch lock alm | 压缩机高压开关锁定告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear compressor HP switch lock alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.88 | hwNetCol5000A010ManClearCompressorDischargeHpLockAlm | Man clear compressor discharge HP lock alm | 压缩机排气高压锁定告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear compressor discharge HP lock alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.89 | hwNetCol5000A010ManuallyClearCompAntifreezeProtectionAlarm | Manually clear compressor antifreeze protection alarm | 压缩机防冻结保护告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Manually clear compressor antifreeze protection alarm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.90 | hwNetCol5000A010ManClearCompressorSuctionLpLockAlm | Man clear compressor suction LP lock alm | 压缩机吸气低压锁定告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear compressor suction LP lock alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.91 | hwNetCol5000A010ManClearCompressorDriveAlm | Man clear compressor drive alm | 压缩机驱动告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear compressor drive alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.92 | hwNetCol5000A010ManClearCompressorDriveLockAlm | Man clear compressor drive lock alm | 压缩机驱动锁定告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear compressor drive lock alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.93 | hwNetCol5000A010ManClearCompressorDriveShortPeriodAlm | Man clear compressor drive short period alm | 压缩机驱动短周期告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear compressor drive short period alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.94 | hwNetCol5000A010ManClearCompressorLpSwitchLockedAlm | Man clear compressor LP switch locked alm | 压缩机低压开关锁定告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear compressor LP switch locked alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.95 | hwNetCol5000A010CompressorGasPipeTemperatureCalibrationValue | Compressor gas pipe temperature calibration value | 压缩机气管温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Compressor gas pipe temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.96 | hwNetCol5000A010IndoorFanMinReturnorSupplyAirTempDiff | Indoor fan min return/supply air temperature difference | 室内风机回送风最小温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | Indoor fan min return/supply air temperature difference of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.97 | hwNetCol5000A010IndoorFanMaxReturnorSupplyAirTempDiff | Indoor fan max return/supply air temperature difference | 室内风机回送风最大温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | Indoor fan max return/supply air temperature difference of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.98 | hwNetCol5000A010FanStopSupplyAirTemperature | Fan stop supply air temperature | 停风机送风温度 | 1-Read_Write | 读写 | 0..450 | 0..450 | Fan stop supply air temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.99 | hwNetCol5000A010TempDiffForSpeedRiseForPreventCondensation | Temperature difference for speed rise for preventing condensation in dehumidifying | 除湿防凝露升转速温差 | 1-Read_Write | 读写 | -100..50 | -100..50 | Temperature difference for speed rise for preventing condensation in dehumidifying of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.100 | hwNetCol5000A010TempDiffForSpeedDropForPreventCondensation | Temperature difference for speed drop limit for preventing condensation in dehumidifying | 除湿防凝露限降转速温差 | 1-Read_Write | 读写 | -100..50 | -100..50 | Temperature difference for speed drop limit for preventing condensation in dehumidifying of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.101 | hwNetCol5000A010TempDiffForSpeedRiseForPreventCondensationCool | Temperature difference for speed rise for preventing condensation in cooling | 制冷防凝露升转速温差 | 1-Read_Write | 读写 | -100..50 | -100..50 | Temperature difference for speed rise for preventing condensation in cooling of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.102 | hwNetCol5000A010TempDiffForSpeedDropForPreventCondensationCool | Temperature difference for speed drop limit for preventing condensation in cooling | 制冷防凝露限降转速温差 | 1-Read_Write | 读写 | -100..50 | -100..50 | Temperature difference for speed drop limit for preventing condensation in cooling of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.103 | hwNetCol5000A010TempDiffForHighTempSpeedDecreaseLimit | Temperature difference for high temperature speed decrease limit | 高温限降转速温差 | 1-Read_Write | 读写 | -100..100 | -100..100 | Temperature difference for high temperature speed decrease limit of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.104 | hwNetCol5000A010HighTemperatureProtectionDisabledHysteresis | High temperature protection disabled hysteresis | 高温保护解除回差 | 1-Read_Write | 读写 | -100..100 | -100..100 | High temperature protection disabled hysteresis of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.105 | hwNetCol5000A010TemperatureForHighTemperatureSpeedDecreaseLimit | Temperature for high temperature speed decrease limit | 高温限降转速温度需求 | 1-Read_Write | 读写 | 0..500 | 0..500 | Temperature for high temperature speed decrease limit of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.106 | hwNetCol5000A010TempForDisablingHighTempSpeedDecreaseLimit | Temperature for disabling high temperature speed decrease limit | 高温限降转速解除温度需求 | 1-Read_Write | 读写 | 0..500 | 0..500 | Temperature for disabling high temperature speed decrease limit of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.107 | hwNetCol5000A010HighTemperatureProtectionGenerationTime | High temperature protection generation time | 高温保护产生时间 | 1-Read_Write | 读写 | 0..1200 | 0..1200 | High temperature protection generation time of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.108 | hwNetCol5000A010HighTemperatureProtectionReleaseTime | High temperature protection release time | 高温保护解除时间 | 1-Read_Write | 读写 | 5..1200 | 5..1200 | High temperature protection release time of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.109 | hwNetCol5000A010TempDiffForHighTemperatureSpeedIncrease | Temperature difference for high temperature speed increase | 高温升转速温差 | 1-Read_Write | 读写 | -100..100 | -100..100 | Temperature difference for high temperature speed increase of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.110 | hwNetCol5000A010TemperatureForHighTemperatureSpeedIncrease | Temperature for high temperature speed increase | 高温升转速温度需求 | 1-Read_Write | 读写 | 0..500 | 0..500 | Temperature for high temperature speed increase of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.111 | hwNetCol5000A010TempForDisablingHighTemSpeedIncrease | Temperature for disabling high temperature speed increase | 高温升转速解除温度需求 | 1-Read_Write | 读写 | 0..500 | 0..500 | Temperature for disabling high temperature speed increase of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.112 | hwNetCol5000A010AdjustPeriodForHighTemperatureSpeedIncrease | Adjust period for high temperature speed increase | 高温升转速调节周期 | 1-Read_Write | 读写 | 0..1200 | 0..1200 | Adjust period for high temperature speed increase of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.113 | hwNetCol5000A010MaxSpeedOfIndoorFanInSilentMode | Max speed of indoor fan in silent mode | 室内风机静音模式最大转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | Max speed of indoor fan in silent mode of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.114 | hwNetCol5000A010MediumSpeedOfIndoorFanInSilentMode | Medium speed of indoor fan in silent mode | 室内风机静音模式中间转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | Medium speed of indoor fan in silent mode of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.115 | hwNetCol5000A010MinSpeedOfIndoorFanInSilentMode | Min speed of indoor fan in silent mode | 室内风机静音模式最小转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | Min speed of indoor fan in silent mode of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.116 | hwNetCol5000A010MaxReturnorSupplyAirTempDiffInSilentMode | Max return/supply air temperature difference in silent mode | 静音模式回送风最大温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | Max return/supply air temperature difference in silent mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.117 | hwNetCol5000A010MediumReturnorSupplyAirTempDiffInSilentMode | Medium return/supply air temperature difference in silent mode | 静音模式回送风中间温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | Medium return/supply air temperature difference in silent mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.118 | hwNetCol5000A010MinReturnorSupplyAirTempDiffInSilentMode | Min return/supply air temperature difference in silent mode | 静音模式回送风最小温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | Min return/supply air temperature difference in silent mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.119 | hwNetCol5000A010CondenserDelayedCloseTime | Condenser delayed close time | 冷凝器延时关闭时间 | 1-Read_Write | 读写 | 30..300 | 30..300 | Condenser delayed close time of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.120 | hwNetCol5000A010OutdoorTemperatureCalibrationValue | Outdoor temperature calibration value | 室外温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Outdoor temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.121 | hwNetCol5000A010ManuallyClearOutdoorFanDriveLockedAlarm | Manually clear outdoor fan drive locked alarm | 室外风机驱动锁定告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Manually clear outdoor fan drive locked alarm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.122 | hwNetCol5000A010ManuallyClearHumidifierFunctionAbnormalAlarm | Manually clear humidifier function abnormal alarm | 加湿功能异常告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Manually clear humidifier function abnormal alarm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.123 | hwNetCol5000A010ManClearInletSolenoidFaultAlarm | Man clear inlet solenoid fault alm | 进水电磁阀故障告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear inlet solenoid fault alm of the device config table for the NetCol5000A010. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.124 | hwNetCol5000A010ManuallyClearHumidifierWaterSupplyAbnormalAlarm | Manually clear humidifier water supply abnormal alarm | 加湿供水异常告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Manually clear humidifier water supply abnormal alarm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.125 | hwNetCol5000A010ManuallyClearDrainAbnormalAlarm | Manually clear drain abnormal alarm | 排水异常告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Manually clear drain abnormal alarm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.126 | hwNetCol5000A010ManuallyClearDrainPumpFaultAlarm | Manually clear drain pump fault alarm | 排水水泵故障手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Manually clear drain pump fault alarm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.127 | hwNetCol5000A010EevSuctionSuperheatDegreeSetpoint | EEV suction superheat degree setpoint | EEV吸气过热度设定点 | 1-Read_Write | 读写 | 20..200 | 20..200 | EEV suction superheat degree setpoint of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.128 | hwNetCol5000A010EevSuctionSuperheatDegreeDeadband | EEV suction superheat degree deadband | EEV吸气过热度死区 | 1-Read_Write | 读写 | 0..50 | 0..50 | EEV suction superheat degree deadband of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.129 | hwNetCol5000A010EevSuctionSuperheatDegreeProportionalBand | EEV suction superheat degree proportional band | EEV吸气过热度比例带 | 1-Read_Write | 读写 | 20..300 | 20..300 | EEV suction superheat degree proportional band of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.130 | hwNetCol5000A010EevLowSuctionSuperheatDegreeAlarmThreshold | EEV low suction superheat degree alarm threshold | EEV低吸气过热度告警阈值 | 1-Read_Write | 读写 | 10..60 | 10..60 | EEV low suction superheat degree alarm threshold of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.131 | hwNetCol5000A010EevLowDischargeSuperheatDegreeAlarmThreshold | EEV low discharge superheat degree alarm threshold | EEV低排气过热度告警阈值 | 1-Read_Write | 读写 | 10..300 | 10..300 | EEV low discharge superheat degree alarm threshold of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.132 | hwNetCol5000A010TempDiffForLowDischargeShdEevOpeningRiseLimit | Temp diff for low discharge SHD EEV opening rise limit | EEV低排气过热度限升开度温差 | 1-Read_Write | 读写 | 0..500 | 0..500 | Temp diff for low discharge SHD EEV opening rise limit of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.133 | hwNetCol5000A010TempDiffForLowDischargeShdEevOpeningDrop | Temp diff for low discharge SHD EEV opening drop | EEV低排气过热度降开度温差 | 1-Read_Write | 读写 | 0..500 | 0..500 | Temp diff for low discharge SHD EEV opening drop of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.134 | hwNetCol5000A010LowDshdEevProtectHyst | Low DSHD EEV protect hyst | EEV低排气过热度保护回差 | 1-Read_Write | 读写 | -50..200 | -50..200 | Low DSHD EEV protect hyst of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.135 | hwNetCol5000A010ManClearEevLowOverheatingLockedAlm | Man clear EEV low overheating locked alm | EEV低过热度锁定告警手动清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear EEV low overheating locked alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.136 | hwNetCol5000A010ClearCompressorTotalRuntime | Clear compressor total runtime | 清零压缩机累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear compressor total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.137 | hwNetCol5000A010ClearIndoorFan1TotalRuntime | Clear indoor fan 1 total runtime | 清零室内风机1累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear indoor fan 1 total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.138 | hwNetCol5000A010ClearIndoorFan2TotalRuntime | Clear indoor fan 2 total runtime | 清零室内风机2累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear indoor fan 2 total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.139 | hwNetCol5000A010ClearIndoorFan3TotalRuntime | Clear indoor fan 3 total runtime | 清零室内风机3累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear indoor fan 3 total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.140 | hwNetCol5000A010ClearIndoorFan4TotalRuntime | Clear indoor fan 4 total runtime | 清零室内风机4累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear indoor fan 4 total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.141 | hwNetCol5000A010ClearIndoorFan5TotalRuntime | Clear indoor fan 5 total runtime | 清零室内风机5累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear indoor fan 5 total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.142 | hwNetCol5000A010ClearIndoorFan6TotalRuntime | Clear indoor fan 6 total runtime | 清零室内风机6累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear indoor fan 6 total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.143 | hwNetCol5000A010ClearHumidifierTotalRuntime | Clear humidifier total runtime | 清零加湿器累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear humidifier total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.144 | hwNetCol5000A010ClearHumidifierPumpTotalRuntime | Clear humidifier pump total runtime | 清零加湿水泵累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear humidifier pump total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.145 | hwNetCol5000A010ClearElecHeaterTotalRuntime | Clear elec heater total runtime | 清零电加热累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear elec heater total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.146 | hwNetCol5000A010ClearDrainPumpTotalRuntime | Clear drain pump total runtime | 清零排水水泵累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear drain pump total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.147 | hwNetCol5000A010ClearReturnAirFilterTotalRuntime | Clear return air filter total runtime | 清零回风过滤网累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear return air filter total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.148 | hwNetCol5000A010ClearEevTotalRuntime | Clear EEV total runtime | 清零EEV累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear EEV total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.149 | hwNetCol5000A010ClearOutdoorFan1TotalRuntime | Clear outdoor fan 1 total runtime | 清零室外风机1累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear outdoor fan 1 total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.150 | hwNetCol5000A010ClearOutdoorFan2TotalRuntime | Clear outdoor fan 2 total runtime | 清零室外风机2累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear outdoor fan 2 total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.151 | hwNetCol5000A010CondensationTemperatureCalibrationValue | Condensation temperature calibration value | 冷凝温度校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Condensation temperature calibration value of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.152 | hwNetCol5000A010SupplyAirTempToForciblyStartCooling | Supply air temp to forcibly start cooling | 制冷强制开启送风温度 | 1-Read_Write | 读写 | 150..450 | 150..450 | Supply air temp to forcibly start cooling of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.153 | hwNetCol5000A010ClearOutdoorFanTotalRuntime | Clear outdoor fan total runtime | 清零室外风机累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear outdoor fan total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.154 | hwNetCol5000A010ManClearInletSolenoidFaultAlm | Clear indoor fan 5 total runtime | 清零室内风机5累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Man clear inlet solenoid fault alm of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.4.1.200 | hwNetCol5000A010Running2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running 2 row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5 | hwNetCol5000A010RunningAndConfig1Table | / | / |  |  | / | / | The running table of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.1 | hwNetCol5000A010RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | The Index of running table of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.2 | hwNetCol5000A010EEVTempDropnoLiquidRet | EEV temperature drop no liquid ret | EEV防吸气回液温降 | 1-Read_Write | 读写 | 30..150 | 30..150 | The EEV Temp Dropno Liquid Ret of NetCol5000A010.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.3 | hwNetCol5000A010EEVSucHighPressOverheat | EEV high suction overheat thres | EEV吸气高压过热度 | 1-Read_Write | 读写 | 200..350 | 200..350 | The EEV Suc High Press Overheat of NetCol5000A010.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.4 | hwNetCol5000A010Elabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | The E-label of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.5 | hwNetCol5000A010Numberofindoorfans | Number of indoor fans | 室内风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of indoor fans of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.6 | hwNetCol5000A010Numberofcompressors | Number of compressors | 压缩机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of compressors of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.7 | hwNetCol5000A010Numberofheaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of heaters of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.8 | hwNetCol5000A010Numberofhumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of humidifiers of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.9 | hwNetCol5000A010Numberofcondpumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of cond pumps of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.10 | hwNetCol5000A010NumberofPSU | Number of PSU | PUS数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of PSU of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.11 | hwNetCol5000A010NumberofOutdoorfans | Number of outdoor fans | 室外风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of outdoor fans of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.12 | hwNetCol5000A010IndoorFan5TotalRuntime | Indoor fan 5 total runtime | 室内风机5累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 5 total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.13 | hwNetCol5000A010IndoorFan6TotalRuntime | Indoor fan 6 total runtime | 室内风机6累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 6 total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.14 | hwNetCol5000A010SampTeamWorkStatusFlg | Teamwork control status display flag | 群控状态显示标志 | 0-Read_Only | 只读 | 0..1 | 0..1 | The Samp Team Work Status Flg of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.15 | hwNetCol5000A010TeamworkUnitAddress | Air conditioner address | 机组地址 | 1-Read_Write | 读写 | 1..32 | 1..32 | The Teamwork Unit Address of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.16 | hwNetCol5000A010TeamworkFunction | Teamwork function | 群控功能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The Teamwork Function of NetCol5000A010. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.17 | hwNetCol5000A010Rotation | Rotation function | 轮巡功能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The Rotation of NetCol5000A010. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.18 | hwNetCol5000A010RequirementControl | Requirement control | 需求控制 | 1-Read_Write | 读写 | competitiverunningavoidance(1), disable(2), unknown(255) | [禁止=1]/[防竞争运行=2]/[室内风机统一控制=3] | The Requirement Control of NetCol5000A010. Value 1 indicates Competitiverunningavoidance. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.19 | hwNetCol5000A010ColdAisleSensor1 | Cold aisle sensor 1 | 冷通道传感器1 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Cold Aisle Sensor1 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.20 | hwNetCol5000A010ColdAisleSensor2 | Cold aisle sensor 2 | 冷通道传感器2 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Cold Aisle Sensor2 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.21 | hwNetCol5000A010ColdAisleSensor3 | Cold aisle sensor 3 | 冷通道传感器3 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Cold Aisle Sensor3 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.22 | hwNetCol5000A010ColdAisleSensor4 | Cold aisle sensor 4 | 冷通道传感器4 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Cold Aisle Sensor4 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.23 | hwNetCol5000A010ColdAisleSensor5 | Cold aisle sensor 5 | 冷通道传感器5 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Cold Aisle Sensor5 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.24 | hwNetCol5000A010ColdAisleSensor6 | Cold aisle sensor 6 | 冷通道传感器6 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Cold Aisle Sensor6 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.25 | hwNetCol5000A010ColdAisleSensor7 | Cold aisle sensor 7 | 冷通道传感器7 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Cold Aisle Sensor7 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.26 | hwNetCol5000A010ColdAisleSensor8 | Cold aisle sensor 8 | 冷通道传感器8 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Cold Aisle Sensor8 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.27 | hwNetCol5000A010HotAisleSensor1 | Hot aisle sensor 1 | 热通道传感器1 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Hot Aisle Sensor1 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.28 | hwNetCol5000A010HotAisleSensor2 | Hot aisle sensor 2 | 热通道传感器2 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | The Hot Aisle Sensor2 of NetCol5000A010. Value 1 indicates Enable. Value 2 indicates Disable.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.29 | hwNetCol5000A010EEVDischargeOverheatSetting | EEV discharge overheat setting | EEV排气过热度设定点 | 1-Read_Write | 读写 | 100..350 | 100..350 | The EEV Discharge Overheat Setting of NetCol5000A010.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.30 | hwNetCol5000A010IndoorFanTotalRuntime | Indoor fan total runtime | 室内风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.5.1.200 | hwNetCol5000A010RunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running 2 row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6 | hwNetCol5000A010RunningAndConfig2Table | / | / |  |  | / | / | The running table of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.1 | hwNetCol5000A010RunningAndConfig2Index | / | / | 0-Read_Only | 只读 | / | / | The Index of running table of NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.2 | hwNetCol5000A010IPaddress | / | / | 0-Read_Only | 只读 | 0..2147483647 | / | The IP address of NetCol5000A010.Multiple 10.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.3 | hwNetCol5000A010Dehumid | Dehumid | 除湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Dehumid of the device config table for the NetCol5000A010. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.4 | hwNetCol5000A010FluorinePumpTotalRuntime | Fluorine pump total runtime | 氟泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fluorine pump total runtime of the device config table for the NetCol5000A010.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.5 | hwNetCol5000A010TotalOpenTimesOfTheWaterInletSolenoidValve | Total open times of the water inlet solenoid valve | 进水电磁阀累计开启次数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total open times of the water inlet solenoid valve of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.6 | hwNetCol5000A010OutdoorFanProtectionStatus | Outdoor fan protection status | 室外风机保护状态 | 0-Read_Only | 只读 | no(1), speedrise(2), retain(3), speeddroplimit(4), speeddrop(5), speedriselimit(6), forbidspeeddrop(7), forbidspeedrise(8), unknown(255) | [无=1]/[升转速=2]/[保持=3]/[限降转速=4]/[降转速=5]/[限升转速=6]/[禁降转速=7]/[禁升转速=8] | Outdoor fan protection status of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate speed rise Value 3 indicate retain Value 4 indicate speed drop limit Value 5 indicate speed drop Value 6 indicate speed rise limit Value 7 indicate forbid speed drop Value 8 indicate forbid speed rise
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.7 | hwNetCol5000A010AntiFreezeSpeedRiseLimitProtection | Anti-freeze speed rise limit protection | 防冻结限升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-freeze speed rise limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.8 | hwNetCol5000A010AntiFreezeSpeedDropProtection | Anti-freeze speed drop protection | 防冻结降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-freeze speed drop protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.9 | hwNetCol5000A010AntiCondensationSpeedRiseLimitProtection | Anti-condensation speed rise limit protection | 防凝露限升转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-condensation speed rise limit protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.10 | hwNetCol5000A010AntiCondensationSpeedDropProtection | Anti-condensation speed drop protection | 防凝露降转速保护 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Anti-condensation speed drop protection of the device config table for the NetCol5000A010. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.11 | hwNetCol5000A010FluorinePumpOutletSolenoidValveStatus | Fluorine pump outlet solenoid valve status | 氟泵出口电磁阀状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Fluorine pump outlet solenoid valve status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.12 | hwNetCol5000A010CompressorInletSolenoidValveStatus | Compressor inlet solenoid valve status | 压缩机入口电磁阀状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Compressor inlet solenoid valve status of the device config table for the NetCol5000A010. Value 1 indicate closed Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.13 | hwNetCol5000A010EnableFluorinePumpManualControl | Enable fluorine pump manual control | 氟泵手动控制使能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable fluorine pump manual control of the device config table for the NetCol5000A010. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.14 | hwNetCol5000A010FluorinePumpInletPressure | Fluorine pump inlet pressure | 氟泵入口压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | Fluorine pump inlet pressure of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.15 | hwNetCol5000A010FluorinePumpOutletPressure | Fluorine pump outlet pressure | 氟泵出口压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | Fluorine pump outlet pressure of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.16 | hwNetCol5000A010FluorinePumpRunningStatus | Fluorine pump running status | 氟泵运行状态 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Fluorine pump running status of the device config table for the NetCol5000A010.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.17 | hwNetCol5000A010FluorinePumpSpeedControl | Fluorine pump speed control | 氟泵控制状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Fluorine pump speed control of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.18 | hwNetCol5000A010TeamworkOutdoorTemperature | Teamwork outdoor temperature | 群组室外温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Teamwork outdoor temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.19 | hwNetCol5000A010Cleartotalopentimesofthewaterinletsolenoidvalve | Clear total open times of the water inlet solenoid valve | 清零进水电磁阀累计开启次数 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear total open times of the water inlet solenoid valve of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.20 | hwNetCol5000A010PressureDiffForStartSuctionAndDischarge | Pressure difference for starting suction and discharge | 吸排气开启压差 | 1-Read_Write | 读写 | 0..100 | 0..100 | Pressure difference for starting suction and discharge of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.21 | hwNetCol5000A010CondenserAdvanceStartTime | Condenser advance start time | 冷凝器提前开启时间 | 1-Read_Write | 读写 | 1..180 | 1..180 | Condenser advance start time of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.22 | hwNetCol5000A010OutdoorFanNormalAdjustmentPeriod | Outdoor fan Normal adjustment period | 室外风机正常调节周期 | 1-Read_Write | 读写 | 1..600 | 1..600 | Outdoor fan Normal adjustment period of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.23 | hwNetCol5000A010OutdoorFanMaxAdjustmentStep | Outdoor fan Max adjustment step | 室外风机最大调节步长 | 1-Read_Write | 读写 | 1..10 | 1..10 | Outdoor fan Max adjustment step of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.24 | hwNetCol5000A010OutdoorFanProtectionAdjustmentStep | Outdoor fan Protection adjustment step | 室外风机保护调节步长 | 1-Read_Write | 读写 | 1..10 | 1..10 | Outdoor fan Protection adjustment step of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.25 | hwNetCol5000A010WetFilmHumidifierPumpControlCycle | Wet film humidifier pump control cycle | 湿膜加湿控制周期 | 1-Read_Write | 读写 | 120..600 | 120..600 | Wet film humidifier pump control cycle of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.26 | hwNetCol5000A010MaxHumidCapacity | Max humid capacity | 最大加湿量 | 1-Read_Write | 读写 | 1..100 | 1..100 | Max humid capacity of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.27 | hwNetCol5000A010MinHumidCapacity | Min humid capacity | 最小加湿量 | 1-Read_Write | 读写 | 1..100 | 1..100 | Min humid capacity of the device config table for the NetCol5000A010.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.28 | hwNetCol5000A010FluorinePumpMinRuntime | Fluorine pump min runtime | 氟泵最短运行时间 | 1-Read_Write | 读写 | 30..600 | 30..600 | Fluorine pump min runtime of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.29 | hwNetCol5000A010UpperLimitForFluorinePumpRunningTemperature | Upper limit for fluorine pump running temperature | 氟泵工作温度上限 | 1-Read_Write | 读写 | -150..250 | -150..250 | Upper limit for fluorine pump running temperature of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.30 | hwNetCol5000A010SetpointOfEevSuctSuperheatDegInFluPump | Setpoint of EEV suction superheat degree in fluorine pump mode | 氟泵模式EEV吸气过热度设定点 | 1-Read_Write | 读写 | 0..100 | 0..100 | Setpoint of EEV suction superheat degree in fluorine pump mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.31 | hwNetCol5000A010OutdoorFanProportionCoefficientInFluPump | Outdoor fan proportional coefficient in fluorine pump mode | 氟泵模式外风机比例系数 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | Outdoor fan proportional coefficient in fluorine pump mode of the device config table for the NetCol5000A010.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.32 | hwNetCol5000A010OutdoorFanIntegralTimeConstantInFluPump | Outdoor fan integral time constant in fluorine pump mode | 氟泵模式外风机积分时间常数 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | Outdoor fan integral time constant in fluorine pump mode of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.33 | hwNetCol5000A010OutdoorFanDiffTimeConstantInFluPumpMode | Outdoor fan differential time constant in fluorine pump mode | 氟泵模式外风机微分时间常数 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | Outdoor fan differential time constant in fluorine pump mode of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.34 | hwNetCol5000A010OutdoorFanNormalAdjustPeriodInFluorinePumpMode | Outdoor fan normal adjust period in fluorine pump mode | 氟泵模式外风机正常调节周期 | 1-Read_Write | 读写 | 0..1800 | 0..1800 | Outdoor fan normal adjust period in fluorine pump mode of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.35 | hwNetCol5000A010OutdoorFanSlowSpeedAdjustPeriodInFluPump | Outdoor fan slow speed adjust period in fluorine pump mode | 氟泵模式外风机慢速调节周期 | 1-Read_Write | 读写 | 0..180 | 0..180 | Outdoor fan slow speed adjust period in fluorine pump mode of the device config table for the NetCol5000A010.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.36 | hwNetCol5000A010UpperLimitForOutdoorFanMinSpeedInFluPump | Upper limit for outdoor fan min speed in fluorine pump mode | 氟泵模式外风机最小转速上限 | 1-Read_Write | 读写 | 300..1000 | 300..1000 | Upper limit for outdoor fan min speed in fluorine pump mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.37 | hwNetCol5000A010TempAtLowLimitForOutdoorFanMinSpeedInFluPump | Temp at lower limit for outdoor fan min speed in fluorine pump mode | 氟泵模式外风机最小转速下限对应温度 | 1-Read_Write | 读写 | -400..-50 | -400..-50 | Temp at lower limit for outdoor fan min speed in fluorine pump mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.38 | hwNetCol5000A010CommonStartTemperatureInFluorinePumpMode | Common start temperature in fluorine pump mode | 氟泵模式通用开启温度 | 1-Read_Write | 读写 | -200..50 | -200..50 | Common start temperature in fluorine pump mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.39 | hwNetCol5000A010ProportCoeffOfEevSuctSuperheatDegInFluPump | Proportional coefficient of EEV suction superheat degree in fluorine pump mode | 氟泵模式EEV吸气过热度比例系数 | 1-Read_Write | 读写 | 1..10000 | 1..10000 | Proportional coefficient of EEV suction superheat degree in fluorine pump mode of the device config table for the NetCol5000A010.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.40 | hwNetCol5000A010IntegTimeConstOfEevSuctSuperheatDegInFluPump | Integral time constant of EEV suction superheat degree in fluorine pump mode | 氟泵模式EEV吸气过热度积分时间常数 | 1-Read_Write | 读写 | 0..600 | 0..600 | Integral time constant of EEV suction superheat degree in fluorine pump mode of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.41 | hwNetCol5000A010DiffTimeConstOfEevSuctSuperheatDegInFluPump | Differential time constant of EEV suction superheat degree in fluorine pump mode | 氟泵模式EEV吸气过热度微分时间常数 | 1-Read_Write | 读写 | 0..600 | 0..600 | Differential time constant of EEV suction superheat degree in fluorine pump mode of the device config table for the NetCol5000A010.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.42 | hwNetCol5000A010DeadbandOfEevSuctionSuperheatDegInFluPump | Deadband of EEV suction superheat degree in fluorine pump mode | 氟泵模式EEV吸气过热度死区 | 1-Read_Write | 读写 | 0..50 | 0..50 | Deadband of EEV suction superheat degree in fluorine pump mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.43 | hwNetCol5000A010ProportionBandOfEevSuctSuperheatDegInFluPump | Proportional band of EEV suction superheat degree in fluorine pump mode | 氟泵模式EEV吸气过热度比例带 | 1-Read_Write | 读写 | 20..300 | 20..300 | Proportional band of EEV suction superheat degree in fluorine pump mode of the device config table for the NetCol5000A010.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.44 | hwNetCol5000A010FluorinePumpInletPressureCalibrationValue | Fluorine pump inlet pressure calibration value | 氟泵入口压力校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Fluorine pump inlet pressure calibration value of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.45 | hwNetCol5000A010FluorinePumpOutletPressureCalibrationValue | Fluorine pump outlet pressure calibration value | 氟泵出口压力校准值 | 1-Read_Write | 读写 | -100..100 | -100..100 | Fluorine pump outlet pressure calibration value of the device config table for the NetCol5000A010.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.46 | hwNetCol5000A010ManuallyClearEevLowSuperheatDegreeAlarm | Manually clear EEV low superheat degree alarm | EEV低过热度告警手动清除 | 1-Read_Write | 读写 | clear(1), unknown(255) | [清除=1] | Manually clear EEV low superheat degree alarm of the device config table for the NetCol5000A010. Value 1 indicate clear
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.47 | hwNetCol5000A010ManuallyClearFluorinePumpMalfunctionAlarm | Manually clear fluorine pump malfunction alarm | 氟泵功能异常手动清除 | 1-Read_Write | 读写 | clear(1), unknown(255) | [清除=1] | Manually clear fluorine pump malfunction alarm of the device config table for the NetCol5000A010. Value 1 indicate clear
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.48 | hwNetCol5000A010WetFilmHumidifierControlStatusNew | Wet film humidifier control status | 湿膜加湿控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier control status of the NetCol5000A010. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.49 | hwNetCol5000A010Returnairfilter | Return air filter | 回风过滤网 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Return air filter of the device config table for the NetCol5000A010. Value 1 indicate no. Value 2 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.50 | hwNetCol5000A010Floorwateroverflowalarmaction | Floor water overflow alarm action | 地板溢水告警动作 | 1-Read_Write | 读写 | shutdown(1), inactivity(2), onlyindoorfanrunning(3), humidificationstopped(4), unknown(255) | [停机=1]/[无动作=2]/[仅运行室内风机=3]/[仅停加湿=4] | Floor water overflow alarm action of the device config table for the NetCol5000A010. Value 1 indicate Shutdown. Value 2 indicate Inactivity. Value 3 indicate Only indoor fan running. Value 4 indicate Humidification stopped.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.51 | hwNetCol5000A010Incabinetwateroverflowalarmaction | In-cabinet water overflow alarm action | 柜内溢水告警动作 | 1-Read_Write | 读写 | shutdown(1), inactivity(2), onlyindoorfanrunning(3), humidificationstopped(4), unknown(255) | [停机=1]/[无动作=2]/[仅运行室内风机=3]/[仅停加湿=4] | In-cabinet water overflow alarm action of the device config table for the NetCol5000A010. Value 1 indicate Shutdown. Value 2 indicate Inactivity. Value 3 indicate Only indoor fan running. Value 4 indicate Humidification stopped.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.52 | hwNetCol5000A010Wateroverflowalarmaction | Water overflow alarm action | 溢水告警动作 | 1-Read_Write | 读写 | shutdown(1), inactivity(2), onlyindoorfanrunning(3), humidificationstopped(4), unknown(255) | [停机=1]/[无动作=2]/[仅运行室内风机=3]/[仅停加湿=4] | Water overflow alarm action of the device config table for the NetCol5000A010. Value 1 indicate Shutdown. Value 2 indicate Inactivity. Value 3 indicate Only indoor fan running. Value 4 indicate Humidification stopped.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.53 | hwNetCol5000A010Clearfluorinepumptotalruntime | Clear fluorine pump total runtime | 清零氟泵累计运行时间 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Clear fluorine pump total runtime of the device config table for the NetCol5000A010. Value 1 indicate yes.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.54 | hwNetCol5000A010Outdoorfanmaxadjuststepinfluorinepumpmode | Outdoor fan max adjust step in fluorine pump mode | 氟泵模式外风机最大调节步长 | 1-Read_Write | 读写 | 1..10 | 1..10 | Outdoor fan max adjust step in fluorine pump mode of the NetCol5000A010. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.55 | hwNetCol5000A010Outdoorfanprotectadjustperiodinfluorinepump | Outdoor fan protection adjust period in fluorine pump mode | 氟泵模式外风机保护调节周期 | 1-Read_Write | 读写 | 0..1800 | 0..1800 | Outdoor fan protection adjust period in fluorine pump mode of the NetCol5000A010. SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.10.2.6.1.200 | hwNetCol5000A010RunningAndConfig2Status | / | / | 2-Read_Create | 读构建 | / | / | The The running row status of Device.

## NetCol5000-A025
NetCol5000-A025
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.3 | NetCol5000A025 | NetCol5000-A025 | NetCol5000-A025 | / | / | / | / | The NetColPoe Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1 | hwNetCol5000A025RunningAndConfig1Table | / | / |  |  | / | / | The running table of Huawei NetColPoe Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.1 | hwNetCol5000A025RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.2 | hwNetCol5000A025CommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.3 | hwNetCol5000A025SlotNO | Slot No. | 槽位号 | 0-Read_Only | 只读 | 0..6 | 0..6 | Slot NO of the device config table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.4 | hwNetCol5000A025PortNO | Port No. | 端口号 | 0-Read_Only | 只读 | 1..5 | 1..5 | Port NO of the device config table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.5 | hwNetCol5000A025CompressorTotalTime | Compressor total runtime | 压缩机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.6 | hwNetCol5000A025Fan1TotalTime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan 1 Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.7 | hwNetCol5000A025Fan2TotalTime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan 2 Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.8 | hwNetCol5000A025Fan3TotalTime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan 3 Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.9 | hwNetCol5000A025Fan4TotalTime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan 4 Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.10 | hwNetCol5000A025Fan5TotalTime | Indoor fan 5 total runtime | 室内风机5累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan 5 Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.11 | hwNetCol5000A025Fan6TotalTime | Indoor fan 6 total runtime | 室内风机6累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan 6 Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.12 | hwNetCol5000A025HumidifierTotalTime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.13 | hwNetCol5000A025HeaterTotalTime | Heater total runtime | 电加热累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Heater Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.14 | hwNetCol5000A025PumpTotalTime | Cond pump total runtime | 冷凝水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Pump Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.15 | hwNetCol5000A025AirfilterTotalTime | Air filter total runtime | 过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Airfilter Total Time of the device config table for the NetColPoe. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.16 | hwNetCol5000A025UnitOnOffStatus | Unit on/off status | 机组开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Unit On/Off Status. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.17 | hwNetCol5000A025RemoteOnOffStatus | / | / | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | / | Remote On/Off Status. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.18 | hwNetCol5000A025CoolOutput | Cooling output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Cool Output of the device config table for the NetColPoe. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.19 | hwNetCol5000A025FanOutput | Fan output | 风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Fan Output of the device config table for the NetColPoe. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.20 | hwNetCol5000A025HumidOutput | Humidifying output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humid Output of the device config table for the NetColPoe. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.21 | hwNetCol5000A025HeatOutput | Heating output | 加热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Heat Output of the device config table for the NetColPoe. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.22 | hwNetCol5000A025TeamworkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), intelligentteamworkcontrol(2), iCooling(3), unknown(255) | [单机=1]/[智能群控=2]/[iCooling=3] | The Teamwork Status. Value 1 indicates Single. Value 2 indicates Intelligent teamwork control. Value 3 indicates iCooling.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.23 | hwNetCol5000A025PhaseAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Phase A Voltage of the device config table for the NetColPoe. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.24 | hwNetCol5000A025PhaseBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Phase B Voltage of the device config table for the NetColPoe. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.25 | hwNetCol5000A025PhaseCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Phase C Voltage of the device config table for the NetColPoe. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.26 | hwNetCol5000A025PowerFrequency | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | Power Frequency of the device config table for the NetColPoe. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.27 | hwNetCol5000A025TempHumidCtrlType | T/H control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnair(1), supplyair(2), coldaisle(3), hotaisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | Temp Humid Ctrl Type. Value 1 indicates return-air. Value 2 indicates supply-air. Value 3 indicates cold-aisle. Value 4 indicates hot-aisle.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.28 | hwNetCol5000A025CurrentTemp | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Current Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.29 | hwNetCol5000A025CurrentHumidity | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Current Humidity of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.30 | hwNetCol5000A025SupplyAirAvgTemp | Supply-air average temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply Air Avg Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.31 | hwNetCol5000A025ReturnAirAvgTemp | Return-air average temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return Air Avg Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.32 | hwNetCol5000A025ColdAisleAvgTemp | Cold-aisle average temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Poe Cold Aisle Avg Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.33 | hwNetCol5000A025HotAisleAvgTemp | Hot-aisle average temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Poe Hot Aisle Avg Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.34 | hwNetCol5000A025SupplyAirAvgHumid | Supply-air average humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Supply Air Avg Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.35 | hwNetCol5000A025ReturnAirAvgHumid | Return-air average humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Return Air Avg Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.36 | hwNetCol5000A025ColdAisleAvgHumid | Cold-aisle average humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold Aisle Avg Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.37 | hwNetCol5000A025HotAisleAvgHumid | Hot-aisle average humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot Aisle Avg Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.38 | hwNetCol5000A025SupplyAir1Temp | Supply-air 1 temperature | 送风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply Air 1 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.39 | hwNetCol5000A025SupplyAir2Temp | Supply-air 2 temperature | 送风2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply Air 2 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.40 | hwNetCol5000A025ReturnAir1Temp | Return-air 1 temperature | 回风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return Air 1 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.41 | hwNetCol5000A025ReturnAir2Temp | Return-air 2 temperature | 回风2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return Air 2 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.42 | hwNetCol5000A025ReturnAir2Humid | Return-air 2 humidity | 回风2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Return Air 2 Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.43 | hwNetCol5000A025ColdAisle1Temp | Cold aisle 1 temperature | 冷通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold Aisle 1 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.44 | hwNetCol5000A025ColdAisle2Temp | Cold aisle 2 temperature | 冷通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold Aisle 2 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.45 | hwNetCol5000A025ColdAisle3Temp | Cold aisle 3 temperature | 冷通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold Aisle 3 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.46 | hwNetCol5000A025ColdAisle1Humid | Cold aisle 1 humidity | 冷通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold Aisle 1 Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.47 | hwNetCol5000A025ColdAisle2Humid | Cold aisle 2 humidity | 冷通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold Aisle 2 Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.48 | hwNetCol5000A025ColdAisle3Humid | Cold aisle 3 humidity | 冷通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold Aisle 3 Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.49 | hwNetCol5000A025HotAisle1Temp | Hot aisle 1 temperature | 热通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot Aisle 1 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.50 | hwNetCol5000A025HotAisle2Temp | Hot aisle 2 temperature | 热通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot Aisle 2 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.51 | hwNetCol5000A025HotAisle3Temp | Hot aisle 3 temperature | 热通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot Aisle 3 Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.52 | hwNetCol5000A025HotAisle1Humid | Hot aisle 1 humidity | 热通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot Aisle 1 Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.53 | hwNetCol5000A025HotAisle2Humid | Hot aisle 2 humidity | 热通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot Aisle 2 Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.54 | hwNetCol5000A025HotAisle3Humid | Hot aisle 3 humidity | 热通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot Aisle 3 Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.55 | hwNetCol5000A025CompRunningStatus | Comp run status | 压缩机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Comp Running Status of the device config table for the NetColPoe. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.56 | hwNetCol5000A025Dehumidsolenoidcontrolstat | Dehumidity solenoid control stat | 除湿电磁阀控制状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | Communication Status. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.57 | hwNetCol5000A025IndoorFan1RunningStatus | Indoor fan 1 run status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor Fan 1 Running Status of the device config table for the NetColPoe. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.58 | hwNetCol5000A025IndoorFan2RunningStatus | Indoor fan 2 run status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor Fan 2 Running Status of the device config table for the NetColPoe. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.59 | hwNetCol5000A025IndoorFan3RunningStatus | Indoor fan 3 run status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor Fan 3 Running Status of the device config table for the NetColPoe. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.60 | hwNetCol5000A025IndoorFan4RunningStatus | Indoor fan 4 run status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor Fan 4 Running Status of the device config table for the NetColPoe. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.61 | hwNetCol5000A025IndoorFan5RunningStatus | Indoor fan 5 run status | 室内风机5运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor Fan 5 Running Status of the device config table for the NetColPoe. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.62 | hwNetCol5000A025IndoorFan6RunningStatus | Indoor fan 6 run status | 室内风机6运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor Fan 6 Running Status of the device config table for the NetColPoe. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.63 | hwNetCol5000A025OutdoorFanCtrlStatus | / | / | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | / | Outdoor Fan Ctrl Status. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.64 | hwNetCol5000A025HeaterCtrlStatus | Elec heater control status | 电加热控制状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | Heater Ctrl Status. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.65 | hwNetCol5000A025Pump1CtrlStatus | Cond pump control status | 冷凝水泵控制状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关闭=1]/[开启=2] | Pump1 Ctrl Status. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.66 | hwNetCol5000A025PortMAC | / | / | 0-Read_Only | 只读 | 0..28 | / | The MAC Address of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.67 | hwNetCol5000A025SoftVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Soft Version of the device config table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.68 | hwNetCol5000A025EquipELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | Equip ELabel of the device config table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.69 | hwNetCol5000A025EquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.70 | hwNetCol5000A025HostFlag | Host identity | 主机标识 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | Host flag. Value 1 indicates slave. Value 2 indicates master.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.71 | hwNetCol5000A025SetBaseinfoComplete | / | / | 0-Read_Only | 只读 | unreceived(1), received(2), unknown(255) | / | Set Baseinfo Complete. Value 1 indicates unreceived. Value 2 indicates received.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.72 | hwNetCol5000A025TeamworkAddr | / | / | 0-Read_Only | 只读 | 0..32 | / | Teamwork Addr of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.74 | hwNetCol5000A025Psu1InputType | PSU 1 input type | 电源模块1输入类型 | 0-Read_Only | 只读 | dc(1), ac(2), unknown(255) | [直流=1]/[交流=2] | Psu 1 Input Type. Value 1 indicates DC. Value 2 indicates AC.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.75 | hwNetCol5000A025Psu1InputVoltage | PSU 1 input voltage | 电源模块1输入电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Psu1 Input Voltage of the device config table for the NetColPoe. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.76 | hwNetCol5000A025Psu1InputCurrent | PSU 1 input current | 电源模块1输入电流 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Psu1 Input Current of the device config table for the NetColPoe. Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.77 | hwNetCol5000A025Psu1OutputVoltage | PSU 1 output voltage | 电源模块1输出电压 | 0-Read_Only | 只读 | 0..700 | 0..700 | Psu1 Onput Voltage of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.78 | hwNetCol5000A025Psu1OutputCurrent | PSU 1 output current | 电源模块1输出电流 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Psu1 Onput Current of the device config table for the NetColPoe. Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.79 | hwNetCol5000A025Psu1OutputPower | PSU 1 input power | 电源模块1输入功率 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Psu1 Onput Power of the device config table for the NetColPoe. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.80 | hwNetCol5000A025Psu2InputType | PSU 2 input type | 电源模块2输入类型 | 0-Read_Only | 只读 | dc(1), ac(2), unknown(255) | [直流=1]/[交流=2] | Psu 2 Input Type. Value 1 indicates DC. Value 2 indicates AC.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.81 | hwNetCol5000A025Psu2InputVoltage | PSU 2 input voltage | 电源模块2输入电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Psu2 Input Voltage of the device config table for the NetColPoe. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.82 | hwNetCol5000A025Psu2InputCurrent | PSU 2 input current | 电源模块2输入电流 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Psu2 Input Current of the device config table for the NetColPoe. Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.83 | hwNetCol5000A025Psu2OutputVoltage | PSU 2 output voltage | 电源模块2输出电压 | 0-Read_Only | 只读 | 0..700 | 0..700 | Psu2 Onput Voltage of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.84 | hwNetCol5000A025Psu2OutputCurrent | PSU 2 output current | 电源模块2输出电流 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Psu2 Onput Current of the device config table for the NetColPoe. Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.85 | hwNetCol5000A025Psu2OutputPower | PSU 2 input power | 电源模块2输入功率 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Psu2 Onput Power of the device config table for the NetColPoe. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.86 | hwNetCol5000A025EEVCtlStatus | EEV control status | EEV控制状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | EEV Ctl Status of the device config table for the NetColPoe. SigUnitInfo:step
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.87 | hwNetCol5000A025EEVRunStatus | EEV run status | EEV运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | EEV Run Status of the device config table for the NetColPoe. SigUnitInfo:step
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.88 | hwNetCol5000A025EmsStatus | Startup/shutdown control | 控制开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Ems Status. Value 1 indicates on. Value 2 indicates off.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.89 | hwNetCol5000A025ReturnairTemp | Return-air temperature set point | 回风温度设定点 | 1-Read_Write | 读写 | 180..450 | 180..450 | Return air Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.90 | hwNetCol5000A025SupplyairTemp | Supply-air temperature set point | 送风温度设定点 | 1-Read_Write | 读写 | 150..350 | 150..350 | Supply air Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.91 | hwNetCol5000A025ColdaisleTemp | Cold-aisle temperature set point | 冷通道温度设定点 | 1-Read_Write | 读写 | 150..350 | 150..350 | Coldaisle Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.92 | hwNetCol5000A025HotaisleTemp | Hot-aisle temperature set point | 热通道温度设定点 | 1-Read_Write | 读写 | 180..450 | 180..450 | Hotaisle Temp of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.93 | hwNetCol5000A025ReturnairHumid | Return-air humidity set point | 回风湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Return Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.94 | hwNetCol5000A025SupplyairHumid | Supply-air humidity set point | 送风湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Supplyair Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.95 | hwNetCol5000A025ColdaisleHumid | Cold-aisle humidity set point | 冷通道湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Coldaisle Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.96 | hwNetCol5000A025HotaisleHumid | Hot-aisle humidity set point | 热通道湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Hotaisle Humid of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.97 | hwNetCol5000A025ReturnairHTThreshold | Return-air HT threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Return HT Threshold of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.98 | hwNetCol5000A025ReturnairLTThreshold | Return-air LT threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Return LT Threshold of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.99 | hwNetCol5000A025SupplyairHTThreshold | Supply-air HT threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Supplyair HT Threshold of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.100 | hwNetCol5000A025SupplyairLTThreshold | Supply-air LT threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | Supplyair LT Threshold of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.101 | hwNetCol5000A025ColdAisleHTThreshold | Cold-aisle HT threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Cold Aisle HT Threshold of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.102 | hwNetCol5000A025HotAisleHTThreshold | Hot-aisle HT threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Hot Aisle HT Threshold of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.103 | hwNetCol5000A025HighumidThreshold | Humidity high threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | Highumid Threshold of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.104 | hwNetCol5000A025LowhumidThreshold | Humidity low threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | Lowhumid Threshold of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.105 | hwNetCol5000A025ReturnairHTAction | Return-air HT action | 回风高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Returnair HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.106 | hwNetCol5000A025ReturnairLTAction | Return-air LT action | 回风低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Returnair LT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.107 | hwNetCol5000A025SupplyairHTAction | Supply-air HT action | 送风高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Supplyair HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.108 | hwNetCol5000A025SupplyairLTAction | Supply-air LT action | 送风低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Supplyair HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.109 | hwNetCol5000A025ColdAisleHTAction | Cold-aisle HT action | 冷通道高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | ColdAisle HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.110 | hwNetCol5000A025HotAisleHTAction | Hot-aisle HT action | 热通道高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | HotAisle HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.111 | hwNetCol5000A025HighumidAction | High humidity action | 高湿告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Highumid Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.112 | hwNetCol5000A025LowhumidAction | Low humidity action | 低湿告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Lowhumid Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.113 | hwNetCol5000A025DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of the device config table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.114 | hwNetCol5000A025OutdoorFanCtr | Outdoor fan run status | 室外风机运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Outdoor fan run status of NetCol5000A025. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.115 | hwNetCol5000A025Electric | Electricity | 电量 | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | The Electricity of NetCol5000A025.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.116 | hwNetCol5000A025Power | Power | 功率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | The Power of NetCol5000A025.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.117 | hwNetCol5000A025Hardwareversion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | The Hardware version of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.118 | hwNetCol5000A025RatedCoolingCapacity | Rated cooling capacity (cooling power) | 额定的制冷容量（制冷功率） | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Rated Cooling Capacity of NetCol5000A025.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.3.1.1.200 | hwNetCol5000A0255RunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.2 | hwNetCol5000A025RunningTable | / | / |  |  | / | / | The running table of Huawei NetColPoe Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.3.2.1.1 | hwNetCol5000A025RunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.2.1.2 | hwNetCol5000A025RefrigerantStatus | Refrigerant status | 制冷剂状态 | 0-Read_Only | 只读 | normal(1),inadequate(2),serinadequate(3),overcharged(4),unknown(255) | [正常=1]/[不足=2]/[严重不足=3]/[过充=4] | Refrigerant status. Value 1 indicates norma. Value 2 indicates Inadequate. Value 3 indicates Serinadequate. Value 4 indicates Overcharged.
1.3.6.1.4.1.2011.6.178.1.1.10.3.2.1.3 | hwNetCol5000A025TemperatureSetPoint | Temperature setpoint | 温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | The value range of the temperature setting point is related to the temperature and humidity control type. 1. When the temperature and humidity control type is return air; 2. When the temperature and humidity control type is used for air supply; 3. When the temperature and humidity control type is cold aisle; 4. When the temperature and humidity control type is hot aisle. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.2.1.4 | hwNetCol5000A025HumiditySetPoint | Humidity setpoint | 湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Humidity set point of the device config table for the NetColPoe. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.2.1.5 | hwNetCol5000A025OutDoortemp | Outdoor temperature | 室外温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | The Outdoor temperature of NetCol5000A025.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.2.1.6 | hwNetCol5000A025EEVsuctionoverheatingdegree | EEV suction overheating degree | EEV吸气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | The EEV suction overheating degree of NetCol5000A025.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.2.1.7 | hwNetCol5000A025EEVdischoverheatingdegree | EEV disch overheating degree | EEV排气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | The EEV disch overheating degree of NetCol5000A025.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.2.1.100 | hwNetCol5000A025RunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running 2 row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3 | hwNetCol5000A025RunningAndConfig2Table | / | / |  |  | / | / | The running table of Huawei NetColPoe Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.1 | hwNetCol5000A025RunningAndConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.2 | hwNetCol5000A025Model | Model | 机型 | 0-Read_Only | 只读 | netCol5000A(1), netCol5000C(2), unknown(255) | [NetCol5000A=1]/[NetCol5000C=2] | The Model of NetCol5000A025. Value 1 indicates NetCol5000A. Value 2 indicates NetCol5000C.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.3 | hwNetCol5000A025Netcolpower | NetCol Power | NetCol功率 | 0-Read_Only | 只读 | power20kw(1), power25kw(2), power30kw(3), power35kw(4), power50kw(5), unknown(255) | [20KW=1]/[25KW=2]/[30KW=3]/[35KW=4]/[50KW=5] | The Netcol power of NetCol5000A025. Value 1 indicates 20KW. Value 2 indicates 25KW. Value 3 indicates 30KW. Value 4 indicates 35KW. Value 5 indicates 50KW.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.4 | hwNetCol5000A025Numberofindoorfans | Number of indoor fans | 风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of indoor fans of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.5 | hwNetCol5000A025Numberofcompressors | Number of compressors | 压缩机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of compressors of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.6 | hwNetCol5000A025Numberofheaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of heaters of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.7 | hwNetCol5000A025Numberofhumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of humidifiers of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.8 | hwNetCol5000A025Numberofcondpumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of cond pumps of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.9 | hwNetCol5000A025Numberofpsu | Number of PSU | 电源模块数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of psu of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.10 | hwNetCol5000A025Indoorfancontrolstatus | Indoor fan control status | 室内风机控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Indoor fan control status of NetCol5000A025. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.11 | hwNetCol5000A025Numberofalarm | Number of alarm | 告警数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Number of alarm of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.12 | hwNetCol5000A025Humidifierpumptotalruntime | Humidifier pump total runtime | 加湿水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Humidifier pump total runtime of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.13 | hwNetCol5000A025Humidifierwetfilmtotalruntime | Humidifier wet film total runtime | 加湿湿膜累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Humidifier wet film total runtime of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.14 | hwNetCol5000A025EEVtotalruntime | EEV total runtime | EEV累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The EEV total runtime of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.15 | hwNetCol5000A025Outfantotalruntime | Out fan total runtime | 室外风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Out fan total runtime of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.16 | hwNetCol5000A025Heatmode | Heat mode | 加热方式 | 0-Read_Only | 只读 | dehumidHeat(1), lowAndTempHeat(2), dehumidAndLTHeat(3), unknown(255) | [除湿补热=1]/[低温加热=2]/[除湿补热且低温加热=3] | The Heat mode of NetCol5000A025. Value 1 indicates Dehumid heat. Value 2 indicates Low-temp heat. Value 3 indicates Dehumid and LT heat.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.17 | hwNetCol5000A025Indoorfancontroltype | Indoor fan control type | 室内风机控制类型 | 0-Read_Only | 只读 | retAirTempDiffRateControl(1), pressureDiffControl(2), unknown(255) | [回送风温差比例控制=1]/[压差控制=2] | The Indoor fan control type of NetCol5000A025. Value 1 indicates Ret air temp diff rate control. Value 2 indicates Pressure diff control.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.18 | hwNetCol5000A025Dischargepressure | Discharge pressure | 排气压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | The Discharge pressure of NetCol5000A025.Multiple:100. SigUnitInfo:Mpa
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.19 | hwNetCol5000A025Suctionpressure | Suction pressure | 吸气压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | The Suction pressure of NetCol5000A025.Multiple:100. SigUnitInfo:Mpa
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.20 | hwNetCol5000A025Dischargetemperature | Discharge temperature | 排气温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The Discharge temperature of NetCol5000A025.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.21 | hwNetCol5000A025Suctiontemperature | Suction temperature | 吸气温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The Suction temperature of NetCol5000A025.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.22 | hwNetCol5000A025Liquidpipetemperature | Liquid pipe temperature | 液管温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The Liquid pipe temperature of NetCol5000A025.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.23 | hwNetCol5000A025Averageairsidepressuredifference | Average air side pressure difference | 风侧平均压差 | 0-Read_Only | 只读 | 0..500 | 0..500 | The Average air side pressure difference of NetCol5000A025. SigUnitInfo:Pa
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.24 | hwNetCol5000A025Phasecurrent | Phase current | 相电流 | 0-Read_Only | 只读 | 0..25000 | 0..25000 | The Phase current of NetCol5000A025.Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.25 | hwNetCol5000A025IPaddress | / | / | 0-Read_Only | 只读 | 0..65535 | / | The IP address of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.26 | hwNetCol5000A025CurrentCoolingCapacity | Cooling capacity | 制冷量 | 1-Read_Write | 读写 | 0..200000 | 0..200000 | Current Cooling Capacity of the NetColPoe. Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.27 | hwNetCol5000A025Current | Current | 电流 | 0-Read_Only | 只读 | -100000..100000 | -100000..100000 | The Current of NetCol5000A025. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.28 | hwNetCol5000A025iCoolingrunstatus | iCooling run status | iCooling运行状态 | 0-Read_Only | 只读 | normal(1), abnormalairconditioner(2), invalidcabinettemperature(3), invalidcabinetpower(4), dataupdatingtimeout(5), inconsistentnumberofteamworkunits(6), notcoldaislecontainment(7), unknown(255) | [正常=1]/[空调异常=2]/[机柜温度无效=3]/[机柜功率无效=4]/[数据更新超时=5]/[群控机组数目不一致=6]/[封闭通道非冷通道=7] | The iCooling run status of NetCol5000A025. Value 1 indicates Normal. Value 2 indicates Abnormal air conditioner. Value 3 indicates Invalid cabinet temperature. Value 4 indicates Invalid cabinet power. Value 5 indicates Data updating timeout. Value 6 indicates Inconsistent number of teamwork units. Value 7 indicates Not cold aisle containment.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.29 | hwNetCol5000A025Baudrate | Baud rate | 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate19200(2), unknown(255) | [9600=1]/[19200=2] | The Baud rate of NetCol5000A025. Value 1 indicates 9600. Value 2 indicates 19200.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.30 | hwNetCol5000A025Communicationaddress | Communication address | 通信地址 | 1-Read_Write | 读写 | 1..255 | 1..255 | The Communication address of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.31 | hwNetCol5000A025Teamworkmode | / | / | 1-Read_Write | 读写 | smart(1), iCooling(2), unknown(255) | / | The Teamwork mode of NetCol5000A025. Value 1 indicates smart. Value 2 indicates iCooling.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.32 | hwNetCol5000A025L1andL2linkageenableflag | L1&L2 linkage enable flag | L1L2联动使能标志 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The L1&L2 linkage enable flag of NetCol5000A025. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.33 | hwNetCol5000A025L1andL2linkagetargettemperature | L1/L2 linkage target temperature | L1/L2联动目标温度 | 1-Read_Write | 读写 | 150..450 | 150..450 | The L1/L2 linkage target temperature of NetCol5000A025.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.34 | hwNetCol5000A025L1andL2linkagetargethumidity | L1/L2 linkage target humidity | L1/L2联动目标湿度 | 1-Read_Write | 读写 | 200..800 | 200..800 | The L1/L2 linkage target humidity of NetCol5000A025.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.35 | hwNetCol5000A025Branch1Name | supplyInfo | 第一路供电信息 | 1-Read_Write | 读写 | 0..2147483647 | 0..2147483647 | The Branch 1 Name of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.36 | hwNetCol5000A025Branch2Name | supplyInfo | 第二路供电信息 | 1-Read_Write | 读写 | 0..2147483647 | 0..2147483647 | The Branch 2 Name of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.37 | hwNetCol5000A025SupplyMode | supplyInfo | 供电制式 | 1-Read_Write | 读写 | 1..2 | 1..2 | The Supply Mode of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.38 | hwNetCol5000A025SupplyBranchNum | supplyInfo | 供电路数 | 1-Read_Write | 读写 | 1..2 | 1..2 | The Supply Branch Num of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.3.1.100 | hwNetCol5000A025RunningAndConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running 2 row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4 | hwNetCol5000A025RunningAndConfig3Table | / | / |  |  | / | / | The running table of Huawei NetColPoe Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.1 | hwNetCol5000A025RunningAndConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.2 | hwNetCol5000A025Totalnumberofunits | Total number of units | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | The Total number of units of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.3 | hwNetCol5000A025Numberofrunningunits | Number of running units | 本群组运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | The Number of running units of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.4 | hwNetCol5000A025Averagetemperature | Average temperature | 群组平均温度 | 0-Read_Only | 只读 | -990..990 | -990..990 | The Average temperature of NetCol5000A025.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.5 | hwNetCol5000A025Averagehumidity | Average humidity | 群组平均湿度 | 0-Read_Only | 只读 | 0..990 | 0..990 | The Average humidity of NetCol5000A025.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.6 | hwNetCol5000A025Requiredcoolingcapacity | Required cooling capacity | 群组总冷量需求 | 0-Read_Only | 只读 | -5000..5000 | -5000..5000 | The Required cooling capacity of NetCol5000A025. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.7 | hwNetCol5000A025Requiredhumidity | Required humidity | 群组总湿度需求 | 0-Read_Only | 只读 | -5000..5000 | -5000..5000 | The Required humidity of NetCol5000A025. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.8 | hwNetCol5000A025Teamworkstatusold | Teamwork status | 群控运行状态 | 0-Read_Only | 只读 | invalid(1), cool(2), heat(3), dehumid(4), humid(5), coolandhumid(6), heatanddehumid(7), heatandhumid(8), coolanddehumid(9), unknown(255) | [无效=1]/[制冷=2]/[加热=3]/[除湿=4]/[加湿=5]/[制冷且加湿=6]/[加热且除湿=7]/[加热且加湿=8]/[制冷且除湿=9] | The Teamwork status of Old NetCol5000A025. Value 1 indicates Invalid. Value 2 indicates Cool. Value 3 indicates Heat. Value 4 indicates Dehumid. Value 5 indicates Humid. Value 6 indicates Cool and humid. Value 7 indicates Heat and dehumid. Value 8 indicates Heat and humid. Value 9 indicates Cool and dehumid.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.9 | hwNetCol5000A025Waterinletsolenoidcontrolstatus | Water inlet solenoid control status | 进水电磁阀控制状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Water inlet solenoid control status of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.10 | hwNetCol5000A025Drainagesolenoidcontrolstatus | Drainage solenoid control status | 排水电磁阀控制状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Drainage solenoid control status of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.11 | hwNetCol5000A025Outdoorfancontrolmode | Outdoor fan control mode | 室外风机控制模式 | 0-Read_Only | 只读 | drycontact(1), communicate(2), unknown(255) | [干接点=1]/[通信=2] | The Outdoor fan control mode of NetCol5000A025. Value 1 indicates Dry contact. Value 2 indicates Communicate.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.12 | hwNetCol5000A025HeatOutp | Heating output | 制热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The heat outp of NetCol5000A025. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.13 | hwNetCol5000A025Compexceedruntimethreshold | Comp exceed runtime threshold | 压缩机运行超时告警阈值 | 1-Read_Write | 读写 | 20000..40000 | 20000..40000 | The Comp exceed runtime threshold of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.14 | hwNetCol5000A025Cylindermaintenanceduethreshold | Cylinder maintenance due threshold | 加湿桶维护时间到告警阈值 | 1-Read_Write | 读写 | 2000..5000 | 2000..5000 | The Cylinder maintenance due threshold of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.15 | hwNetCol5000A025Cylinderreplacementduethreshold | Cylinder replacement due threshold | 加湿桶更换时间到告警阈值 | 1-Read_Write | 读写 | 2000..5000 | 2000..5000 | The Cylinder replacement due threshold of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.16 | hwNetCol5000A025Elecheaterexceedruntimethreshold | Elec heater exceed runtime threshold | 电加热运行超时告警阈值 | 1-Read_Write | 读写 | 20000..40000 | 20000..40000 | The Elec heater exceed runtime threshold of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.17 | hwNetCol5000A025Condpumpexceedruntimethreshold | Cond pump exceed runtime threshold | 冷凝水泵运行超时告警阈值 | 1-Read_Write | 读写 | 1000..50000 | 1000..50000 | The Cond pump exceed runtime threshold of NetCol5000A025. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.18 | hwNetCol5000A025OnOrOffStatusOnEMS | On/off status on EMS | 网管开关机状态 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | The on or off status on EMS of NetCol5000A025. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.19 | hwNetCol5000A025Dehumidoutput | Dehumidity output | 除湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Dehumid out put of NetCol5000A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.20 | hwNetCol5000A025IcoolingType | iCooling type | iCooling类型 | 1-Read_Write | 读写 | 1..2 | 1..2 | iCooling type of the device config table for the NetCol5000-A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.21 | hwNetCol5000A025IcoolingTemperatureAndHumidityControlType | iCooling temperature and humidity control type | iCooling温湿度控制类型 | 1-Read_Write | 读写 | returnair(1), supplyair(2), coldaisle(3), hotaisle(4), unknown(255) | [回风=0]/[送风=1]/[冷通道=2]/[热通道=3] | iCooling temperature and humidity control type of the device config table for the NetCol5000-A025. Value 1 indicate return-air Value 2 indicate supply-air Value 3 indicate cold-aisle Value 4 indicate hot-aisle
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.22 | hwNetCol5000A025IcoolingHeartbeat | iCooling heartbeat | iCooling心跳 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | iCooling heartbeat of the device config table for the NetCol5000-A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.23 | hwNetCol5000A025IcoolingIndoorFanMaxReturnorSupplyAirTemperatureDifference | icooling indoor fan max return/supply air temperature difference | iCooling室内风机回送风最大温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | icooling indoor fan max return/supply air temperature difference of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.24 | hwNetCol5000A025IcoolingMaxIndoorFanSpeed | iCooling max indoor fan speed | iCooling室内风机最大转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | iCooling max indoor fan speed of the device config table for the NetCol5000-A025.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.25 | hwNetCol5000A025IcoolingMaxOutdoorFanRunningPressure | iCooling max outdoor fan running pressure | iCooling室外风机最大运行压力 | 1-Read_Write | 读写 | 150..400 | 150..400 | iCooling max outdoor fan running pressure of the device config table for the NetCol5000-A025.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.26 | hwNetCol5000A025IcoolingIndoorFanControlType | iCooling indoor fan control type | iCooling室内风机控制类型 | 1-Read_Write | 读写 | retairtempdiffratecontro(1), retairtempdiffcontrol(2), coldsourceopeningctrl(3), pressurediffcontrol(4), returnairtempctrl(5), supplyairtempctrl(6), unknown(255) | [回送风温差比例控制=1]/[回送风温差控制=2]/[冷源开度控制=3]/[压差控制=4]/[回风温度控制=5]/[送风温度控制=6] | iCooling indoor fan control type of the device config table for the NetCol5000-A025. Value 1 indicate retairtempdiffratecontro Value 2 indicate retairtempdiffcontrol Value 3 indicate coldsourceopeningctrl Value 4 indicate pressurediffcontrol Value 5 indicate returnairtempctrl Value 6 indicate supplyairtempctrl
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.27 | hwNetCol5000A025IcoolingTemperatureSetpoint | iCooling temperature setpoint | iCooling温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | iCooling temperature setpoint of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.28 | hwNetCol5000A025IcoolingHumiditySetpoint | iCooling humidity setpoint | iCooling湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | iCooling humidity setpoint of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.29 | hwNetCol5000A025IcoolingStartuporShutdownControl | iCooling startup/shutdown control | iCooling控制开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=0]/[开机=1] | iCooling startup/shutdown control of the device config table for the NetCol5000-A025. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.3.4.1.100 | hwNetCol5000A025RunningAndConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running and config 3 row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5 | hwNetCol5000A025Running2Table | / | / |  |  | / | / | The running table of NetCol5000-A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.1 | hwNetCol5000A025Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetCol5000-A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.2 | hwNetCol5000A025WaterCooledModuleWaterValveRunningStatus | Water-cooled module water valve running status | 冷冻水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Water-cooled module water valve running status of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.3 | hwNetCol5000A025WaterCooledModuleSupplyWaterTemperature | Water-cooled module supply-water temperature | 供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Water-cooled module supply-water temperature of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.4 | hwNetCol5000A025WaterCooledModuleReturnWaterTemperature | Water-cooled module return-water temperature | 回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Water-cooled module return-water temperature of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.5 | hwNetCol5000A025OutdoorUnitCondensateMode | Outdoor unit condensate mode | 室外机冷凝方式 | 0-Read_Only | 只读 | aircooled(1), watercooled(2), unknown(255) | [风冷=1]/[水冷=2] | Outdoor unit condensate mode of the device config table for the NetCol5000-A025. Value 1 indicate air-cooled Value 2 indicate water-cooled
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.6 | hwNetCol5000A025ColdAisle4Temperature | Cold aisle 4 temperature | 冷通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 4 temperature of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.7 | hwNetCol5000A025ColdAisle5Temperature | Cold aisle 5 temperature | 冷通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 5 temperature of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.8 | hwNetCol5000A025ColdAisle4Humidity | Cold aisle 4 humidity | 冷通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 4 humidity of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.9 | hwNetCol5000A025ColdAisle5Humidity | Cold aisle 5 humidity | 冷通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 5 humidity of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.10 | hwNetCol5000A025HotAisle4Temperature | Hot aisle 4 temperature | 热通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 4 temperature of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.11 | hwNetCol5000A025HotAisle5Temperature | Hot aisle 5 temperature | 热通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 5 temperature of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.12 | hwNetCol5000A025HotAisle4Humidity | Hot aisle 4 humidity | 热通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 4 humidity of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.13 | hwNetCol5000A025HotAisle5Humidity | Hot aisle 5 humidity | 热通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 5 humidity of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.14 | hwNetCol5000A025SystemPower | System power | 机组总功率 | 0-Read_Only | 只读 | 0..4000 | 0..4000 | System power of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.15 | hwNetCol5000A025OutdoorFanHumidity | Outdoor fan humidity | 室外机湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Outdoor fan humidity of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.16 | hwNetCol5000A025OutdoorSprayRunningStatus | Outdoor spray running status | 室外机喷淋运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor spray running status of the device config table for the NetCol5000-A025.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.17 | hwNetCol5000A025SystemTotalPowerConsumptionFlag | System total power consumption flag | 机组累计耗电量标识 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | System total power consumption flag of the device config table for the NetCol5000-A025. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.18 | hwNetCol5000A025AcInputTotalPowerConsumption | AC input total power consumption | 机组交流输入累计电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AC input total power consumption of the device config table for the NetCol5000-A025.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.19 | hwNetCol5000A025TotalOpenTimesOfTheWaterInletSolenoidValve | Total open times of the water inlet solenoid valve | 进水电磁阀累计开启次数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total open times of the water inlet solenoid valve of the device config table for the NetCol5000-A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.20 | hwNetCol5000A025NumberOfOutdoorSpray |  |  | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Number of outdoor spray of the device config table for the NetCol5000-A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.21 | hwNetCol5000A025DrainPumpRunningStatus | Drain pump running status | 排水水泵运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Drain pump running status of the device config table for the NetCol5000-A025.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.22 | hwNetCol5000A025OutdoorSprayTotalRuntime | Outdoor spray total runtime | 室外机喷淋累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor spray total runtime of the device config table for the NetCol5000-A025.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.23 | hwNetCol5000A025IndoorFan7RunningStatus | Indoor fan 7 running status | 室内风机7运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 7 running status of the device config table for the NetCol5000-A025.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.24 | hwNetCol5000A025IndoorFan8RunningStatus | Indoor fan 8 running status | 室内风机8运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 8 running status of the device config table for the NetCol5000-A025.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.25 | hwNetCol5000A025IndoorFan9RunningStatus | Indoor fan 9 running status | 室内风机9运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 9 running status of the device config table for the NetCol5000-A025.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.26 | hwNetCol5000A025IndoorFan10RunningStatus | Indoor fan 10 running status | 室内风机10运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 10 running status of the device config table for the NetCol5000-A025.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.27 | hwNetCol5000A025IndoorFan11RunningStatus | Indoor fan 11 running status | 室内风机11运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 11 running status of the device config table for the NetCol5000-A025.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.28 | hwNetCol5000A025IndoorFan12RunningStatus | Indoor fan 12 running status | 室内风机12运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 12 running status of the device config table for the NetCol5000-A025.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.29 | hwNetCol5000A025IndoorFan13RunningStatus | Indoor fan 13 running status | 室内风机13运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 13 running status of the device config table for the NetCol5000-A025.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.30 | hwNetCol5000A025IndoorFan14RunningStatus | Indoor fan 14 running status | 室内风机14运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 14 running status of the device config table for the NetCol5000-A025.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.33 | hwNetCol5000A025NumberOfWaterCooled |  |  | 0-Read_Only | 只读 | 0..225 | 0..225 | Number of water cooled of the device config table for the NetCol5000-A025.
1.3.6.1.4.1.2011.6.178.1.1.10.3.5.1.300 | hwNetCol5000A025Running2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol5000-A025.

## NetCol5000-A035
NetCol5000-A035
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.4 | NetCol5000A035 | NetCol5000-A035 | NetCol5000-A035 | / | / | / | / | The NetCol5000A035 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1 | hwNetCol5000A035RunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei NetCol5000A035 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.1 | hwNetCol5000A035RunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.2 | hwNetCol5000A035CommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Comm Status of the device config table for the NetCol5000A035. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.3 | hwNetCol5000A035SlotNO | / | / | 0-Read_Only | 只读 | 0..6 | / | Slot NO of the device config table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.4 | hwNetCol5000A035PortNO | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port NO of the device config table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.5 | hwNetCol5000A035SoftwareVer | Software version | 软件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | Software Ver of the device config table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.6 | hwNetCol5000A035ESN | ESN No. | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.7 | hwNetCol5000A035CompressorTotalTime | Compressor total runtime | 压缩机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.8 | hwNetCol5000A035Fan1TotalTime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan1 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.9 | hwNetCol5000A035Fan2TotalTime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan2 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.10 | hwNetCol5000A035Fan3TotalTime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan3 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.11 | hwNetCol5000A035Fan4TotalTime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan4 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.12 | hwNetCol5000A035Fan5TotalTime | Indoor fan 5 total runtime | 室内风机5累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan5 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.13 | hwNetCol5000A035Fan6TotalTime | Indoor fan 6 total runtime | 室内风机6累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan6 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.14 | hwNetCol5000A035Fan7TotalTime | Indoor fan 7 total runtime | 室内风机7累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan7 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.15 | hwNetCol5000A035Fan8TotalTime | Indoor fan 8 total runtime | 室内风机8累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fan8 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.16 | hwNetCol5000A035HumidifierTotalTime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.17 | hwNetCol5000A035HeaterTotalTime | Heater total runtime | 电加热累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Heater Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.18 | hwNetCol5000A035Pump1TotalTime | Cond pump 1 total runtime | 冷凝水泵1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Pump1 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.19 | hwNetCol5000A035Pump2TotalTime | Cond pump 2 total runtime | 冷凝水泵2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Pump2 Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.20 | hwNetCol5000A035PumpTotalTime | Cond pump total runtime | 冷凝水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Pump Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.21 | hwNetCol5000A035AirFilterTotalTime | Air filter total runtime | 过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Air Filter Total Time of the device config table for the NetCol5000A035. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.22 | hwNetCol5000A035UnitONOFFStatus | Unit on/off status | 机组开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Unit ON OFF Status. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.23 | hwNetCol5000A035RemoteONOFFStatus | On/Off status on remote | 远程开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Remote ON OFF Status. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.24 | hwNetCol5000A035CoolOutput | Cool output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Cool Output of the device config table for the NetCol5000A035. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.25 | hwNetCol5000A035FanOutput | Fan output | 风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Fan Output of the device config table for the NetCol5000A035. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.26 | hwNetCol5000A035HumidOutput | Humidity output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humid Output of the device config table for the NetCol5000A035. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.27 | hwNetCol5000A035HeatOutput | Heat output | 制热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Heat Output of the device config table for the NetCol5000A035. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.28 | hwNetCol5000A035TeamworkStatus | Teamwork status | 群控运行状态 | 0-Read_Only | 只读 | invalid(1), cool(2), heat(3), dehumid(4), humid(5), coolHumid(6), heatDehumid(7), heatHumid(8), coolDehumid(9), unknown(255) | [无效=1]/[制冷=2]/[加热=3]/[除湿=4]/[加湿=5]/[制冷且加湿=6]/[加热且除湿=7]/[加热且加湿=8]/[制冷且除湿=9] | Teamwork status. Value 1 indicates Invalid. Value 2 indicates Cool. Value 3 indicates Heat. Value 4 indicates Dehumid. Value 5 indicates Humid. Value 6 indicates Cool & humid. Value 7 indicates Heat & dehumid. Value 8 indicates heat & humid. Value 9 indicates cool & dehumid.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.29 | hwNetCol5000A035PowerVoltage | Power voltage | 电源电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Power Voltage of the device config table for the NetCol5000A035. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.30 | hwNetCol5000A035TempHumidCtrlType | T/H control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnAir(1), supplyAir(2), coldAisle(3), hotAisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | Temp Humid Ctrl Type. Value 1 indicates return-air. Value 2 indicates supply-air. Value 3 indicates cold-aisle. Value 4 indicates hot-aisle.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.31 | hwNetCol5000A035CurrentTemp | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Current Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.32 | hwNetCol5000A035CurrentHumidity | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Current Humidity of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.33 | hwNetCol5000A035SupplyairAvgTemp | Supply-air average temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply air Avg Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.34 | hwNetCol5000A035ReturnairAvgTemp | Return-air average temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return air Avg Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.35 | hwNetCol5000A035ColdAisleAvgTemp | Cold-aisle average temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold Aisle Avg Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.36 | hwNetCol5000A035HotAisleAvgTemp | Hot-aisle average temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot Aisle Avg Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.37 | hwNetCol5000A035SupplyAirAvgHumid | Supply-air average humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Supply Air Avg Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.38 | hwNetCol5000A035ReturnAirAvgHumid | Return-air average humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Return Air Avg Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.39 | hwNetCol5000A035ColdAisleAvgHumid | Cold-aisle average humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold Aisle Avg Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.40 | hwNetCol5000A035HotAisleAvgHumid | Hot-aisle average humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot Aisle Avg Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.41 | hwNetCol5000A035SupplyAir1Temp | Supply-air 1 temperature | 送风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply Air 1 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.42 | hwNetCol5000A035SupplyAir2Temp | Supply-air 2 temperature | 送风2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply Air 2 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.43 | hwNetCol5000A035SupplyAir3Temp | Supply-air 3 temperature | 送风3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply Air 3 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.44 | hwNetCol5000A035ReturnAir1Temp | Return-air 1 temperature | 回风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return Air 1 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.45 | hwNetCol5000A035ReturnAir2Temp | Return-air 2 temperature | 回风2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return Air 2 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.46 | hwNetCol5000A035ReturnAir3Temp | Return-air 3 temperature | 回风3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return Air 3 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.47 | hwNetCol5000A035ReturnAir3Humid | Return-air 3 humidity | 回风3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Return Air 3 Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.48 | hwNetCol5000A035ColdAisle1Temp | Cold-aisle 1 temperature | 冷通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold Aisle 1 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.49 | hwNetCol5000A035ColdAisle2Temp | Cold-aisle 2 temperature | 冷通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold Aisle 2 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.50 | hwNetCol5000A035ColdAisle3Temp | Cold-aisle 3 temperature | 冷通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold Aisle 3 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.51 | hwNetCol5000A035ColdAisle1Humid | Cold-aisle 1 humidity | 冷通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold Aisle 1 Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.52 | hwNetCol5000A035ColdAisle2Humid | Cold-aisle 2 humidity | 冷通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold Aisle 2 Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.53 | hwNetCol5000A035ColdAisle3Humid | Cold-aisle 3 humidity | 冷通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold Aisle 3 Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.54 | hwNetCol5000A035HotAisle1Temp | Hot-aisle 1 temperature | 热通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot Aisle 1 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.55 | hwNetCol5000A035HotAisle2Temp | Hot-aisle 2 temperature | 热通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot Aisle 2 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.56 | hwNetCol5000A035HotAisle3Temp | Hot-aisle 3 temperature | 热通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot Aisle 3 Temp of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.57 | hwNetCol5000A035HotAisle1Humid | Hot-aisle 1 humidity | 热通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot Aisle 1 Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.58 | hwNetCol5000A035HotAisle2Humid | Hot-aisle 2 humidity | 热通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot Aisle 2 Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.59 | hwNetCol5000A035HotAisle3Humid | Hot-aisle 3 humidity | 热通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot Aisle 3 Humid of the device config table for the NetCol5000A035. Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.60 | hwNetCol5000A035CompRunningStatus | Comp run status | 压缩机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Comp Running Status of the device config table for the NetCol5000A035. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.61 | hwNetCol5000A035LiquidSolenoidValve | Liquid solenoid valve | 液路电磁阀状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Liquid Solenoid Valve. Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.62 | hwNetCol5000A035IndoorFan1CtrlStatus | Indoor fan 1 control status | 室内风机1控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor Fan 1 Ctrl Status of the device config table for the NetCol5000A035. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.63 | hwNetCol5000A035IndoorFan2CtrlStatus | Indoor fan 2 control status | 室内风机2控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor Fan 2 Ctrl Status of the device config table for the NetCol5000A035. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.64 | hwNetCol5000A035OutdoorFanCtrlStatus | Outdoor fan control status | 室外风机控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Outdoor Fan Ctrl Status. Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.65 | hwNetCol5000A035HumidifierCtrlStatus | Humidifier control status | 加湿器控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidifier Ctrl Status of the device config table for the NetCol5000A035. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.66 | hwNetCol5000A035HeaterCtrlStatus | Elec heater control status | 电加热控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Heater Ctrl Status. Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.67 | hwNetCol5000A035PumpCtrlStatus | Cond pump control status | 冷凝水泵控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Pump Ctrl Status. Value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.68 | hwNetCol5000A035EquipELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | Equip ELabel of the device config table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.69 | hwNetCol5000A035HostFlag | Host identity | 主机标识 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | Host Flag. Value 1 indicates slave. Value 2 indicates master.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.70 | hwNetCol5000A035BaseinfoComplete | / | / | 0-Read_Only | 只读 | unreceived(1), received(2), unknown(255) | / | Baseinfo Complete. Value 1 indicates unreceived. Value 2 indicates received.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.71 | hwNetCol5000A035TeamworkAddr | / | / | 0-Read_Only | 只读 | 0..32 | / | Teamwork Addr of the device config table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.72 | hwNetCol5000A035Type | / | / | 0-Read_Only | 只读 | netcol5000a(1), netcol5000c(2), netcol8000a(3), netcol8000c(4), netcol5000aR2(5), netcol5000cf(6), netcol5000aHcv(7), netcol5000ssmb(8), unknown(255) | / | NetCol5000-A035 Type. Value 2 indicates netcol5000a. Value 3 indicates netcol5000c. Value 4 indicates netcol8000a. Value 5 indicates netcol8000c. Value 6 indicates netcol5000a_r2. Value 7 indicates netcol5000cf. Value 8 indicates netcol5000a_hcv. Value 9 indicates netcol5000ssmb.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.73 | hwNetCol5000A035EmsStatus | On/Off control | 开关机控制 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Ems Status. Value 1 indicates on. Value 2 indicates off.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.74 | hwNetCol5000A035ReturnairTemp | Return-air temperature set point | 回风温度设定点 | 1-Read_Write | 读写 | 180..450 | 180..450 | Returnair Temp of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.75 | hwNetCol5000A035SupplyairTemp | Supply-air temperature set point | 送风温度设定点 | 1-Read_Write | 读写 | 150..350 | 150..350 | Supplyair Temp of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.76 | hwNetCol5000A035ColdAisleTemp | Cold-aisle temperature set point | 冷通道温度设定点 | 1-Read_Write | 读写 | 150..350 | 150..350 | Cold Aisle Temp of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.77 | hwNetCol5000A035HotAisleTemp | Hot-aisle temperature set point | 热通道温度设定点 | 1-Read_Write | 读写 | 180..450 | 180..450 | Hot Aisle Temp of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.78 | hwNetCol5000A035ReturnairHumid | Return-air humidity set point | 回风湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Returnair Humid of the device config table for the NetCol5000A035. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.79 | hwNetCol5000A035SupplyairHumid | Supply-air humidity set point | 送风湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Supplyair Humid of the device config table for the NetCol5000A035. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.80 | hwNetCol5000A035ColdAisleHumid | Cold-aisle humidity set point | 冷通道湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Cold Aisle Humid of the device config table for the NetCol5000A035. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.81 | hwNetCol5000A035HotAisleHumid | Hot-aisle humidity set point | 热通道湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Hot Aisle Humid of the device config table for the NetCol5000A035. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.82 | hwNetCol5000A035ReturnairHTThreshold | Return-air HT threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Returnair HT Threshold of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.83 | hwNetCol5000A035ReturnairLTThreshold | Return-air LT threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Returnair LT Threshold of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.84 | hwNetCol5000A035SupplyairHTThreshold | Supply-air HT threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Supplyair HT Threshold of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.85 | hwNetCol5000A035SupplyairLTThreshold | Supply-air LT threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | Supplyair LT Threshold of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.86 | hwNetCol5000A035ColdAisleHTThreshold | Cold-aisle HT threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Cold Aisle HT Threshold of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.87 | hwNetCol5000A035HotAisleHTThreshold | Hot-aisle HT threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Hot Aisle HT Threshold of the device config table for the NetCol5000A035. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.88 | hwNetCol5000A035HighumidThreshold | Humidity high threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | Highumid Threshold of the device config table for the NetCol5000A035. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.89 | hwNetCol5000A035LowhumidThreshold | Humidity low threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | Lowhumid Threshold of the device config table for the NetCol5000A035. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.90 | hwNetCol5000A035ReturnairHTAction | Return-air HT action | 回风高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Returnair HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.91 | hwNetCol5000A035ReturnairLTAction | Return-air LT action | 回风低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Returnair LT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.92 | hwNetCol5000A035SupplyairHTAction | Supply-air HT action | 送风高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Supplyair HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.93 | hwNetCol5000A035SupplyairLTAction | Supply-air LT action | 送风低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Supplyair LT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.94 | hwNetCol5000A035ColdAisleHTAction | Cold-aisle HT action | 冷通道高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Cold Aisle HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.95 | hwNetCol5000A035HotAisleHTAction | Hot-aisle HT action | 热通道高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Hot Aisle HT Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.96 | hwNetCol5000A035HighumidAction | High humidity action | 高湿告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Highumid Action. Value 1 indicates disable. Value 2 indicates block. Value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.97 | hwNetCol5000A035LowhumidAction | Low humidity action | 低湿告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | Lowhumid Action. value 1 indicates disable. value 2 indicates block. value 3 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.98 | hwNetCol5000A035DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of the device config table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.110 | hwNetCol5000A035ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Modbus Address of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.111 | hwNetCol5000A035softwareversion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | The softwareversion of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.112 | hwNetCol5000A035CondPump1CtrlStatus | Cond pump 1 control status | 冷凝水泵1控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Cond Pump1 Ctrl Status: Value 1 indicates Close. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.113 | hwNetCol5000A035CondPump2CtrlStatus | Cond pump 2 control status | 冷凝水泵2控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Cond Pump2 Ctrl Status: Value 1 indicates Close. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.1.1.200 | hwNetCol5000A035RunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2 | hwNetCol5000A035RunningTable | / | / |  |  | / | / | The running table of Huawei NetCol5000A035 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.1 | hwNetCol5000A035RunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.2 | hwNetCol5000A035Indoorfan1runstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The Indoor fan 1 run status of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.3 | hwNetCol5000A035Indoorfan2runstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The Indoor fan 2 run status of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.4 | hwNetCol5000A035Indoorfan3runstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The Indoor fan 3 run status of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.5 | hwNetCol5000A035Indoorfan4runstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The Indoor fan 4 run status of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.6 | hwNetCol5000A035Indoorfan5runstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The Indoor fan 5 run status of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.7 | hwNetCol5000A035Indoorfan6runstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The Indoor fan 6 run status of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.8 | hwNetCol5000A035Indoorfan7runstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The Indoor fan 7 run status of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.9 | hwNetCol5000A035Indoorfan8runstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The Indoor fan 8 run status of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.2.1.100 | hwNetCol5000A035RunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running 2 row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3 | hwNetCol5000A035RunningAndConfig2Table | / | / |  |  | / | / | The running table of Huawei NetColPoe Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.1 | hwNetCol5000A035RunningAndConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.2 | hwNetCol5000A035Model | Model | 机型 | 0-Read_Only | 只读 | netCol5000A(1), netCol5000C(2), unknown(255) | [NetCol5000A=1]/[NetCol5000C=2] | The Model of NetCol5000A035. Value 1 indicates NetCol5000A. Value 2 indicates NetCol5000C.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.3 | hwNetCol5000A035Hardwareversion | / | / | 0-Read_Only | 只读 | 1..32 | / | The Hardware version of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.4 | hwNetCol5000A035Netcolpower | / | / | 0-Read_Only | 只读 | power20kw(1), power25kw(2), power30kw(3), power35kw(4), power50kw(5), unknown(255) | / | The Netcol power of NetCol5000A035. Value 1 indicates 20KW. Value 2 indicates 25KW. Value 3 indicates 30KW. Value 4 indicates 35KW. Value 5 indicates 50KW.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.5 | hwNetCol5000A035Numberofindoorfans | Number of indoor fans | 风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of indoor fans of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.6 | hwNetCol5000A035Numberofcompressors | Number of compressors | 压缩机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of compressors of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.7 | hwNetCol5000A035Numberofheaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of heaters of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.8 | hwNetCol5000A035Numberofhumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of humidifiers of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.9 | hwNetCol5000A035Numberofcondpumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of cond pumps of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.10 | hwNetCol5000A035Numberofpsu | / | / | 0-Read_Only | 只读 | 0..254 | / | The Number of psu of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.11 | hwNetCol5000A035PhaseAvoltage | / | / | 0-Read_Only | 只读 | 0..1000 | / | The Phase A voltage of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.12 | hwNetCol5000A035PhaseBvoltage | / | / | 0-Read_Only | 只读 | 0..1000 | / | The Phase B voltage of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.13 | hwNetCol5000A035PhaseCvoltage | / | / | 0-Read_Only | 只读 | 0..1000 | / | The Phase C voltage of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.14 | hwNetCol5000A035Powerfrequency | / | / | 0-Read_Only | 只读 | 0..200 | / | The Power frequency of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.15 | hwNetCol5000A035Returnair2humidity | / | / | 0-Read_Only | 只读 | 0..1000 | / | The Return-air 2 humidity of NetCol5000A035.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.16 | hwNetCol5000A035Compcontrolstatus | / | / | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | / | The Comp control status of NetCol5000A035. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.17 | hwNetCol5000A035Indoorfancontrolstatus | / | / | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | / | The Indoor fan control status of NetCol5000A035. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.18 | hwNetCol5000A035Condpump1controlstatus | Cond pump 1 control status | 冷凝水泵1控制状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | The Cond pump 1 control status of NetCol5000A035. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.19 | hwNetCol5000A035Condpump2controlstatus | Cond pump 2 control status | 冷凝水泵2控制状态 | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | [关闭=1]/[开启=2] | The Cond pump 2 control status of NetCol5000A035. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.20 | hwNetCol5000A035Typeofport | Type of port | 端口类型 | 1-Read_Write | 读写 | uart(1), pth(2), tcp(3), unknown(255) | [UART=1]/[PTH=2]/[TCP=3] | The Type of port of NetCol5000A035. Value 1 indicates uart. Value 2 indicates pth. Value 3 indicates tcp.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.21 | hwNetCol5000A035Baudrate | Baud rate | 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate19200(2), unknown(255) | [9600=1]/[19200=2] | The Baud rate of NetCol5000A035. Value 1 indicates 9600. Value 2 indicates 19200.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.22 | hwNetCol5000A035Commaddress | Comm address | 通信地址 | 1-Read_Write | 读写 | 1..255 | 1..255 | The Communication address of NetCol5000A035.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.23 | hwNetCol5000A035Teamworkmode | Teamwork mode | 群控模式 | 1-Read_Write | 读写 | smart(1), iCooling(2), unknown(255) | [智能=1]/[iCooling=2] | The Teamwork mode of NetCol5000A035. Value 1 indicates smart. Value 2 indicates iCooling.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.24 | hwNetCol5000A035L1OrL2linkageenable | L1/L2 linkage enable | L1L2联动使能标志 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The L1&L2 linkage enable flag of NetCol5000A035. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.27 | hwNetCol5000A035CoolingCapacity | Rated cooling capacity (cooling power) | 额定的制冷容量（制冷功率） | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Cooling Capacityof NetCol5000A035.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.4.3.1.100 | hwNetCol5000A035RunningAndConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running 2 row status of Device.

## NetCol5000-C030
NetCol5000-C030
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.5 | NetCol5000C030 | NetCol5000-C030 | NetCol5000-C030 | / | / | / | / | The NetCol5000 C030 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1 | hwNetCol5000C030RunningAndConfig1Table | / | / |  |  | / | / | The running and config table of Huawei NetCol5000 C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.1 | hwNetCol5000C030RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.2 | hwNetCol5000C030CommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The NetCol5000C030 Comm Status: value 1 indicates normal, value 2 indicates abnormal,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.7 | hwNetCol5000C030UnitOnOffStatus | Unit on/off status | 机组开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | The NetCol5000C030 Unit On Off Status: value 1 indicates off, value 2 indicates on,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.8 | hwNetCol5000C030OnOffStatusOnRemote | On/Off status on remote | 远程开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | The NetCol5000C030 On Off Status On Remote: value 1 indicates off, value 2 indicates on,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.9 | hwNetCol5000C030CoolOutput | Cool output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The NetCol5000C030 Cool Output. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.10 | hwNetCol5000C030FanOutput | Fan output | 风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The NetCol5000C030 Fan Output. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.11 | hwNetCol5000C030TeamworkStatus | Teamwork status | 群控运行状态 | 0-Read_Only | 只读 | invalid(1), cool(2), heat(3), dehumid(4), humid(5), coolAndHumid(6), heaAndDehumid(7), heatAndHumid(8), coolAndDehumid(9), unknown(255) | [无效=1]/[制冷=2]/[加热=3]/[除湿=4]/[加湿=5]/[制冷且加湿=6]/[加热且除湿=7]/[加热且加湿=8]/[制冷且除湿=9] | The NetCol5000C030 Teamwork Status: value 1 indicates invalid, value 2 indicates cool, value 3 indicates heat, value 4 indicates dehumid, value 5 indicates humid, value 6 indicates cool and humid, value 7 indicates hea and dehumid, value 8 indicates hea and humid, value 9 indicates coo and dehumid,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.12 | hwNetCol5000C030TotalnumberofActualUnits | Total number of actual units | 本群组实际机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The NetCol5000C030 Total number Of Actual Units.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.13 | hwNetCol5000C030NumberofActiveUnits | Number of active units | 本群组实际运行机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The NetCol5000C030 Number Of Active Units.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.14 | hwNetCol5000C030NumberofStandbyUnits | Number of standby units | 本群组实际备机机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The NetCol5000C030 Number Of Standby Units.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.15 | hwNetCol5000C030TotalNumberofUnits | Total number of units | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | The NetCol5000C030 Total number Of Units.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.16 | hwNetCol5000C030NumberofRunningUnits | Number of running units | 本群组运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | The NetCol5000C030 Number Of Running Units.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.17 | hwNetCol5000C030GroupTemp | Group temperature | 群组温度 | 0-Read_Only | 只读 | -990..990 | -990..990 | The NetCol5000C030 Avg Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.18 | hwNetCol5000C030GroupHumidity | Group humidity | 群组湿度 | 0-Read_Only | 只读 | 0..990 | 0..990 | The NetCol5000C030 Avg Humidity. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.19 | hwNetCol5000C030RequiredCoolingCapacity | Required cooling capacity | 群组总冷量需求 | 0-Read_Only | 只读 | -5000..5000 | -5000..5000 | The NetCol5000C030 Required Cooling capacity. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.20 | hwNetCol5000C030RequiredHumidity | Required humidity | 群组总湿度需求 | 0-Read_Only | 只读 | -5000..5000 | -5000..5000 | The NetCol5000C030 Required Humidity. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.21 | hwNetCol5000C030PSU1InputType | PSU 1 input type | 电源模块1输入类型 | 0-Read_Only | 只读 | dc(1), ac(2), unknown(255) | [直流=1]/[交流=2] | The NetCol5000C030 PSU 1 Input Type: value 1 indicates dc, value 2 indicates ac,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.22 | hwNetCol5000C030PSU1InputVoltage | PSU 1 input voltage | 电源模块1输入电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | The NetCol5000C030 PSU 1 Input Voltage. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.23 | hwNetCol5000C030PSU1InputCurrent | PSU 1 input current | 电源模块1输入电流 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 PSU 1 Input Current. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.24 | hwNetCol5000C030PSU1OutputVoltage | PSU 1 output voltage | 电源模块1输出电压 | 0-Read_Only | 只读 | 0..700 | 0..700 | The NetCol5000C030 PSU 1 Output Voltage. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.25 | hwNetCol5000C030PSU1OutputCurrent | PSU 1 output current | 电源模块1输出电流 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The NetCol5000C030 PSU 1 Output Current. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.26 | hwNetCol5000C030PSU1InputPower | PSU 1 input power | 电源模块1输入功率 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The NetCol5000C030 PSU 1 Input Power. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.27 | hwNetCol5000C030PSU2InputType | PSU 2 input type | 电源模块2输入类型 | 0-Read_Only | 只读 | dc(1), ac(2), unknown(255) | [直流=1]/[交流=2] | The NetCol5000C030 PSU 2 Input Type: value 1 indicates dc, value 2 indicates ac,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.28 | hwNetCol5000C030PSU2InputVoltage | PSU 2 input voltage | 电源模块2输入电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | The NetCol5000C030 PSU 2 Input Voltage. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.29 | hwNetCol5000C030PSU2InputCurrent | PSU 2 input current | 电源模块2输入电流 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 PSU 2 Input Current. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.30 | hwNetCol5000C030PSU2OutputVoltage | PSU 2 output voltage | 电源模块2输出电压 | 0-Read_Only | 只读 | 0..700 | 0..700 | The NetCol5000C030 PSU 2 Output Voltage. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.31 | hwNetCol5000C030PSU2OutputCurrent | PSU 2 output current | 电源模块2输出电流 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The NetCol5000C030 PSU 2 Output Current. Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.32 | hwNetCol5000C030PSU2InputPower | PSU 2 input power | 电源模块2输入功率 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The NetCol5000C030 PSU 2 Input Power. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.33 | hwNetCol5000C030TemperatureandHumidityControlType | T/H control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnAir(1), supplyAir(2), coldAisle(3), hotAisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | The NetCol5000C030 T/H cOntrol Type: value 1 indicates return air, value 2 indicates supply air, value 3 indicates cold aisle, value 4 indicates hot aisle,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.34 | hwNetCol5000C030CurrentTemp | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 Current Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.35 | hwNetCol5000C030CurrentHumid | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 Current Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.36 | hwNetCol5000C030SupplyAirAvgTemp | Supply-air average temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 SupplyAir Avg Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.37 | hwNetCol5000C030ReturnAirAvgTemp | Return-air average temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 ReturnAir Avg Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.38 | hwNetCol5000C030ColdAisleAvgTemp | Cold-aisle average temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The NetCol5000C030 ColdAisle Avg Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.39 | hwNetCol5000C030HotAisleAvgTemp | Hot-aisle average temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The NetCol5000C030 HotAisle Avg Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.40 | hwNetCol5000C030SupplyAirAvgHumid | Supply-air average humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 SupplyAir Avg Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.41 | hwNetCol5000C030ReturnAirAvgHumid | Return-air average humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 ReturnAir Avg Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.42 | hwNetCol5000C030ColdAisleAvgHumid | Cold-aisle average humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 ColdAisle Avg Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.43 | hwNetCol5000C030HotAisleAvgHumid | Hot-aisle average humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 HotAisle Avg Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.44 | hwNetCol5000C030SupplyAir1Temp | Supply-air 1 temperature | 送风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 SupplyAir 1 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.45 | hwNetCol5000C030SupplyAir2Temp | Supply-air 2 temperature | 送风2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 SupplyAir 2 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.46 | hwNetCol5000C030ReturnAir1Temp | Return-air 1 temperature | 回风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 ReturnAir 1 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.47 | hwNetCol5000C030ReturnAir2Temp | Return-air 2 temperature | 回风2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 ReturnAir 2 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.48 | hwNetCol5000C030ColdAisle1Temp | Cold-aisle 1 temperature | 冷通道1温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The NetCol5000C030 ColdAisle 1 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.49 | hwNetCol5000C030ColdAisle2Temp | Cold-aisle 2 temperature | 冷通道2温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The NetCol5000C030 ColdAisle 2 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.50 | hwNetCol5000C030ColdAisle3Temp | Cold-aisle 3 temperature | 冷通道3温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The NetCol5000C030 ColdAisle 3 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.51 | hwNetCol5000C030ColdAisle1Humid | Cold-aisle 1 humidity | 冷通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 ColdAisle 1 Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.52 | hwNetCol5000C030ColdAisle2Humid | Cold-aisle 2 humidity | 冷通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 ColdAisle 2 Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.53 | hwNetCol5000C030ColdAisle3Humid | Cold-aisle 3 humidity | 冷通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 ColdAisle 3 Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.54 | hwNetCol5000C030HotAisle1Temp | Hot-aisle 1 temperature | 热通道1温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The NetCol5000C030 HotAisle 1 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.55 | hwNetCol5000C030HotAisle2Temp | Hot-aisle 2 temperature | 热通道2温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The NetCol5000C030 HotAisle 2 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.56 | hwNetCol5000C030HotAisle3Temp | Hot-aisle 3 temperature | 热通道3温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The NetCol5000C030 HotAisle 3 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.57 | hwNetCol5000C030HotAisle1Humid | Hot-aisle 1 humidity | 热通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 HotAisle 1 Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.58 | hwNetCol5000C030HotAisle2Humid | Hot-aisle 2 humidity | 热通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 HotAisle 2 Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.59 | hwNetCol5000C030HotAisle3Humid | Hot-aisle 3 humidity | 热通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 HotAisle 3 Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.60 | hwNetCol5000C030IndoorFan1RunStatus | Indoor fan 1 run status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Indoor Fan 1 Run Status. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.61 | hwNetCol5000C030IndoorFan2RunStatus | Indoor fan 2 run status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Indoor Fan 2 Run Status. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.62 | hwNetCol5000C030IndoorFan3RunStatus | Indoor fan 3 run status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Indoor Fan 3 Run Status. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.63 | hwNetCol5000C030IndoorFan4RunStatus | Indoor fan 4 run status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Indoor Fan 4 Run Status. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.64 | hwNetCol5000C030IndoorFan5RunStatus | Indoor fan 5 run status | 室内风机5运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Indoor Fan 5 Run Status. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.65 | hwNetCol5000C030IndoorFan6RunStatus | Indoor fan 6 run status | 室内风机6运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Indoor Fan 6 Run Status. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.66 | hwNetCol5000C030IndoorFan7RunStatus | Indoor fan 7 run status | 室内风机7运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Indoor Fan 7 Run Status. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.67 | hwNetCol5000C030IndoorFan8RunStatus | Indoor fan 8 run status | 室内风机8运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Indoor Fan 8 Run Status. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.68 | hwNetCol5000C030COndpump1CtrlStatus | Cond pump 1 control status | 冷凝水泵1控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | The NetCol5000C030 COnd pump 1 Ctrl Status: value 1 indicates close, value 2 indicates open,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.69 | hwNetCol5000C030COndpump2CtrlStatus | Cond pump 2 control status | 冷凝水泵2控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | The NetCol5000C030 COnd pump 2 Ctrl Status: value 1 indicates close, value 2 indicates open,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.70 | hwNetCol5000C030CWValveRunStatus | CW valve run status | 冷冻水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 CW Valve Run Status. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.71 | hwNetCol5000C030SupplyWaterTemp | Supply-water temperature | 供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 SupplyWater Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.72 | hwNetCol5000C030ReturnWaterTemp | Return-water temperature | 回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 ReturnWater Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.84 | hwNetCol5000C030IndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Indoor Fan 1 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.85 | hwNetCol5000C030IndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Indoor Fan 2 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.86 | hwNetCol5000C030IndoorFan3TotalRuntime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Indoor Fan 3 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.87 | hwNetCol5000C030IndoorFan4TotalRuntime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Indoor Fan 4 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.88 | hwNetCol5000C030IndoorFan5TotalRuntime | Indoor fan 5 total runtime | 室内风机5累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Indoor Fan 5 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.89 | hwNetCol5000C030IndoorFan6TotalRuntime | Indoor fan 6 total runtime | 室内风机6累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Indoor Fan 6 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.90 | hwNetCol5000C030IndoorFan7TotalRuntime | Indoor fan 7 total runtime | 室内风机7累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Indoor Fan 7 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.91 | hwNetCol5000C030IndoorFan8TotalRuntime | Indoor fan 8 total runtime | 室内风机8累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Indoor Fan 8 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.92 | hwNetCol5000C030COndpump1TotalRuntime | Cond pump 1 total runtime | 冷凝水泵1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 COnd pump 1 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.93 | hwNetCol5000C030COndpump2TotalRuntime | Cond pump 2 total runtime | 冷凝水泵2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 COnd pump 2 Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.94 | hwNetCol5000C030AirFilterTotalRuntime | Air filter total runtime | 过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Air Filter Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.95 | hwNetCol5000C030CWValveTotalRuntime | CW valve total runtime | 冷冻水阀累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 CW Valve Total Runtime. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.96 | hwNetCol5000C030IPAddress | IP address | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 IP Address
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.97 | hwNetCol5000C030ESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | The NetCol5000C030 ESN
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.99 | hwNetCol5000C030SoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | The NetCol5000C030 Software Version
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.100 | hwNetCol5000C030MAC | / | / | 0-Read_Only | 只读 | 0..28 | / | The NetCol5000C030 MAC
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.103 | hwNetCol5000C030HumidifierTotalRuntime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Humidifier Total Runtime SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.104 | hwNetCol5000C030ElecHeaterTotalRuntime | Elec heater total runtime | 电加热累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The NetCol5000C030 Elec Heater Total Runtime SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.105 | hwNetCol5000C030HumidOutp | Humidity output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The NetCol5000C030 Humid Outp SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.106 | hwNetCol5000C030HeatOutp | Heat output | 制热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The NetCol5000C030 Heat Outp SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.107 | hwNetCol5000C030TransfOutpVolt | Transf output voltage | 变压器输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The NetCol5000C030 Transf Outp Volt Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.108 | hwNetCol5000C030HumidifierCtrlStatus | Humidifier control status | 加湿器控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The NetCol5000C030 Humidifier Ctrl Status SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.109 | hwNetCol5000C030ElecHeaterCtrlStatus | Elec heater control status | 电加热控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | The NetCol5000C030 Elec Heater Ctrl Status: value 1 indicates close, value 2 indicates open,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.110 | hwNetCol5000C030OnOffStatusOnEMS | On/Off status on EMS | 网管开关机状态 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [开机=1]/[关机=2] | The NetCol5000C030 On off status on EMS: value 1 indicates off, value 2 indicates on,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.111 | hwNetCol5000C030ReturnAirTempSetPoint | Return-air temperature set point | 回风温度设定点 | 1-Read_Write | 读写 | 180..450 | 180..450 | The NetCol5000C030 Return-air temp set point Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.112 | hwNetCol5000C030SupplyAirTempSetPoint | Supply-air temperature set point | 送风温度设定点 | 1-Read_Write | 读写 | 150..350 | 150..350 | The NetCol5000C030 Supply-air temp set point Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.113 | hwNetCol5000C030ColdAisleTempSetPoint | Cold-aisle temperature set point | 冷通道温度设定点 | 1-Read_Write | 读写 | 150..350 | 150..350 | The NetCol5000C030 Cold-aisle temp set point Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.114 | hwNetCol5000C030HotAisleTempSetPoint | Hot-aisle temperature set point | 热通道温度设定点 | 1-Read_Write | 读写 | 180..450 | 180..450 | The NetCol5000C030 Hot-aisle temp set point Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.115 | hwNetCol5000C030ReturnAirHumidSetPoint | Return-air humidity set point | 回风湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | The NetCol5000C030 Return-air humid set point Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.116 | hwNetCol5000C030SupplyAirHumidSetPoint | Supply-air humidity set point | 送风湿度设定点 | 1-Read_Write | 读写 | 200..800 | 200..800 | The NetCol5000C030 Supply-air humid set point Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.117 | hwNetCol5000C030ColdAisleHumidSetPoint | Cold-aisle humidity set point | 冷通道湿度设定点 | 1-Read_Write | 读写 | 200..800 | 200..800 | The NetCol5000C030 Cold-aisle humid set point Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.118 | hwNetCol5000C030HotAisleHumidSetPoint | Hot-aisle humidity set point | 热通道湿度设定点 | 1-Read_Write | 读写 | 150..550 | 150..550 | The NetCol5000C030 Hot-aisle humid set point Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.119 | hwNetCol5000C030ReturnAirHTThreshold | Return-air HT threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | The NetCol5000C030 Return-air HT threshold Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.120 | hwNetCol5000C030ReturnAirLTThreshold | Return-air LT threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | The NetCol5000C030 Return-air LT threshold Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.121 | hwNetCol5000C030SupplyAirHTThreshold | Supply-air HT threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The NetCol5000C030 Supply-air HT threshold Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.122 | hwNetCol5000C030SupplyAirLTThreshold | Supply-air LT threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | The NetCol5000C030 Supply-air LT threshold Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.123 | hwNetCol5000C030ColdAisleHTThreshold | Cold-aisle HT threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The NetCol5000C030 Cold-aisle HT threshold Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.124 | hwNetCol5000C030ColdAisleLTThreshold | Cold-aisle LT threshold | 冷通道低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | The NetCol5000C030 Cold-aisle LT threshold Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.125 | hwNetCol5000C030HotAisleHTThreshold | Hot-aisle HT threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | The NetCol5000C030 Hot-aisle HT threshold Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.126 | hwNetCol5000C030HotAisleLTThreshold | Hot-aisle LT threshold | 热通道低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | The NetCol5000C030 Hot-aisle LT threshold Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.127 | hwNetCol5000C030HumidhighThreshold | Humidity high threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | The NetCol5000C030 Humid high threshold Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.128 | hwNetCol5000C030HumidlowThreshold | Humidity low threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | The NetCol5000C030 Humid low threshold Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.129 | hwNetCol5000C030ReturnAirHTAction | Return-air HT action | 回风高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Return-air HT action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.130 | hwNetCol5000C030ReturnAirLTAction | Return-air LT action | 回风低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Return-air LT action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.131 | hwNetCol5000C030SupplyAirHTAction | Supply-air HT action | 送风高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Supply-air HT action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.132 | hwNetCol5000C030SupplyAirLTAction | Supply-air LT action | 送风低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Supply-air LT action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.133 | hwNetCol5000C030ColdAisleHTAction | Cold-aisle HT action | 冷通道高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Cold-aisle HT action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.134 | hwNetCol5000C030ColdAisleLTAction | Cold-aisle LT action | 冷通道低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Cold-aisle LT action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.135 | hwNetCol5000C030HotAisleHTAction | Hot-aisle HT action | 热通道高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Hot-aisle HT action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.136 | hwNetCol5000C030HotAisleLTAction | Hot-aisle LT action | 热通道低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Hot-aisle LT action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.137 | hwNetCol5000C030HighHumidityAction | High humidity action | 高湿告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 High humidity action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.138 | hwNetCol5000C030LowHumidityAction | Low humidity action | 低湿告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The NetCol5000C030 Low humidity action: value 1 indicates disable, value 2 indicates block, value 3 indicates enable,
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.139 | hwNetCol5000C030IndoorFan1ExceedRuntimeThreshold | Indoor fan 1 exceed runtime threshold | 室内风机1运行超时告警阈值 | 1-Read_Write | 读写 | 30000..80000 | 30000..80000 | The NetCol5000C030 Indoor fan 1 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.140 | hwNetCol5000C030IndoorFan2ExceedRuntimeThreshold | Indoor fan 2 exceed runtime threshold | 室内风机2运行超时告警阈值 | 1-Read_Write | 读写 | 30000..80000 | 30000..80000 | The NetCol5000C030 Indoor fan 2 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.141 | hwNetCol5000C030IndoorFan3ExceedRuntimeThreshold | Indoor fan 3 exceed runtime threshold | 室内风机3运行超时告警阈值 | 1-Read_Write | 读写 | 30000..80000 | 30000..80000 | The NetCol5000C030 Indoor fan 3 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.142 | hwNetCol5000C030IndoorFan4ExceedRuntimeThreshold | Indoor fan 4 exceed runtime threshold | 室内风机4运行超时告警阈值 | 1-Read_Write | 读写 | 30000..80000 | 30000..80000 | The NetCol5000C030 Indoor fan 4 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.143 | hwNetCol5000C030IndoorFan5ExceedRuntimeThreshold | Indoor fan 5 exceed runtime threshold | 室内风机5运行超时告警阈值 | 1-Read_Write | 读写 | 30000..80000 | 30000..80000 | The NetCol5000C030 Indoor fan 5 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.144 | hwNetCol5000C030IndoorFan6ExceedRuntimeThreshold | Indoor fan 6 exceed runtime threshold | 室内风机6运行超时告警阈值 | 1-Read_Write | 读写 | 30000..80000 | 30000..80000 | The NetCol5000C030 Indoor fan 6 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.145 | hwNetCol5000C030IndoorFan7ExceedRuntimeThreshold | Indoor fan 7 exceed runtime threshold | 室内风机7运行超时告警阈值 | 1-Read_Write | 读写 | 30000..80000 | 30000..80000 | The NetCol5000C030 Indoor fan 7 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.146 | hwNetCol5000C030IndoorFan8ExceedRuntimeThreshold | Indoor fan 8 exceed runtime threshold | 室内风机8运行超时告警阈值 | 1-Read_Write | 读写 | 30000..80000 | 30000..80000 | The NetCol5000C030 Indoor fan 8 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.147 | hwNetCol5000C030CondPump1ExceedRuntimeThreshold | Cond pump 1 exceed runtime threshold | 冷凝水泵1运行超时告警阈值 | 1-Read_Write | 读写 | 1000..50000 | 1000..50000 | The NetCol5000C030 Cond pump 1 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.148 | hwNetCol5000C030CondPump2ExceedRuntimeThreshold | Cond pump 2 exceed runtime threshold | 冷凝水泵2运行超时告警阈值 | 1-Read_Write | 读写 | 1000..50000 | 1000..50000 | The NetCol5000C030 Cond pump 2 exceed runtime threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.152 | hwNetCol5000C030DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The NetCol5000C030 Device Name
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.154 | hwNetCol5000C030HumidifierExceedRuntimeThreshold | Humidifier exceed runtime threshold | 加湿器运行超时告警阈值 | 1-Read_Write | 读写 | 2000..4000 | 2000..4000 | The NetCol5000C030 Humidifier Exceed Runtime Threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.155 | hwNetCol5000C030ElecHeaterExceedRuntimeThreshold | Elec heater exceed runtime threshold | 电加热运行超时告警阈值 | 1-Read_Write | 读写 | 20000..40000 | 20000..40000 | The NetCol5000C030 Elec Heater Exceed Runtime Threshold SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.156 | hwNetCol5000C030ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The NetCol5000C030 ModbusAddress.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.157 | hwNetCol5000C030PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The NetCol5000C030 PortNo.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.158 | hwNetCol5000C030ReturnAir3Temp | Return-air 3 temperature | 回风3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 ReturnAir 3 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.159 | hwNetCol5000C030ReturnAir4Temp | Return-air 4 temperature | 回风4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The NetCol5000C030 ReturnAir 4 Temp. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.160 | hwNetCol5000C030ReturnAir3Humid | Return-air 3 humidity | 回风3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 ReturnAir 3 Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.161 | hwNetCol5000C030ReturnAir4Humid | Return-air 4 humidity | 回风4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The NetCol5000C030 ReturnAir 4 Humid. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.5.1.1.198 | hwNetCol5000C030RunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the NetCol5000 C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.2 | hwNetCol5000C030RunningAndConfig2Table | / | / |  |  | / | / | The running and config table of Huawei NetCol5000 C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.2.1.1 | hwNetCol5000C030RunningAndConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.2.1.2 | hwNetCol5000C030CondPumpCtrlStatus | Cond pump control status | 冷凝水泵控制状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | The cond pump control statues of the NetCol5000 C030: value 1 indicates close. Value 2 indicates open.
1.3.6.1.4.1.2011.6.178.1.1.10.5.2.1.3 | hwNetCol5000C030CondPumpTotalRuntime | Cond pump total runtime | 冷凝水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The cond pump total runtime of the NetCol5000 C030. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.2.1.4 | hwNetCol5000C030CondPumpExceedRuntimeThreshold | Cond pump exceed runtime threshold | 冷凝水泵运行超时告警阈值 | 1-Read_Write | 读写 | 1000..50000 | 1000..50000 | The cond pump exceed rutime threshold of the NetCol5000 C030. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.5.2.1.198 | hwNetCol5000C030RunningAndConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the NetCol5000 C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3 | hwNetCol5000C030RunningAndConfig3Table | / | / |  |  | / | / | The running and config table of Huawei NetCol5000 C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.1 | hwNetCol5000C030RunningAndConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.2 | hwNetCol5000C030Numberofcondpumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The NetCol5000C030 Number of condpumps.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.3 | hwNetCol5000C030NumberofCWvalves | Number of CW valves | 冷冻水阀数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The NetCol5000C030 Number of CWvalves.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.4 | hwNetCol5000C030NumberofPSU | Number of PSU | 电源模块数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The NetCol5000C030 Number of PSU.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.5 | hwNetCol5000C030Hosttag | Host identity | 主机标志 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | Host tag: Value 1 indicates slave. Value 2 indicates master.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.6 | hwNetCol5000C030Configreceivedtag | Basic information received | 基本信息已接收标志 | 0-Read_Only | 只读 | unreceived(1), received(2), unknown(255) | [未接收=1]/[已接收=2] | Config received tag: Value 1 indicates unreceived. Value 2 indicates received.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.7 | hwNetCol5000C030AcceptableMaxtempofwatersupply | Acceptable max temperature of water supply | 可接受最高供水温度 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | The Accep table Max temp of water supply of NetCol5000C030.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.8 | hwNetCol5000C030Maxcoolingcapacity | Max cooling capacity | 空调最大制冷量 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | The Max cooling capacity of NetCol5000C030.Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.9 | hwNetCol5000C030Electric | Electricity | 电量 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Electric of NetCol5000C030.Multiple:10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.10 | hwNetCol5000C030Power | Power | 功率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | The Power of NetCol5000C030.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.11 | hwNetCol5000C030TeamworkUnitAddress | Air conditioner address | 机组地址 | 0-Read_Only | 只读 | 1..32 | 1..32 | The Teamwork Unit Address of NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.12 | hwNetCol5000C030CoolingPower | Rated cooling capacity (cooling power) | 额定的制冷容量（制冷功率） | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Cooling Power of NetCol5000C030.Multiple:10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.13 | hwNetCol5000C030WaterChillingunitSetTemp | water chilling unit set temperature | 冷水机控制目标温度 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | The Water Chillingunit Set Temp of NetCol5000C030.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.14 | hwNetCol5000C030Numberofindoorfans | Number of indoor fans | 风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of indoorfans of NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.15 | hwNetCol5000C030Numberofheaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of heaters of NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.16 | hwNetCol5000C030Numberofhumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of humidifiers of NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.17 | hwNetCol5000C030Current | Current | 电流 | 0-Read_Only | 只读 | -100000..100000 | -100000..100000 | The Current of NetCol5000C030.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.18 | hwNetCol5000C030Elabel | E-label | 电子标签 | 0-Read_Only | 只读 | 1..2048 | 1..2048 | The Elabel of NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.19 | hwNetCol5000C030HardwareVersion | / | / | 0-Read_Only | 只读 | 1..32 | / | The Insert mode of NetCol5000C030.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.20 | hwNetCol5000C030Insertmode | Insert mode | NetColLCU接入方式 | 1-Read_Write | 读写 | other(1), rtu(2), tcp(3), unknown(255) | [其他=1]/[RTU=2]/[TCP=3] | The Hardware version of NetCol5000C030. Value 1 indicates other. Value 2 indicates rtu. Value 3 indicates tcp.
1.3.6.1.4.1.2011.6.178.1.1.10.5.3.1.100 | hwNetCol5000C030RunningAndConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the NetCol5000 C030.

## SUNRISE-SCU-20K
依米康SCU-20K
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.6 | SUNRISESCU20K | SUNRISE-SCU-20K | 依米康SCU-20K | / | / | / | / | The SUNRISE_SCU_20K Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1 | hwSUNRISESCU20KRunningAndConfigTable | / | / |  |  | / | / | The running and config table of Huawei SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.1 | hwSUNRISESCU20KRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.2 | hwSUNRISESCU20KCommState | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The CommState of the SUNRISE_SCU_20K: Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.3 | hwSUNRISESCU20KFanState | Fan status | 风机状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [开启=1]/[关闭=2] | The Fan State of the SUNRISE_SCU_20K: Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.4 | hwSUNRISESCU20KHotState | Heating status | 制热状态 | 0-Read_Only | 只读 | yes(1), no(2), unknown(255) | [是=1]/[否=2] | The Hot State of the SUNRISE_SCU_20K: Value 1 indicates Hot State. Value 2 indicates No HotState.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.5 | hwSUNRISESCU20KCoolState | Cooling status | 制冷状态 | 0-Read_Only | 只读 | yes(1), no(2), unknown(255) | [是=1]/[否=2] | The Cool State of the SUNRISE_SCU_20K: Value 1 indicates Cold State. Value 2 indicates Not Cold State.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.6 | hwSUNRISESCU20KHumidiferState | Humidification status | 加湿状态 | 0-Read_Only | 只读 | yes(1), no(2), unknown(255) | [是=1]/[否=2] | The Humidifer State of the SUNRISE_SCU_20K: Value 1 indicates Humidifier State. Value 2 indicates Not Humidifier State.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.7 | hwSUNRISESCU20KDehumidiferState | Dehumidification status | 除湿状态 | 0-Read_Only | 只读 | yes(1), no(2), unknown(255) | [是=1]/[否=2] | The Dehumidifer State of the SUNRISE_SCU_20K: Value 1 indicates Dehumidifier State. Value 2 indicates Not Dehumidifier State.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.8 | hwSUNRISESCU20KTeamworkMode | Standalone/Teamwork control mode | 单机/群控模式 | 0-Read_Only | 只读 | single(1), teamwork(2), unknown(255) | [单机=1]/[群控=2] | The Teamwork Mode of the SUNRISE_SCU_20K: Value 1 indicates Single. Value 2 indicates Teamwork.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.9 | hwSUNRISESCU20KReturnAirTemp | Return air temperature | 回风温度值 | 0-Read_Only | 只读 | -2731..2147483647 | -2731..2147483647 | The Return Air Temp of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.10 | hwSUNRISESCU20KReturnAirHumid | Return air humidity | 回风湿度值 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Return Air Humid of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.11 | hwSUNRISESCU20KValveRuntime | Valve runtime | 冷冻水阀运行时间 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Valve Runtime of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.12 | hwSUNRISESCU20KFanRuntime | Fan runtime | 风机运行时间 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Fan RuntimeL of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.15 | hwSUNRISESCU20KSupplyAirTemp | Measured supply air temperature | 送风温度测量值 | 0-Read_Only | 只读 | -2731..2147483647 | -2731..2147483647 | The Supply Air Temp of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.16 | hwSUNRISESCU20KSupplyAirHumid | Measured supply air humidity | 送风湿度测量值 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Supply Air Humid of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.17 | hwSUNRISESCU20KHumidiferElectric | Humidification current | 加湿电流 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Humidifer Electric of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.18 | hwSUNRISESCU20KConductivity | Electrical conductivity | 电导率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Conductivity of the SUNRISE_SCU_20K. SigUnitInfo:S/cm
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.19 | hwSUNRISESCU20KHydrovalveBackSig | Water valve feedback signal | 水阀反馈信号 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Hydrovalve Back Sig of the SUNRISE_SCU_20K. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.20 | hwSUNRISESCU20KCabinetAirOutTemp1 | Cabinet temperature 1 | 机柜温度1 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Cabinet Temp1 of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.21 | hwSUNRISESCU20KAirIndoorSpeed | Indoor fan rotational speed | 室内风机转速 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Air Indoor Speed of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.22 | hwSUNRISESCU20KCabinetAirOutTemp2 | Cabinet temperature 2 | 机柜温度2 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Cabinet Temp2 of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.23 | hwSUNRISESCU20KChilledWaterSupplyTemp | Chilled water supply temperature | 冷冻水入水温度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The ChilledWater EntryTemp of the SUNRISE_SCU_20K. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.24 | hwSUNRISESCU20KAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The AVoltage of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.25 | hwSUNRISESCU20KBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The BVoltage of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.26 | hwSUNRISESCU20KCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The CVoltage of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.27 | hwSUNRISESCU20KElectricSupplyRate | Mains frequency | 市电频率 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The ElectricSupplyRate of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.30 | hwSUNRISESCU20KPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The Port No. of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.31 | hwSUNRISESCU20KModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Modbus Address of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.32 | hwSUNRISESCU20KOnOffState | ON/OFF status | 开关机状态 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | The Ems State of the SUNRISE_SCU_20K: Value 1 indicates ON. Value 2 indicates OFF.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.35 | hwSUNRISESCU20KOnOff | ON/OFF | 开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | The Onoffstatus on EMS of the SUNRISE_SCU_20K: Value 1 indicates ON. Value 2 indicates OFF.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.36 | hwSUNRISESCU20KSetReturnAirTemp | Return air temperature setpoint | 设定回风温度 | 1-Read_Write | 读写 | 150..450 | 150..450 | The Return Air Temp of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.37 | hwSUNRISESCU20KSetReturnAirHumid | Return air humidity setpoint | 设定回风湿度 | 1-Read_Write | 读写 | 200..800 | 200..800 | The Return Air Humid of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.38 | hwSUNRISESCU20KSetSupplyAirTemp | Supply air temperature setpoint | 送风温度设定 | 1-Read_Write | 读写 | 50..350 | 50..350 | The Supply Air Temp of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.39 | hwSUNRISESCU20KSetSupplyAirHumid | Supply air humidity setpoint | 送风湿度设定 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | The Supply Air Humid of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.40 | hwSUNRISESCU20KReturnAirHTthreshold | Return air high temperature alarm threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 250..550 | 250..550 | The Return Air HTthreshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.41 | hwSUNRISESCU20KReturnAirLTthreshold | Return air low temperature alarm threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..280 | 50..280 | The Return Air LTthreshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.42 | hwSUNRISESCU20KReturnAirHHthreshold | Return air high humidity alarm threshold | 回风高湿告警阈值 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | The Return Air HHthreshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.43 | hwSUNRISESCU20KReturnAirLHthreshold | Return air low humidity alarm threshold | 回风低湿告警阈值 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | The Return Air LHthreshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.44 | hwSUNRISESCU20KSupplyAirHTthreshold | Supply air high temperature alarm threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..450 | 200..450 | The Supply Air HTthreshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.45 | hwSUNRISESCU20KSupplyAirLTthreshold | Supply air low temperature alarm threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | The Supply Air LTthreshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.46 | hwSUNRISESCU20KOvervoltThreshold | Overvoltage alarm threshold | 过压告警阈值 | 1-Read_Write | 读写 | 2200..2650 | 2200..2650 | The Overvolt Threshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.47 | hwSUNRISESCU20KUndervoltThreshold | Undervoltage alarm threshold | 欠压告警阈值 | 1-Read_Write | 读写 | 1750..2200 | 1750..2200 | The Undervolt Threshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.48 | hwSUNRISESCU20KWaterHTThreshold | Supply water high temperature alarm threshold | 入水高温告警阈值 | 1-Read_Write | 读写 | 70..300 | 70..300 | The Water HT Threshold of the SUNRISE_SCU_20K. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.54 | hwSUNRISESCU20KDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The Device Name of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.55 | hwSUNRISESCU20KChilledWaterReturnTemp | Chilled water return temperature | 冷冻水出水温度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Chilled Water Return Temperature. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.56 | hwSUNRISESCU20KFanRuntimeH | Fan runtimeH | 风机运行时间高位 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Fan RuntimeH of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.57 | hwSUNRISESCU20KFanRuntimeL | Fan runtimeL | 风机运行时间低位 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Fan RuntimeL of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.58 | hwSUNRISESCU20KValveRuntimeH | Valve runtimeH | 冷冻水阀运行时间高位 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Valve RuntimeH of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.59 | hwSUNRISESCU20KValveRuntimeL | Valve runtimeL | 冷冻水阀运行时间低位 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Valve RuntimeL of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.60 | hwSUNRISESCU20KAlarmState | Alarm status | 告警状态 | 0-Read_Only | 只读 | withoutalarm(1), alarm(2), unknown(255) | [无告警=1]/[告警=2] | The Alarm State of the SUNRISE_SCU_20K. Value 1 indicates withoutalarm. Value 2 indicates alarm.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.61 | hwSUNRISESCU20Ksoftwareversion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | The software version of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.62 | hwSUNRISESCU20Khardwareversion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | The hardware version of the SUNRISE_SCU_20K.
1.3.6.1.4.1.2011.6.178.1.1.10.6.1.1.100 | hwSUNRISESCU20KRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running and config table for the SUNRISE_SCU_20K.

## NetCol5000-A042
NetCol5000-A042
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.7 | NetCol5000A042 | NetCol5000-A042 | NetCol5000-A042 | / | / | / | / | NetCol Equipments.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1 | hwNetCol5000A042Running1Table | / | / |  |  | / | / | The running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.1 | hwNetCol5000A042Running1Index | / | / | 0-Read_Only | 只读 | / | / | The Index of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.2 | hwNetCol5000A042CommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication Status Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.3 | hwNetCol5000A042IndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The Indoorfan1totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.4 | hwNetCol5000A042IndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan2Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.5 | hwNetCol5000A042IndoorFan3TotalRuntime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan3Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.6 | hwNetCol5000A042IndoorFan4TotalRuntime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan4Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.7 | hwNetCol5000A042IndoorFan5TotalRuntime | Indoor fan 5 total runtime | 室内风机5累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan5Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.8 | hwNetCol5000A042IndoorFan6TotalRuntime | Indoor fan 6 total runtime | 室内风机6累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan6Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.9 | hwNetCol5000A042IndoorFan7TotalRuntime | Indoor fan 7 total runtime | 室内风机7累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan7Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.10 | hwNetCol5000A042IndoorFan8TotalRuntime | Indoor fan 8 total runtime | 室内风机8累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan8Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.11 | hwNetCol5000A042IndoorFan9TotalRuntime | Indoor fan 9 total runtime | 室内风机9累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan9Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.12 | hwNetCol5000A042IndoorFan10TotalRuntime | Indoor fan 10 total runtime | 室内风机10累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan10Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.13 | hwNetCol5000A042CompressorTotalRuntime | Compressor total runtime | 压缩机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The compressortotalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.14 | hwNetCol5000A042HumidiferPumpTotalRuntime | Humidifer pump total runtime | 加湿水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The humidifierpumptotalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.15 | hwNetCol5000A042HumidifierTotalRuntime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The humidifierpumptotalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.16 | hwNetCol5000A042EevTotalRuntime | EEV total runtime | EEV累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The humidifierpumptotalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.17 | hwNetCol5000A042OutFanTotalRuntime | Out fan total runtime | 室外风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan9Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.18 | hwNetCol5000A042CondensatePumpTotalRuntime | Drain pump total runtime | 排水水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The condpumptotalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.19 | hwNetCol5000A042ReturnAirFilterTotalRuntime | Return air filter total runtime | 回风过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The airfiltertotalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.20 | hwNetCol5000A042ElecHeaterTotalRuntime | Elec heater total runtime | 电加热累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The elecheatertotalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.21 | hwNetCol5000A042UnitOnOffStatus | Unit on/off status | 机组开关机状态 | 0-Read_Only | 只读 | poweroff(1), poweron(2), unknown(255) | [关机=1]/[开机=2] | The unitonoffstatus of the NetCol. Value 1 indicates poweroff. Value 2 indicates poweron. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.22 | hwNetCol5000A042CoolOutp | Cooling output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The cooloutp of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.23 | hwNetCol5000A042FanOutput | Indoor fan output | 室内风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The fan output of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.24 | hwNetCol5000A042ActualTotalNumberOfSystemsInThisGroup | Actual total number of systems in this group | 本群组实际机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Actual total number of systems in this group of the device config table for the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.25 | hwNetCol5000A042NumberOfActualActiveSystemsInThisGroup | Number of actual active systems in this group | 本群组实际运行机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Number of actual active systems in this group of the device config table for the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.26 | hwNetCol5000A042NumberOfActualStandbySystemsInThisGroup | Number of actual standby systems in this group | 本群组实际备机机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Number of actual standby systems in this group of the device config table for the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.27 | hwNetCol5000A042NumberOfSystemsInThisGroup | Number of systems in this group | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of systems in this group of the device config table for the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.28 | hwNetCol5000A042NumberOfRunningSystemsInThisGroup | Number of running systems in this group | 本群组运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of running systems in this group of the device config table for the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.29 | hwNetCol5000A042TeamworkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), intelligentTeamworkControl(2), iCooling(3), unknown(255) | [单机=1]/[智能群控=2]/[iCooling=3] | The teamworkstatus of the NetCol. Value 1 indicates single. Value 2 indicates intelligentTeamworkControl. Value 3 indicates iCooling. Value 4 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.30 | hwNetCol5000A042Psu1InputType | PSU 1 input type | 电源模块1输入类型 | 0-Read_Only | 只读 | dc(1), ac(2), unknown(255) | [直流=1]/[交流=2] | The psu1Inputtype of the NetCol. Value 1 indicates dc. Value 2 indicates ac. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.31 | hwNetCol5000A042Psu2InputType | PSU 2 input type | 电源模块2输入类型 | 0-Read_Only | 只读 | dc(1), ac(2), unknown(255) | [直流=1]/[交流=2] | The psu2Inputtype of the NetCol. Value 1 indicates dc. Value 2 indicates ac. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.32 | hwNetCol5000A042TemperatureAndHumidityControlType | Temperature and humidity control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnair(1), supplyair(2), coldaisle(3), hotaisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | The thcontroltype of the NetCol. Value 1 indicates returnair. Value 2 indicates supplyair. Value 3 indicates coldaisle. Value 4 indicates hotaisle. Value 5 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.33 | hwNetCol5000A042CurrentTemps | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The currenttemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.34 | hwNetCol5000A042CurrentHumids | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The currenthumid of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.35 | hwNetCol5000A042SupplyAirAvgTemp | Supply-air average temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The supplyairavgtemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.36 | hwNetCol5000A042ReturnAirAvgTemp | Return-air average temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The returnairavgtemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.37 | hwNetCol5000A042ColdAisleAvgTemp | Cold-aisle average temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The coldaisleavgtemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.38 | hwNetCol5000A042HotAisleAvgTemp | Hot-aisle average temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The hotaisleavgtemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.39 | hwNetCol5000A042SupplyAirAvgHumid | Supply-air average humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The supplyairavghumid of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.40 | hwNetCol5000A042ReturnAirAvgHumid | Return-air average humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The returnairavghumid of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.41 | hwNetCol5000A042ColdAisleAvgHumid | Cold-aisle average humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The coldaisleavghumid of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.42 | hwNetCol5000A042HotAisleAvgHumid | Hot-aisle average humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The hotaisleavghumid of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.43 | hwNetCol5000A042SupplyAir1Temp | Supply-air 1 temperature | 送风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The supplyair1Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.44 | hwNetCol5000A042SupplyAir2Temp | Supply-air 2 temperature | 送风2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The supplyair2Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.45 | hwNetCol5000A042ReturnAir1Temp | Return-air 1 temperature | 回风1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The returnair1Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.46 | hwNetCol5000A042ReturnAir2Temp | Return-air 2 temperature | 回风2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The returnair2Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.47 | hwNetCol5000A042ColdAisle1Temp | Cold aisle 1 temperature | 冷通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The coldaisle1Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.48 | hwNetCol5000A042ColdAisle2Temp | Cold aisle 2 temperature | 冷通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The coldaisle2Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.49 | hwNetCol5000A042ColdAisle3Temp | Cold aisle 3 temperature | 冷通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The coldaisle3Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.50 | hwNetCol5000A042ColdAisle4Temp | Cold aisle 4 temperature | 冷通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The coldaisle4Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.51 | hwNetCol5000A042ColdAisle5Temp | Cold aisle 5 temperature | 冷通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The coldaisle5Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.52 | hwNetCol5000A042ColdAisle1Humid | Cold aisle 1 humidity | 冷通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The coldaisle1Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.53 | hwNetCol5000A042ColdAisle2Humid | Cold aisle 2 humidity | 冷通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The coldaisle2Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.54 | hwNetCol5000A042ColdAisle3Humid | Cold aisle 3 humidity | 冷通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The coldaisle3Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.55 | hwNetCol5000A042ColdAisle4Humid | Cold aisle 4 humidity | 冷通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The coldaisle4Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.56 | hwNetCol5000A042ColdAisle5Humid | Cold aisle 5 humidity | 冷通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The coldaisle5Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.57 | hwNetCol5000A042HotAisle1Temp | Hot aisle 1 temperature | 热通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The hotaisle1Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.58 | hwNetCol5000A042HotAisle2Temp | Hot aisle 2 temperature | 热通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The hotaisle2Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.59 | hwNetCol5000A042HotAisle3Temp | Hot aisle 3 temperature | 热通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The hotaisle3Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.60 | hwNetCol5000A042HotAisle4Temp | Hot aisle 4 temperature | 热通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The hotaisle4Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.61 | hwNetCol5000A042HotAisle5Temp | Hot aisle 5 temperature | 热通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The hotaisle5Temp of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.62 | hwNetCol5000A042HotAisle1Humid | Hot aisle 1 humidity | 热通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The hotaisle1Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.63 | hwNetCol5000A042HotAisle2Humid | Hot aisle 2 humidity | 热通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The hotaisle2Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.64 | hwNetCol5000A042HotAisle3Humid | Hot aisle 3 humidity | 热通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The hotaisle3Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.65 | hwNetCol5000A042HotAisle4Humid | Hot aisle 4 humidity | 热通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The hotaisle4Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.66 | hwNetCol5000A042HotAisle5Humid | Hot aisle 5 humidity | 热通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The hotaisle5Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.67 | hwNetCol5000A042IndoorFan1RunStatus | Indoor fan 1 run status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan1Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.68 | hwNetCol5000A042IndoorFan2RunStatus | Indoor fan 2 run status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan2Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.69 | hwNetCol5000A042IndoorFan3RunStatus | Indoor fan 3 run status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan3Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.70 | hwNetCol5000A042IndoorFan4RunStatus | Indoor fan 4 run status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan4Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.71 | hwNetCol5000A042IndoorFan5RunStatus | Indoor fan 5 run status | 室内风机5运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan5Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.72 | hwNetCol5000A042IndoorFan6RunStatus | Indoor fan 6 run status | 室内风机6运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan6Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.73 | hwNetCol5000A042IndoorFan7RunStatus | Indoor fan 7 run status | 室内风机7运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan7Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.74 | hwNetCol5000A042IndoorFan8RunStatus | Indoor fan 8 run status | 室内风机8运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan8Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.75 | hwNetCol5000A042IndoorFan9RunStatus | Indoor fan 9 run status | 室内风机9运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan9Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.76 | hwNetCol5000A042IndoorFan10RunStatus | Indoor fan 10 run status | 室内风机10运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan10Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.77 | hwNetCol5000A042OutdoorFanRunStatus | Outdoor fan run status | 室外风机运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The outdoorfanrunstatus of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.78 | hwNetCol5000A042CondPumpRunStatus | / | / | 0-Read_Only | 只读 | 0..100 | / | The condpumprunstatus of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.79 | hwNetCol5000A042IpAddress | IP address | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The ip of the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.80 | hwNetCol5000A042Esn | ESN | ESN号 | 0-Read_Only | 只读 | 1..50 | 1..50 | The sampesn of the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.81 | hwNetCol5000A042ELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 1..2048 | 1..2048 | The Elabel of the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.82 | hwNetCol5000A042Mac | MAC address | MAC地址 | 0-Read_Only | 只读 | 1..50 | 1..50 | The Mac of the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.83 | hwNetCol5000A042SoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | The Softwareversion of the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.84 | hwNetCol5000A042HumidOutp | Humidifying output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The humidoutp of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.85 | hwNetCol5000A042HeatOutp | Heating output | 加热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The heatoutp of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.86 | hwNetCol5000A042PhaseAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The avoltage of the NetCol. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.87 | hwNetCol5000A042PhaseBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The bvoltage of the NetCol. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.88 | hwNetCol5000A042PhaseCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The PhaseCVoltage of the NetCol. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.89 | hwNetCol5000A042PowerFrequency | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | The electricsupplyrate of the NetCol. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.90 | hwNetCol5000A042CompressorRunStatus | Compressor run status | 压缩机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The compressorrunstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.91 | hwNetCol5000A042EevRunStatus | EEV run status | EEV运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The eevrunstatus of the NetCol. SigUnitInfo:step
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.92 | hwNetCol5000A042ReturnAir2Humid | Return-air 2 humidity | 回风2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The returnair2Humid of the NetCol.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.93 | hwNetCol5000A042HeatFunc | Heat Function | 加热功能 | 0-Read_Only | 只读 | disable(1), enable(2), enableainctivepowersupply(3), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The heatfunc of the NetCol. Value 1 indicates disable. Value 2 indicates enable. Value 3 indicates enableainctivepowersupply. Value 4 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.94 | hwNetCol5000A042HumidFunc | Humidity Function | 加湿功能 | 0-Read_Only | 只读 | disable(1), enable(2), enableainctivepowersupply(3), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The humidfunc of the NetCol. Value 1 indicates disable. Value 2 indicates enable. Value 3 indicates enableainctivepowersupply. Value 4 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.95 | hwNetCol5000A042DehumidFunc | Dehumidity Function | 除湿功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The dehumidfunc of the NetCol. Value 1 indicates disable. Value 2 indicates enable. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.96 | hwNetCol5000A042DischargePressure | Discharge pressure | 排气压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | The dischargepressure of the NetCol.Multiple:100. SigUnitInfo:Mpa
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.97 | hwNetCol5000A042SuctionPressure | Suction pressure | 吸气压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | The suctionpressure of the NetCol.Multiple:100. SigUnitInfo:Mpa
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.98 | hwNetCol5000A042DischargeTemp | Discharge temperature | 排气温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The dischargetemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.99 | hwNetCol5000A042SuctionTemp | Suction temperature | 吸气温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The suctiontemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.100 | hwNetCol5000A042LiquidPipeTemp | Liquid pipe temperature | 液管温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The liquidpipetemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.101 | hwNetCol5000A042PhaseCurrent | Phase current | 相电流 | 0-Read_Only | 只读 | 0..25000 | 0..25000 | The phasecurrent of the NetCol.Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.102 | hwNetCol5000A042IndoorFanCtrlStatus | Indoor fan control status | 室内风机控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The indoorfanctrlstatus of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.103 | hwNetCol5000A042HumidifierFilmRunStatus | Humidifier Film run status | 湿膜加湿运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The humidifierfilmrunstatus of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.104 | hwNetCol5000A042ElecHeaterRunStatus | Elec heater run status | 电加热运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The elecheaterrunstatus of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.105 | hwNetCol5000A042SuctionSuperheatDegree | Suction superheat degree | 吸气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | Suction superheat degree of the device config table for the NetCol. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.106 | hwNetCol5000A042DischargeSuperheatDegree | Discharge superheat degree | 排气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | Discharge superheat degree of the device config table for the NetCol. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.107 | hwNetCol5000A042TeamworkFunction | Teamwork function | 群控功能 | 0-Read_Only | 只读 | disable(1), enable(2) | [禁止=1]/[使能=2] | The teamworkfunction of the NetCol. Value 1 indicates disable. Value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.108 | hwNetCol5000A042HeatMode | Heat mode | 加热方式 | 0-Read_Only | 只读 | dehumidificHeat(1), lowTempHeat(2), dehumheatLowtemheat(3), unknown(255) | [除湿补热=1]/[低温加热=2]/[除湿补热且低温加热=3] | The heatmode of the NetCol. Value 1 indicates dehumidificHeat. Value 2 indicates lowTempHeat. Value 3 indicates dehumheatLowtemheat. Value 4 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.109 | hwNetCol5000A042TeamworkMode | Teamwork mode | 群控模式 | 0-Read_Only | 只读 | smartTeamworkControl(1), iCooling(2), unknown(255) | [智能群控=1]/[iCooling=2] | The teamworkmode of the NetCol. Value 1 indicates smartTeamworkControl. Value 2 indicates iCooling. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.110 | hwNetCol5000A042SystemAddress | / | / | 0-Read_Only | 只读 | 1..32 | / | System address of the device config table for the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.111 | hwNetCol5000A042SidePressureDifference | Average air side pressure difference | 风侧平均压差 | 0-Read_Only | 只读 | 0..500 | 0..500 | The Side pressure difference. SigUnitInfo:Pa
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.112 | hwNetCol5000A042IndoorFanCtrlType | Indoor fan control type | 室内风机控制类型 | 0-Read_Only | 只读 | retairtempdiffratecontrol(1), pressurediffcontrol(2), unknown(255) | [回送风温差比例控制=1]/[压差控制=2] | The Indoor fan ctrl type. Value 1 indicates retairtempdiffratecontrol. Value 2 indicates pressurediffcontrol. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.113 | hwNetCol5000A042DehumidOutput | Dehumid | 除湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The dehumid output of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.114 | hwNetCol5000A042Electricity | Electricity | 电量 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The Electricity of the NetCol.Multiple:100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.115 | hwNetCol5000A042Power | Power | 功率 | 0-Read_Only | 只读 | 0..10000000 | 0..10000000 | The Power of the NetCol.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.116 | hwNetCol5000A042Numberofcondpumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The Numberofcondpumps of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.117 | hwNetCol5000A042Numberofindoorfans | Number of indoor fans | 风机数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The Numberofindoorfans of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.118 | hwNetCol5000A042NumberofCWvalves | Number of CW valves | 压缩机数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The NumberofCWvalves of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.119 | hwNetCol5000A042NumberofPSU | Number of PSU | PSU数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The NumberofPSU of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.120 | hwNetCol5000A042Numberofheaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The Numberofheaters of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.121 | hwNetCol5000A042Numberofhumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The Numberofhumidifiers of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.122 | hwNetCol5000A042MasterSlaveFlag | Master/Slave flag | 主从机标志 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | The Master Slave Flag of NetCol5000A042. Value 1 indicates Slave. Value 2 indicates Master.
1.3.6.1.4.1.2011.6.178.1.1.10.7.1.1.200 | hwNetCol5000A042Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The The running row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2 | hwNetCol5000A042Running2Table | / | / |  |  | / | / | The The running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.1 | hwNetCol5000A042Running2Index | / | / | 0-Read_Only | 只读 | / | / | The The Index of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.3 | hwNetCol5000A042ReturnAirHtThreshold | Return-air HT threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | The returnairhtthreshold of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.4 | hwNetCol5000A042ReturnAirLtThreshold | Return-air LT threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | The returnairltthreshold of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.5 | hwNetCol5000A042SupplyAirHtThreshold | Supply-air HT threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The supplyairhtthreshold of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.6 | hwNetCol5000A042SupplyAirLtThreshold | Supply-air LT threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | The supplyairltthreshold of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.7 | hwNetCol5000A042ColdAisleHtThreshold | Cold-aisle HT threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The coldaislehtthreshold of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.8 | hwNetCol5000A042HotAisleHtThreshold | Hot-aisle HT threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | The hotaislehtthreshold of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.9 | hwNetCol5000A042HumidHighThreshold | Humidity high threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | The humidhighthreshold of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.10 | hwNetCol5000A042HumidLowThreshold | Humidity low threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | The humidlowthreshold of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.14 | hwNetCol5000A042DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The devicename of the NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.15 | hwNetCol5000A042OutdoorFanControlMode | Outdoor fan control mode | 室外风机控制模式 | 1-Read_Write | 读写 | communication(1), dryNode(2), unknown(255) | [通信=1]/[干接点=2] | The outdoorfancontrolmode of the NetCol. Value 1 indicates communication. Value 2 indicates dryNode. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.16 | hwNetCol5000A042CtrlPointTempSetPoint | Temperature setpoint | 温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | The value range of the temperature setting point is related to the temperature and humidity control type. 1. When the temperature and humidity control type is return air; 2. When the temperature and humidity control type is used for air supply; 3. When the temperature and humidity control type is cold aisle; 4. When the temperature and humidity control type is hot aisle. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.17 | hwNetCol5000A042CtrlPointHumidSetPoint | Humidity setpoint | 湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | The ctrlpointhumidsetpoint of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.18 | hwNetCol5000A042Heatmodecfg | / | / | 1-Read_Write | 读写 | dehumidheat(1), lowtempheat(2), dehumidLTheat(3), unknown(255) | / | The Heat mode of the NetCol. Value 1 indicates dehumidheat. Value 2 indicates lowtempheat. Value 3 indicates dehumidLTheat. Value 4 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.19 | hwNetCol5000A042CabinetTeamworkAddr | / | / | 1-Read_Write | 读写 | 0..32 | / | The Cabinet teamwork addr.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.20 | hwNetCol5000A042RefrigerantStatus | Refrigerant status | 制冷剂状态 | 0-Read_Only | 只读 | normal(1),inadequate(2),serinadequate(3),overcharged(4),unknown(255) | [正常=1]/[不足=2]/[严重不足=3]/[过充=4] | Refrigerant status. Value 1 indicates normal. Value 2 indicates Inadequate. Value 3 indicates Serinadequate. Value 4 indicates Overcharged.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.21 | hwNetCol5000A042CurrentCoolingCapacity | Cooling capacity | 制冷量 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | The Current Cooling Capacity of the NetCol.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.22 | hwNetCol5000A042OutDoorTemp | Outdoor temperature | 室外温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | The Out Door Temp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.23 | hwNetCol5000A042CabinetCurr | Current | 电流 | 0-Read_Only | 只读 | -100000..100000 | -100000..100000 | The Cabinet Curr of the NetCol.Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.24 | hwNetCol5000A042L1OrL2LinkageTargetTemperature | L1/L2 linkage target temperature | L1/L2联动目标温度 | 1-Read_Write | 读写 | 150..450 | 150..450 | The L1/L2 linkage target temperature of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.25 | hwNetCol5000A042L1OrL2LinkageTargetHumidity | L1/L2 linkage target humidity | L1/L2联动目标湿度 | 1-Read_Write | 读写 | 200..800 | 200..800 | The L1/L2 linkage target humidity of the NetCol.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.39 | hwNetCol5000A042CoolingCapacity | Rated cooling capacity (cooling power) | 额定的制冷容量（制冷功率） | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Cooling Capacity of NetCol5000A042.Multiple 10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.7.2.1.100 | hwNetCol5000A042Running2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3 | hwNetCol5000A042RunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei NetColPoe Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.1 | hwNetCol5000A042RunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetColPoe.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.2 | hwNetCol5000A042Hostidentity | Master/Slave flag | 主从机标志 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | The Host identity of NetCol5000A042. Value 1 indicates Slave. Value 2 indicates Master.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.3 | hwNetCol5000A042iCoolingrunstatus | iCooling run status | iCooling运行状态 | 0-Read_Only | 只读 | normal(1), abnormalairconditioner(2), invalidcabinettemperature(3), invalidcabinetpower(4), dataupdatingtimeout(5), inconsistentnumberofteamworkunits(6), notcoldaislecontainment(7), unknown(255) | [正常=1]/[空调异常=2]/[机柜温度无效=3]/[机柜功率无效=4]/[数据更新超时=5]/[群控机组数目不一致=6]/[封闭通道非冷通道=7] | The iCooling run status of NetCol5000A042. Value 1 indicates Normal. Value 2 indicates Abnormal air conditioner. Value 3 indicates Invalid cabinet temperature. Value 4 indicates Invalid cabinet power. Value 5 indicates Data updating timeout. Value 6 indicates Inconsistent number of teamwork units. Value 7 indicates Not cold aisle containment.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.4 | hwNetCol5000A042Numberofalarm | Number of alarm | 告警数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Number of alarm of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.5 | hwNetCol5000A042OnOrOffstatusonremote | / | / | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | / | The On/Off status on remote of NetCol5000A042. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.6 | hwNetCol5000A042Grouptemperature | / | / | 0-Read_Only | 只读 | -990..990 | / | The Group temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.7 | hwNetCol5000A042Grouphumidity | / | / | 0-Read_Only | 只读 | 0..990 | / | The Group humidity of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.8 | hwNetCol5000A042Requiredcoolingcapacity | / | / | 0-Read_Only | 只读 | -500000..500000 | / | The Required cooling capacity of NetCol5000A042.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.9 | hwNetCol5000A042Requiredhumidity | / | / | 0-Read_Only | 只读 | -500000..500000 | / | The Required humidity of NetCol5000A042.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.10 | hwNetCol5000A042PSU1inputvoltage | / | / | 0-Read_Only | 只读 | 0..300 | / | The PSU 1 input voltage of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.11 | hwNetCol5000A042PSU1inputcurrent | / | / | 0-Read_Only | 只读 | 0..1000 | / | The PSU 1 input current of NetCol5000A042.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.12 | hwNetCol5000A042PSU1outputvoltage | / | / | 0-Read_Only | 只读 | 0..700 | / | The PSU 1 output voltage of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.13 | hwNetCol5000A042PSU1outputcurrent | / | / | 0-Read_Only | 只读 | 0..3000 | / | The PSU 1 output current of NetCol5000A042.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.14 | hwNetCol5000A042PSU1inputpower | / | / | 0-Read_Only | 只读 | 0..3000 | / | The PSU 1 input power of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.15 | hwNetCol5000A042PSU2inputvoltage | / | / | 0-Read_Only | 只读 | 0..300 | / | The PSU 2 input voltage of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.16 | hwNetCol5000A042PSU2inputcurrent | / | / | 0-Read_Only | 只读 | 0..1000 | / | The PSU 2 input current of NetCol5000A042.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.17 | hwNetCol5000A042PSU2outputvoltage | / | / | 0-Read_Only | 只读 | 0..700 | / | The PSU 2 output voltage of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.18 | hwNetCol5000A042PSU2outputcurrent | / | / | 0-Read_Only | 只读 | 0..3000 | / | The PSU 2 output current of NetCol5000A042.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.19 | hwNetCol5000A042PSU2inputpower | / | / | 0-Read_Only | 只读 | 0..3000 | / | The PSU 2 input power of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.20 | hwNetCol5000A042Outdoorfancontrolstatus | / | / | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | / | The Outdoor fan control status of NetCol5000A042. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.21 | hwNetCol5000A042Condpumpcontrolstatus | / | / | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | / | The Cond pump control status of NetCol5000A042. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.22 | hwNetCol5000A042Hardwareversion | / | / | 0-Read_Only | 只读 | 1..32 | / | The Hardware version of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.23 | hwNetCol5000A042Elecheatercontrolstatus | / | / | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | / | The Elec heater control status of NetCol5000A042. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.24 | hwNetCol5000A042Watercontrol | / | / | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | / | The Water control of NetCol5000A042. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.25 | hwNetCol5000A042Pumpcontrol | / | / | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | / | The Pump control of NetCol5000A042. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.26 | hwNetCol5000A042HumidifierFilmcontrolStatus | / | / | 0-Read_Only | 只读 | closed(1), open(2), unknown(255) | / | The Humidifier Film control Status of NetCol5000A042. Value 1 indicates Closed. Value 2 indicates Open.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.27 | hwNetCol5000A042EEVcontrolstatus | / | / | 0-Read_Only | 只读 | 0..10000 | / | The EEV control status of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.28 | hwNetCol5000A042Insertmode | Insert mode | NetCol42K接入方式 | 1-Read_Write | 读写 | other(1), mac(2), tcp(3), unknown(255) | [其他=1]/[MAC=2]/[TCP=3] | The Insert mode of NetCol5000A042. Value 1 indicates other. Value 2 indicates mac. Value 3 indicates tcp.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.29 | hwNetCol5000A042OnOffStatusOnNMS | Startup/Shutdown control | 控制开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [开机=1]/[关机=2] | The Startup/Shutdown control of NetCol5000A042. Value 1 indicates off. Value 2 indicates on.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.30 | hwNetCol5000A042CommunicationAddress | Communication address | 通信地址 | 1-Read_Write | 读写 | 1..255 | 1..255 | The Communication Address of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.31 | hwNetCol5000A042Teamworkmode | / | / | 1-Read_Write | 读写 | smart(1), iCooling(2), unknown(255) | / | The Teamwork mode of NetCol5000A042. Value 1 indicates smart. Value 2 indicates iCooling.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.32 | hwNetCol5000A042Returnairtemperaturesetpoint | / | / | 1-Read_Write | 读写 | 180..450 | / | The Return-air temperature set point of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.33 | hwNetCol5000A042Supplyairtemperaturesetpoint | / | / | 1-Read_Write | 读写 | 150..350 | / | The Supply-air temperature set point of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.34 | hwNetCol5000A042Coldaisletemperaturesetpoint | / | / | 1-Read_Write | 读写 | 150..350 | / | The Cold-aisle temperature set point of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.35 | hwNetCol5000A042Hotaisletemperaturesetpoint | / | / | 1-Read_Write | 读写 | 180..450 | / | The Hot-aisle temperature set point of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.36 | hwNetCol5000A042Returnairhumiditysetpoint | / | / | 1-Read_Write | 读写 | 150..800 | / | The Return-air humidity set point of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.37 | hwNetCol5000A042Supplyairhumiditysetpoint | / | / | 1-Read_Write | 读写 | 150..800 | / | The Supply-air humidity set point of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.38 | hwNetCol5000A042Coldaislehumiditysetpoint | / | / | 1-Read_Write | 读写 | 150..800 | / | The Cold-aisle humidity set point of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.39 | hwNetCol5000A042Hotaislehumiditysetpoint | / | / | 1-Read_Write | 读写 | 150..800 | / | The Hot-aisle humidity set point of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.40 | hwNetCol5000A042L1OrL2linkageenable | L1/L2 linkage enable | L1L2联动使能标志 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The L1/L2 linkage enable of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.41 | hwNetCol5000A042Modulebasicstatus | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Module basic status of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.42 | hwNetCol5000A042Cabinetnum | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet num of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.43 | hwNetCol5000A042Aislestruct | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Aisle struct of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.44 | hwNetCol5000A042Aislewidth | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Aisle width of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.45 | hwNetCol5000A042Aisleclosetype | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Aisle close type of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.46 | hwNetCol5000A042Cabinetbasicinfo | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet basic info of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.47 | hwNetCol5000A042Cabinettype | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet type of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.48 | hwNetCol5000A042Cabinetwidth | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet width of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.49 | hwNetCol5000A042Cabinetpositioncol | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet position col of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.50 | hwNetCol5000A042Cabinetpositionrow | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet position row of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.51 | hwNetCol5000A042Cabinetmodaddr | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet modaddr of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.52 | hwNetCol5000A042Cabinetstatus | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet status of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.53 | hwNetCol5000A042Cabinetinputpower | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet input power of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.54 | hwNetCol5000A042Cabinetwastepower | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet waste power of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.55 | hwNetCol5000A042Averagecabinetinletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Average cabinet inlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.56 | hwNetCol5000A042Minimumcabinetinletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Minimum cabinet inlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.57 | hwNetCol5000A042Maximumcabinetinletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Maximum cabinet inlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.58 | hwNetCol5000A042Upperlimitofcabinetinletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Upper limit of cabinet inlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.59 | hwNetCol5000A042Lowerlimitofcabinetinletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Lower limit of cabinet inlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.60 | hwNetCol5000A042Averagecabinetinletairhumidity | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Average cabinet inlet air humidity of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.61 | hwNetCol5000A042Minimumcabinetinletairhumidity | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Minimum cabinet inlet air humidity of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.62 | hwNetCol5000A042Maximumcabinetinletairhumidity | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Maximum cabinet inlet air humidity of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.63 | hwNetCol5000A042Upperlimitofcabinetinletairhumidity | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Upper limit of cabinet inlet air humidity of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.64 | hwNetCol5000A042Lowerlimitofcabinetinletairhumidity | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Lower limit of cabinet inlet air humidity of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.65 | hwNetCol5000A042Averagecabinetoutletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Average cabinet outlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.66 | hwNetCol5000A042Minimumcabinetoutletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Minimum cabinet outlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.67 | hwNetCol5000A042Maximumcabinetoutletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Maximum cabinet outlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.68 | hwNetCol5000A042Upperlimitofcabinetoutletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Upper limit of cabinet outlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.69 | hwNetCol5000A042Lowerlimitofcabinetoutletairtemperature | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Lower limit of cabinet outlet air temperature of NetCol5000A042.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.70 | hwNetCol5000A042Cabinetseqno | / | / | 1-Read_Write | 读写 | 0..65535 | / | The Cabinet seqno of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.71 | hwNetCol5000A042Branch1Name | supplyInfo | 第一路供电信息 | 1-Read_Write | 读写 | 0..2147483647 | 0..2147483647 | The Branch 1 Name of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.72 | hwNetCol5000A042Branch2Name | supplyInfo | 第二路供电信息 | 1-Read_Write | 读写 | 0..2147483647 | 0..2147483647 | The Branch 2 Name of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.73 | hwNetCol5000A042SupplyMode | supplyInfo | 供电制式 | 1-Read_Write | 读写 | 1..2 | 1..2 | The Supply Mode of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.74 | hwNetCol5000A042SupplyBranchNum | supplyInfo | 供电路数 | 1-Read_Write | 读写 | 1..2 | 1..2 | The Supply Branch Num of NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.75 | hwNetCol5000A042ReturnairHTaction | Return-air HT action | 回风高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The Return-air HT action of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Block. Value 3 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.76 | hwNetCol5000A042ReturnairLTaction | Return-air LT action | 回风低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The Return-air LT action of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Block. Value 3 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.77 | hwNetCol5000A042SupplyairHTaction | Supply-air HT action | 送风高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The Supply-air HT action of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Block. Value 3 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.78 | hwNetCol5000A042SupplyairLTaction | Supply-air LT action | 送风低温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The Supply-air LT action of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Block. Value 3 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.79 | hwNetCol5000A042ColdaisleHTaction | Cold-aisle HT action | 冷通道高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The Cold-aisle HT action of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Block. Value 3 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.80 | hwNetCol5000A042HotaisleHTaction | Hot-aisle HT action | 热通道高温告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The Hot-aisle HT action of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Block. Value 3 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.81 | hwNetCol5000A042Highhumidityaction | High humidity action | 高湿告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The High humidity action of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Block. Value 3 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.82 | hwNetCol5000A042Lowhumidityaction | Low humidity action | 低湿告警使能 | 1-Read_Write | 读写 | disable(1), block(2), enable(3), unknown(255) | [禁止=1]/[阻塞=2]/[使能=3] | The Low humidity action of NetCol5000A042. Value 1 indicates Disable. Value 2 indicates Block. Value 3 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.83 | hwNetCol5000A042IcoolingType | iCooling type | iCooling类型 | 1-Read_Write | 读写 | iCooling1.0(1), iCooling2.0(2), unknown(255) | [iCooling1.0=1]/[iCooling2.0=2] | iCooling type of the device config table for the NetCol5000A042. Value 1 indicate iCooling1.0 Value 2 indicate iCooling2.0
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.84 | hwNetCol5000A042IcoolingTemperatureAndHumidityControlType | iCooling temperature and humidity control type | iCooling温湿度控制类型 | 1-Read_Write | 读写 | returnAir(1), supplyAir(2), coldAisle(3), hotAisle(4), unknown(255) | [回风=0]/[送风=1]/[冷通道=2]/[热通道=3] | iCooling temperature and humidity control type of the device config table for the NetCol5000A042. Value 1 indicate return-air Value 2 indicate supply-air Value 3 indicate cold-aisle Value 4 indicate hot-aisle
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.85 | hwNetCol5000A042IcoolingHeartbeat | iCooling heartbeat | iCooling心跳 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | iCooling heartbeat of the device config table for the NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.86 | hwNetCol5000A042IcoolingIndoorFanMaxReturnorSupplyAirTemperatur | icooling indoor fan max return/supply air temperature difference | iCooling室内风机回送风最大温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | icooling indoor fan max return/supply air temperature difference of the device config table for the NetCol5000A042.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.87 | hwNetCol5000A042IcoolingMaxIndoorFanSpeed | iCooling max indoor fan speed | iCooling室内风机最大转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | iCooling max indoor fan speed of the device config table for the NetCol5000A042.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.88 | hwNetCol5000A042IcoolingMaxOutdoorFanRunningPressure | iCooling max outdoor fan running pressure | iCooling室外风机最大运行压力 | 1-Read_Write | 读写 | 150..400 | 150..400 | iCooling max outdoor fan running pressure of the device config table for the NetCol5000A042.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.89 | hwNetCol5000A042IcoolingIndoorFanControlType | iCooling indoor fan control type | iCooling室内风机控制类型 | 1-Read_Write | 读写 | retairtempdiffratecontrol(1), pressurediffcontrol(2), unknown(255) | [回送风温差比例控制=1]/[压差控制=4] | iCooling indoor fan control type of the device config table for the NetCol5000A042. Value 1 indicate retairtempdiffratecontrol Value 4 indicate pressurediffcontrol
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.90 | hwNetCol5000A042IcoolingTemperatureSetpoint | iCooling temperature setpoint | iCooling温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | iCooling temperature setpoint of the device config table for the NetCol5000A042.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.91 | hwNetCol5000A042IcoolingHumiditySetpoint | iCooling humidity setpoint | iCooling湿度设定点 | 1-Read_Write | 读写 | 200..800 | 200..800 | iCooling humidity setpoint of the device config table for the NetCol5000A042.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.92 | hwNetCol5000A042IcoolingStartuporShutdownControl | iCooling startup/shutdown control | iCooling控制开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=0]/[开机=1] | iCooling startup/shutdown control of the device config table for the NetCol5000A042. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.7.3.1.100 | hwNetCol5000A042RunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running and config row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4 | hwNetCol5000A042Running3Table | / | / |  |  | / | / | The The running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.1 | hwNetCol5000A042Running3Index | / | / | 0-Read_Only | 只读 | / | / | The Index of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.2 | hwNetCol5000A042OutdoorUintCondensingMode | Outdoor unit condensate mode | 室外机冷凝方式 | 0-Read_Only | 只读 | aircooled(1), watercooled(2), unknown(255) | [风冷=1]/[水冷=2] | Outdoor Uint Condensing Mode: value 1 indicates air cooled. Value 2 indicates water cooled.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.3 | hwNetCol5000A042WaterValveRunningStatus | Water-cooled module water valve running status | 水冷模块水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The water valve running status of the NetCol. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.4 | hwNetCol5000A042SupplywaterTemp | Water-cooled module supply-water temperature | 水冷模块供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The supplywaterTemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.5 | hwNetCol5000A042ReturnwaterTemp | Water-cooled module return-water temperature | 水冷模块回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The returnwaterTemp of the NetCol.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.6 | hwNetCol5000A042ABLineVoltage | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The AB line voltage of NetCol5000A042.Mult. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.7 | hwNetCol5000A042BCLineVoltage | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The BC line voltage of NetCol5000A042. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.8 | hwNetCol5000A042CAlineVoltage | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The CA line voltage of NetCol5000A042. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.9 | hwNetCol5000A042BackupABLineVoltage | Backup A-B line voltage | 备路AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The backup AB line voltage of NetCol5000A042. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.10 | hwNetCol5000A042BackupBCLineVoltage | Backup B-C line voltage | 备路BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The backup BC line voltage of NetCol5000A042. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.11 | hwNetCol5000A042BackupCALineVoltage | Backup C-A line voltage | 备路CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The backup CA line voltage of NetCol5000A042. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.12 | hwNetCol5000A042BackupPowerFrequency | Backup power frequency | 备路电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | The backup power voltage of NetCol5000A042. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.13 | hwNetCol5000A042TeamworkGroupNumber | Teamwork group number | 群控组号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Teamwork group number of the device config table for the NetCol5000A042.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.14 | hwNetCol5000A042ActiveorStandbyFlag | Active/Standby flag | 运行机备机标志 | 0-Read_Only | 只读 | active(1), standby(2), unknown(255) | [运行机=1]/[备机=2] | Active/Standby flag of the device config table for the NetCol5000A042. Value 1 indicate active Value 2 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.15 | hwNetCol5000A042IndoorFan11RunStatus | Indoor fan 11 run status | 室内风机11运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan11Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.16 | hwNetCol5000A042IndoorFan12RunStatus | Indoor fan 12 run status | 室内风机12运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan12Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.17 | hwNetCol5000A042IndoorFan13RunStatus | Indoor fan 13 run status | 室内风机13运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan13Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.18 | hwNetCol5000A042IndoorFan14RunStatus | Indoor fan 14 run status | 室内风机14运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The indoorfan14Runstatus of the NetCol. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.19 | hwNetCol5000A042IndoorFan11TotalRuntime | Indoor fan 11 total runtime | 室内风机11累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan11Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.20 | hwNetCol5000A042IndoorFan12TotalRuntime | Indoor fan 12 total runtime | 室内风机12累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan12Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.21 | hwNetCol5000A042IndoorFan13TotalRuntime | Indoor fan 13 total runtime | 室内风机13累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan13Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.22 | hwNetCol5000A042IndoorFan14TotalRuntime | Indoor fan 14 total runtime | 室内风机14累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The indoorfan14Totalruntime of the NetCol. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.23 | hwNetCol5000A042SystemPower | System power | 机组总功率 | 0-Read_Only | 只读 | 0..4000 | 0..4000 | System power of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.24 | hwNetCol5000A042PhaseACurrent | Phase A current | 系统电源A相电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase A current of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.25 | hwNetCol5000A042PhaseBCurrent | Phase B current | 系统电源B相电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase B current of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.26 | hwNetCol5000A042PhaseCCurrent | Phase C current | 系统电源C相电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase C current of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.27 | hwNetCol5000A042FluorinePumpRunningStatus | Refrigerant pump running status | 氟泵运行状态 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Fluorine pump running status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.28 | hwNetCol5000A042FluorinePump1RunningStatus | Refrigerant pump 1 running status | 氟泵1运行状态 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Fluorine pump 1 running status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.29 | hwNetCol5000A042FluorinePumpType | Refrigerant pump type | 氟泵类型 | 0-Read_Only | 只读 | no(1), nonVFDFluorinePump(2), vFDFluorinePump(3), unknown(255) | [无=1]/[定频氟泵=2]/[变频氟泵=3] | Fluorine pump type of the device config table for the NetCol5000-A. Value 1 indicate no Value 2 indicate non-vfdfluorinepump Value 3 indicate vfdfluorinepump
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.30 | hwNetCol5000A042FluorinePumpTotalRuntime | Refrigerant pump total runtime | 氟泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fluorine pump total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.31 | hwNetCol5000A042FluorinePump1TotalRuntime | Refrigerant pump 1 total runtime | 氟泵1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fluorine pump 1 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.32 | hwNetCol5000A042NumberOfFluorinePumps | Number of fluorine pumps | 氟泵数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Number of fluorine pumps of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.156 | hwNetCol5000A042DrainPumpRunningStatus | Drain pump running status | 排水水泵运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Drain pump running status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.157 | hwNetCol5000A042TotalSprayRunningTimeOfOutdoorUnit1 | Total spray running time of outdoor unit 1 | 室外机1喷淋累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total spray running time of outdoor unit 1 of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.158 | hwNetCol5000A042TotalSprayRunningTimeOfOutdoorUnit2 | Total spray running time of outdoor unit 2 | 室外机2喷淋累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total spray running time of outdoor unit 2 of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.159 | hwNetCol5000A042OutdoorUnitSprayingFunction | Outdoor unit spraying function | 室外机喷淋功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Outdoor unit spraying function of the device config table for the NetCol5000-A. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.160 | hwNetCol5000A042OutdoorUnit1SprayRunningStatus | Outdoor unit 1 spray running status | 室外机1喷淋运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor unit 1 spray running status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.161 | hwNetCol5000A042OutdoorUnit2SprayRunningStatus | Outdoor unit 2 spray running status | 室外机2喷淋运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor unit 2 spray running status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.162 | hwNetCol5000A042FluorinePump2TotalRuntime | Refrigerant pump 2 total runtime | 氟泵2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Fluorine pump 2 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.163 | hwNetCol5000A042NumberOfOutdoorFans | Number of outdoor fans | 室外风机数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Number of outdoor fans of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.164 | hwNetCol5000A042OutdoorFanHumidity | Outdoor fan humidity | 室外机湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Outdoor fan humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.165 | hwNetCol5000A042AcInputTotalPowerConsumption | AC input total power consumption | 机组交流输入累计电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AC input total power consumption of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.166 | hwNetCol5000A042TotalOpenTimesOfTheWaterInletSolenoidValve | Total open times of the water inlet solenoid valve | 进水电磁阀累计开启次数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total open times of the water inlet solenoid valve of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.167 | hwNetCol5000A042NumberOfOutdoorSpray | Number of outdoorspray | 室外机喷淋数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Number of outdoor spray of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.168 | hwNetCol5000A042SystemTotalPowerConsumption | System total power consumption | 机组累计耗电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System total power consumption of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.7.4.1.200 | hwNetCol5000A042Running3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The The running row status of Device.

## ENVICOOL-CRU
英维克CRU
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.8 | ENVICOOLCRU | ENVICOOL-CRU | 英维克CRU | / | / | / | / | The ENVICOOL-CRU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1 | hwENVICOOLCRURunningAndConfigTable | / | / |  |  | / | / | The running table of Huawei ENVICOOL-CRU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.1 | hwENVICOOLCRURunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the ENVICOOL-CRU.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.2 | hwENVICOOLCRUCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Inamecommstate. Value 1 indicates normal. Value 2 indicates abnormal. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.3 | hwENVICOOLCRUSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Inamesoftwareversion
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.4 | hwENVICOOLCRUOutdoorTemperature | Outdoor temperature | 室外温度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Inameoutdoortemperature.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.5 | hwENVICOOLCRUPumpInletTemperature | Pump inlet temperature | 泵进口温度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Inamepumpinlettemperature.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.6 | hwENVICOOLCRUPumpOutletTemperature | Pump outlet temperature | 泵出口温度（液管） | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Inamepumpoutlettemperature.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.7 | hwENVICOOLCRUPlateHeatExchangerInletWaterTemperature | Plate heat exchanger inlet water temperature | 板换进水温度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Inameplateheatexchangerinletwatertemperature.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.8 | hwENVICOOLCRUPlateHeatExchangerOutletWaterTemperature | Plate heat exchanger outlet water temperature | 板换出水温度 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Inameplateheatexchangeroutletwatertemperature.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.9 | hwENVICOOLCRUPlateHeatExchangerOutletRefrigerantTemperature | Plate heat exchanger outlet refrigerant temperature | 板换出水温度（冷媒） | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Inameplateheatexchangeroutletrefrigeranttemperature.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.10 | hwENVICOOLCRUPumpInletPressure | Pump inlet pressure | 泵进口压力 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Inamepumpinletpressure.Multiple 100. SigUnitInfo:Bar
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.11 | hwENVICOOLCRUPumpOutletPressure | Pump outlet pressure | 泵出口压力 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Inamepumpoutletpressure.Multiple 100. SigUnitInfo:Bar
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.12 | hwENVICOOLCRUVoltage | Voltage | 电压检测 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Inamevoltage SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.13 | hwENVICOOLCRUPumpCurrent | Pump current | 泵电流检测 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Inamepumpcurrent SigUnitInfo:mA
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.14 | hwENVICOOLCRU1PumpStatus | 1# Pump status | 1#泵 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Iname1Pumpstatus Value 1 indicates close. Value 2 indicates open. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.15 | hwENVICOOLCRU2PumpStatus | 2# Pump status | 2#泵 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Iname2Pumpstatus Value 1 indicates close. Value 2 indicates open. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.16 | hwENVICOOLCRUWaterValveStatus | Water valve status | 水阀 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Inamewatervalvestatus
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.17 | hwENVICOOLCRUSystemOnOff | System ON/OFF | 开关机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Inamesystemonoff Value 1 indicates close. Value 2 indicates open. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.18 | hwENVICOOLCRUPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Inameportno
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.19 | hwENVICOOLCRUModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Inamemodbusaddress
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.20 | hwENVICOOLCRURemoteOnOff | Remote ON/OFF | 监控开关机 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Inameonoffstatusonems Value 1 indicates on. Value 2 indicates off. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.21 | hwENVICOOLCRUCabinetWidth | Cabinet Width | 机柜宽度 | 1-Read_Write | 读写 | halfsize(1), fullsize(2), unknown(255) | [半柜=1]/[全柜=2] | Inamecabinetwidth Value 1 indicates halfsize. Value 2 indicates fullsize. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.22 | hwENVICOOLCRUDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Inamedevicename
1.3.6.1.4.1.2011.6.178.1.1.10.8.1.1.100 | hwENVICOOLCRUDRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the ENVICOOL-CRU.

## NetCol5000CF-110
NetCol5000CF_110
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.9 | NetCol5000CF110 | NetCol5000CF_110 | NetCol5000CF_110 | / | / | / | / | NetCol Equipments.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1 | hwNetCol5000CF110Running1Table | / | / |  |  | / | / | The running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.1 | hwNetCol5000CF110Running1Index | / | / | 0-Read_Only | 只读 | / | / | The Index of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.2 | hwNetCol5000CF110Commstate | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Commstate of the NetCol5000CF110. Value 1 indicates normal. Value 2 indicates abnormal. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.3 | hwNetCol5000CF110CurrentTemp | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The CurrentTemp of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.4 | hwNetCol5000CF110CurrentHumid | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The CurrentHumid of the NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.5 | hwNetCol5000CF110SupplywaterTemp | Supply-water temperature | 供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The SupplywaterTemp of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.6 | hwNetCol5000CF110ReturnwaterTemp | Return-water temperature | 回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The ReturnwaterTemp of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.7 | hwNetCol5000CF110CoolOutp | Cool output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The CoolOutp of the NetCol5000CF110. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.8 | hwNetCol5000CF110FanOutp | Fan output | 风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The FanOutp of the NetCol5000CF110. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.9 | hwNetCol5000CF110HeatOutp | Heat output | 加热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The HeatOutp of the NetCol5000CF110. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.10 | hwNetCol5000CF110HumidOutp | Humidity output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The HumidOutp of the NetCol5000CF110. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.11 | hwNetCol5000CF110IndoorfanCtrlStatus | Indoor fan control status | 室内风机控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The IndoorfanCtrlStatus of the NetCol5000CF110. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.12 | hwNetCol5000CF110CwvalveRunStatus | CW valve run status | 冷冻水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The CwvalveRunStatus of the NetCol5000CF110.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.13 | hwNetCol5000CF110CondpumpRunStatus | Drain pump run status | 排水水泵运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The CondpumpRunStatus of the NetCol5000CF110. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.14 | hwNetCol5000CF110UnitOnOffStatus | On/Off status of air conditioner | 机组开关机状态 | 0-Read_Only | 只读 | poweroff(1), poweron(2), unknown(255) | [关机=1]/[开机=2] | The UnitOnOffStatus of the NetCol5000CF110. Value 1 indicates poweroff. Value 2 indicates poweron. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.15 | hwNetCol5000CF110BestWaterTemp | Recommended supply water temperature | 供水温度建议值 | 0-Read_Only | 只读 | 7..19 | 7..19 | The BestWaterTemp of the NetCol5000CF110. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.16 | hwNetCol5000CF110CurCool | Cooling capacity | 制冷量 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | The CurCool of the NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.17 | hwNetCol5000CF110CurLoad | Cooling load factor | 制冷负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The CurLoad of the NetCol5000CF110. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.18 | hwNetCol5000CF110IpAddr | IP address | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IpAddr of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.19 | hwNetCol5000CF110EquipEsn | ESN No. | ESN号 | 0-Read_Only | 只读 | 1..50 | 1..50 | The EquipEsn of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.20 | hwNetCol5000CF110EquipElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 1..2048 | 1..2048 | The EquipElabel of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.21 | hwNetCol5000CF110PortMac | / | / | 0-Read_Only | 只读 | 1..50 | / | The PortMac of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.22 | hwNetCol5000CF110SoftVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | The SoftVersion of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.23 | hwNetCol5000CF110IndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan1TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.24 | hwNetCol5000CF110IndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan2TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.25 | hwNetCol5000CF110IndoorFan3TotalRuntime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan3TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.26 | hwNetCol5000CF110IndoorFan4TotalRuntime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan4TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.27 | hwNetCol5000CF110IndoorFan5TotalRuntime | Indoor fan 5 total runtime | 室内风机5累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan5TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.28 | hwNetCol5000CF110IndoorFan6TotalRuntime | Indoor fan 6 total runtime | 室内风机6累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan6TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.29 | hwNetCol5000CF110IndoorFan7TotalRuntime | Indoor fan 7 total runtime | 室内风机7累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan7TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.30 | hwNetCol5000CF110IndoorFan8TotalRuntime | Indoor fan 8 total runtime | 室内风机8累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan8TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.31 | hwNetCol5000CF110IndoorFan9TotalRuntime | Indoor fan 9 total runtime | 室内风机9累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan9TotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.32 | hwNetCol5000CF110IndoorFan10totalRuntime | Indoor fan 10 total runtime | 室内风机10累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan10totalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.33 | hwNetCol5000CF110IndoorFan11totalRuntime | Indoor fan 11 total runtime | 室内风机11累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan11totalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.34 | hwNetCol5000CF110IndoorFan12totalRuntime | Indoor fan 12 total runtime | 室内风机12累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan12totalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.35 | hwNetCol5000CF110HumidifierPumpTotalRuntime | Humidifier pump total runtime | 加湿水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The HumidifierPumpTotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.36 | hwNetCol5000CF110HumidifierWetTotalRuntime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The HumidifierWetTotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.37 | hwNetCol5000CF110CondpumpTotalRuntime | Drain pump total runtime | 排水水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The CondpumpTotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.38 | hwNetCol5000CF110AirfilterTotalRuntime | Return air filter total runtime | 回风过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The AirfilterTotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.39 | hwNetCol5000CF110CwvalveTotalRuntime | CW valve total runtime | 冷冻水阀累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The CwvalveTotalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.40 | hwNetCol5000CF110TotalNumberOfUnits | Total number of units | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | The TotalNumberOfUnits of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.41 | hwNetCol5000CF110NumberOfRunningUnits | Number of running units | 本群组运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | The NumberOfRunningUnits of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.42 | hwNetCol5000CF110TeamWorkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), intelligentTeamworkControl(2), iCooling(3), unknown(255) | [单机=1]/[智能群控=2]/[iCooling=3] | The TeamWorkStatus of the NetCol5000CF110. Value 1 indicates single. Value 2 indicates intelligent teamwork control. Value 3 indicates iCooling. Value 4 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.43 | hwNetCol5000CF110PowerVolt | Power input voltage | 电源输入电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The PowerVolt of the NetCol5000CF110. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.44 | hwNetCol5000CF110ElectricSupplyRate | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | The ElectricSupplyRate of the NetCol5000CF110. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.45 | hwNetCol5000CF110SupplyAirAvgTemp | Supply-air average temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The SupplyAirAvgTemp of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.46 | hwNetCol5000CF110ReturnAirAvgTemp | Return-air average temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The ReturnAirAvgTemp of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.47 | hwNetCol5000CF110ColdAisleAvgTemp | Cold-aisle average temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The ColdAisleAvgTemp of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.48 | hwNetCol5000CF110HotAisleAvgTemp | Hot-aisle average temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The HotAisleAvgTemp of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.49 | hwNetCol5000CF110SupplyAirAvgHumid | Supply-air average humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The SupplyAirAvgHumid of the NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.50 | hwNetCol5000CF110ReturnAirAvgHumid | Return-air average humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The ReturnAirAvgHumid of the NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.51 | hwNetCol5000CF110ColdAisleAvgHumid | Cold-aisle average humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The ColdAisleAvgHumid of the NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.52 | hwNetCol5000CF110HotAisleAvgHumid | Hot-aisle average humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The HotAisleAvgHumid of the NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.53 | hwNetCol5000CF110SidePressureDiff | Side pressure difference | 风侧压差 | 0-Read_Only | 只读 | 0..500 | 0..500 | The SidePressureDiff of the NetCol5000CF110. SigUnitInfo:Pa
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.54 | hwNetCol5000CF110THControlType | Temperature and humidity control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnair(1), supplyair(2), coldaisle(3), hotaisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | The THControlType of the NetCol5000CF110. Value 1 indicates returnair. Value 2 indicates supplyair. Value 3 indicates coldaisle. Value 4 indicates hotaisle. Value 5 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.9.1.1.200 | hwNetCol5000CF110Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The unning row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2 | hwNetCol5000CF110Running2Table | / | / |  |  | / | / | The unning table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.1 | hwNetCol5000CF110Running2Index | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.2 | hwNetCol5000CF110SetEmsStatus | Startup/Shutdown control | 控制开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | The SetEmsStatus of the NetCol5000CF110. Value 1 indicates on. Value 2 indicates off. Value 3 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.3 | hwNetCol5000CF110SetTemperatureSetpoint | Temperature setpoint | 温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | The value range of the temperature setting point is related to the temperature and humidity control type. 1. When the temperature and humidity control type is return air; 2. When the temperature and humidity control type is used for air supply; 3. When the temperature and humidity control type is cold aisle; 4. When the temperature and humidity control type is hot aisle. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.4 | hwNetCol5000CF110SetHumiditySetpoint | Humidity setpoint | 湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | The SetHumiditySetpoint of the NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.5 | hwNetCol5000CF110SetRetWaterTempDiff | Supply/return water temperature difference setpoint | 供回水温差设定点 | 1-Read_Write | 读写 | 5..7 | 5..7 | The SetRetWaterTempDiff of the NetCol5000CF110. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.6 | hwNetCol5000CF110SetCoolManager | Cooling capacity management function | 冷量管理功能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The SetCoolManager of the NetCol5000CF110. Value 1 indicates disable. Value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.7 | hwNetCol5000CF110SetLoadFactorTarget | Target cooling load factor | 制冷负载率目标值 | 1-Read_Write | 读写 | 50..90 | 50..90 | The SetLoadFactorTarget of the NetCol5000CF110. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.8 | hwNetCol5000CF110SetSupplyWaterTempUpper | Maximum supply water temperature | 供水温度上限 | 1-Read_Write | 读写 | 10..19 | 10..19 | The SetSupplyWaterTempUpper of the NetCol5000CF110. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.9 | hwNetCol5000CF110SetSupplyWaterTempLower | Minimum supply water temperature | 供水温度下限 | 1-Read_Write | 读写 | 10..19 | 10..19 | The SetSupplyWaterTempLower of the NetCol5000CF110. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.10 | hwNetCol5000CF110SetRetAirHTempAlmThreshold | Return air high temperature alarm threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | The SetRetAirHTempAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.11 | hwNetCol5000CF110SetRetAirLTempAlmThreshold | Return air low temperature alarm threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | The SetRetAirLTempAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.12 | hwNetCol5000CF110SetSupplyAirHTempAlmThreshold | Supply air high temperature alarm threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The SetSupplyAirHTempAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.13 | hwNetCol5000CF110SetSupplyAirLTempAlmThreshold | Supply air low temperature alarm threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | The SetSupplyAirLTempAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.14 | hwNetCol5000CF110SetColdAisleHTempAlmThreshold | Cold aisle high temperature alarm threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The SetColdAisleHTempAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.15 | hwNetCol5000CF110SetColdAisleLTempAlmThreshold | Cold aisle low temperature alarm threshold | 冷通道低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | The SetColdAisleLTempAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.16 | hwNetCol5000CF110SetHotAisleHTempAlmThreshold | Hot aisle high temperature alarm threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | The SetHotAisleHTempAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.17 | hwNetCol5000CF110SetHotAisleLTempAlmThreshold | Hot aisle low temperature alarm threshold | 热通道低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | The SetHotAisleLTempAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.18 | hwNetCol5000CF110SetHotHumAlmThreshold | High humidity alarm threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | The SetHotHumAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.19 | hwNetCol5000CF110SetLowHumAlmThreshold | Low humidity alarm threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | The SetLowHumAlmThreshold of the NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.20 | hwNetCol5000CF110DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The devicename of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.2.1.200 | hwNetCol5000CF110Running2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3 | hwNetCol5000CF110Running3Table | / | / |  |  | / | / | The unning table of NetColCF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.1 | hwNetCol5000CF110Running3Index | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.2 | hwNetCol5000CF110hardwareversion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | The hardware version of the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.3 | hwNetCol5000CF110Calculatedratedcoolingcapacity2 | Calculated rated cooling capacity 2 | 额定制冷量计算值2 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 2 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.4 | hwNetCol5000CF110Calculatedratedcoolingcapacity3 | Calculated rated cooling capacity 3 | 额定制冷量计算值3 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 3 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.5 | hwNetCol5000CF110Calculatedratedcoolingcapacity4 | Calculated rated cooling capacity 4 | 额定制冷量计算值4 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 4 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.6 | hwNetCol5000CF110Calculatedratedcoolingcapacity5 | Calculated rated cooling capacity 5 | 额定制冷量计算值5 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 5 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.7 | hwNetCol5000CF110Calculatedratedcoolingcapacity6 | Calculated rated cooling capacity 6 | 额定制冷量计算值6 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 6 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.8 | hwNetCol5000CF110Calculatedratedcoolingcapacity7 | Calculated rated cooling capacity 7 | 额定制冷量计算值7 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 7 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.9 | hwNetCol5000CF110Calculatedratedcoolingcapacity8 | Calculated rated cooling capacity 8 | 额定制冷量计算值8 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 8 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.10 | hwNetCol5000CF110Calculatedratedcoolingcapacity9 | Calculated rated cooling capacity 9 | 额定制冷量计算值9 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 9 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.11 | hwNetCol5000CF110Calculatedratedcoolingcapacity10 | Calculated rated cooling capacity 10 | 额定制冷量计算值10 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 10 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.12 | hwNetCol5000CF110Calculatedratedcoolingcapacity11 | Calculated rated cooling capacity 11 | 额定制冷量计算值11 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 11 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.13 | hwNetCol5000CF110Calculatedratedcoolingcapacity12 | Calculated rated cooling capacity 12 | 额定制冷量计算值12 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 12 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.14 | hwNetCol5000CF110Calculatedratedcoolingcapacity13 | Calculated rated cooling capacity 13 | 额定制冷量计算值13 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 13 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.15 | hwNetCol5000CF110Calculatedratedcoolingcapacity14 | Calculated rated cooling capacity 14 | 额定制冷量计算值14 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 14 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.16 | hwNetCol5000CF110Calculatedratedcoolingcapacity15 | Calculated rated cooling capacity 15 | 额定制冷量计算值15 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 15 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.17 | hwNetCol5000CF110Calculatedratedcoolingcapacity16 | Calculated rated cooling capacity 16 | 额定制冷量计算值16 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 16 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.18 | hwNetCol5000CF110Calculatedratedcoolingcapacity17 | Calculated rated cooling capacity 17 | 额定制冷量计算值17 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 17 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.19 | hwNetCol5000CF110Calculatedratedcoolingcapacity18 | Calculated rated cooling capacity 18 | 额定制冷量计算值18 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 18 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.20 | hwNetCol5000CF110Calculatedratedcoolingcapacity19 | Calculated rated cooling capacity 19 | 额定制冷量计算值19 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 19 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.21 | hwNetCol5000CF110Calculatedratedcoolingcapacity20 | Calculated rated cooling capacity 20 | 额定制冷量计算值20 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 20 of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.22 | hwNetCol5000CF110HeatMode | Heat mode | 加热方式 | 0-Read_Only | 只读 | dehumidheat(1), lowtempheat(2), dehumidltheat(3) | [除湿补热=1]/[低温加热=2]/[除湿补热且低温加热=3] | The Heat Mode of NetCol5000CF110. Value 1 indicates dehumidheat. Value 2 indicates lowtempheat. Value 3 indicates dehumidltheat.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.23 | hwNetCol5000CF110HeatFunc | Heat | 加热功能 | 0-Read_Only | 只读 | disable(1), enable(2), enableinactivepowersupply(3), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The Heat Func of NetCol5000CF110. Value 1 indicates Disable. Value 2 indicates Enable. Value 3 indicates enable in active power supply.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.24 | hwNetCol5000CF110HumidFunc | Humidity | 加湿功能 | 0-Read_Only | 只读 | disable(1), enable(2), enableinactivepowersupply(3), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The Heat Func of NetCol5000CF110. Value 1 indicates Disable. Value 2 indicates Enable. Value 3 indicates enable in active power supply.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.25 | hwNetCol5000CF110DehumidFunc | Dehumidity | 除湿功能 | 0-Read_Only | 只读 | disable(1), enable(2), enableinactivepowersupply(3), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The Heat Func of NetCol5000CF110. Value 1 indicates Disable. Value 2 indicates Enable. Value 3 indicates enable in active power supply.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.26 | hwNetCol5000CF110TeamworkFunction | Teamwork function | 群控功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The Teamwork Function of NetCol5000CF110. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.27 | hwNetCol5000CF110Totalnumberofactualunits | Total number of actual units | 本群组实际机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The Total number of actual units of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.28 | hwNetCol5000CF110Numberofactiveunits | Number of active units | 本群组实际运行机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The Number of active units of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.29 | hwNetCol5000CF110Numberofstandbyunits | Number of standby units | 本群组实际备机机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The Number of standby units of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.30 | hwNetCol5000CF110TeamworkMode | Teamwork mode | 群控模式 | 0-Read_Only | 只读 | smart(1), iCooling(2), unknown(255) | [智能=1]/[iCooling=2] | The Teamwork Mode of NetCol5000CF110. Value 1 indicates Smart. Value 2 indicates iCooling.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.31 | hwNetCol5000CF110IndoorFanCtrlType | Indoor fan control type | 室内风机控制类型 | 0-Read_Only | 只读 | randsairtempdiffratecontrol(1), pressurediffcontrol(2), supairtempcontrol(3), unknown(255) | [回送风温差比例控制=1]/[压差控制=2]/[送风温度控制=3] | The Indoor Fan Ctrl Type of NetCol5000CF110. Value 1 indicates R/S air temp diff rate control. Value 2 indicates Pressure diff control. Value 3 indicates Sup air temp control.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.32 | hwNetCol5000CF110Electric | Electricity | 电量 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The Electric of NetCol5000CF110.Multiple:100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.33 | hwNetCol5000CF110Power | Power | 功率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | The Power of NetCol5000CF110.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.34 | hwNetCol5000CF110Numberofcondpumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of condpumps of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.35 | hwNetCol5000CF110Numberofindoorfans | Number of indoor fans | 风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of indoorfans of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.36 | hwNetCol5000CF110NumberofCWvalves | Number of CW valves | 冷冻水阀数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of CWvalves of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.37 | hwNetCol5000CF110NumberofPSU | Number of PSU | PSU数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of PSU of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.38 | hwNetCol5000CF110NumberofHumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of Humidifiers of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.39 | hwNetCol5000CF110NumberofHeaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | The Number of Heaters of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.40 | hwNetCol5000CF110TeamworkUnitAddress | Air conditioner address | 机组地址 | 0-Read_Only | 只读 | 1..32 | 1..32 | The Teamwork UnitAddress of NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.41 | hwNetCol5000CF110Curr | Current | 电流 | 0-Read_Only | 只读 | -100000..100000 | -100000..100000 | The Curr of NetCol5000CF110.Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.42 | hwNetCol5000CF110iCoolingRunningStatus | iCooling run status | iCooling运行状态 | 0-Read_Only | 只读 | normal(1), abnormalairconditioner(2), invalidcabinettemperature(3), invalidcabinetpower(4), dataupdatingtimeout(5), inconsistentnumberofteamworkunits(6), notcoldaislecontainment(7), unknown(255) | [正常=1]/[空调异常=2]/[机柜温度无效=3]/[机柜功率无效=4]/[数据更新超时=5]/[群控机组数目不一致=6]/[封闭通道非冷通道=7] | The iCooling Running Status of NetCol5000CF110. Value 1 indicates Normal. Value 2 indicates Abnormal air conditioner. Value 3 indicates Invalid cabinet temperature. Value 4 indicates Invalid cabinet power. Value 5 indicates Data updating timeout. Value 6 indicates Inconsistent number of teamwork units. Value 7 indicates Not cold aisle containment.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.43 | hwNetCol5000CF110SupplyAirHighTemperatureAlarmThreshold | Supply air high temperature alarm threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The Supply Air High Temperature Alarm Threshold of NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.44 | hwNetCol5000CF110L1L2linkagetemperature | L1/L2 linkage target temperature | L1/L2联动目标温度 | 1-Read_Write | 读写 | 150..450 | 150..450 | The L1 L2 linkage temperature of NetCol5000CF110.Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.45 | hwNetCol5000CF110L1L2linkagehumidity | L1/L2 linkage target humidity | L1/L2联动目标湿度 | 1-Read_Write | 读写 | 20..800 | 20..800 | The L1 L2 linkage humidity of NetCol5000CF110.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.46 | hwNetCol5000CF110Calculatedratedcoolingcapacity1 | Calculated rated cooling capacity 1 | 额定制冷量计算值1 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 1 of NetCol5000CF110.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.47 | hwNetCol5000CF110CoolingPower | Rated cooling capacity (cooling power) | 额定的制冷容量（制冷功率） | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Cooling Power of NetCol5000CF110.Multiple:10. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.9.3.1.100 | hwNetCol5000CF110Running3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.4 | hwNetCol5000CF110Running4Table | / | / |  |  | / | / | The unning table of NetColCF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.1 | hwNetCol5000CF110Running4Index | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.3 | hwNetCol5000CF110HostFlag | / | / | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | / | The Host Flag of the NetCol5000CF110. value 1 indicates slave, value 2 indicates master,
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.4 | hwNetCol5000CF110IndoorFan1RunStatus | Indoor fan 1 run status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan1 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.5 | hwNetCol5000CF110IndoorFan2RunStatus | Indoor fan 2 run status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan2 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.6 | hwNetCol5000CF110IndoorFan3RunStatus | Indoor fan 3 run status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan3 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.7 | hwNetCol5000CF110IndoorFan4RunStatus | Indoor fan 4 run status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan4 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.8 | hwNetCol5000CF110IndoorFan5RunStatus | Indoor fan 5 run status | 室内风机5运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan5 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.9 | hwNetCol5000CF110IndoorFan6RunStatus | Indoor fan 6 run status | 室内风机6运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan6 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.10 | hwNetCol5000CF110IndoorFan7RunStatus | Indoor fan 7 run status | 室内风机7运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan7 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.11 | hwNetCol5000CF110IndoorFan8RunStatus | Indoor fan 8 run status | 室内风机8运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan8 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.12 | hwNetCol5000CF110IndoorFan9RunStatus | Indoor fan 9 run status | 室内风机9运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan9 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.13 | hwNetCol5000CF110IndoorFan10RunStatus | Indoor fan 10 run status | 室内风机10运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan10 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.14 | hwNetCol5000CF110IndoorFan11RunStatus | Indoor fan 11 run status | 室内风机11运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan11 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.15 | hwNetCol5000CF110IndoorFan12RunStatus | Indoor fan 12 run status | 室内风机12运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan12 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.16 | hwNetCol5000CF110Tempsetpointhigh | Indoor fan pressure difference setpoint | 室内风机压差设定点 | 1-Read_Write | 读写 | 5..45 | 5..45 | Temp set point high of the NetCol5000CF110.SigUnitInfo:Pa.
1.3.6.1.4.1.2011.6.178.1.1.10.9.4.1.100 | hwNetCol5000CF110Running4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6 | hwNetCol5000CF110Running5Table | / | / |  |  | / | / | The unning table of NetColCF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6.1.1 | hwNetCol5000CF110Running5Index | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6.1.2 | hwNetCol5000CF110Dehumid | Dehumid | 除湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Dehumid of the NetCol5000CF110. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6.1.3 | hwNetCol5000CF110MasterSlaveflag | Master/Slave flag | 主从机标志 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | Master\Slave flag of the NetCol5000CF110. Value 1 indicate slave. Value 2 indicate master.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6.1.4 | hwNetCol5000CF110Indoorfanpressuredifferencesetpoint | Indoor fan pressure difference set point | 室内风机压差设定点 | 0-Read_Only | 只读 | 5..45 | 5..45 | Indoor fan pressure difference set point of the NetCol5000CF110. SigUnitInfo:Pa.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6.1.5 | hwNetCol5000CF110Indoorfansupplyairtemperaturesetpoint | Indoor fan supply air temperature setpoint | 室内风机送风温度设定点 | 0-Read_Only | 只读 | 150..350 | 150..350 | Indoor fan supply air temperature setpoint of the NetCol5000CF110. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6.1.6 | hwNetCol5000CF110Wetfilmhumidifierrunningstatus | Wet film humidifier running status | 湿膜加湿运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier running status of the NetCol5000CF110. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6.1.7 | hwNetCol5000CF110Wetfilmhumidifiercontrolstatus | Wet film humidifier control status | 湿膜加湿控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier control status of the NetCol5000CF110. SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.9.6.1.100 | hwNetCol5000CF110Running5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the NetCol5000CF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.5 | hwNetCol5000CF110ConfigTable | / | / |  |  | / | / | The unning table of NetColCF110.
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.1 | hwNetCol5000CF110ConfigIndex | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.2 | hwNetCol5000CF110IndoorFanMinReturnSupplyAirTempDiff | Indoor fan min return/supply air temperature difference | 室内风机回送风最小温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | The Indoor fan min return/supply air temperature difference of the NetCol5000CF110.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.3 | hwNetCol5000CF110IndoorFanMaxReturnSupplyAirTempDiff | Indoor fan max return/supply air temperature difference | 室内风机回送风最大温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | The Indoor fan max return/supply air temperature difference of the NetCol5000CF110.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.4 | hwNetCol5000CF110IndoorFanTempDiffrence | Indoor fan temperature difference set point | 室内风机温差设定点 | 1-Read_Write | 读写 | 0..450 | 0..450 | The Indoor fan temperature difference set point of the NetCol5000CF110.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.5 | hwNetCol5000CF110IndoorFanControlType | Indoor fan control type | 室内风机控制类型 | 1-Read_Write | 读写 | rSAirtempDiffRateControl(1), pressureDiffControl(2), supplyAirTempControl(3), unknown(255) | [回送风温差比例控制=1]/[压差控制=2]/[送风温度控制=3] | The Indoor fan control type of the NetCol5000CF110. value 1 indicates R/S air temp diff rate control. Value 2 indicates Pressure diff control. Value 3 indicates Supply air temp control.
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.6 | hwNetCol5000CF110TempAndHumControlType | Temperature and humidity control type | 温湿度控制类型 | 1-Read_Write | 读写 | returnair(1), supplyair(2), coldaisle(3), hotaisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | The Temperature and humidity control type of the NetCol5000CF110. value 1 indicates Return air. value 2 indicates Supply air. value 3 indicates Cold aisle. value 4 indicates Hot aisle.
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.7 | hwNetCol5000CF110IndoorFan13totalRuntime | Indoor fan 13 total runtime | 室内风机13累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan13totalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.8 | hwNetCol5000CF110IndoorFan14totalRuntime | Indoor fan 14 total runtime | 室内风机14累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan14totalRuntime of the NetCol5000CF110. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.9 | hwNetCol5000CF110IndoorFan13RunStatus | Indoor fan 13 run status | 室内风机13运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan13 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.10 | hwNetCol5000CF110IndoorFan14RunStatus | Indoor fan 14 run status | 室内风机14运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan14 Run Status of the NetCol5000CF110. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.10.9.5.1.100 | hwNetCol5000CF110ConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the NetCol5000CF110.

## NetCol5000-A
NetCol5000-A
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.10 | NetCol5000A | NetCol5000-A | NetCol5000-A | / | / | / | / | NetCol5000-A Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1 | hwNetCol5000ARunning1Table | / | / |  |  | / | / | The running table of NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.1 | hwNetCol5000ARunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.2 | hwNetCol5000AModel | Model | 机型 | 0-Read_Only | 只读 | netcol5000a(1), netcol5000c(2), unknown(255) | [NetCol5000A=1]/[NetCol5000C=2] | Model of the device config table for the NetCol5000-A. Value 1 indicate netcol5000a Value 2 indicate netcol5000c
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.3 | hwNetCol5000ANumberOfIndoorFans | Number of indoor fans | 风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of indoor fans of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.4 | hwNetCol5000ANumberOfCompressors | Number of compressors | 压缩机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of compressors of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.6 | hwNetCol5000ANumberOfHeaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of heaters of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.7 | hwNetCol5000ANumberOfHumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of humidifiers of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.8 | hwNetCol5000ANumberOfCondPumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of cond pumps of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.9 | hwNetCol5000ANumberOfPsu | Number of PSU | PSU块数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of psu of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.10 | hwNetCol5000ACompressorTotalRuntime | Compressor total runtime | 压缩机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.11 | hwNetCol5000AIndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 1 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.12 | hwNetCol5000AIndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 2 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.13 | hwNetCol5000AIndoorFan3TotalRuntime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 3 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.14 | hwNetCol5000AIndoorFan4TotalRuntime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 4 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.15 | hwNetCol5000AIndoorFan5TotalRuntime | Indoor fan 5 total runtime | 室内风机5累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 5 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.16 | hwNetCol5000AIndoorFan6TotalRuntime | Indoor fan 6 total runtime | 室内风机6累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 6 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.17 | hwNetCol5000AIndoorFan7TotalRuntime | Indoor fan 7 total runtime | 室内风机7累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 7 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.18 | hwNetCol5000AIndoorFan8TotalRuntime | Indoor fan 8 total runtime | 室内风机8累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 8 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.19 | hwNetCol5000AIndoorFan9TotalRuntime | Indoor fan 9 total runtime | 室内风机9累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 9 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.20 | hwNetCol5000AIndoorFan10TotalRuntime | Indoor fan 10 total runtime | 室内风机10累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 10 total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.21 | hwNetCol5000AHumidifierTotalRuntime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.22 | hwNetCol5000AHeaterTotalRuntime | Heater total runtime | 电加热累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Heater total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.23 | hwNetCol5000ADrainPumpTotalRuntime | Drain pump total runtime | 排水水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Drain pump total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.24 | hwNetCol5000AReturnAirFilterTotalRuntime | Return air filter total runtime | 回风过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Return air filter total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.25 | hwNetCol5000AHumidifierPumpTotalRuntime | Humidifier pump total runtime | 加湿水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier pump total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.26 | hwNetCol5000AEevTotalRuntime | EEV total runtime | EEV累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EEV total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.27 | hwNetCol5000AOutFanTotalRuntime | Out fan total runtime | 室外风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Out fan total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.28 | hwNetCol5000AIndoorFanTotalRuntime | Indoor fan total runtime | 室内风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.29 | hwNetCol5000AUnitOnorOffStatus | Unit on/off status | 机组开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Unit on/off status of the device config table for the NetCol5000-A. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.30 | hwNetCol5000ACoolingOutput | Cooling output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Cooling output of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.31 | hwNetCol5000AFanOutput | Fan output | 室内风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Fan output of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.32 | hwNetCol5000AHumidifyingOutput | Humidifying output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidifying output of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.33 | hwNetCol5000AHeatingOutput | Heating output | 加热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Heating output of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.34 | hwNetCol5000ADehumidityOutput | Dehumidity output | 除湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Dehumidity output of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.35 | hwNetCol5000ACoolingCapacity | Cooling capacity | 制冷量 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | Cooling capacity of the device config table for the NetCol5000-A.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.36 | hwNetCol5000ATeamworkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), intelligentteamworkcontrol(2), icooling(3), unknown(255) | [单机=1]/[智能群控=2]/[iCooling=3] | Teamwork status of the device config table for the NetCol5000-A. Value 1 indicate single Value 2 indicate intelligent teamwork control Value 3 indicate icooling
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.37 | hwNetCol5000ATotalNumberOfUnits | Total number of units | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Total number of units of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.38 | hwNetCol5000ANumberOfRunningUnits | Number of running units | 本群组运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of running units of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.39 | hwNetCol5000AHeatMode | Heat mode | 加热方式 | 0-Read_Only | 只读 | dehumidheat(1), lowTempheat(2), dehumidandltheat(3), unknown(255) | [除湿补热=1]/[低温加热=2]/[除湿补热且低温加热=3] | Heat mode of the device config table for the NetCol5000-A. Value 1 indicate dehumid heat Value 2 indicate low-temp heat Value 3 indicate dehumid & lt heat
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.40 | hwNetCol5000AOutdoorUnitCondensateMode | Outdoor unit condensate mode | 室外机冷凝方式 | 0-Read_Only | 只读 | airCooled(1), waterCooled(2), unknown(255) | [风冷=1]/[水冷=2] | Outdoor unit condensate mode of the device config table for the NetCol5000-A. Value 1 indicate air-cooled Value 2 indicate water-cooled
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.41 | hwNetCol5000APowerFrequency | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | Power frequency of the device config table for the NetCol5000-A.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.42 | hwNetCol5000AABLineVoltage | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | A-B line voltage of the device config table for the NetCol5000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.43 | hwNetCol5000ABCLineVoltage | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | B-C line voltage of the device config table for the NetCol5000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.44 | hwNetCol5000ACALineVoltage | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | C-A line voltage of the device config table for the NetCol5000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.45 | hwNetCol5000ABackupABLineVoltage | Backup A-B line voltage | 备路AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup A-B line voltage of the device config table for the NetCol5000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.46 | hwNetCol5000ABackupBCLineVoltage | Backup B-C line voltage | 备路BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup B-C line voltage of the device config table for the NetCol5000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.47 | hwNetCol5000ABackupCALineVoltage | Backup C-A line voltage | 备路CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup C-A line voltage of the device config table for the NetCol5000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.48 | hwNetCol5000ABackupPowerFrequency | Backup power frequency | 备路电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | Backup power frequency of the device config table for the NetCol5000-A.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.49 | hwNetCol5000ALoadForPrimaryLine | Load for primary line | 主路带载 | 0-Read_Only | 只读 | 0..1 | 0..1 | Load for primary line of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.50 | hwNetCol5000ALoadForBackupLine | Load for backup line | 备路带载 | 0-Read_Only | 只读 | 0..1 | 0..1 | Load for backup line of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.51 | hwNetCol5000ATorHControlType | T/H control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnAir(1), supplyAir(2), coldAisle(3), hotAisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | T/H control type of the device config table for the NetCol5000-A. Value 1 indicate return-air Value 2 indicate supply-air Value 3 indicate cold-aisle Value 4 indicate hot-aisle
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.52 | hwNetCol5000ACurrentTemperature | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Current temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.53 | hwNetCol5000ACurrentHumidity | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Current humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.54 | hwNetCol5000ASupplyAirAverageTemperature | Supply-air average temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply-air average temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.55 | hwNetCol5000AReturnAirAverageTemperature | Return-air average temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return-air average temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.56 | hwNetCol5000AColdAisleAverageTemperature | Cold-aisle average temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold-aisle average temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.57 | hwNetCol5000AHotAisleAverageTemperature | Hot-aisle average temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot-aisle average temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.58 | hwNetCol5000ASupplyAirAverageHumidity | Supply-air average humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Supply-air average humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.59 | hwNetCol5000AReturnAirAverageHumidity | Return-air average humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Return-air average humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.60 | hwNetCol5000AColdAisleAverageHumidity | Cold-aisle average humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold-aisle average humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.61 | hwNetCol5000AHotAisleAverageHumidity | Hot-aisle average humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot-aisle average humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.62 | hwNetCol5000ACompRunStatus | Comp run status | 压缩机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Comp run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.63 | hwNetCol5000ADischargePressure | Discharge pressure | 排气压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | Discharge pressure of the device config table for the NetCol5000-A.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.64 | hwNetCol5000ASuctionPressure | Suction pressure | 吸气压力 | 0-Read_Only | 只读 | -10..1000 | -10..1000 | Suction pressure of the device config table for the NetCol5000-A.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.65 | hwNetCol5000ADischargeTemperature | Discharge temperature | 排气温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Discharge temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.66 | hwNetCol5000ASuctionTemperature | Suction temperature | 吸气温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Suction temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.67 | hwNetCol5000ALiquidPipeTemperature | Liquid pipe temperature | 液管温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Liquid pipe temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.68 | hwNetCol5000APhaseCurrent | Phase current | 相电流 | 0-Read_Only | 只读 | 0..25000 | 0..25000 | Phase current of the device config table for the NetCol5000-A.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.69 | hwNetCol5000ARefrigerantStatus | Refrigerant status | 制冷剂状态 | 0-Read_Only | 只读 | normal(1), inadequate(2), seriouslyinadequate(3), overcharged(4), unknown(255) | [正常=1]/[不足=2]/[严重不足=3]/[过充=4] | Refrigerant status of the device config table for the NetCol5000-A. Value 1 indicate normal Value 2 indicate inadequate Value 3 indicate seriously inadequate Value 4 indicate overcharged
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.70 | hwNetCol5000AIndoorFan1RunStatus | Indoor fan 1 run status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 1 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.71 | hwNetCol5000AIndoorFan2RunStatus | Indoor fan 2 run status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 2 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.72 | hwNetCol5000AIndoorFan3RunStatus | Indoor fan 3 run status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 3 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.73 | hwNetCol5000AIndoorFan4RunStatus | Indoor fan 4 run status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 4 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.74 | hwNetCol5000AIndoorFan5RunStatus | Indoor fan 5 run status | 室内风机5运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 5 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.75 | hwNetCol5000AIndoorFan6RunStatus | Indoor fan 6 run status | 室内风机6运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 6 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.76 | hwNetCol5000AIndoorFan7RunStatus | Indoor fan 7 run status | 室内风机7运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 7 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.77 | hwNetCol5000AIndoorFan8RunStatus | Indoor fan 8 run status | 室内风机8运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 8 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.78 | hwNetCol5000AIndoorFan9RunStatus | Indoor fan 9 run status | 室内风机9运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 9 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.79 | hwNetCol5000AIndoorFan10RunStatus | Indoor fan 10 run status | 室内风机10运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 10 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.80 | hwNetCol5000AIndoorFanRunStatus | Indoor fan run status | 室内风机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.81 | hwNetCol5000AAverageAirSidePressureDifference | Average air side pressure difference | 风侧平均压差 | 0-Read_Only | 只读 | 0..500 | 0..500 | Average air side pressure difference of the device config table for the NetCol5000-A.SigUnitInfo:Pa.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.82 | hwNetCol5000AIndoorFanControlStatus | Indoor fan control status | 室内风机控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan control status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.83 | hwNetCol5000AIndoorFanControlType | Indoor fan control type | 室内风机控制类型 | 0-Read_Only | 只读 | retairtempdiffratecontrol(1), pressurediffcontrol(2), unknown(255) | [回送风温差比例控制=1]/[压差控制=2] | Indoor fan control type of the device config table for the NetCol5000-A. Value 1 indicate ret air temp diff rate control Value 2 indicate pressure diff control
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.84 | hwNetCol5000AOutdoorFanRunningStatus | Outdoor fan running status | 室外风机运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor fan running status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.85 | hwNetCol5000AOutdoorTemperature | Outdoor temperature | 室外温度 | 0-Read_Only | 只读 | -3000..3000 | -3000..3000 | Outdoor temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.86 | hwNetCol5000AWetFilmHumidifierRunningStatus | Wet film humidifier running status | 湿膜加湿运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier running status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.87 | hwNetCol5000AWetFilmHumidifierControlStatus | Wet film humidifier control status | 湿膜加湿控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier control status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.88 | hwNetCol5000AElectricHeaterRunningStatus | Electric heater running status | 电加热运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Electric heater running status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.89 | hwNetCol5000AEevRunningStatus | EEV running status | EEV运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | EEV running status of the device config table for the NetCol5000-A.SigUnitInfo:step.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.90 | hwNetCol5000AEevSuctionSuperheatDegree | EEV suction superheat degree | EEV吸气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | EEV suction superheat degree of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.91 | hwNetCol5000AEevDischargeSuperheatDegree | EEV discharge superheat degree | EEV排气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | EEV discharge superheat degree of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.92 | hwNetCol5000AWaterValveRunningStatus | Water-cooled module water valve running status | 水冷模块水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Water valve running status of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.93 | hwNetCol5000ASupplyWaterTemp | Water-cooled module supply-water temperature | 水冷模块供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Supply-water temp of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.94 | hwNetCol5000AReturnWaterTemp | Water-cooled module return-water temperature | 水冷模块回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Return-water temp of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.95 | hwNetCol5000ANumberOfAlarm | Number of alarm | 告警数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Number of alarm of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.96 | hwNetCol5000AElectricity | Electricity | 电量 | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Electricity of the device config table for the NetCol5000-A.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.97 | hwNetCol5000APower | Power | 功率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | Power of the device config table for the NetCol5000-A.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.98 | hwNetCol5000ACommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the NetCol5000-A. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.99 | hwNetCol5000AIpAddress | / | / | 0-Read_Only | 只读 | 0..4294967295 | / | IP address of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.100 | hwNetCol5000AEsn | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.101 | hwNetCol5000ASoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.102 | hwNetCol5000AHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.103 | hwNetCol5000AELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.104 | hwNetCol5000AHostIdentity | Host identity | 主机标识 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | Host identity of the device config table for the NetCol5000-A. Value 1 indicate slave Value 2 indicate master
1.3.6.1.4.1.2011.6.178.1.1.10.10.1.1.201 | hwNetCol5000ARunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2 | hwNetCol5000AConfig2Table | / | / |  |  | / | / | The config table of NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.1 | hwNetCol5000AConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.2 | hwNetCol5000ADeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.3 | hwNetCol5000AStartuporShutdownControl | Startup/shutdown control | 控制开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Startup/shutdown control of the device config table for the NetCol5000-A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.4 | hwNetCol5000ABaudRate | Baud rate | 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate19200(2), unknown(255) | [9600=1]/[19200=2] | Baud rate of the device config table for the NetCol5000-A. Value 1 indicate 9600 Value 2 indicate 19200
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.5 | hwNetCol5000ACommunicationAddress | Communication address | 通信地址 | 1-Read_Write | 读写 | 1..255 | 1..255 | Communication address of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.6 | hwNetCol5000AReturnAirHtThreshold | Return-air HT threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Return-air HT threshold of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.7 | hwNetCol5000AReturnAirLtThreshold | Return-air LT threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Return-air LT threshold of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.8 | hwNetCol5000ASupplyAirHtThreshold | Supply-air HT threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Supply-air HT threshold of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.9 | hwNetCol5000ASupplyAirLtThreshold | Supply-air LT threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | Supply-air LT threshold of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.10 | hwNetCol5000AColdAisleHtThreshold | Cold-aisle HT threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Cold-aisle HT threshold of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.11 | hwNetCol5000AHotAisleHtThreshold | Hot-aisle HT threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | Hot-aisle HT threshold of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.12 | hwNetCol5000AHumidityHighThreshold | Humidity high threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | Humidity high threshold of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.13 | hwNetCol5000AHumidityLowThreshold | Humidity low threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | Humidity low threshold of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.14 | hwNetCol5000ATemperatureSetpoint | Temperature setpoint | 温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | Temperature setpoint of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.15 | hwNetCol5000AHumiditySetpoint | Humidity setpoint | 湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Humidity setpoint of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.16 | hwNetCol5000AVerflag | VerFlag | 版本标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | VerFlag of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.17 | hwNetCol5000APortMAC | MAC address | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.18 | hwNetCol5000AIcoolingType | iCooling type | iCooling类型 | 1-Read_Write | 读写 | iCooling1.0(1), iCooling2.0(2), unknown(255) | [iCooling1.0=1]/[iCooling2.0=2] | iCooling type of the device config table for the NetCol5000-A. Value 1 indicate iCooling1.0 Value 2 indicate iCooling2.0
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.19 | hwNetCol5000AIcoolingTemperatureAndHumidityControlType | iCooling temperature and humidity control type | iCooling温湿度控制类型 | 1-Read_Write | 读写 | returnAir(1), supplyAir(2), coldAisle(3), hotAisle(4), unknown(255) | [回风=0]/[送风=1]/[冷通道=2]/[热通道=3] | iCooling temperature and humidity control type of the device config table for the NetCol5000-A. Value 1 indicate return-air Value 2 indicate supply-air Value 3 indicate cold-aisle Value 4 indicate hot-aisle
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.20 | hwNetCol5000AIcoolingHeartbeat | iCooling heartbeat | iCooling心跳 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | iCooling heartbeat of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.21 | hwNetCol5000AIcoolingIndoorFanMaxReturnorSupplyAirTemperatur | icooling indoor fan max return/supply air temperature difference | iCooling室内风机回送风最大温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | icooling indoor fan max return/supply air temperature difference of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.22 | hwNetCol5000AIcoolingMaxIndoorFanSpeed | iCooling max indoor fan speed | iCooling室内风机最大转速 | 1-Read_Write | 读写 | 30..100 | 30..100 | iCooling max indoor fan speed of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.23 | hwNetCol5000AIcoolingMaxOutdoorFanRunningPressure | iCooling max outdoor fan running pressure | iCooling室外风机最大运行压力 | 1-Read_Write | 读写 | 150..400 | 150..400 | iCooling max outdoor fan running pressure of the device config table for the NetCol5000-A.Multiple:100.SigUnitInfo:MPa.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.24 | hwNetCol5000AIcoolingIndoorFanControlType | iCooling indoor fan control type | iCooling室内风机控制类型 | 1-Read_Write | 读写 | retairtempdiffratecontrol(1), pressurediffcontrol(2), unknown(255) | [回送风温差比例控制=1]/[压差控制=4] | iCooling indoor fan control type of the device config table for the NetCol5000-A. Value 1 indicate retairtempdiffratecontrol Value 4 indicate pressurediffcontrol
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.25 | hwNetCol5000AIcoolingTemperatureSetpoint | iCooling temperature setpoint | iCooling温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | iCooling temperature setpoint of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.26 | hwNetCol5000AIcoolingHumiditySetpoint | iCooling humidity setpoint | iCooling湿度设定点 | 1-Read_Write | 读写 | 200..800 | 200..800 | iCooling humidity setpoint of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.27 | hwNetCol5000AIcoolingStartuporShutdownControl | iCooling startup/shutdown control | iCooling控制开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=0]/[开机=1] | iCooling startup/shutdown control of the device config table for the NetCol5000-A. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.10.2.1.101 | hwNetCol5000AConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3 | hwNetCol5000ARunning2Table | / | / |  |  | / | / | The running table of NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.1 | hwNetCol5000ARunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.2 | hwNetCol5000ANumberOfWaterCooledModule | Number of water-cooled module | 水冷模块数量 | 0-Read_Only | 只读 | 0..225 | 0..225 | Number of water-cooled module of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.3 | hwNetCol5000AColdAisle1Temperature | Cold aisle 1 temperature | 冷通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 1 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.4 | hwNetCol5000AColdAisle2Temperature | Cold aisle 2 temperature | 冷通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 2 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.5 | hwNetCol5000AColdAisle3Temperature | Cold aisle 3 temperature | 冷通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 3 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.6 | hwNetCol5000AColdAisle4Temperature | Cold aisle 4 temperature | 冷通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 4 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.7 | hwNetCol5000AColdAisle5Temperature | Cold aisle 5 temperature | 冷通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 5 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.8 | hwNetCol5000AColdAisle1Humidity | Cold aisle 1 humidity | 冷通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 1 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.9 | hwNetCol5000AColdAisle2Humidity | Cold aisle 2 humidity | 冷通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 2 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.10 | hwNetCol5000AColdAisle3Humidity | Cold aisle 3 humidity | 冷通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 3 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.11 | hwNetCol5000AColdAisle4Humidity | Cold aisle 4 humidity | 冷通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 4 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.12 | hwNetCol5000AColdAisle5Humidity | Cold aisle 5 humidity | 冷通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 5 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.13 | hwNetCol5000AHotAisle1Temperature | Hot aisle 1 temperature | 热通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 1 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.14 | hwNetCol5000AHotAisle2Temperature | Hot aisle 2 temperature | 热通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 2 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.15 | hwNetCol5000AHotAisle3Temperature | Hot aisle 3 temperature | 热通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 3 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.16 | hwNetCol5000AHotAisle4Temperature | Hot aisle 4 temperature | 热通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 4 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.17 | hwNetCol5000AHotAisle5Temperature | Hot aisle 5 temperature | 热通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 5 temperature of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.18 | hwNetCol5000AHotAisle1Humidity | Hot aisle 1 humidity | 热通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 1 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.19 | hwNetCol5000AHotAisle2Humidity | Hot aisle 2 humidity | 热通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 2 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.20 | hwNetCol5000AHotAisle3Humidity | Hot aisle 3 humidity | 热通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 3 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.21 | hwNetCol5000AHotAisle4Humidity | Hot aisle 4 humidity | 热通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 4 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.22 | hwNetCol5000AHotAisle5Humidity | Hot aisle 5 humidity | 热通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 5 humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.23 | hwNetCol5000AIndoorFan11RunStatus | Indoor fan 11 run status | 室内风机11运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 11 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.24 | hwNetCol5000AIndoorFan12RunStatus | Indoor fan 12 run status | 室内风机12运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 12 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.25 | hwNetCol5000AIndoorFan13RunStatus | Indoor fan 13 run status | 室内风机13运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 13 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.26 | hwNetCol5000AIndoorFan14RunStatus | Indoor fan 14 run status | 室内风机14运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 14 run status of the device config table for the NetCol5000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.27 | hwNetCol5000ASystemPower | System power | 机组总功率 | 0-Read_Only | 只读 | 0..4000 | 0..4000 | System power of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.28 | hwNetCol5000AOutdoorFanHumidity | Outdoor fan humidity | 室外机湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Outdoor fan humidity of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.29 | hwNetCol5000AOutdoorSprayRunningStatus | Outdoor spray running status | 室外机喷淋运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor spray running status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.30 | hwNetCol5000ASystemTotalPowerConsumptionFlag | System total power consumption flag | 机组累计耗电量标识 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | System total power consumption flag of the device config table for the NetCol5000-A. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.31 | hwNetCol5000AAcInputTotalPowerConsumption | AC input total power consumption | 机组交流输入累计电量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AC input total power consumption of the device config table for the NetCol5000-A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.32 | hwNetCol5000ATotalOpenTimesOfTheWaterInletSolenoidValve | Total open times of the water inlet solenoid valve | 进水电磁阀累计开启次数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total open times of the water inlet solenoid valve of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.33 | hwNetCol5000AOutdoorSprayNum |  |  | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Number of outdoor spray of the device config table for the NetCol5000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.34 | hwNetCol5000ADrainPumpRunningStatus | Drain pump running status | 排水水泵运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Drain pump running status of the device config table for the NetCol5000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.35 | hwNetCol5000AOutdoorSprayTotalRuntime | Outdoor spray total runtime | 室外机喷淋累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor spray total runtime of the device config table for the NetCol5000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.10.3.1.300 | hwNetCol5000ARunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol5000-A.

## NetCol8000-A
NetCol8000-A
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.10.11 | NetCol8000A | NetCol8000-A | NetCol8000-A | / | / | / | / | NetCol8000-A Equipment.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1 | hwNetCol8000ARunning1Table | / | / |  |  | / | / | The running table of NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.1 | hwNetCol8000ARunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.2 | hwNetCol8000ACompressorTotalRuntime | Compressor total runtime | 压缩机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.3 | hwNetCol8000ACompressor1TotalRuntime | Compressor 1 total runtime | 压缩机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor 1 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.4 | hwNetCol8000ACompressor2TotalRuntime | Compressor 2 total runtime | 压缩机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor 2 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.5 | hwNetCol8000AIndoorFanTotalRuntime | Indoor fan total runtime | 室内风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.6 | hwNetCol8000AIndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 1 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.7 | hwNetCol8000AIndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Indoor fan 2 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.8 | hwNetCol8000AHumidifierPumpTotalRuntime | Humidifier pump total runtime | 加湿水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier pump total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.9 | hwNetCol8000AHumidifierTotalRuntime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Humidifier total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.10 | hwNetCol8000AElectricHeaterTotalRuntime | Electric heater total runtime | 电加热累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Electric heater total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.11 | hwNetCol8000AElectricHeater1TotalRuntime | Electric heater 1 total runtime | 电加热1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Electric heater 1 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.12 | hwNetCol8000AElectricHeater2TotalRuntime | Electric heater 2 total runtime | 电加热2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Electric heater 2 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.13 | hwNetCol8000AReturnAirFilterTotalRuntime | Return air filter total runtime | 回风过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Return air filter total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.14 | hwNetCol8000AEevTotalRuntime | EEV total runtime | EEV累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EEV total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.15 | hwNetCol8000AEev1TotalRuntime | EEV 1 total runtime | EEV1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EEV 1 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.16 | hwNetCol8000AEev2TotalRuntime | EEV 2 total runtime | EEV2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | EEV 2 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.17 | hwNetCol8000AOutdoorFanTotalRuntime | Outdoor fan total runtime | 室外风机累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor fan total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.18 | hwNetCol8000AOutdoorFan1TotalRuntime | Outdoor fan 1 total runtime | 室外风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor fan 1 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.19 | hwNetCol8000AOutdoorFan2TotalRuntime | Outdoor fan 2 total runtime | 室外风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor fan 2 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.20 | hwNetCol8000AOnorOffStatusOfSystem | On/Off status of system | 机组开关机状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | On/Off status of system of the device config table for the NetCol8000-A. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.21 | hwNetCol8000ACoolingOutput | Cooling output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Cooling output of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.22 | hwNetCol8000AIndoorFanOutput | Indoor fan output | 室内风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan output of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.23 | hwNetCol8000AHumidifyingOutput | Humidifying output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidifying output of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.24 | hwNetCol8000AHeatingOutput | Heating output | 加热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Heating output of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.25 | hwNetCol8000ADehumid | Dehumid | 除湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | Dehumid of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.26 | hwNetCol8000ACoolingCapacity | Cooling capacity | 制冷量 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | Cooling capacity of the device config table for the NetCol8000-A.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.27 | hwNetCol8000AActualTotalNumberOfSystemsInThisGroup | Actual total number of systems in this group | 本群组实际机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Actual total number of systems in this group of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.28 | hwNetCol8000ANumberOfActualActiveSystemsInThisGroup | Number of actual active systems in this group | 本群组实际运行机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Number of actual active systems in this group of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.29 | hwNetCol8000ANumberOfActualStandbySystemsInThisGroup | Number of actual standby systems in this group | 本群组实际备机机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | Number of actual standby systems in this group of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.30 | hwNetCol8000ANumberOfSystemsInThisGroup | Number of systems in this group | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of systems in this group of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.31 | hwNetCol8000ANumberOfRunningSystemsInThisGroup | Number of running systems in this group | 本群组运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | Number of running systems in this group of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.32 | hwNetCol8000AMasterorSlaveFlag | Master/Slave flag | 主从机标志 | 0-Read_Only | 只读 | slaveunit(1), masterunit(2), unknown(255) | [从机=1]/[主机=2] | Master/Slave flag of the device config table for the NetCol8000-A. Value 1 indicate slaveUnit Value 2 indicate masterUnit
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.33 | hwNetCol8000ATeamworkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), smartteamworkcontrol(2), icooling(3), unknown(255) | [单机=1]/[智能群控=2]/[iCooling=3] | Teamwork status of the device config table for the NetCol8000-A. Value 1 indicate single Value 2 indicate smartteamworkcontrol Value 3 indicate icooling
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.34 | hwNetCol8000APowerFrequency | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | Power frequency of the device config table for the NetCol8000-A.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.35 | hwNetCol8000AABLineVoltage | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | A-B line voltage of the device config table for the NetCol8000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.36 | hwNetCol8000ABCLineVoltage | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | B-C line voltage of the device config table for the NetCol8000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.37 | hwNetCol8000ACALineVoltage | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | C-A line voltage of the device config table for the NetCol8000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.38 | hwNetCol8000ABackupABLineVoltage | Backup A-B line voltage | 备路AB线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup A-B line voltage of the device config table for the NetCol8000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.39 | hwNetCol8000ABackupBCLineVoltage | Backup B-C line voltage | 备路BC线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup B-C line voltage of the device config table for the NetCol8000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.40 | hwNetCol8000ABackupCALineVoltage | Backup C-A line voltage | 备路CA线电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Backup C-A line voltage of the device config table for the NetCol8000-A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.41 | hwNetCol8000ABackupPowerFrequency | Backup power frequency | 备路电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | Backup power frequency of the device config table for the NetCol8000-A.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.42 | hwNetCol8000ACompressorRunningStatus | Compressor running status | 压缩机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Compressor running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.43 | hwNetCol8000ACompressorRefrigerantStatus | Compressor refrigerant status | 压缩机制冷剂状态 | 0-Read_Only | 只读 | normal(1), inadequate(2), seriouslyinadequate(3), overcharged(4), unknown(255) | [正常=1]/[不足=2]/[严重不足=3]/[过充=4] | Compressor refrigerant status of the device config table for the NetCol8000-A. Value 1 indicate normal Value 2 indicate inadequate Value 3 indicate seriouslyInadequate Value 4 indicate overcharged
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.44 | hwNetCol8000ACompressor1RunningStatus | Compressor 1 running status | 压缩机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Compressor 1 running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.45 | hwNetCol8000ACompressor1RefrigerantStatus | Compressor 1 refrigerant status | 压缩机1制冷剂状态 | 0-Read_Only | 只读 | normal(1), inadequate(2), seriouslyinadequate(3), overcharged(4), unknown(255) | [正常=1]/[不足=2]/[严重不足=3]/[过充=4] | Compressor 1 refrigerant status of the device config table for the NetCol8000-A. Value 1 indicate normal Value 2 indicate inadequate Value 3 indicate seriouslyInadequate Value 4 indicate overcharged
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.46 | hwNetCol8000ACompressor2RunningStatus | Compressor 2 running status | 压缩机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Compressor 2 running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.47 | hwNetCol8000ACompressor2RefrigerantStatus | Compressor 2 refrigerant status | 压缩机2制冷剂状态 | 0-Read_Only | 只读 | normal(1), inadequate(2), seriouslyinadequate(3), overcharged(4), unknown(255) | [正常=1]/[不足=2]/[严重不足=3]/[过充=4] | Compressor 2 refrigerant status of the device config table for the NetCol8000-A. Value 1 indicate normal Value 2 indicate inadequate Value 3 indicate seriouslyInadequate Value 4 indicate overcharged
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.48 | hwNetCol8000ATemperatureAndHumidityControlType | Temperature and humidity control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnair(1), supplyair(2), coldaisle(3), hotaisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | Temperature and humidity control type of the device config table for the NetCol8000-A. Value 1 indicate returnair Value 2 indicate supplyair Value 3 indicate coldaisle Value 4 indicate hotaisle
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.49 | hwNetCol8000ACurrentTemperature | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Current temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.50 | hwNetCol8000ACurrentHumidity | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Current humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.51 | hwNetCol8000AAverageSupplyAirTemperature | Average supply air temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Average supply air temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.52 | hwNetCol8000AAverageReturnAirTemperature | Average return air temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Average return air temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.53 | hwNetCol8000AAverageColdAisleTemperature | Average cold aisle temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Average cold aisle temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.54 | hwNetCol8000AAverageHotAisleTemperature | Average hot aisle temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Average hot aisle temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.55 | hwNetCol8000AAverageSupplyAirHumidity | Average supply air humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Average supply air humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.56 | hwNetCol8000AAverageReturnAirHumidity | Average return air humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Average return air humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.57 | hwNetCol8000AAverageColdAisleHumidity | Average cold aisle humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Average cold aisle humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.58 | hwNetCol8000AAverageHotAisleHumidity | Average hot aisle humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Average hot aisle humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.59 | hwNetCol8000AIndoorFan1RunningStatus | Indoor fan 1 running status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 1 running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.60 | hwNetCol8000AIndoorFanRunningStatus | Indoor fan running status | 室内风机运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.61 | hwNetCol8000AIndoorFan2RunningStatus | Indoor fan 2 running status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Indoor fan 2 running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.62 | hwNetCol8000AAverageAirSidePressureDifference | Average air side pressure difference | 风侧平均压差 | 0-Read_Only | 只读 | 0..500 | 0..500 | Average air side pressure difference of the device config table for the NetCol8000-A.SigUnitInfo:Pa.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.63 | hwNetCol8000AIndoorFan1ControlStatus | Indoor fan 1 control status | 室内风机1控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan 1 control status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.64 | hwNetCol8000AIndoorFanControlStatus | Indoor fan control status | 室内风机控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan control status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.65 | hwNetCol8000AIndoorFan2ControlStatus | Indoor fan 2 control status | 室内风机2控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Indoor fan 2 control status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.66 | hwNetCol8000AOutdoorFan1RunningStatus | Outdoor fan 1 running status | 室外机1风机运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor fan 1 running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.67 | hwNetCol8000AOutdoorFan1Temperature | Outdoor fan 1 temperature | 室外机1室外温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Outdoor fan 1 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.68 | hwNetCol8000AOutdoorFanRunningStatus | Outdoor fan running status | 室外机风机运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor fan running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.69 | hwNetCol8000AOutdoorFanTemperature | Outdoor fan temperature | 室外机室外温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Outdoor fan temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.70 | hwNetCol8000AOutdoorFan2RunningStatus | Outdoor fan 2 running status | 室外机2风机运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor fan 2 running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.71 | hwNetCol8000AOutdoorFan2Temperature | Outdoor fan 2 temperature | 室外机2室外温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Outdoor fan 2 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.72 | hwNetCol8000AWetFilmHumidifierRunningStatus | Wet film humidifier running status | 湿膜加湿运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.73 | hwNetCol8000AWetFilmHumidifierControlStatus | Wet film humidifier control status | 湿膜加湿控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Wet film humidifier control status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.74 | hwNetCol8000AElectricHeater1RunningStatus | Electric heater 1 running status | 电加热1运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Electric heater 1 running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.75 | hwNetCol8000AElectricHeaterRunningStatus | Electric heater running status | 电加热运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Electric heater running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.76 | hwNetCol8000AElectricHeater2RunningStatus | Electric heater 2 running status | 电加热2运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Electric heater 2 running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.77 | hwNetCol8000AEev1RunningStatus | EEV 1 running status | EEV1运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | EEV 1 running status of the device config table for the NetCol8000-A.SigUnitInfo:step.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.78 | hwNetCol8000ASuctionSuperheatDegree1 | Suction superheat degree 1 | 吸气过热度1 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | Suction superheat degree 1 of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.79 | hwNetCol8000ADischargeSuperheatDegree1 | Discharge superheat degree 1 | 排气过热度1 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | Discharge superheat degree 1 of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.80 | hwNetCol8000AEevRunningStatus | EEV running status | EEV运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | EEV running status of the device config table for the NetCol8000-A.SigUnitInfo:step.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.81 | hwNetCol8000ASuctionSuperheatDegree | Suction superheat degree | 吸气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | Suction superheat degree of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.82 | hwNetCol8000ADischargeSuperheatDegree | Discharge superheat degree | 排气过热度 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | Discharge superheat degree of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.83 | hwNetCol8000AEev2RunningStatus | EEV 2 running status | EEV2运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | EEV 2 running status of the device config table for the NetCol8000-A.SigUnitInfo:step.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.84 | hwNetCol8000ASuctionSuperheatDegree2 | Suction superheat degree 2 | 吸气过热度2 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | Suction superheat degree 2 of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.85 | hwNetCol8000ADischargeSuperheatDegree2 | Discharge superheat degree 2 | 排气过热度2 | 0-Read_Only | 只读 | -2000..2000 | -2000..2000 | Discharge superheat degree 2 of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.86 | hwNetCol8000ACommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the NetCol8000-A. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.87 | hwNetCol8000ASoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.88 | hwNetCol8000AHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.89 | hwNetCol8000AIpAddress | IP address | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IP address of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.90 | hwNetCol8000AEsn | ESN | ESN号 | 0-Read_Only | 只读 | 0..32 | 0..32 | ESN of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.91 | hwNetCol8000AELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.92 | hwNetCol8000ATeamworkGroupNumber | Teamwork group number | 群控组号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Teamwork group number of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.93 | hwNetCol8000AActiveorStandbyFlag | Active/Standby flag | 运行机备机标志 | 0-Read_Only | 只读 | active(1), standby(2), unknown(255) | [运行机=1]/[备机=2] | Active/Standby flag of the device config table for the NetCol8000-A. Value 1 indicate active Value 2 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.94 | hwNetCol8000ARefrigerantPumpRunningStatus | refrigerant pump running status | 氟泵运行状态 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Refrigerant pump running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.95 | hwNetCol8000ARefrigerantPump1RunningStatus | refrigerant pump 1 running status | 氟泵1运行状态 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Refrigerant pump 1 running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.96 | hwNetCol8000ARefrigerantPumpType | refrigerant pump type | 氟泵类型 | 0-Read_Only | 只读 | no(1), nonVFDRefrigerantPump(2), vFDRefrigerantPump(3), unknown(255) | [无=1]/[定频氟泵=2]/[变频氟泵=3] | Refrigerant pump type of the device config table for the NetCol8000-A. Value 1 indicate no Value 2 indicate non-vfdrefrigerantpump Value 3 indicate vfdrefrigerantpump
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.97 | hwNetCol8000ARefrigerantPumpTotalRuntime | refrigerant pump total runtime | 氟泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Refrigerant pump total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.98 | hwNetCol8000ARefrigerantPump1TotalRuntime | refrigerant pump 1 total runtime | 氟泵1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Refrigerant pump 1 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.99 | hwNetCol8000ANumberOfIndoorFans | Number of indoor fans | 室内风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of indoor fans of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.100 | hwNetCol8000ANumberOfCompressors | Number of compressors | 压缩机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of compressors of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.101 | hwNetCol8000ANumberOfHeaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of heaters of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.102 | hwNetCol8000ANumberOfHumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of humidifiers of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.103 | hwNetCol8000ANumberOfCondPumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of cond pumps of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.104 | hwNetCol8000ANumberOfPsu | Number of PSU | PSU数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of PSU of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.105 | hwNetCol8000ANumberOfOutdoorFans | Number of outdoor fans | 室外风机数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of outdoor fans of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.106 | hwNetCol8000ANumberOfEev | Number of EEV | 电子膨胀阀数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of EEV of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.107 | hwNetCol8000ANumberOfRefrigerantPumps | Number of refrigerant pumps | 氟泵数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of Refrigerant pumps of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.1.1.300 | hwNetCol8000ARunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2 | hwNetCol8000AConfig2Table | / | / |  |  | / | / | The config table of NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.1 | hwNetCol8000AConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.2 | hwNetCol8000ADeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.3 | hwNetCol8000AStartuporShutdownControl | Startup/Shutdown control | 控制开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Startup/Shutdown control of the device config table for the NetCol8000-A. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.4 | hwNetCol8000ATeamworkMode | Teamwork mode | 群控模式 | 1-Read_Write | 读写 | smartteamworkcontrol(1), icooling(2), unknown(255) | [智能群控=1]/[iCooling=2] | Teamwork mode of the device config table for the NetCol8000-A. Value 1 indicate smartteamworkcontrol Value 2 indicate icooling
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.5 | hwNetCol8000AReturnAirHighTemperatureAlarmThreshold | Return air high temperature alarm threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 250..550 | 250..550 | Return air high temperature alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.6 | hwNetCol8000AReturnAirLowTemperatureAlarmThreshold | Return air low temperature alarm threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Return air low temperature alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.7 | hwNetCol8000ASupplyAirHighTemperatureAlarmThreshold | Supply air high temperature alarm threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Supply air high temperature alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.8 | hwNetCol8000ASupplyAirLowTemperatureAlarmThreshold | Supply air low temperature alarm threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | Supply air low temperature alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.9 | hwNetCol8000AColdAisleHighTemperatureAlarmThreshold | Cold aisle high temperature alarm threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | Cold aisle high temperature alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.10 | hwNetCol8000AColdAisleLowTemperatureAlarmThreshold | Cold aisle low temperature alarm threshold | 冷通道低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | Cold aisle low temperature alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.11 | hwNetCol8000AHotAisleHighTemperatureAlarmThreshold | Hot aisle high temperature alarm threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 250..550 | 250..550 | Hot aisle high temperature alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.12 | hwNetCol8000AHotAisleLowTemperatureAlarmThreshold | Hot aisle low temperature alarm threshold | 热通道低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | Hot aisle low temperature alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.13 | hwNetCol8000AHighHumidityAlarmThreshold | High humidity alarm threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | High humidity alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.14 | hwNetCol8000ALowHumidityAlarmThreshold | Low humidity alarm threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | Low humidity alarm threshold of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.15 | hwNetCol8000ATemperatureSetpoint | Temperature setpoint | 温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | Temperature setpoint of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.16 | hwNetCol8000AHumiditySetpoint | Humidity setpoint | 湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | Humidity setpoint of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.17 | hwNetCol8000APortMAC | MAC address | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC Address of Device.
1.3.6.1.4.1.2011.6.178.1.1.10.11.2.1.300 | hwNetCol8000AConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3 | hwNetCol8000ARunning2Table | / | / |  |  | / | / | The running table of NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.1 | hwNetCol8000ARunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.2 | hwNetCol8000AWaterCooledModule1WaterValveRunningStatus | Water-cooled module 1 water valve running status | 水冷模块1水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Water-cooled module 1 water valve running status of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.3 | hwNetCol8000AWaterCooledModule1SupplyWaterTemperature | Water-cooled module 1 supply-water temperature | 水冷模块1供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Water-cooled module 1 supply-water temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.4 | hwNetCol8000AWaterCooledModule1ReturnWaterTemperature | Water-cooled module 1 return-water temperature | 水冷模块1回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Water-cooled module 1 return-water temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.5 | hwNetCol8000AOutdoorUnitCondensateMode | Outdoor unit condensate mode | 室外机冷凝方式 | 0-Read_Only | 只读 | aircooled(1), watercooled(2), unknown(255) | [风冷=1]/[水冷=2] | Outdoor unit condensate mode of the device config table for the NetCol8000-A. Value 1 indicate air-cooled Value 2 indicate water-cooled
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.6 | hwNetCol8000AWaterCooledModule2WaterValveRunningStatus | Water-cooled module 2 water valve running status | 水冷模块2水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Water-cooled module 2 water valve running status of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.7 | hwNetCol8000AWaterCooledModule2SupplyWaterTemperature | Water-cooled module 2 supply-water temperature | 水冷模块2供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Water-cooled module 2 supply-water temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.8 | hwNetCol8000AWaterCooledModule2ReturnWaterTemperature | Water-cooled module 2 return-water temperature | 水冷模块2回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Water-cooled module 2 return-water temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.9 | hwNetCol8000ANumberOfWaterCooledModule | Number of water-cooled module | 水冷模块数量 | 0-Read_Only | 只读 | 0..254 | 0..254 | Number of water-cooled module of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.10 | hwNetCol8000AWaterCooledModuleWaterValveRunningStatus | Water-cooled module water valve running status | 水冷模块水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Water-cooled module water valve running status of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.11 | hwNetCol8000AWaterCooledModuleSupplyWaterTemperature | Water-cooled module supply-water temperature | 水冷模块供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Water-cooled module supply-water temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.12 | hwNetCol8000AWaterCooledModuleReturnWaterTemperature | Water-cooled module return-water temperature | 水冷模块回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Water-cooled module return-water temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.13 | hwNetCol8000AColdAisle1Temperature | Cold aisle 1 temperature | 冷通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 1 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.14 | hwNetCol8000AColdAisle2Temperature | Cold aisle 2 temperature | 冷通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 2 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.15 | hwNetCol8000AColdAisle3Temperature | Cold aisle 3 temperature | 冷通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 3 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.16 | hwNetCol8000AColdAisle4Temperature | Cold aisle 4 temperature | 冷通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 4 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.17 | hwNetCol8000AColdAisle5Temperature | Cold aisle 5 temperature | 冷通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Cold aisle 5 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.18 | hwNetCol8000AColdAisle1Humidity | Cold aisle 1 humidity | 冷通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 1 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.19 | hwNetCol8000AColdAisle2Humidity | Cold aisle 2 humidity | 冷通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 2 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.20 | hwNetCol8000AColdAisle3Humidity | Cold aisle 3 humidity | 冷通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 3 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.21 | hwNetCol8000AColdAisle4Humidity | Cold aisle 4 humidity | 冷通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 4 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.22 | hwNetCol8000AColdAisle5Humidity | Cold aisle 5 humidity | 冷通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle 5 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.23 | hwNetCol8000AHotAisle1Temperature | Hot aisle 1 temperature | 热通道1温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 1 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.24 | hwNetCol8000AHotAisle2Temperature | Hot aisle 2 temperature | 热通道2温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 2 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.25 | hwNetCol8000AHotAisle3Temperature | Hot aisle 3 temperature | 热通道3温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 3 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.26 | hwNetCol8000AHotAisle4Temperature | Hot aisle 4 temperature | 热通道4温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 4 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.27 | hwNetCol8000AHotAisle5Temperature | Hot aisle 5 temperature | 热通道5温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | Hot aisle 5 temperature of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.28 | hwNetCol8000AHotAisle1Humidity | Hot aisle 1 humidity | 热通道1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 1 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.29 | hwNetCol8000AHotAisle2Humidity | Hot aisle 2 humidity | 热通道2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 2 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.30 | hwNetCol8000AHotAisle3Humidity | Hot aisle 3 humidity | 热通道3湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 3 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.31 | hwNetCol8000AHotAisle4Humidity | Hot aisle 4 humidity | 热通道4湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 4 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.32 | hwNetCol8000AHotAisle5Humidity | Hot aisle 5 humidity | 热通道5湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle 5 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.33 | hwNetCol8000ARefrigerantPump2RunningStatus | Refrigerant pump 2 running status | 氟泵2运行状态 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Refrigerant pump 2 running status of the device config table for the NetCol8000-A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.34 | hwNetCol8000AOutdoorFan1Humidity | Outdoor fan 1 humidity | 室外机1湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Outdoor fan 1 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.35 | hwNetCol8000AOutdoorFan2Humidity | Outdoor fan 2 humidity | 室外机2湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Outdoor fan 2 humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.36 | hwNetCol8000AOutdoorFanHumidity | Outdoor fan humidity | 室外机湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Outdoor fan humidity of the device config table for the NetCol8000-A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.37 | hwNetCol8000AOutdoor1SprayRunningStatus | Outdoor 1 spray running status | 室外机1喷淋运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor 1 spray running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.38 | hwNetCol8000AOutdoor2SprayRunningStatus | Outdoor 1 spray running status | 室外机2喷淋运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor 1 spray running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.39 | hwNetCol8000AOutdoorSprayRunningStatus | Outdoor spray running status | 室外机喷淋运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Outdoor spray running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.40 | hwNetCol8000ATotalOpenTimesOfTheWaterInletSolenoidValve | Total open times of the water inlet solenoid valve | 进水电磁阀累计开启次数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total open times of the water inlet solenoid valve of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.41 | hwNetCol8000ANumberOfOutdoor1Spray |  |  | 0-Read_Only | 只读 | 0..65535 | 0..65535 | of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.42 | hwNetCol8000ANumberOfOutdoor2Spray |  |  | 0-Read_Only | 只读 | 0..65535 | 0..65535 | of the device config table for the NetCol8000-A.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.43 | hwNetCol8000ARefrigerantPump2TotalRuntime | refrigerant pump 2 total runtime | 氟泵2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Refrigerant pump 2 total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.44 | hwNetCol8000ADrainPumpRunningStatus | Drain pump running status | 排水水泵运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | Drain pump running status of the device config table for the NetCol8000-A.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.45 | hwNetCol8000AOutdoorSprayTotalRuntime | Outdoor spray total runtime | 室外机喷淋累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor spray total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.46 | hwNetCol8000AOutdoor1SprayTotalRuntime | Outdoor 1 spray total runtime | 室外机1喷淋累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor 1 spray total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.47 | hwNetCol8000AOutdoor2SprayTotalRuntime | Outdoor 2 spray total runtime | 室外机2喷淋累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Outdoor 2 spray total runtime of the device config table for the NetCol8000-A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.10.11.3.1.300 | hwNetCol8000ARunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of NetCol8000-A.

## Integrated PDU
一体化配电柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.4 | IntegratedPDUCabinet | Integrated PDU | 一体化配电柜 | / | / | / | / | The Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1 | hwIntegratedPDUCabinetRunning1Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.1 | hwIntegratedPDUCabinetRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.2 | hwIntegratedPDUCabinetCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Comm State of Integrated PDU Cabinet. Value 1 indicates commok. Value 2 indicates commfail.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.3 | hwIntegratedPDUCabinetMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | The MAC of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.4 | hwIntegratedPDUCabinetIP | PDU IP | PDU IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IP of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.5 | hwIntegratedPDUCabinetEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | The Equip ESN of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.6 | hwIntegratedPDUCabinetSoftwareVer | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | The Software Ver of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.7 | hwIntegratedPDUCabinetInputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | dualItDualAc(1), dualItSingleAc(2), dualItAtsAc(3), singleItDualAc(4), singleItSingleAc(5), singleItAtsAc(6), unknown(255) | [IT双路空调双路=1]/[IT双路空调单路=2]/[IT双路ATS空调=3]/[IT单路空调双路=4]/[IT单路空调单路=5]/[IT单路ATS空调=6] | The Input Mode of Integrated PDU Cabinet. Value 1 indicates Dual_it_dual_a/c. Value 2 indicates Dual_it_single_a/c. Value 3 indicates Dual_it_ats_a/c. Value 4 indicates Single_it_dual_a/c. Value 5 indicates Single_it_single_a/c. Value 6 indicates Single_it_ats_a/c.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.8 | hwIntegratedPDUCabinetInputTotalValidEnergy | Total active electricity energy of PDU input | PDU输入总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Input Total Valid Energy of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.9 | hwIntegratedPDUCabinetItOutputTotalValidEnergy | Total active electricity energy of IT load output | IT负载输出总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The It Output Total Valid Energy of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.10 | hwIntegratedPDUCabinetAirConditionValidEnergy | Total active electricity energy of A/C load output | 空调负载输出总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The Air Condition Valid Energy of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.11 | hwIntegratedPDUCabinetIValidEnergy | Main input 1-input active power | 主路1-输入有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The I Valid Energy of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.12 | hwIntegratedPDUCabinetIIValidEnergy | Main input 2-input active power | 主路2-输入有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The II Valid Energy of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.13 | hwIntegratedPDUCabinetIIIValidEnergy | Main input 3-input active power | 主路3-输入有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The III Valid Energy of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.14 | hwIntegratedPDUCabinetIVValidEnergy | Main input 4-input active power | 主路4-输入有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The IV Valid Energy of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.15 | hwIntegratedPDUCabinetIPhaseVoltL1 | Main input 1-L1 input voltage | 主路1-L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I Phase Volt l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.16 | hwIntegratedPDUCabinetIPhaseVoltL2 | Main input 1-L2 input voltage | 主路1-L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I Phase Volt l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.17 | hwIntegratedPDUCabinetIPhaseVoltL3 | Main input 1-L3 input voltage | 主路1-L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I Phase Volt l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.18 | hwIntegratedPDUCabinetILineVoltL1L2 | Main input 1-L1-L2 input line voltage | 主路1-L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I Line Volt l1l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.19 | hwIntegratedPDUCabinetILineVoltL2L3 | Main input 1-L2-L3 input line voltage | 主路1-L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I Line Volt l2l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.20 | hwIntegratedPDUCabinetILineVoltL3L1 | Main input 1-L1-L3 input line voltage | 主路1-L1-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I Line Volt l3l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.21 | hwIntegratedPDUCabinetICurrL1 | Main input 1-L1 input current | 主路1-L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The I Curr l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.22 | hwIntegratedPDUCabinetICurrL2 | Main input 1-L2 input current | 主路1-L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The I Curr l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.23 | hwIntegratedPDUCabinetICurrL3 | Main input 1-L3 input current | 主路1-L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The I Curr l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.24 | hwIntegratedPDUCabinetIFrequency | Main input 1 input frequency | 主路1-输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I Frequency of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.25 | hwIntegratedPDUCabinetIValidPowerL1 | Main input 1-L1 input active power | 主路1-L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The I Valid Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.26 | hwIntegratedPDUCabinetIValidPowerL2 | Main input 1-L2 input active power | 主路1-L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The I Valid Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.27 | hwIntegratedPDUCabinetIValidPowerL3 | Main input 1-L3 input active power | 主路1-L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The I Valid Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.28 | hwIntegratedPDUCabinetIApparentPowerL1 | Main input 1-L1 input apparent power | 主路1-L1输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The I Apparent Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.29 | hwIntegratedPDUCabinetIApparentPowerL2 | Main input 1-L2 input apparent power | 主路1-L2输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The I Apparent Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.30 | hwIntegratedPDUCabinetIApparentPowerL3 | Main input 1-L3 input apparent power | 主路1-L3输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The I Apparent Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.31 | hwIntegratedPDUCabinetIInValidPowerL1 | Main input 1-L1 input reactive power | 主路1-L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The I Invalid Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.32 | hwIntegratedPDUCabinetIInValidPowerL2 | Main input 1-L2 input reactive power | 主路1-L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The I Invalid Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.33 | hwIntegratedPDUCabinetIInValidPowerL3 | Main input 1-L3 input reactive power | 主路1-L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The I Invalid Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.34 | hwIntegratedPDUCabinetIPowerFactorL1 | Main input 1-L1 input power factor | 主路1-L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The I Power Factor l1 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.35 | hwIntegratedPDUCabinetIPowerFactorL2 | Main input 1-L2 input power factor | 主路1-L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The I Power Factor l2 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.36 | hwIntegratedPDUCabinetIPowerFactorL3 | Main input 1-L3 input power factor | 主路1-L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The I Power Factor l3 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.37 | hwIntegratedPDUCabinetIL1InputLoadFactor | Main input 1-L1 input power load rate | 主路1-L1输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The I l1 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.38 | hwIntegratedPDUCabinetIL2InputLoadFactor | Main input 1-L2 input power load rate | 主路1-L2输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The I l2 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.39 | hwIntegratedPDUCabinetIL3InputLoadFactor | Main input 1-L3 input power load rate | 主路1-L3输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The I l3 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.40 | hwIntegratedPDUCabinetIInputNLineCurr | Main input 1-N wire current | 主路1-输入N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I Input N Line Curr of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.41 | hwIntegratedPDUCabinetIL1VoltHarmonic | Main input 1-L1 THDu | 主路1-L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The I l1 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.42 | hwIntegratedPDUCabinetIL2VoltHarmonic | Main input 1-L2 THDu | 主路1-L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The I l2 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.43 | hwIntegratedPDUCabinetIL3VoltHarmonic | Main input 1-L3 THDu | 主路1-L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The I l3 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.44 | hwIntegratedPDUCabinetIL1CurrHarmonic | Main input 1-L1 THDi | 主路1-L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The I l1 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.45 | hwIntegratedPDUCabinetIL2CurrHarmonic | Main input 1-L2 THDi | 主路1-L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The I l2 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.46 | hwIntegratedPDUCabinetIL3CurrHarmonic | Main input 1-L3 THDi | 主路1-L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The I l3 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.47 | hwIntegratedPDUCabinetIInputTotalValidPower | Main input 1-total input active power | 主路1-总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | The I Input Total Valid Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.48 | hwIntegratedPDUCabinetIInputTotalApparentPower | Main input 1-total input apparent power | 主路1-总输入视在功率 | 0-Read_Only | 只读 | 0..7500 | 0..7500 | The I Input Total Apparent Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.49 | hwIntegratedPDUCabinetIInputTotalInvalidPower | Main input 1-total input reactive power | 主路1-总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | The I Input Total Invalid Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.50 | hwIntegratedPDUCabinetINPeVolt | Main input 1-N-PE input voltage | 主路1-输入N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The I N Pe Volt of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.51 | hwIntegratedPDUCabinetIBusTemp | Main input 1-busbar temperature | 主路1-母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Bus Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.52 | hwIntegratedPDUCabinetIIPhaseVoltL1 | Main input 2-L1 input voltage | 主路2-L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II Phase Volt l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.53 | hwIntegratedPDUCabinetIIPhaseVoltL2 | Main input 2-L2 input voltage | 主路2-L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II Phase Volt l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.54 | hwIntegratedPDUCabinetIIPhaseVoltL3 | Main input 2-L3 input voltage | 主路2-L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II Phase Volt l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.55 | hwIntegratedPDUCabinetIILineVoltL1L2 | Main input 2-L1-L2 input line voltage | 主路2-L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II Line Volt l1l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.56 | hwIntegratedPDUCabinetIILineVoltL2L3 | Main input 2-L2-L3 input line voltage | 主路2-L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II Line Volt l2l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.57 | hwIntegratedPDUCabinetIILineVoltL3L1 | Main input 2-L3-L1 input line voltage | 主路2-L1-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II Line Volt l3l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.58 | hwIntegratedPDUCabinetIICurrL1 | Main input 2-L1 input current | 主路2-L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The II Curr l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.59 | hwIntegratedPDUCabinetIICurrL2 | Main input 2-L2 input current | 主路2-L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The II Curr l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.60 | hwIntegratedPDUCabinetIICurrL3 | Main input 2-L3 input current | 主路2-L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The II Curr l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.61 | hwIntegratedPDUCabinetIIFrequency | Main input 2 input frequency | 主路2-输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II Frequency of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.62 | hwIntegratedPDUCabinetIIValidPowerL1 | Main input 2-L1 input active power | 主路2-L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The II Valid Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.63 | hwIntegratedPDUCabinetIIValidPowerL2 | Main input 2-L2 input active power | 主路2-L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The II Valid Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.64 | hwIntegratedPDUCabinetIIValidPowerL3 | Main input 2-L3 input active power | 主路2-L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The II Valid Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.65 | hwIntegratedPDUCabinetIIApparentPowerL1 | Main input 2-L1 input apparent power | 主路2-L1输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The II Apparent Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.66 | hwIntegratedPDUCabinetIIApparentPowerL2 | Main input 2-L2 input apparent power | 主路2-L2输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The II Apparent Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.67 | hwIntegratedPDUCabinetIIApparentPowerL3 | Main input 2-L3 input apparent power | 主路2-L3输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The II Apparent Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.68 | hwIntegratedPDUCabinetIIInValidPowerL1 | Main input 2-L1 input reactive power | 主路2-L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The II Invalid Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.69 | hwIntegratedPDUCabinetIIInValidPowerL2 | Main input 2-L2 input reactive power | 主路2-L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The II Invalid Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.70 | hwIntegratedPDUCabinetIIInValidPowerL3 | Main input 2-L3 input reactive power | 主路2-L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The II Invalid Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.71 | hwIntegratedPDUCabinetIIPowerFactorL1 | Main input 2-L1 input power factor | 主路2-L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The II Power Factor l1 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.72 | hwIntegratedPDUCabinetIIPowerFactorL2 | Main input 2-L2 input power factor | 主路2-L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The II Power Factor l2 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.73 | hwIntegratedPDUCabinetIIPowerFactorL3 | Main input 2-L3 input power factor | 主路2-L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The II Power Factor l3 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.74 | hwIntegratedPDUCabinetIIL1InputLoadFactor | Main input 2-L1 input power load rate | 主路2-L1输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The II l1 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.75 | hwIntegratedPDUCabinetIIL2InputLoadFactor | Main input 2-L2 input power load rate | 主路2-L2输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The II l2 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.76 | hwIntegratedPDUCabinetIIL3InputLoadFactor | Main input 2-L3 input power load rate | 主路2-L3输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The II l3 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.77 | hwIntegratedPDUCabinetIIInputNLineCurr | Main input 2-N wire current | 主路2-输入N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II Input N Line Curr of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.78 | hwIntegratedPDUCabinetIIL1VoltHarmonic | Main input 2-L1 THDu | 主路2-L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The II l1 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.79 | hwIntegratedPDUCabinetIIL2VoltHarmonic | Main input 2-L2 THDu | 主路2-L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The II l2 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.80 | hwIntegratedPDUCabinetIIL3VoltHarmonic | Main input 2-L3 THDu | 主路2-L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The II l3 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.81 | hwIntegratedPDUCabinetIIL1CurrHarmonic | Main input 2-L1 THDi | 主路2-L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The II l1 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.82 | hwIntegratedPDUCabinetIIL2CurrHarmonic | Main input 2-L2 THDi | 主路2-L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The II l2 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.83 | hwIntegratedPDUCabinetIIL3CurrHarmonic | Main input 2-L3 THDi | 主路2-L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The II l3 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.84 | hwIntegratedPDUCabinetIIInputTotalValidPower | Main input 2-total input active power | 主路2-总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | The II Input Total Valid Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.85 | hwIntegratedPDUCabinetIIInputTotalApparentPower | Main input 2-total input apparent power | 主路2-总输入视在功率 | 0-Read_Only | 只读 | 0..7500 | 0..7500 | The II Input Total Apparent Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.86 | hwIntegratedPDUCabinetIIInputTotalInvalidPower | Main input 2-total input reactive power | 主路2-总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | The II Input Total Invalid Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.1.1.100 | hwIntegratedPDUCabinet1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2 | hwIntegratedPDUCabinetRunning2Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.1 | hwIntegratedPDUCabinetRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.2 | hwIntegratedPDUCabinetIINPeVolt | Main input 2-N-PE input voltage | 主路2-输入N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The II N Pe Volt of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.3 | hwIntegratedPDUCabinetIIBusTemp | Main input 2-busbar temperature | 主路2-母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Bus Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.4 | hwIntegratedPDUCabinetIIIPhaseVoltL1 | Main input 3-L1 input voltage | 主路3-L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III Phase Volt l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.5 | hwIntegratedPDUCabinetIIIPhaseVoltL2 | Main input 3-L2 input voltage | 主路3-L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III Phase Volt l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.6 | hwIntegratedPDUCabinetIIIPhaseVoltL3 | Main input 3-L3 input voltage | 主路3-L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III Phase Volt l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.7 | hwIntegratedPDUCabinetIIILineVoltL1L2 | Main input 3-L1-L2 input line voltage | 主路3-L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III Line Volt l1l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.8 | hwIntegratedPDUCabinetIIILineVoltL2L3 | Main input 3-L2-L3 input line voltage | 主路3-L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III Line Volt l2l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.9 | hwIntegratedPDUCabinetIIILineVoltL3L1 | Main input 3-L3-L1 input line voltage | 主路3-L1-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III Line Volt l3l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.10 | hwIntegratedPDUCabinetIIICurrL1 | Main input 3-L1 input current | 主路3-L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The III Curr l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.11 | hwIntegratedPDUCabinetIIICurrL2 | Main input 3-L2 input current | 主路3-L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The III Curr l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.12 | hwIntegratedPDUCabinetIIICurrL3 | Main input 3-L3 input current | 主路3-L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The III Curr l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.13 | hwIntegratedPDUCabinetIIIFrequency | Main input 3 input frequency | 主路3-输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III Frequency Integrated PDU Cabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.14 | hwIntegratedPDUCabinetIIIValidPowerL1 | Main input 3-L1 input active power | 主路3-L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The III Valid Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.15 | hwIntegratedPDUCabinetIIIValidPowerL2 | Main input 3-L2 input active power | 主路3-L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The III Valid Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.16 | hwIntegratedPDUCabinetIIIValidPowerL3 | Main input 3-L3 input active power | 主路3-L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The III Valid Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.17 | hwIntegratedPDUCabinetIIIApparentPowerL1 | Main input 3-L1 input apparent power | 主路3-L1输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The III Apparent Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.18 | hwIntegratedPDUCabinetIIIApparentPowerL2 | Main input 3-L2 input apparent power | 主路3-L2输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The III Apparent Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.19 | hwIntegratedPDUCabinetIIIApparentPowerL3 | Main input 3-L3 input apparent power | 主路3-L3输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The III Apparent Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.20 | hwIntegratedPDUCabinetIIIInValidPowerL1 | Main input 3-L1 input reactive power | 主路3-L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The III Invalid Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.21 | hwIntegratedPDUCabinetIIIInValidPowerL2 | Main input 3-L2 input reactive power | 主路3-L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The III Invalid Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.22 | hwIntegratedPDUCabinetIIIInValidPowerL3 | Main input 3-L3 input reactive power | 主路3-L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The III Invalid Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.23 | hwIntegratedPDUCabinetIIIPowerFactorL1 | Main input 3-L1 input power factor | 主路3-L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The III Power Factor l1 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.24 | hwIntegratedPDUCabinetIIIPowerFactorL2 | Main input 3-L2 input power factor | 主路3-L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The III Power Factor l2 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.25 | hwIntegratedPDUCabinetIIIPowerFactorL3 | Main input 3-L3 input power factor | 主路3-L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The III Power Factor l3 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.26 | hwIntegratedPDUCabinetIIIL1InputLoadFactor | Main input 3-L1 input power load rate | 主路3-L1输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The III l1 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.27 | hwIntegratedPDUCabinetIIIL2InputLoadFactor | Main input 3-L2 input power load rate | 主路3-L2输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The III l2 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.28 | hwIntegratedPDUCabinetIIIL3InputLoadFactor | Main input 3-L3 input power load rate | 主路3-L3输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The III l3 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.29 | hwIntegratedPDUCabinetIIIInputNLineCurr | Main input 3-N wire current | 主路3-输入N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III Input N Line Curr of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.30 | hwIntegratedPDUCabinetIIIL1VoltHarmonic | Main input 3-L1 THDu | 主路3-L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The III l1 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.31 | hwIntegratedPDUCabinetIIIL2VoltHarmonic | Main input 3-L2 THDu | 主路3-L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The III l2 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.32 | hwIntegratedPDUCabinetIIIL3VoltHarmonic | Main input 3-L3 THDu | 主路3-L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The III l3 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.33 | hwIntegratedPDUCabinetIIIL1CurrHarmonic | Main input 3-L1 THDi | 主路3-L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The III l1 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.34 | hwIntegratedPDUCabinetIIIL2CurrHarmonic | Main input 3-L2 THDi | 主路3-L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The III l2 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.35 | hwIntegratedPDUCabinetIIIL3CurrHarmonic | Main input 3-L3 THDi | 主路3-L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The III l3 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.36 | hwIntegratedPDUCabinetIIIInputTotalValidPower | Main input 3-total input active power | 主路3-总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | The III Input Total Valid Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.37 | hwIntegratedPDUCabinetIIIInputTotalApparentPower | Main input 3-total input apparent power | 主路3-总输入视在功率 | 0-Read_Only | 只读 | 0..7500 | 0..7500 | The III Input Total Apparent Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.38 | hwIntegratedPDUCabinetIIIInputTotalInvalidPower | Main input 3-total input reactive power | 主路3-总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | The III Input Total Invalid Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.39 | hwIntegratedPDUCabinetIIINPEVolt | Main input 3-N-PE input voltage | 主路3-输入N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The III N PE Volt of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.40 | hwIntegratedPDUCabinetIIIBusTemp | Main input 3-busbar temperature | 主路3-母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Bus Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.41 | hwIntegratedPDUCabinetIVPhaseVoltL1 | Main input 4-L1 input voltage | 主路4-L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV Phase Volt l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.42 | hwIntegratedPDUCabinetIVPhaseVoltL2 | Main input 4-L2 input voltage | 主路4-L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV Phase Volt l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.43 | hwIntegratedPDUCabinetIVPhaseVoltL3 | Main input 4-L3 input voltage | 主路4-L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV Phase Volt l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.44 | hwIntegratedPDUCabinetIVLineVoltL1L2 | Main input 4-L1-L2 input line voltage | 主路4-L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV Line Volt l1l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.45 | hwIntegratedPDUCabinetIVLineVoltL2L3 | Main input 4-L2-L3 input line voltage | 主路4-L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV Line Volt l2l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.46 | hwIntegratedPDUCabinetIVLineVoltL3L1 | Main input 4-L3-L1 input line voltage | 主路4-L1-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV Line Volt l3l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.47 | hwIntegratedPDUCabinetIVCurrL1 | Main input 4-L1 input current | 主路4-L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The IV Curr l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.48 | hwIntegratedPDUCabinetIVCurrL2 | Main input 4-L2 input current | 主路4-L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The IV Curr l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.49 | hwIntegratedPDUCabinetIVCurrL3 | Main input 4-L3 input current | 主路4-L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | The IV Curr l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.50 | hwIntegratedPDUCabinetIVFrequency | Main input 4 input frequency | 主路4-输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV Frequency of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.51 | hwIntegratedPDUCabinetIVValidPowerL1 | Main input 4-L1 input active power | 主路4-L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The IV Valid Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.52 | hwIntegratedPDUCabinetIVValidPowerL2 | Main input 4-L2 input active power | 主路4-L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The IV Valid Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.53 | hwIntegratedPDUCabinetIVValidPowerL3 | Main input 4-L3 input active power | 主路4-L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The IV Valid Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.54 | hwIntegratedPDUCabinetIVApparentPowerL1 | Main input 4-L1 input apparent power | 主路4-L1输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The IV Apparent Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.55 | hwIntegratedPDUCabinetIVApparentPowerL2 | Main input 4-L2 input apparent power | 主路4-L2输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The IV Apparent Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.56 | hwIntegratedPDUCabinetIVApparentPowerL3 | Main input 4-L3 input apparent power | 主路4-L3输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | The IV Apparent Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.57 | hwIntegratedPDUCabinetIVInValidPowerL1 | Main input 4-L1 input reactive power | 主路4-L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The IV Invalid Power l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.58 | hwIntegratedPDUCabinetIVInValidPowerL2 | Main input 4-L2 input reactive power | 主路4-L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The IV Invalid Power l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.59 | hwIntegratedPDUCabinetIVInValidPowerL3 | Main input 4-L3 input reactive power | 主路4-L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | The IV Invalid Power l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.60 | hwIntegratedPDUCabinetIVPowerFactorL1 | Main input 4-L1 input power factor | 主路4-L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The IV Power Factor l1 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.61 | hwIntegratedPDUCabinetIVPowerFactorL2 | Main input 4-L2 input power factor | 主路4-L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The IV Power Factor l2 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.62 | hwIntegratedPDUCabinetIVPowerFactorL3 | Main input 4-L3 input power factor | 主路4-L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The IV Power Factor l3 of Integrated PDU Cabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.63 | hwIntegratedPDUCabinetIVL1InputLoadFactor | Main input 4-L1 input power load rate | 主路4-L1输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The IV l1 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.64 | hwIntegratedPDUCabinetIVL2InputLoadFactor | Main input 4-L2 input power load rate | 主路4-L2输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The IV l2 Input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.65 | hwIntegratedPDUCabinetIVL3inputLoadFactor | Main input 4-L3 input power load rate | 主路4-L3输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | The IV l3 input Load Factor of Integrated PDU Cabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.66 | hwIntegratedPDUCabinetIVInputNLineCurr | Main input 4-N wire current | 主路4-输入N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV Input N Line Curr of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.67 | hwIntegratedPDUCabinetIVL1VoltHarmonic | Main input 4-L1 THDu | 主路4-L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The IV l1 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.68 | hwIntegratedPDUCabinetIVL2VoltHarmonic | Main input 4-L2 THDu | 主路4-L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The IV l2 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.69 | hwIntegratedPDUCabinetIVL3VoltHarmonic | Main input 4-L3 THDu | 主路4-L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The IV l3 Volt Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.70 | hwIntegratedPDUCabinetIVL1CurrHarmonic | Main input 4-L1 THDi | 主路4-L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The IV l1 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.71 | hwIntegratedPDUCabinetIVL2CurrHarmonic | Main input 4-L2 THDi | 主路4-L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The IV l2 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.72 | hwIntegratedPDUCabinetIVL3CurrHarmonic | Main input 4-L3 THDi | 主路4-L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The IV l3 Curr Harmonic of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.73 | hwIntegratedPDUCabinetIVInputTotalValidPower | Main input 4-total input active power | 主路4-总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | The IV Input Total Valid Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.74 | hwIntegratedPDUCabinetIVInputTotalApparentPower | Main input 4-total input apparent power | 主路4-总输入视在功率 | 0-Read_Only | 只读 | 0..7500 | 0..7500 | The IV Input Total Apparent Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.75 | hwIntegratedPDUCabinetIVInputTotalInvalidPower | Main input 4-total input reactive power | 主路4-总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | The IV Input Total Invalid Power of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.76 | hwIntegratedPDUCabinetIVNPeVolt | Main input 4-N-PE input voltage | 主路4-输入N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The IV N Pe Volt of Integrated PDU Cabinet of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.77 | hwIntegratedPDUCabinetIVBusTemp | Main input 4-busbar temperature | 主路4-母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Bus Temp of Integrated PDU Cabinet of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.78 | hwIntegratedPDUCabinetLn1PowerPhasevoltL1 | LN1 phase L1 voltage | LN1电源L1相电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln1 Power Phase volt l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.79 | hwIntegratedPDUCabinetLn1PowerPhasevoltL2 | LN1 phase L2 voltage | LN1电源L2相电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln1 Power Phase volt l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.80 | hwIntegratedPDUCabinetLn1PowerPhasevoltL3 | LN1 phase L3 voltage | LN1电源L3相电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln1 Power Phase volt l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.81 | hwIntegratedPDUCabinetLn1PowerLinevoltL1L2 | LN1 phase L1-L2 voltage | LN1电源L1-L2电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln1 Power Line volt l1l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.82 | hwIntegratedPDUCabinetLn1PowerLinevoltL2L3 | LN1 phase L2-L3 voltage | LN1电源L2-L3电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln1 Power Line volt l2l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.83 | hwIntegratedPDUCabinetLn1PowerLinevoltL3L1 | LN1 phase L3-L1 voltage | LN1电源L3-L1电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln1 Power Line volt l3l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.84 | hwIntegratedPDUCabinetLn2PowerPhasevoltL1 | LN2 phase L1 voltage | LN2电源L1相电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln2 Power Phase volt l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.85 | hwIntegratedPDUCabinetLn2PowerPhasevoltL2 | LN2 phase L2 voltage | LN2电源L2相电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln2 Power Phase volt l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.86 | hwIntegratedPDUCabinetLn2PowerPhasevoltL3 | LN2 phase L3 voltage | LN2电源L3相电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln2 Power Phase volt l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.87 | hwIntegratedPDUCabinetLn2PowerLinevoltL1L2 | LN2 phase L1-L2 voltage | LN2电源L1-L2电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln2 Power Line volt l1l2 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.88 | hwIntegratedPDUCabinetLn2PowerLinevoltL2L3 | LN2 phase L2-L3 voltage | LN2电源L2-L3电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln2 Power Line volt l2l3 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.89 | hwIntegratedPDUCabinetLn2PowerLinevoltL3L1 | LN2 phase L3-L1 voltage | LN2电源L3-L1电压 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | The Ln2 Power Line volt l3l1 of Integrated PDU Cabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.90 | hwIntegratedPDUCabinetLn1Freq | LN1 frequency | LN1频率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | The Ln1 Freq of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.91 | hwIntegratedPDUCabinetLn2Freq | LN2 frequency | LN2频率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | The Ln2 Freq of Integrated PDU Cabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.4.2.1.100 | hwIntegratedPDUCabinet2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3 | hwIntegratedPDUCabinetRunning3Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.1 | hwIntegratedPDUCabinetRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.2 | hwIntegratedPDUCabinetIBrh1ValidPower | 1QF1 power(L1) | 1QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh1 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.3 | hwIntegratedPDUCabinetIBrh2ValidPower | 1QF2 power(L2) | 1QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh2 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.4 | hwIntegratedPDUCabinetIBrh3ValidPower | 1QF3 power(L3) | 1QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh3 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.5 | hwIntegratedPDUCabinetIBrh4ValidPower | 1QF4 power(L1) | 1QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh4 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.6 | hwIntegratedPDUCabinetIBrh5ValidPower | 1QF5 power(L2) | 1QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh5 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.7 | hwIntegratedPDUCabinetIBrh6ValidPower | 1QF6 power(L3) | 1QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh6 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.8 | hwIntegratedPDUCabinetIBrh7ValidPower | 1QF7 power(L1) | 1QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh7 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.9 | hwIntegratedPDUCabinetIBrh8ValidPower | 1QF8 power(L2) | 1QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh8 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.10 | hwIntegratedPDUCabinetIBrh9ValidPower | 1QF9 power(L3) | 1QF9 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh9 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.11 | hwIntegratedPDUCabinetIBrh10ValidPower | 1QF10 power(L1) | 1QF10 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh10 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.12 | hwIntegratedPDUCabinetIBrh11ValidPower | 1QF11 power(L2) | 1QF11 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh11 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.13 | hwIntegratedPDUCabinetIBrh12ValidPower | 1QF12 power(L3) | 1QF12 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh12 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.14 | hwIntegratedPDUCabinetIBrh13ValidPower | 1QF13 power(L1) | 1QF13 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh13 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.15 | hwIntegratedPDUCabinetIBrh14ValidPower | 1QF14 power(L2) | 1QF14 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh14 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.16 | hwIntegratedPDUCabinetIBrh15ValidPower | 1QF15 power(L3) | 1QF15 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh15 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.17 | hwIntegratedPDUCabinetIBrh16ValidPower | 1QF16 power(L1) | 1QF16 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh16 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.18 | hwIntegratedPDUCabinetIBrh17ValidPower | 1QF17 power(L2) | 1QF17 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh17 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.19 | hwIntegratedPDUCabinetIBrh18ValidPower | 1QF18 power(L3) | 1QF18 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh18 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.20 | hwIntegratedPDUCabinetIBrh19ValidPower | 1QF19 power(L1) | 1QF19 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh19 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.21 | hwIntegratedPDUCabinetIBrh20ValidPower | 1QF20 power(L2) | 1QF20 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh20 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.22 | hwIntegratedPDUCabinetIBrh21ValidPower | 1QF21 power(L3) | 1QF21 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh21 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.23 | hwIntegratedPDUCabinetIBrh22ValidPower | 1QF22 power(L1) | 1QF22 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh22 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.24 | hwIntegratedPDUCabinetIBrh23ValidPower | 1QF23 power(L2) | 1QF23 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh23 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.25 | hwIntegratedPDUCabinetIBrh24ValidPower | 1QF24 power(L3) | 1QF24 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh24 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.26 | hwIntegratedPDUCabinetIBrh1ValidEnergy | 1QF1 electricity energy(L1) | 1QF1 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh1 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.27 | hwIntegratedPDUCabinetIBrh2ValidEnergy | 1QF2 electricity energy(L2) | 1QF2 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh2 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.28 | hwIntegratedPDUCabinetIBrh3ValidEnergy | 1QF3 electricity energy(L3) | 1QF3 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh3 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.29 | hwIntegratedPDUCabinetIBrh4ValidEnergy | 1QF4 electricity energy(L1) | 1QF4 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh4 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.30 | hwIntegratedPDUCabinetIBrh5ValidEnergy | 1QF5 electricity energy(L2) | 1QF5 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh5 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.31 | hwIntegratedPDUCabinetIBrh6ValidEnergy | 1QF6 electricity energy(L3) | 1QF6 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh6 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.32 | hwIntegratedPDUCabinetIBrh7ValidEnergy | 1QF7 electricity energy(L1) | 1QF7 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh7 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.33 | hwIntegratedPDUCabinetIBrh8ValidEnergy | 1QF8 electricity energy(L2) | 1QF8 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh8 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.34 | hwIntegratedPDUCabinetIBrh9ValidEnergy | 1QF9 electricity energy(L3) | 1QF9 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh9 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.35 | hwIntegratedPDUCabinetIBrh10ValidEnergy | 1QF10 electricity energy(L1) | 1QF10 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh10 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.36 | hwIntegratedPDUCabinetIBrh11ValidEnergy | 1QF11 electricity energy(L2) | 1QF11 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh11 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.37 | hwIntegratedPDUCabinetIBrh12ValidEnergy | 1QF12 electricity energy(L3) | 1QF12 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh12 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.38 | hwIntegratedPDUCabinetIBrh13ValidEnergy | 1QF13 electricity energy(L1) | 1QF13 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh13 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.39 | hwIntegratedPDUCabinetIBrh14ValidEnergy | 1QF14 electricity energy(L2) | 1QF14 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh14 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.40 | hwIntegratedPDUCabinetIBrh15ValidEnergy | 1QF15 electricity energy(L3) | 1QF15 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh15 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.41 | hwIntegratedPDUCabinetIBrh16ValidEnergy | 1QF16 electricity energy(L1) | 1QF16 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh16 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.42 | hwIntegratedPDUCabinetIBrh17ValidEnergy | 1QF17 electricity energy(L2) | 1QF17 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh17 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.43 | hwIntegratedPDUCabinetIBrh18ValidEnergy | 1QF18 electricity energy(L3) | 1QF18 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh18 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.44 | hwIntegratedPDUCabinetIBrh19ValidEnergy | 1QF19 electricity energy(L1) | 1QF19 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh19 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.45 | hwIntegratedPDUCabinetIBrh20ValidEnergy | 1QF20 electricity energy(L2) | 1QF20 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh20 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.46 | hwIntegratedPDUCabinetIBrh21ValidEnergy | 1QF21 electricity energy(L3) | 1QF21 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh21 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.47 | hwIntegratedPDUCabinetIBrh22ValidEnergy | 1QF22 electricity energy(L1) | 1QF22 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh22 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.48 | hwIntegratedPDUCabinetIBrh23ValidEnergy | 1QF23 electricity energy(L2) | 1QF23 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh23 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.49 | hwIntegratedPDUCabinetIBrh24ValidEnergy | 1QF24 electricity energy(L3) | 1QF24 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh24 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.50 | hwIntegratedPDUCabinetIBrh1Temp | 1QF1 temperature(L1) | 1QF1 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh1 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.51 | hwIntegratedPDUCabinetIBrh2Temp | 1QF2 temperature(L2) | 1QF2 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh2 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.52 | hwIntegratedPDUCabinetIBrh3Temp | 1QF3 temperature(L3) | 1QF3 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh3 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.53 | hwIntegratedPDUCabinetIBrh4Temp | 1QF4 temperature(L1) | 1QF4 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh4 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.54 | hwIntegratedPDUCabinetIBrh5Temp | 1QF5 temperature(L2) | 1QF5 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh5 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.55 | hwIntegratedPDUCabinetIBrh6Temp | 1QF6 temperature(L3) | 1QF6 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh6 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.56 | hwIntegratedPDUCabinetIBrh7Temp | 1QF7 temperature(L1) | 1QF7 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh7 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.57 | hwIntegratedPDUCabinetIBrh8Temp | 1QF8 temperature(L2) | 1QF8 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh8 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.58 | hwIntegratedPDUCabinetIBrh9Temp | 1QF9 temperature(L3) | 1QF9 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh9 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.59 | hwIntegratedPDUCabinetIBrh10Temp | 1QF10 temperature(L1) | 1QF10 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh10 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.60 | hwIntegratedPDUCabinetIBrh11Temp | 1QF11 temperature(L2) | 1QF11 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh11 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.61 | hwIntegratedPDUCabinetIBrh12Temp | 1QF12 temperature(L3) | 1QF12 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh12 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.62 | hwIntegratedPDUCabinetIBrh13Temp | 1QF13 temperature(L1) | 1QF13 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh13 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.63 | hwIntegratedPDUCabinetIBrh14Temp | 1QF14 temperature(L2) | 1QF14 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh14 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.64 | hwIntegratedPDUCabinetIBrh15Temp | 1QF15 temperature(L3) | 1QF15 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh15 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.65 | hwIntegratedPDUCabinetIBrh16Temp | 1QF16 temperature(L1) | 1QF16 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh16 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.66 | hwIntegratedPDUCabinetIBrh17Temp | 1QF17 temperature(L2) | 1QF17 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh17 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.67 | hwIntegratedPDUCabinetIBrh18Temp | 1QF18 temperature(L3) | 1QF18 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh18 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.68 | hwIntegratedPDUCabinetIBrh19Temp | 1QF19 temperature(L1) | 1QF19 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh19 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.69 | hwIntegratedPDUCabinetIBrh20Temp | 1QF20 temperature(L2) | 1QF20 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh20 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.70 | hwIntegratedPDUCabinetIBrh21Temp | 1QF21 temperature(L3) | 1QF21 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh21 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.71 | hwIntegratedPDUCabinetIBrh22Temp | 1QF22 temperature(L1) | 1QF22 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh22 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.72 | hwIntegratedPDUCabinetIBrh23Temp | 1QF23 temperature(L2) | 1QF23 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh23 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.73 | hwIntegratedPDUCabinetIBrh24Temp | 1QF24 temperature(L3) | 1QF24 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh24 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.74 | hwIntegratedPDUCabinetIIBrh1ValidPower | 2QF1 power(L1) | 2QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh1 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.75 | hwIntegratedPDUCabinetIIBrh2ValidPower | 2QF2 power(L2) | 2QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh2 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.76 | hwIntegratedPDUCabinetIIBrh3ValidPower | 2QF3 power(L3) | 2QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh3 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.77 | hwIntegratedPDUCabinetIIBrh4ValidPower | 2QF4 power(L1) | 2QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh4 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.78 | hwIntegratedPDUCabinetIIBrh5ValidPower | 2QF5 power(L2) | 2QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh5 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.79 | hwIntegratedPDUCabinetIIBrh6ValidPower | 2QF6 power(L3) | 2QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh6 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.80 | hwIntegratedPDUCabinetIIBrh7ValidPower | 2QF7 power(L1) | 2QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh7 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.81 | hwIntegratedPDUCabinetIIBrh8ValidPower | 2QF8 power(L2) | 2QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh8 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.82 | hwIntegratedPDUCabinetIIBrh9ValidPower | 2QF9 power(L3) | 2QF9 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh9 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.83 | hwIntegratedPDUCabinetIIBrh10ValidPower | 2QF10 power(L1) | 2QF10 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh10 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.84 | hwIntegratedPDUCabinetIIBrh11ValidPower | 2QF11 power(L2) | 2QF11 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh11 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.85 | hwIntegratedPDUCabinetIIBrh12ValidPower | 2QF12 power(L3) | 2QF12 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh12 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.86 | hwIntegratedPDUCabinetIIBrh13ValidPower | 2QF13 power(L1) | 2QF13 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh13 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.87 | hwIntegratedPDUCabinetIIBrh14ValidPower | 2QF14 power(L2) | 2QF14 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh14 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.88 | hwIntegratedPDUCabinetIIBrh15ValidPower | 2QF15 power(L3) | 2QF15 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh15 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.89 | hwIntegratedPDUCabinetIIBrh16ValidPower | 2QF16 power(L1) | 2QF16 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh16 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.90 | hwIntegratedPDUCabinetIIBrh17ValidPower | 2QF17 power(L2) | 2QF17 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh17 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.91 | hwIntegratedPDUCabinetIIBrh18ValidPower | 2QF18 power(L3) | 2QF18 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh18 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.92 | hwIntegratedPDUCabinetIIBrh19ValidPower | 2QF19 power(L1) | 2QF19 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh19 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.93 | hwIntegratedPDUCabinetIIBrh20ValidPower | 2QF20 power(L2) | 2QF20 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh20 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.94 | hwIntegratedPDUCabinetIIBrh21ValidPower | 2QF21 power(L3) | 2QF21 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh21 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.95 | hwIntegratedPDUCabinetIIBrh22ValidPower | 2QF22 power(L1) | 2QF22 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh22 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.96 | hwIntegratedPDUCabinetIIBrh23ValidPower | 2QF23 power(L2) | 2QF23 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh23 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.97 | hwIntegratedPDUCabinetIIBrh24ValidPower | 2QF24 power(L3) | 2QF24 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The II Brh24 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.3.1.100 | hwIntegratedPDUCabinet3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4 | hwIntegratedPDUCabinetRunning4Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.1 | hwIntegratedPDUCabinetRunning4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.2 | hwIntegratedPDUCabinetIIBrh1ValidEnergy | 2QF1 electricity energy(L1) | 2QF1 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh1 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.3 | hwIntegratedPDUCabinetIIBrh2ValidEnergy | 2QF2 electricity energy(L2) | 2QF2 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh2 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.4 | hwIntegratedPDUCabinetIIBrh3ValidEnergy | 2QF3 electricity energy(L3) | 2QF3 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh3 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.5 | hwIntegratedPDUCabinetIIBrh4ValidEnergy | 2QF4 electricity energy(L1) | 2QF4 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh4 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.6 | hwIntegratedPDUCabinetIIBrh5ValidEnergy | 2QF5 electricity energy(L2) | 2QF5 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh5 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.7 | hwIntegratedPDUCabinetIIBrh6ValidEnergy | 2QF6 electricity energy(L3) | 2QF6 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh6 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.8 | hwIntegratedPDUCabinetIIBrh7ValidEnergy | 2QF7 electricity energy(L1) | 2QF7 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh7 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.9 | hwIntegratedPDUCabinetIIBrh8ValidEnergy | 2QF8 electricity energy(L2) | 2QF8 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh8 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.10 | hwIntegratedPDUCabinetIIBrh9ValidEnergy | 2QF9 electricity energy(L3) | 2QF9 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh9 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.11 | hwIntegratedPDUCabinetIIBrh10ValidEnergy | 2QF10 electricity energy(L1) | 2QF10 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh10 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.12 | hwIntegratedPDUCabinetIIBrh11ValidEnergy | 2QF11 electricity energy(L2) | 2QF11 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh11 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.13 | hwIntegratedPDUCabinetIIBrh12ValidEnergy | 2QF12 electricity energy(L3) | 2QF12 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh12 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.14 | hwIntegratedPDUCabinetIIBrh13ValidEnergy | 2QF13 electricity energy(L1) | 2QF13 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh13 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.15 | hwIntegratedPDUCabinetIIBrh14ValidEnergy | 2QF14 electricity energy(L2) | 2QF14 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh14 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.16 | hwIntegratedPDUCabinetIIBrh15ValidEnergy | 2QF15 electricity energy(L3) | 2QF15 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh15 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.17 | hwIntegratedPDUCabinetIIBrh16ValidEnergy | 2QF16 electricity energy(L1) | 2QF16 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh16 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.18 | hwIntegratedPDUCabinetIIBrh17ValidEnergy | 2QF17 electricity energy(L2) | 2QF17 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh17 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.19 | hwIntegratedPDUCabinetIIBrh18ValidEnergy | 2QF18 electricity energy(L3) | 2QF18 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh18 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.20 | hwIntegratedPDUCabinetIIBrh19ValidEnergy | 2QF19 electricity energy(L1) | 2QF19 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh19 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.21 | hwIntegratedPDUCabinetIIBrh20ValidEnergy | 2QF20 electricity energy(L2) | 2QF20 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh20 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.22 | hwIntegratedPDUCabinetIIBrh21ValidEnergy | 2QF21 electricity energy(L3) | 2QF21 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh21 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.23 | hwIntegratedPDUCabinetIIBrh22ValidEnergy | 2QF22 electricity energy(L1) | 2QF22 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh22 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.24 | hwIntegratedPDUCabinetIIBrh23ValidEnergy | 2QF23 electricity energy(L2) | 2QF23 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh23 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.25 | hwIntegratedPDUCabinetIIBrh24ValidEnergy | 2QF24 electricity energy(L3) | 2QF24 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The II Brh24 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.26 | hwIntegratedPDUCabinetIIBrh1Temp | 2QF1 temperature(L1) | 2QF1 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh1 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.27 | hwIntegratedPDUCabinetIIBrh2Temp | 2QF2 temperature(L2) | 2QF2 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh2 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.28 | hwIntegratedPDUCabinetIIBrh3Temp | 2QF3 temperature(L3) | 2QF3 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh3 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.29 | hwIntegratedPDUCabinetIIBrh4Temp | 2QF4 temperature(L1) | 2QF4 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh4 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.30 | hwIntegratedPDUCabinetIIBrh5Temp | 2QF5 temperature(L2) | 2QF5 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh5 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.31 | hwIntegratedPDUCabinetIIBrh6Temp | 2QF6 temperature(L3) | 2QF6 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh6 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.32 | hwIntegratedPDUCabinetIIBrh7Temp | 2QF7 temperature(L1) | 2QF7 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh7 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.33 | hwIntegratedPDUCabinetIIBrh8Temp | 2QF8 temperature(L2) | 2QF8 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh8 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.34 | hwIntegratedPDUCabinetIIBrh9Temp | 2QF9 temperature(L3) | 2QF9 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh9 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.35 | hwIntegratedPDUCabinetIIBrh10Temp | 2QF10 temperature(L1) | 2QF10 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh10 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.36 | hwIntegratedPDUCabinetIIBrh11Temp | 2QF11 temperature(L2) | 2QF11 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh11 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.37 | hwIntegratedPDUCabinetIIBrh12Temp | 2QF12 temperature(L3) | 2QF12 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh12 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.38 | hwIntegratedPDUCabinetIIBrh13Temp | 2QF13 temperature(L1) | 2QF13 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh13 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.39 | hwIntegratedPDUCabinetIIBrh14Temp | 2QF14 temperature(L2) | 2QF14 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh14 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.40 | hwIntegratedPDUCabinetIIBrh15Temp | 2QF15 temperature(L3) | 2QF15 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh15 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.41 | hwIntegratedPDUCabinetIIBrh16Temp | 2QF16 temperature(L1) | 2QF16 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh16 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.42 | hwIntegratedPDUCabinetIIBrh17Temp | 2QF17 temperature(L2) | 2QF17 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh17 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.43 | hwIntegratedPDUCabinetIIBrh18Temp | 2QF18 temperature(L3) | 2QF18 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh18 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.44 | hwIntegratedPDUCabinetIIBrh19Temp | 2QF19 temperature(L1) | 2QF19 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh19 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.45 | hwIntegratedPDUCabinetIIBrh20Temp | 2QF20 temperature(L2) | 2QF20 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh20 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.46 | hwIntegratedPDUCabinetIIBrh21Temp | 2QF21 temperature(L3) | 2QF21 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh21 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.47 | hwIntegratedPDUCabinetIIBrh22Temp | 2QF22 temperature(L1) | 2QF22 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh22 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.48 | hwIntegratedPDUCabinetIIBrh23Temp | 2QF23 temperature(L2) | 2QF23 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh23 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.49 | hwIntegratedPDUCabinetIIBrh24Temp | 2QF24 temperature(L3) | 2QF24 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The II Brh24 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.50 | hwIntegratedPDUCabinetIIIBrh1ValidPower | 3QF1 power(L1) | 3QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh1 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.51 | hwIntegratedPDUCabinetIIIBrh2ValidPower | 3QF1 power(L2) | 3QF1 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh2 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.52 | hwIntegratedPDUCabinetIIIBrh3ValidPower | 3QF1 power(L3) | 3QF1 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh3 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.53 | hwIntegratedPDUCabinetIIIBrh4ValidPower | 3QF2 power(L1) | 3QF2 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh4 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.54 | hwIntegratedPDUCabinetIIIBrh5ValidPower | 3QF2 power(L2) | 3QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh5 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.55 | hwIntegratedPDUCabinetIIIBrh6ValidPower | 3QF2 power(L3) | 3QF2 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh6 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.56 | hwIntegratedPDUCabinetIIIBrh7ValidPower | 3QF3 power(L1) | 3QF3 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh7 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.57 | hwIntegratedPDUCabinetIIIBrh8ValidPower | 3QF3 power(L2) | 3QF3 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh8 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.58 | hwIntegratedPDUCabinetIIIBrh9ValidPower | 3QF3 power(L3) | 3QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh9 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.59 | hwIntegratedPDUCabinetIIIBrh10ValidPower | 3QF4 power(L1) | 3QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh10 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.60 | hwIntegratedPDUCabinetIIIBrh11ValidPower | 3QF4 power(L2) | 3QF4 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh11 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.61 | hwIntegratedPDUCabinetIIIBrh12ValidPower | 3QF4 power(L3) | 3QF4 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh12 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.62 | hwIntegratedPDUCabinetIIIBrh13ValidPower | 3QF5 power(L1) | 3QF5 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh13 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.63 | hwIntegratedPDUCabinetIIIBrh14ValidPower | 3QF5 power(L2) | 3QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh14 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.64 | hwIntegratedPDUCabinetIIIBrh15ValidPower | 3QF5 power(L3) | 3QF5 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh15 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.65 | hwIntegratedPDUCabinetIIIBrh16ValidPower | 3QF6 power(L1) | 3QF6 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh16 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.66 | hwIntegratedPDUCabinetIIIBrh17ValidPower | 3QF6 power(L2) | 3QF6 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh17 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.67 | hwIntegratedPDUCabinetIIIBrh18ValidPower | 3QF6 power(L3) | 3QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh18 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.68 | hwIntegratedPDUCabinetIIIBrh19ValidPower | 3QF7 power(L1) | 3QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh19 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.69 | hwIntegratedPDUCabinetIIIBrh20ValidPower | 3QF7 power(L2) | 3QF7 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh20 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.70 | hwIntegratedPDUCabinetIIIBrh21ValidPower | 3QF7 power(L3) | 3QF7 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh21 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.71 | hwIntegratedPDUCabinetIIIBrh22ValidPower | 3QF8 power(L1) | 3QF8 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh22 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.72 | hwIntegratedPDUCabinetIIIBrh23ValidPower | 3QF8 power(L2) | 3QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh23 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.73 | hwIntegratedPDUCabinetIIIBrh24ValidPower | 3QF8 power(L3) | 3QF8 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh24 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.74 | hwIntegratedPDUCabinetIIIBrh25ValidPower | 3QF9 power(L1) | 3QF9 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh25 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.75 | hwIntegratedPDUCabinetIIIBrh26ValidPower | 3QF9 power(L2) | 3QF9 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh26 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.76 | hwIntegratedPDUCabinetIIIBrh27ValidPower | 3QF9 power(L3) | 3QF9 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh27 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.77 | hwIntegratedPDUCabinetIIIBrh28ValidPower | 3QF10 power(L1) | 3QF10 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh28 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.78 | hwIntegratedPDUCabinetIIIBrh29ValidPower | 3QF10 power(L2) | 3QF10 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh29 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.79 | hwIntegratedPDUCabinetIIIBrh30ValidPower | 3QF10 power(L3) | 3QF10 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh30 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.80 | hwIntegratedPDUCabinetIIIBrh31ValidPower | 3QF11 power(L1) | 3QF11 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh31 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.81 | hwIntegratedPDUCabinetIIIBrh32ValidPower | 3QF11 power(L2) | 3QF11 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh32 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.82 | hwIntegratedPDUCabinetIIIBrh33ValidPower | 3QF11 power(L3) | 3QF11 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh33 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.83 | hwIntegratedPDUCabinetIIIBrh34ValidPower | 3QF12 power(L1) | 3QF12 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh34 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.84 | hwIntegratedPDUCabinetIIIBrh35ValidPower | 3QF12 power(L2) | 3QF12 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh35 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.85 | hwIntegratedPDUCabinetIIIBrh36ValidPower | 3QF12 power(L3) | 3QF12 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh36 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.86 | hwIntegratedPDUCabinetIIIBrh37ValidPower | 3QF13 power(L1) | 3QF13 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh37 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.87 | hwIntegratedPDUCabinetIIIBrh38ValidPower | 3QF13 power(L2) | 3QF13 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh38 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.88 | hwIntegratedPDUCabinetIIIBrh39ValidPower | 3QF13 power(L3) | 3QF13 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh39 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.89 | hwIntegratedPDUCabinetIIIBrh40ValidPower | 3QF14 power(L1) | 3QF14 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh40 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.90 | hwIntegratedPDUCabinetIIIBrh41ValidPower | 3QF14 power(L2) | 3QF14 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh41 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.91 | hwIntegratedPDUCabinetIIIBrh42ValidPower | 3QF14 power(L3) | 3QF14 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh42 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.92 | hwIntegratedPDUCabinetIIIBrh43ValidPower | 3QF15 power(L1) | 3QF15 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh43 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.93 | hwIntegratedPDUCabinetIIIBrh44ValidPower | 3QF15 power(L2) | 3QF15 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh44 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.94 | hwIntegratedPDUCabinetIIIBrh45ValidPower | 3QF15 power(L3) | 3QF15 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh45 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.95 | hwIntegratedPDUCabinetIIIBrh46ValidPower | 3QF16 power(L1) | 3QF16 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh46 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.96 | hwIntegratedPDUCabinetIIIBrh47ValidPower | 3QF16 power(L2) | 3QF16 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh47 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.97 | hwIntegratedPDUCabinetIIIBrh48ValidPower | 3QF16 power(L3) | 3QF16 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The III Brh48 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.4.1.100 | hwIntegratedPDUCabinet4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5 | hwIntegratedPDUCabinetRunning5Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.1 | hwIntegratedPDUCabinetRunning5Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.2 | hwIntegratedPDUCabinetIIIBrh1ValidEnergy | 3QF1 electricity energy(L1) | 3QF1 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh1 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.3 | hwIntegratedPDUCabinetIIIBrh2ValidEnergy | 3QF1 electricity energy(L2) | 3QF1 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh2 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.4 | hwIntegratedPDUCabinetIIIBrh3ValidEnergy | 3QF1 electricity energy(L3) | 3QF1 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh3 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.5 | hwIntegratedPDUCabinetIIIBrh4ValidEnergy | 3QF2 electricity energy(L1) | 3QF2 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh4 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.6 | hwIntegratedPDUCabinetIIIBrh5ValidEnergy | 3QF2 electricity energy(L2) | 3QF2 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh5 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.7 | hwIntegratedPDUCabinetIIIBrh6ValidEnergy | 3QF2 electricity energy(L3) | 3QF2 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh6 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.8 | hwIntegratedPDUCabinetIIIBrh7ValidEnergy | 3QF3 electricity energy(L1) | 3QF3 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh7 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.9 | hwIntegratedPDUCabinetIIIBrh8ValidEnergy | 3QF3 electricity energy(L2) | 3QF3 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh8 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.10 | hwIntegratedPDUCabinetIIIBrh9ValidEnergy | 3QF3 electricity energy(L3) | 3QF3 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh9 valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.11 | hwIntegratedPDUCabinetIIIBrh10ValidEnergy | 3QF4 electricity energy(L1) | 3QF4 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh10 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.12 | hwIntegratedPDUCabinetIIIBrh11ValidEnergy | 3QF4 electricity energy(L2) | 3QF4 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh11 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.13 | hwIntegratedPDUCabinetIIIBrh12ValidEnergy | 3QF4 electricity energy(L3) | 3QF4 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh12 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.14 | hwIntegratedPDUCabinetIIIBrh13ValidEnergy | 3QF5 electricity energy(L1) | 3QF5 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh13 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.15 | hwIntegratedPDUCabinetIIIBrh14ValidEnergy | 3QF5 electricity energy(L2) | 3QF5 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh14 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.16 | hwIntegratedPDUCabinetIIIBrh15ValidEnergy | 3QF5 electricity energy(L3) | 3QF5 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh15 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.17 | hwIntegratedPDUCabinetIIIBrh16ValidEnergy | 3QF6 electricity energy(L1) | 3QF6 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh16 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.18 | hwIntegratedPDUCabinetIIIBrh17ValidEnergy | 3QF6 electricity energy(L2) | 3QF6 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh17 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.19 | hwIntegratedPDUCabinetIIIBrh18ValidEnergy | 3QF6 electricity energy(L3) | 3QF6 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh18 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.20 | hwIntegratedPDUCabinetIIIBrh19ValidEnergy | 3QF7 electricity energy(L1) | 3QF7 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh19 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.21 | hwIntegratedPDUCabinetIIIBrh20ValidEnergy | 3QF7 electricity energy(L2) | 3QF7 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh20 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.22 | hwIntegratedPDUCabinetIIIBrh21ValidEnergy | 3QF7 electricity energy(L3) | 3QF7 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh21 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.23 | hwIntegratedPDUCabinetIIIBrh22ValidEnergy | 3QF8 electricity energy(L1) | 3QF8 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh22 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.24 | hwIntegratedPDUCabinetIIIBrh23ValidEnergy | 3QF8 electricity energy(L2) | 3QF8 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh23 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.25 | hwIntegratedPDUCabinetIIIBrh24ValidEnergy | 3QF8 electricity energy(L3) | 3QF8 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh24 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.26 | hwIntegratedPDUCabinetIIIBrh25ValidEnergy | 3QF9 electricity energy(L1) | 3QF9 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh25 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.27 | hwIntegratedPDUCabinetIIIBrh26ValidEnergy | 3QF9 electricity energy(L2) | 3QF9 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh26 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.28 | hwIntegratedPDUCabinetIIIBrh27ValidEnergy | 3QF9 electricity energy(L3) | 3QF9 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh27 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.29 | hwIntegratedPDUCabinetIIIBrh28ValidEnergy | 3QF10 electricity energy(L1) | 3QF10 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh28 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.30 | hwIntegratedPDUCabinetIIIBrh29ValidEnergy | 3QF10 electricity energy(L2) | 3QF10 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh29 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.31 | hwIntegratedPDUCabinetIIIBrh30ValidEnergy | 3QF10 electricity energy(L3) | 3QF10 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh30 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.32 | hwIntegratedPDUCabinetIIIBrh31ValidEnergy | 3QF11 electricity energy(L1) | 3QF11 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh31 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.33 | hwIntegratedPDUCabinetIIIBrh32ValidEnergy | 3QF11 electricity energy(L2) | 3QF11 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh32 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.34 | hwIntegratedPDUCabinetIIIBrh33ValidEnergy | 3QF11 electricity energy(L3) | 3QF11 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh33 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.35 | hwIntegratedPDUCabinetIIIBrh34ValidEnergy | 3QF12 electricity energy(L1) | 3QF12 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh34 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.36 | hwIntegratedPDUCabinetIIIBrh35ValidEnergy | 3QF12 electricity energy(L2) | 3QF12 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh35 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.37 | hwIntegratedPDUCabinetIIIBrh36ValidEnergy | 3QF12 electricity energy(L3) | 3QF12 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh36 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.38 | hwIntegratedPDUCabinetIIIBrh37ValidEnergy | 3QF13 electricity energy(L1) | 3QF13 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh37 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.39 | hwIntegratedPDUCabinetIIIBrh38ValidEnergy | 3QF13 electricity energy(L2) | 3QF13 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh38 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.40 | hwIntegratedPDUCabinetIIIBrh39ValidEnergy | 3QF13 electricity energy(L3) | 3QF13 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh39 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.41 | hwIntegratedPDUCabinetIIIBrh40ValidEnergy | 3QF14 electricity energy(L1) | 3QF14 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh40 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.42 | hwIntegratedPDUCabinetIIIBrh41ValidEnergy | 3QF14 electricity energy(L2) | 3QF14 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh41 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.43 | hwIntegratedPDUCabinetIIIBrh42ValidEnergy | 3QF14 electricity energy(L3) | 3QF14 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh42 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.44 | hwIntegratedPDUCabinetIIIBrh43ValidEnergy | 3QF15 electricity energy(L1) | 3QF15 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh43 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.45 | hwIntegratedPDUCabinetIIIBrh44ValidEnergy | 3QF15 electricity energy(L2) | 3QF15 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh44 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.46 | hwIntegratedPDUCabinetIIIBrh45ValidEnergy | 3QF15 electricity energy(L3) | 3QF15 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh45 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.47 | hwIntegratedPDUCabinetIIIBrh46ValidEnergy | 3QF16 electricity energy(L1) | 3QF16 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh46 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.48 | hwIntegratedPDUCabinetIIIBrh47ValidEnergy | 3QF16 electricity energy(L2) | 3QF16 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh47 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.49 | hwIntegratedPDUCabinetIIIBrh48ValidEnergy | 3QF16 electricity energy(L3) | 3QF16 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The III Brh48 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.50 | hwIntegratedPDUCabinetIIIBrh1Temp | 3QF1 temperature(L1) | 3QF1 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh1 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.51 | hwIntegratedPDUCabinetIIIBrh2Temp | 3QF1 temperature(L2) | 3QF1 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh2 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.52 | hwIntegratedPDUCabinetIIIBrh3Temp | 3QF1 temperature(L3) | 3QF1 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh3 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.53 | hwIntegratedPDUCabinetIIIBrh4Temp | 3QF2 temperature(L1) | 3QF2 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh4 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.54 | hwIntegratedPDUCabinetIIIBrh5Temp | 3QF2 temperature(L2) | 3QF2 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh5 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.55 | hwIntegratedPDUCabinetIIIBrh6Temp | 3QF2 temperature(L3) | 3QF2 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh6 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.56 | hwIntegratedPDUCabinetIIIBrh7Temp | 3QF3 temperature(L1) | 3QF3 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh7 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.57 | hwIntegratedPDUCabinetIIIBrh8Temp | 3QF3 temperature(L2) | 3QF3 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh8 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.58 | hwIntegratedPDUCabinetIIIBrh9Temp | 3QF3 temperature(L3) | 3QF3 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh9 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.59 | hwIntegratedPDUCabinetIIIBrh10Temp | 3QF4 temperature(L1) | 3QF4 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh10 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.60 | hwIntegratedPDUCabinetIIIBrh11Temp | 3QF4 temperature(L2) | 3QF4 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh11 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.61 | hwIntegratedPDUCabinetIIIBrh12Temp | 3QF4 temperature(L3) | 3QF4 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh12 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.62 | hwIntegratedPDUCabinetIIIBrh13Temp | 3QF5 temperature(L1) | 3QF5 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh13 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.63 | hwIntegratedPDUCabinetIIIBrh14Temp | 3QF5 temperature(L2) | 3QF5 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh14 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.64 | hwIntegratedPDUCabinetIIIBrh15Temp | 3QF5 temperature(L3) | 3QF5 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh15 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.65 | hwIntegratedPDUCabinetIIIBrh16Temp | 3QF6 temperature(L1) | 3QF6 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh16 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.66 | hwIntegratedPDUCabinetIIIBrh17Temp | 3QF6 temperature(L2) | 3QF6 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh17 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.67 | hwIntegratedPDUCabinetIIIBrh18Temp | 3QF6 temperature(L3) | 3QF6 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh18 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.68 | hwIntegratedPDUCabinetIIIBrh19Temp | 3QF7 temperature(L1) | 3QF7 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh19 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.69 | hwIntegratedPDUCabinetIIIBrh20Temp | 3QF7 temperature(L2) | 3QF7 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh20 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.70 | hwIntegratedPDUCabinetIIIBrh21Temp | 3QF7 temperature(L3) | 3QF7 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh21 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.71 | hwIntegratedPDUCabinetIIIBrh22Temp | 3QF8 temperature(L1) | 3QF8 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh22 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.72 | hwIntegratedPDUCabinetIIIBrh23Temp | 3QF8 temperature(L2) | 3QF8 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh23 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.73 | hwIntegratedPDUCabinetIIIBrh24Temp | 3QF8 temperature(L3) | 3QF8 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh24 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.74 | hwIntegratedPDUCabinetIIIBrh25Temp | 3QF9 temperature(L1) | 3QF9 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh25 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.75 | hwIntegratedPDUCabinetIIIBrh26Temp | 3QF9 temperature(L2) | 3QF9 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh26 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.76 | hwIntegratedPDUCabinetIIIBrh27Temp | 3QF9 temperature(L3) | 3QF9 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh27 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.77 | hwIntegratedPDUCabinetIIIBrh28Temp | 3QF10 temperature(L1) | 3QF10 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh28 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.78 | hwIntegratedPDUCabinetIIIBrh29Temp | 3QF10 temperature(L2) | 3QF10 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh29 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.79 | hwIntegratedPDUCabinetIIIBrh30Temp | 3QF10 temperature(L3) | 3QF10 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh30 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.80 | hwIntegratedPDUCabinetIIIBrh31Temp | 3QF11 temperature(L1) | 3QF11 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh31 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.81 | hwIntegratedPDUCabinetIIIBrh32Temp | 3QF11 temperature(L2) | 3QF11 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh32 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.82 | hwIntegratedPDUCabinetIIIBrh33Temp | 3QF11 temperature(L3) | 3QF11 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh33 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.83 | hwIntegratedPDUCabinetIIIBrh34Temp | 3QF12 temperature(L1) | 3QF12 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh34 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.84 | hwIntegratedPDUCabinetIIIBrh35Temp | 3QF12 temperature(L2) | 3QF12 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh35 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.85 | hwIntegratedPDUCabinetIIIBrh36Temp | 3QF12 temperature(L3) | 3QF12 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh36 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.86 | hwIntegratedPDUCabinetIIIBrh37Temp | 3QF13 temperature(L1) | 3QF13 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh37 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.87 | hwIntegratedPDUCabinetIIIBrh38Temp | 3QF13 temperature(L2) | 3QF13 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh38 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.88 | hwIntegratedPDUCabinetIIIBrh39Temp | 3QF13 temperature(L3) | 3QF13 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh39 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.89 | hwIntegratedPDUCabinetIIIBrh40Temp | 3QF14 temperature(L1) | 3QF14 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh40 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.90 | hwIntegratedPDUCabinetIIIBrh41Temp | 3QF14 temperature(L2) | 3QF14 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh41 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.91 | hwIntegratedPDUCabinetIIIBrh42Temp | 3QF14 temperature(L3) | 3QF14 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh42 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.92 | hwIntegratedPDUCabinetIIIBrh43Temp | 3QF15 temperature(L1) | 3QF15 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh43 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.93 | hwIntegratedPDUCabinetIIIBrh44Temp | 3QF15 temperature(L2) | 3QF15 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh44 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.94 | hwIntegratedPDUCabinetIIIBrh45Temp | 3QF15 temperature(L3) | 3QF15 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh45 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.95 | hwIntegratedPDUCabinetIIIBrh46Temp | 3QF16 temperature(L1) | 3QF16 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh46 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.96 | hwIntegratedPDUCabinetIIIBrh47Temp | 3QF16 temperature(L2) | 3QF16 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh47 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.97 | hwIntegratedPDUCabinetIIIBrh48Temp | 3QF16 temperature(L3) | 3QF16 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The III Brh48 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.5.1.100 | hwIntegratedPDUCabinet5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6 | hwIntegratedPDUCabinetRunning6Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.1 | hwIntegratedPDUCabinetRunning6Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.2 | hwIntegratedPDUCabinetIVBrh1ValidPower | 4QF1 power(L1) | 4QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh1 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.3 | hwIntegratedPDUCabinetIVBrh2ValidPower | 4QF1 power(L2) | 4QF1 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh2 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.4 | hwIntegratedPDUCabinetIVBrh3ValidPower | 4QF1 power(L3) | 4QF1 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh3 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.5 | hwIntegratedPDUCabinetIVBrh4ValidPower | 4QF2 power(L1) | 4QF2 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh4 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.6 | hwIntegratedPDUCabinetIVBrh5ValidPower | 4QF2 power(L2) | 4QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh5 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.7 | hwIntegratedPDUCabinetIVBrh6ValidPower | 4QF2 power(L3) | 4QF2 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh6 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.8 | hwIntegratedPDUCabinetIVBrh7ValidPower | 4QF3 power(L1) | 4QF3 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh7 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.9 | hwIntegratedPDUCabinetIVBrh8ValidPower | 4QF3 power(L2) | 4QF3 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh8 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.10 | hwIntegratedPDUCabinetIVBrh9ValidPower | 4QF3 power(L3) | 4QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh9 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.11 | hwIntegratedPDUCabinetIVBrh10ValidPower | 4QF4 power(L1) | 4QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh10 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.12 | hwIntegratedPDUCabinetIVBrh11ValidPower | 4QF4 power(L2) | 4QF4 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh11 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.13 | hwIntegratedPDUCabinetIVBrh12ValidPower | 4QF4 power(L3) | 4QF4 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh12 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.14 | hwIntegratedPDUCabinetIVBrh13ValidPower | 4QF5 power(L1) | 4QF5 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh13 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.15 | hwIntegratedPDUCabinetIVBrh14ValidPower | 4QF5 power(L2) | 4QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh14 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.16 | hwIntegratedPDUCabinetIVBrh15ValidPower | 4QF5 power(L3) | 4QF5 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh15 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.17 | hwIntegratedPDUCabinetIVBrh16ValidPower | 4QF6 power(L1) | 4QF6 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh16 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.18 | hwIntegratedPDUCabinetIVBrh17ValidPower | 4QF6 power(L2) | 4QF6 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh17 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.19 | hwIntegratedPDUCabinetIVBrh18ValidPower | 4QF6 power(L3) | 4QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh18 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.20 | hwIntegratedPDUCabinetIVBrh19ValidPower | 4QF7 power(L1) | 4QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh19 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.21 | hwIntegratedPDUCabinetIVBrh20ValidPower | 4QF7 power(L2) | 4QF7 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh20 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.22 | hwIntegratedPDUCabinetIVBrh21ValidPower | 4QF7 power(L3) | 4QF7 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh21 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.23 | hwIntegratedPDUCabinetIVBrh22ValidPower | 4QF8 power(L1) | 4QF8 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh22 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.24 | hwIntegratedPDUCabinetIVBrh23ValidPower | 4QF8 power(L2) | 4QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh23 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.25 | hwIntegratedPDUCabinetIVBrh24ValidPower | 4QF8 power(L3) | 4QF8 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The IV Brh24 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.26 | hwIntegratedPDUCabinetIVBrh1ValidEnergy | 4QF1 electricity energy(L1) | 4QF1 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh1 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.27 | hwIntegratedPDUCabinetIVBrh2ValidEnergy | 4QF1 electricity energy(L2) | 4QF1 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh2 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.28 | hwIntegratedPDUCabinetIVBrh3ValidEnergy | 4QF1 electricity energy(L3) | 4QF1 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh3 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.29 | hwIntegratedPDUCabinetIVBrh4ValidEnergy | 4QF2 electricity energy(L1) | 4QF2 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh4 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.30 | hwIntegratedPDUCabinetIVBrh5ValidEnergy | 4QF2 electricity energy(L2) | 4QF2 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh5 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.31 | hwIntegratedPDUCabinetIVBrh6ValidEnergy | 4QF2 electricity energy(L3) | 4QF2 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh6 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.32 | hwIntegratedPDUCabinetIVBrh7ValidEnergy | 4QF3 electricity energy(L1) | 4QF3 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh7 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.33 | hwIntegratedPDUCabinetIVBrh8ValidEnergy | 4QF3 electricity energy(L2) | 4QF3 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh8 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.34 | hwIntegratedPDUCabinetIVBrh9ValidEnergy | 4QF3 electricity energy(L3) | 4QF3 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh9 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.35 | hwIntegratedPDUCabinetIVBrh10ValidEnergy | 4QF4 electricity energy(L1) | 4QF4 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh10 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.36 | hwIntegratedPDUCabinetIVBrh11ValidEnergy | 4QF4 electricity energy(L2) | 4QF4 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh11 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.37 | hwIntegratedPDUCabinetIVBrh12ValidEnergy | 4QF4 electricity energy(L3) | 4QF4 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh12 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.38 | hwIntegratedPDUCabinetIVBrh13ValidEnergy | 4QF5 electricity energy(L1) | 4QF5 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh13 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.39 | hwIntegratedPDUCabinetIVBrh14ValidEnergy | 4QF5 electricity energy(L2) | 4QF5 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh14 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.40 | hwIntegratedPDUCabinetIVBrh15ValidEnergy | 4QF5 electricity energy(L3) | 4QF5 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh15 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.41 | hwIntegratedPDUCabinetIVBrh16ValidEnergy | 4QF6 electricity energy(L1) | 4QF6 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh16 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.42 | hwIntegratedPDUCabinetIVBrh17ValidEnergy | 4QF6 electricity energy(L2) | 4QF6 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh17 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.43 | hwIntegratedPDUCabinetIVBrh18ValidEnergy | 4QF6 electricity energy(L3) | 4QF6 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh18 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.44 | hwIntegratedPDUCabinetIVBrh19ValidEnergy | 4QF7 electricity energy(L1) | 4QF7 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh19 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.45 | hwIntegratedPDUCabinetIVBrh20ValidEnergy | 4QF7 electricity energy(L2) | 4QF7 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh20 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.46 | hwIntegratedPDUCabinetIVBrh21ValidEnergy | 4QF7 electricity energy(L3) | 4QF7 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh21 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.47 | hwIntegratedPDUCabinetIVBrh22ValidEnergy | 4QF8 electricity energy(L1) | 4QF8 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh22 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.48 | hwIntegratedPDUCabinetIVBrh23ValidEnergy | 4QF8 electricity energy(L2) | 4QF8 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh23 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.49 | hwIntegratedPDUCabinetIVBrh24ValidEnergy | 4QF8 electricity energy(L3) | 4QF8 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The IV Brh24 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.50 | hwIntegratedPDUCabinetIVBrh1Temp | 4QF1 temperature(L1) | 4QF1 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh1 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.51 | hwIntegratedPDUCabinetIVBrh2Temp | 4QF1 temperature(L2) | 4QF1 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh2 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.52 | hwIntegratedPDUCabinetIVBrh3Temp | 4QF1 temperature(L3) | 4QF1 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh3 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.53 | hwIntegratedPDUCabinetIVBrh4Temp | 4QF2 temperature(L1) | 4QF2 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh4 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.54 | hwIntegratedPDUCabinetIVBrh5Temp | 4QF2 temperature(L2) | 4QF2 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh5 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.55 | hwIntegratedPDUCabinetIVBrh6Temp | 4QF2 temperature(L3) | 4QF2 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh6 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.56 | hwIntegratedPDUCabinetIVBrh7Temp | 4QF3 temperature(L1) | 4QF3 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh7 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.57 | hwIntegratedPDUCabinetIVBrh8Temp | 4QF3 temperature(L2) | 4QF3 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh8 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.58 | hwIntegratedPDUCabinetIVBrh9Temp | 4QF3 temperature(L3) | 4QF3 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh9 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.59 | hwIntegratedPDUCabinetIVBrh10Temp | 4QF4 temperature(L1) | 4QF4 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh10 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.60 | hwIntegratedPDUCabinetIVBrh11Temp | 4QF4 temperature(L2) | 4QF4 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh11 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.61 | hwIntegratedPDUCabinetIVBrh12Temp | 4QF4 temperature(L3) | 4QF4 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh12 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.62 | hwIntegratedPDUCabinetIVBrh13Temp | 4QF5 temperature(L1) | 4QF5 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh13 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.63 | hwIntegratedPDUCabinetIVBrh14Temp | 4QF5 temperature(L2) | 4QF5 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh14 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.64 | hwIntegratedPDUCabinetIVBrh15Temp | 4QF5 temperature(L3) | 4QF5 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh15 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.65 | hwIntegratedPDUCabinetIVBrh16Temp | 4QF6 temperature(L1) | 4QF6 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh16 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.66 | hwIntegratedPDUCabinetIVBrh17Temp | 4QF6 temperature(L2) | 4QF6 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh17 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.67 | hwIntegratedPDUCabinetIVBrh18Temp | 4QF6 temperature(L3) | 4QF6 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh18 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.68 | hwIntegratedPDUCabinetIVBrh19Temp | 4QF7 temperature(L1) | 4QF7 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh19 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.69 | hwIntegratedPDUCabinetIVBrh20Temp | 4QF7 temperature(L2) | 4QF7 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh20 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.70 | hwIntegratedPDUCabinetIVBrh21Temp | 4QF7 temperature(L3) | 4QF7 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh21 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.71 | hwIntegratedPDUCabinetIVBrh22Temp | 4QF8 temperature(L1) | 4QF8 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh22 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.72 | hwIntegratedPDUCabinetIVBrh23Temp | 4QF8 temperature(L2) | 4QF8 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh23 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.73 | hwIntegratedPDUCabinetIVBrh24Temp | 4QF8 temperature(L3) | 4QF8 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The IV Brh24 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.6.1.100 | hwIntegratedPDUCabinet6RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.7 | hwIntegratedPDUCabinetConfigTable | / | / |  |  | / | / | The config table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.1 | hwIntegratedPDUCabinetConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device configuration table for Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.2 | hwIntegratedPDUCabinetSysPhaseFailVolt | Phase open voltage | 系统缺相电压 | 1-Read_Write | 读写 | 0..60 | 0..60 | The Sys Phase Fail Volt of the Integrated PDU Cabinet. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.3 | hwIntegratedPDUCabinetHarmonicAlmEnable | Enable harmonic alarm | 谐波告警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The Harmonic Alm Enable of the Integrated PDU Cabinet. value 1 indicates disable. value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.4 | hwIntegratedPDUCabinetVoltHarmonicAlmPoint | Voltage harmonic alarm | 电压谐波告警 | 1-Read_Write | 读写 | 10..300 | 10..300 | The Volt Harmonic Alm Point of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.5 | hwIntegratedPDUCabinetCurrHarmonicAlmPoint | Current harmonic alarm | 电流谐波告警 | 1-Read_Write | 读写 | 0..300 | 0..300 | The Curr Harmonic Alm Point of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.6 | hwIntegratedPDUCabinetSysOvVoltAlmPoint | Overvoltage | 系统过压 | 1-Read_Write | 读写 | 1050..1250 | 1050..1250 | The Sys Ov Volt Alm Point of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.7 | hwIntegratedPDUCabinetSysUnVoltAlmPoint | Undervoltage | 系统欠压 | 1-Read_Write | 读写 | 750..950 | 750..950 | The Sys Un Volt Alm Point of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.8 | hwIntegratedPDUCabinetOvLoadAlmPoint | Overload | 负载过载 | 1-Read_Write | 读写 | 1000..1200 | 1000..1200 | The Ov Load Alm Point of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.9 | hwIntegratedPDUCabinetSysFrqOvAlmPoint | Overfrequency | 系统频率越限 | 1-Read_Write | 读写 | 10..100 | 10..100 | The Sys Frq Ov Alm Point of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.10 | hwIntegratedPDUCabinetLoadCurrOvAlmPoint | Load overcurrent threshold | 负载电流高阈值 | 1-Read_Write | 读写 | 800..1000 | 800..1000 | The Load Curr Ov Alm Point of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.11 | hwIntegratedPDUCabinetLoadCurrUnAlmPoint | Load undercurrent threshold | 负载电流低阈值 | 1-Read_Write | 读写 | 300..800 | 300..800 | The Load Curr Un Alm Point of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.12 | hwIntegratedPDUCabinetThreePhaseCurrUnbalanceDeg | Three-phase current imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..500 | 0..500 | The Three Phase Curr Unbalance Deg of the Integrated PDU Cabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.13 | hwIntegratedPDUCabinetDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | The Device Name of the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.7.1.100 | hwIntegratedPDUCabinetConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the Integrated PDU Cabinet config table.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8 | hwIntegratedPDUCabinetRunning8Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.1 | hwIntegratedPDUCabinetRunning8Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.2 | hwIntegratedPDUCabinetIBrh25ValidPower | 1QF25 power(L1) | 1QF25 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh25 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.3 | hwIntegratedPDUCabinetIBrh26ValidPower | 1QF26 power(L2) | 1QF26 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh26 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.4 | hwIntegratedPDUCabinetIBrh27ValidPower | 1QF27 power(L3) | 1QF27 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh27 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.5 | hwIntegratedPDUCabinetIBrh28ValidPower | 1QF28 power(L1) | 1QF28 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh28 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.6 | hwIntegratedPDUCabinetIBrh29ValidPower | 1QF29 power(L2) | 1QF29 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh29 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.7 | hwIntegratedPDUCabinetIBrh30ValidPower | 1QF30 power(L3) | 1QF30 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh30 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.8 | hwIntegratedPDUCabinetIBrh31ValidPower | 1QF31 power(L1) | 1QF31 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh31Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.9 | hwIntegratedPDUCabinetIBrh32ValidPower | 1QF32 power(L2) | 1QF32 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh32 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.10 | hwIntegratedPDUCabinetIBrh33ValidPower | 1QF33 power(L3) | 1QF33 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh33 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.11 | hwIntegratedPDUCabinetIBrh34ValidPower | 1QF34 power(L1) | 1QF34 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh34 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.12 | hwIntegratedPDUCabinetIBrh35ValidPower | 1QF35 power(L2) | 1QF35 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh35 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.13 | hwIntegratedPDUCabinetIBrh36ValidPower | 1QF36 power(L3) | 1QF36 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh36 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.14 | hwIntegratedPDUCabinetIBrh37ValidPower | 1QF37 power(L1) | 1QF37 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh37 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.15 | hwIntegratedPDUCabinetIBrh38ValidPower | 1QF38 power(L2) | 1QF38 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh38 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.16 | hwIntegratedPDUCabinetIBrh39ValidPower | 1QF39 power(L3) | 1QF39 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh39 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.17 | hwIntegratedPDUCabinetIBrh40ValidPower | 1QF40 power(L1) | 1QF40 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh40 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.18 | hwIntegratedPDUCabinetIBrh41ValidPower | 1QF41 power(L2) | 1QF41 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh41 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.19 | hwIntegratedPDUCabinetIBrh42ValidPower | 1QF42 power(L3) | 1QF42 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh42 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.20 | hwIntegratedPDUCabinetIBrh43ValidPower | 1QF43 power(L1) | 1QF43 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh43 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.21 | hwIntegratedPDUCabinetIBrh44ValidPower | 1QF44 power(L2) | 1QF44 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh44 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.22 | hwIntegratedPDUCabinetIBrh45ValidPower | 1QF45 power(L3) | 1QF45 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh45 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.23 | hwIntegratedPDUCabinetIBrh46ValidPower | 1QF46 power(L1) | 1QF46 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh46 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.24 | hwIntegratedPDUCabinetIBrh47ValidPower | 1QF47 power(L2) | 1QF47 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh47 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.25 | hwIntegratedPDUCabinetIBrh48ValidPower | 1QF48 power(L3) | 1QF48 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | The I Brh48 Valid Power of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.26 | hwIntegratedPDUCabinetIBrh25ValidEnergy | 1QF25 electricity energy(L1) | 1QF25 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh25 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.27 | hwIntegratedPDUCabinetIBrh26ValidEnergy | 1QF26 electricity energy(L2) | 1QF26 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh26 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.28 | hwIntegratedPDUCabinetIBrh27ValidEnergy | 1QF27 electricity energy(L3) | 1QF27 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh27 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.29 | hwIntegratedPDUCabinetIBrh28ValidEnergy | 1QF28 electricity energy(L1) | 1QF28 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh28 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.30 | hwIntegratedPDUCabinetIBrh29ValidEnergy | 1QF29 electricity energy(L2) | 1QF29 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh29 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.31 | hwIntegratedPDUCabinetIBrh30ValidEnergy | 1QF30 electricity energy(L3) | 1QF30 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh30 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.32 | hwIntegratedPDUCabinetIBrh31ValidEnergy | 1QF31 electricity energy(L1) | 1QF31 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh31 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.33 | hwIntegratedPDUCabinetIBrh32ValidEnergy | 1QF32 electricity energy(L2) | 1QF32 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh32 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.34 | hwIntegratedPDUCabinetIBrh33ValidEnergy | 1QF33 electricity energy(L3) | 1QF33 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh33 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.35 | hwIntegratedPDUCabinetIBrh34ValidEnergy | 1QF34 electricity energy(L1) | 1QF34 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh34 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.36 | hwIntegratedPDUCabinetIBrh35ValidEnergy | 1QF35 electricity energy(L2) | 1QF35 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh35 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.37 | hwIntegratedPDUCabinetIBrh36ValidEnergy | 1QF36 electricity energy(L3) | 1QF36 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh36 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.38 | hwIntegratedPDUCabinetIBrh37ValidEnergy | 1QF37 electricity energy(L1) | 1QF37 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh37 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.39 | hwIntegratedPDUCabinetIBrh38ValidEnergy | 1QF38 electricity energy(L2) | 1QF38 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh38 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.40 | hwIntegratedPDUCabinetIBrh39ValidEnergy | 1QF39 electricity energy(L3) | 1QF39 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh39 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.41 | hwIntegratedPDUCabinetIBrh40ValidEnergy | 1QF40 electricity energy(L1) | 1QF40 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh40 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.42 | hwIntegratedPDUCabinetIBrh41ValidEnergy | 1QF41 electricity energy(L2) | 1QF41 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh41 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.43 | hwIntegratedPDUCabinetIBrh42ValidEnergy | 1QF42 electricity energy(L3) | 1QF42 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh42 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.44 | hwIntegratedPDUCabinetIBrh43ValidEnergy | 1QF43 electricity energy(L1) | 1QF43 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh43 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.45 | hwIntegratedPDUCabinetIBrh44ValidEnergy | 1QF44 electricity energy(L2) | 1QF44 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh44 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.46 | hwIntegratedPDUCabinetIBrh45ValidEnergy | 1QF45 electricity energy(L3) | 1QF45 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh45 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.47 | hwIntegratedPDUCabinetIBrh46ValidEnergy | 1QF46 electricity energy(L1) | 1QF46 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh46 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.48 | hwIntegratedPDUCabinetIBrh47ValidEnergy | 1QF47 electricity energy(L2) | 1QF47 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh47 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.49 | hwIntegratedPDUCabinetIBrh48ValidEnergy | 1QF48 electricity energy(L3) | 1QF48 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | The I Brh48 Valid Energy of Integrated PDU Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.50 | hwIntegratedPDUCabinetIBrh25Temp | 1QF25 temperature(L1) | 1QF25 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh25 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.51 | hwIntegratedPDUCabinetIBrh26Temp | 1QF26 temperature(L2) | 1QF26 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh26 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.52 | hwIntegratedPDUCabinetIBrh27Temp | 1QF27 temperature(L3) | 1QF27 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh27 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.53 | hwIntegratedPDUCabinetIBrh28Temp | 1QF28 temperature(L1) | 1QF28 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh28 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.54 | hwIntegratedPDUCabinetIBrh29Temp | 1QF29 temperature(L2) | 1QF29 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh29 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.55 | hwIntegratedPDUCabinetIBrh30Temp | 1QF30 temperature(L3) | 1QF30 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh30 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.56 | hwIntegratedPDUCabinetIBrh31Temp | 1QF31 temperature(L1) | 1QF31 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh31 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.57 | hwIntegratedPDUCabinetIBrh32Temp | 1QF32 temperature(L2) | 1QF32 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh32 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.58 | hwIntegratedPDUCabinetIBrh33Temp | 1QF33 temperature(L3) | 1QF33 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh33 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.59 | hwIntegratedPDUCabinetIBrh34Temp | 1QF34 temperature(L1) | 1QF34 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh34 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.60 | hwIntegratedPDUCabinetIBrh35Temp | 1QF35 temperature(L2) | 1QF35 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh35 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.61 | hwIntegratedPDUCabinetIBrh36Temp | 1QF36 temperature(L3) | 1QF36 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh36 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.62 | hwIntegratedPDUCabinetIBrh37Temp | 1QF37 temperature(L1) | 1QF37 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh37 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.63 | hwIntegratedPDUCabinetIBrh38Temp | 1QF38 temperature(L2) | 1QF38 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh38 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.64 | hwIntegratedPDUCabinetIBrh39Temp | 1QF39 temperature(L3) | 1QF39 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh39 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.65 | hwIntegratedPDUCabinetIBrh40Temp | 1QF40 temperature(L1) | 1QF40 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh40 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.66 | hwIntegratedPDUCabinetIBrh41Temp | 1QF41 temperature(L2) | 1QF41 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh41 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.67 | hwIntegratedPDUCabinetIBrh42Temp | 1QF42 temperature(L3) | 1QF42 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh42 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.68 | hwIntegratedPDUCabinetIBrh43Temp | 1QF43 temperature(L1) | 1QF43 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh43 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.69 | hwIntegratedPDUCabinetIBrh44Temp | 1QF44 temperature(L2) | 1QF44 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh44 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.70 | hwIntegratedPDUCabinetIBrh45Temp | 1QF45 temperature(L3) | 1QF45 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh45 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.71 | hwIntegratedPDUCabinetIBrh46Temp | 1QF46 temperature(L1) | 1QF46 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh46 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.72 | hwIntegratedPDUCabinetIBrh47Temp | 1QF47 temperature(L2) | 1QF47 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh27 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.73 | hwIntegratedPDUCabinetIBrh48Temp | 1QF48 temperature(L3) | 1QF48 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The I Brh28 Temp of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.8.1.100 | hwIntegratedPDUCabinet8RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9 | hwIntegratedPDUCabinetRunning9Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.1 | hwIntegratedPDUCabinetRunning9Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.2 | hwIntegratedPDUCabinetQF1outputCurrent | 1QF1 current(L1) | 1QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF1 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.3 | hwIntegratedPDUCabinetQF2outputCurrent | 1QF2 current(L2) | 1QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF2 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.4 | hwIntegratedPDUCabinetQF3outputCurrent | 1QF3 current(L3) | 1QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF3 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.5 | hwIntegratedPDUCabinetQF4outputCurrent | 1QF4 current(L1) | 1QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF4 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.6 | hwIntegratedPDUCabinetQF5outputCurrent | 1QF5 current(L2) | 1QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF5 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.7 | hwIntegratedPDUCabinetQF6outputCurrent | 1QF6 current(L3) | 1QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF6 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.8 | hwIntegratedPDUCabinetQF7outputCurrent | 1QF7 current(L1) | 1QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF7 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.9 | hwIntegratedPDUCabinetQF8outputCurrent | 1QF8 current(L2) | 1QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF8 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.10 | hwIntegratedPDUCabinetQF9outputCurrent | 1QF9 current(L3) | 1QF9 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF9 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.11 | hwIntegratedPDUCabinetQF10outputCurrent | 1QF10 current(L1) | 1QF10 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF10 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.12 | hwIntegratedPDUCabinetQF11outputCurrent | 1QF11 current(L2) | 1QF11 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF11 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.13 | hwIntegratedPDUCabinetQF12outputCurrent | 1QF12 current(L3) | 1QF12 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF12 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.14 | hwIntegratedPDUCabinetQF13outputCurrent | 1QF13 current(L1) | 1QF13 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF13 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.15 | hwIntegratedPDUCabinetQF14outputCurrent | 1QF14 current(L2) | 1QF14 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF14 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.16 | hwIntegratedPDUCabinetQF15outputCurrent | 1QF15 current(L3) | 1QF15 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF15 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.17 | hwIntegratedPDUCabinetQF16outputCurrent | 1QF16 current(L1) | 1QF16 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF16 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.18 | hwIntegratedPDUCabinetQF17outputCurrent | 1QF17 current(L2) | 1QF17 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF17 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.19 | hwIntegratedPDUCabinetQF18outputCurrent | 1QF18 current(L3) | 1QF18 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF18 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.20 | hwIntegratedPDUCabinetQF19outputCurrent | 1QF19 current(L1) | 1QF19 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF19 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.21 | hwIntegratedPDUCabinetQF20outputCurrent | 1QF20 current(L2) | 1QF20 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF20 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.22 | hwIntegratedPDUCabinetQF21outputCurrent | 1QF21 current(L3) | 1QF21 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF21 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.23 | hwIntegratedPDUCabinetQF22outputCurrent | 1QF22 current(L1) | 1QF22 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF22 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.24 | hwIntegratedPDUCabinetQF23outputCurrent | 1QF23 current(L2) | 1QF23 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF23 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.25 | hwIntegratedPDUCabinetQF24outputCurrent | 1QF24 current(L3) | 1QF24 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF24 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.26 | hwIntegratedPDUCabinetQF1PowerLoadFactor | 1QF1 load factor(L1) | 1QF1 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF1 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.27 | hwIntegratedPDUCabinetQF2PowerLoadFactor | 1QF2 load factor(L2) | 1QF2 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF2 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.28 | hwIntegratedPDUCabinetQF3PowerLoadFactor | 1QF3 load factor(L3) | 1QF3 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF3 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.29 | hwIntegratedPDUCabinetQF4PowerLoadFactor | 1QF4 load factor(L1) | 1QF4 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF4 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.30 | hwIntegratedPDUCabinetQF5PowerLoadFactor | 1QF5 load factor(L2) | 1QF5 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF5 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.31 | hwIntegratedPDUCabinetQF6PowerLoadFactor | 1QF6 load factor(L3) | 1QF6 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF6 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.32 | hwIntegratedPDUCabinetQF7PowerLoadFactor | 1QF7 load factor(L1) | 1QF7 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF7 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.33 | hwIntegratedPDUCabinetQF8PowerLoadFactor | 1QF8 load factor(L2) | 1QF8 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF8 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.34 | hwIntegratedPDUCabinetQF9PowerLoadFactor | 1QF9 load factor(L3) | 1QF9 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF9 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.35 | hwIntegratedPDUCabinetQF10PowerLoadFactor | 1QF10 load factor(L1) | 1QF10 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF10 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.36 | hwIntegratedPDUCabinetQF11PowerLoadFactor | 1QF11 load factor(L2) | 1QF11 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF11 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.37 | hwIntegratedPDUCabinetQF12PowerLoadFactor | 1QF12 load factor(L3) | 1QF12 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF12 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.38 | hwIntegratedPDUCabinetQF13PowerLoadFactor | 1QF13 load factor(L1) | 1QF13 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF13 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.39 | hwIntegratedPDUCabinetQF14PowerLoadFactor | 1QF14 load factor(L2) | 1QF14 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF14 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.40 | hwIntegratedPDUCabinetQF15PowerLoadFactor | 1QF15 load factor(L3) | 1QF15 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF15 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.41 | hwIntegratedPDUCabinetQF16PowerLoadFactor | 1QF16 load factor(L1) | 1QF16 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF16 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.42 | hwIntegratedPDUCabinetQF17PowerLoadFactor | 1QF17 load factor(L2) | 1QF17 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF17 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.43 | hwIntegratedPDUCabinetQF18PowerLoadFactor | 1QF18 load factor(L3) | 1QF18 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF18 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.44 | hwIntegratedPDUCabinetQF19PowerLoadFactor | 1QF19 load factor(L1) | 1QF19 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF19 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.45 | hwIntegratedPDUCabinetQF20PowerLoadFactor | 1QF20 load factor(L2) | 1QF20 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF20 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.46 | hwIntegratedPDUCabinetQF21PowerLoadFactor | 1QF21 load factor(L3) | 1QF21 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF21 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.47 | hwIntegratedPDUCabinetQF22PowerLoadFactor | 1QF22 load factor(L1) | 1QF22 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF22 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.48 | hwIntegratedPDUCabinetQF23PowerLoadFactor | 1QF23 load factor(L2) | 1QF23 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF23 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.49 | hwIntegratedPDUCabinetQF24PowerLoadFactor | 1QF24 load factor(L3) | 1QF24 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF24 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.50 | hwIntegratedPDUCabinetQF1SwitchStatus | 1QF1 switch status(L1) | 1QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF1 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.51 | hwIntegratedPDUCabinetQF2SwitchStatus | 1QF2 switch status(L2) | 1QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF2 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.52 | hwIntegratedPDUCabinetQF3SwitchStatus | 1QF3 switch status(L3) | 1QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF3 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.53 | hwIntegratedPDUCabinetQF4SwitchStatus | 1QF4 switch status(L1) | 1QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF4 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.54 | hwIntegratedPDUCabinetQF5SwitchStatus | 1QF5 switch status(L2) | 1QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF5 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.55 | hwIntegratedPDUCabinetQF6SwitchStatus | 1QF6 switch status(L3) | 1QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF6 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.56 | hwIntegratedPDUCabinetQF7SwitchStatus | 1QF7 switch status(L1) | 1QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF7 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.57 | hwIntegratedPDUCabinetQF8SwitchStatus | 1QF8 switch status(L2) | 1QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF8 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.58 | hwIntegratedPDUCabinetQF9SwitchStatus | 1QF9 switch status(L3) | 1QF9 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF9 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.59 | hwIntegratedPDUCabinetQF10SwitchStatus | 1QF10 switch status(L1) | 1QF10 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF10 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.60 | hwIntegratedPDUCabinetQF11SwitchStatus | 1QF11 switch status(L2) | 1QF11 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF11 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.61 | hwIntegratedPDUCabinetQF12SwitchStatus | 1QF12 switch status(L3) | 1QF12 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF12 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.62 | hwIntegratedPDUCabinetQF13SwitchStatus | 1QF13 switch status(L1) | 1QF13 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF13 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.63 | hwIntegratedPDUCabinetQF14SwitchStatus | 1QF14 switch status(L2) | 1QF14 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF14 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.64 | hwIntegratedPDUCabinetQF15SwitchStatus | 1QF15 switch status(L3) | 1QF15 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF15 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.65 | hwIntegratedPDUCabinetQF16SwitchStatus | 1QF16 switch status(L1) | 1QF16 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF16 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.66 | hwIntegratedPDUCabinetQF17SwitchStatus | 1QF17 switch status(L2) | 1QF17 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF17 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.67 | hwIntegratedPDUCabinetQF18SwitchStatus | 1QF18 switch status(L3) | 1QF18 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF18 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.68 | hwIntegratedPDUCabinetQF19SwitchStatus | 1QF19 switch status(L1) | 1QF19 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF19 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.69 | hwIntegratedPDUCabinetQF20SwitchStatus | 1QF20 switch status(L2) | 1QF20 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF20 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.70 | hwIntegratedPDUCabinetQF21SwitchStatus | 1QF21 switch status(L3) | 1QF21 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF21 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.71 | hwIntegratedPDUCabinetQF22SwitchStatus | 1QF22 switch status(L1) | 1QF22 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF22 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.72 | hwIntegratedPDUCabinetQF23SwitchStatus | 1QF23 switch status(L2) | 1QF23 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF23 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.73 | hwIntegratedPDUCabinetQF24SwitchStatus | 1QF24 switch status(L3) | 1QF24 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF24 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.9.1.200 | hwIntegratedPDUCabinetRunning9RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10 | hwIntegratedPDUCabinetRunning10Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.1 | hwIntegratedPDUCabinetRunning10Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.2 | hwIntegratedPDUCabinet2QF1outputCurrent | 2QF1 current(L1) | 2QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF1 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.3 | hwIntegratedPDUCabinet2QF2outputCurrent | 2QF2 current(L2) | 2QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF2 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.4 | hwIntegratedPDUCabinet2QF3outputCurrent | 2QF3 current(L3) | 2QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF3 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.5 | hwIntegratedPDUCabinet2QF4outputCurrent | 2QF4 current(L1) | 2QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF4 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.6 | hwIntegratedPDUCabinet2QF5outputCurrent | 2QF5 current(L2) | 2QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF5 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.7 | hwIntegratedPDUCabinet2QF6outputCurrent | 2QF6 current(L3) | 2QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF6 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.8 | hwIntegratedPDUCabinet2QF7outputCurrent | 2QF7 current(L1) | 2QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF7 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.9 | hwIntegratedPDUCabinet2QF8outputCurrent | 2QF8 current(L2) | 2QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF8 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.10 | hwIntegratedPDUCabinet2QF9outputCurrent | 2QF9 current(L3) | 2QF9 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF9 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.11 | hwIntegratedPDUCabinet2QF10outputCurrent | 2QF10 current(L1) | 2QF10 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF10 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.12 | hwIntegratedPDUCabinet2QF11outputCurrent | 2QF11 current(L2) | 2QF11 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF11 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.13 | hwIntegratedPDUCabinet2QF12outputCurrent | 2QF12 current(L3) | 2QF12 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF12 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.14 | hwIntegratedPDUCabinet2QF13outputCurrent | 2QF13 current(L1) | 2QF13 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF13 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.15 | hwIntegratedPDUCabinet2QF14outputCurrent | 2QF14 current(L2) | 2QF14 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF14 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.16 | hwIntegratedPDUCabinet2QF15outputCurrent | 2QF15 current(L3) | 2QF15 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF15 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.17 | hwIntegratedPDUCabinet2QF16outputCurrent | 2QF16 current(L1) | 2QF16 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF16 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.18 | hwIntegratedPDUCabinet2QF17outputCurrent | 2QF17 current(L2) | 2QF17 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF17 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.19 | hwIntegratedPDUCabinet2QF18outputCurrent | 2QF18 current(L3) | 2QF18 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF18 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.20 | hwIntegratedPDUCabinet2QF19outputCurrent | 2QF19 current(L1) | 2QF19 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF19 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.21 | hwIntegratedPDUCabinet2QF20outputCurrent | 2QF20 current(L2) | 2QF20 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF20 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.22 | hwIntegratedPDUCabinet2QF21outputCurrent | 2QF21 current(L3) | 2QF21 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF21 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.23 | hwIntegratedPDUCabinet2QF22outputCurrent | 2QF22 current(L1) | 2QF22 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF22 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.24 | hwIntegratedPDUCabinet2QF23outputCurrent | 2QF23 current(L2) | 2QF23 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF23 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.25 | hwIntegratedPDUCabinet2QF24outputCurrent | 2QF24 current(L3) | 2QF24 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet2QF24 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.26 | hwIntegratedPDUCabinet2QF1PowerLoadFactor | 2QF1 load factor(L1) | 2QF1 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF1 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.27 | hwIntegratedPDUCabinet2QF2PowerLoadFactor | 2QF2 load factor(L2) | 2QF2 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF2 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.28 | hwIntegratedPDUCabinet2QF3PowerLoadFactor | 2QF3 load factor(L3) | 2QF3 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF3 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.29 | hwIntegratedPDUCabinet2QF4PowerLoadFactor | 2QF4 load factor(L1) | 2QF4 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF4 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.30 | hwIntegratedPDUCabinet2QF5PowerLoadFactor | 2QF5 load factor(L2) | 2QF5 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF5 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.31 | hwIntegratedPDUCabinet2QF6PowerLoadFactor | 2QF6 load factor(L3) | 2QF6 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF6 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.32 | hwIntegratedPDUCabinet2QF7PowerLoadFactor | 2QF7 load factor(L1) | 2QF7 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF7 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.33 | hwIntegratedPDUCabinet2QF8PowerLoadFactor | 2QF8 load factor(L2) | 2QF8 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF8 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.34 | hwIntegratedPDUCabinet2QF9PowerLoadFactor | 2QF9 load factor(L3) | 2QF9 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF9 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.35 | hwIntegratedPDUCabinet2QF10PowerLoadFactor | 2QF10 load factor(L1) | 2QF10 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF10 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.36 | hwIntegratedPDUCabinet2QF11PowerLoadFactor | 2QF11 load factor(L2) | 2QF11 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF11 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.37 | hwIntegratedPDUCabinet2QF12PowerLoadFactor | 2QF12 load factor(L3) | 2QF12 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF12 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.38 | hwIntegratedPDUCabinet2QF13PowerLoadFactor | 2QF13 load factor(L1) | 2QF13 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF13 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.39 | hwIntegratedPDUCabinet2QF14PowerLoadFactor | 2QF14 load factor(L2) | 2QF14 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF14 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.40 | hwIntegratedPDUCabinet2QF15PowerLoadFactor | 2QF15 load factor(L3) | 2QF15 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF15 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.41 | hwIntegratedPDUCabinet2QF16PowerLoadFactor | 2QF16 load factor(L1) | 2QF16 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF16 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.42 | hwIntegratedPDUCabinet2QF17PowerLoadFactor | 2QF17 load factor(L2) | 2QF17 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF17 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.43 | hwIntegratedPDUCabinet2QF18PowerLoadFactor | 2QF18 load factor(L3) | 2QF18 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF18 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.44 | hwIntegratedPDUCabinet2QF19PowerLoadFactor | 2QF19 load factor(L1) | 2QF19 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF19 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.45 | hwIntegratedPDUCabinet2QF20PowerLoadFactor | 2QF20 load factor(L2) | 2QF20 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF20 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.46 | hwIntegratedPDUCabinet2QF21PowerLoadFactor | 2QF21 load factor(L3) | 2QF21 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF21 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.47 | hwIntegratedPDUCabinet2QF22PowerLoadFactor | 2QF22 load factor(L1) | 2QF22 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF22 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.48 | hwIntegratedPDUCabinet2QF23PowerLoadFactor | 2QF23 load factor(L2) | 2QF23 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF23 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.49 | hwIntegratedPDUCabinet2QF24PowerLoadFactor | 2QF24 load factor(L3) | 2QF24 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet2QF24 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.50 | hwIntegratedPDUCabinet2QF1SwitchStatus | 2QF1 switch status(L1) | 2QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF1 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.51 | hwIntegratedPDUCabinet2QF2SwitchStatus | 2QF2 switch status(L2) | 2QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF2 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.52 | hwIntegratedPDUCabinet2QF3SwitchStatus | 2QF3 switch status(L3) | 2QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF3 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.53 | hwIntegratedPDUCabinet2QF4SwitchStatus | 2QF4 switch status(L1) | 2QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF4 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.54 | hwIntegratedPDUCabinet2QF5SwitchStatus | 2QF5 switch status(L2) | 2QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF5 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.55 | hwIntegratedPDUCabinet2QF6SwitchStatus | 2QF6 switch status(L3) | 2QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF6 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.56 | hwIntegratedPDUCabinet2QF7SwitchStatus | 2QF7 switch status(L1) | 2QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF7 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.57 | hwIntegratedPDUCabinet2QF8SwitchStatus | 2QF8 switch status(L2) | 2QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF8 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.58 | hwIntegratedPDUCabinet2QF9SwitchStatus | 2QF9 switch status(L3) | 2QF9 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF9 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.59 | hwIntegratedPDUCabinet2QF10SwitchStatus | 2QF10 switch status(L1) | 2QF10 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF10 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.60 | hwIntegratedPDUCabinet2QF11SwitchStatus | 2QF11 switch status(L2) | 2QF11 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF11 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.61 | hwIntegratedPDUCabinet2QF12SwitchStatus | 2QF12 switch status(L3) | 2QF12 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF12 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.62 | hwIntegratedPDUCabinet2QF13SwitchStatus | 2QF13 switch status(L1) | 2QF13 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF13 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.63 | hwIntegratedPDUCabinet2QF14SwitchStatus | 2QF14 switch status(L2) | 2QF14 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF14 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.64 | hwIntegratedPDUCabinet2QF15SwitchStatus | 2QF15 switch status(L3) | 2QF15 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF15 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.65 | hwIntegratedPDUCabinet2QF16SwitchStatus | 2QF16 switch status(L1) | 2QF16 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF16 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.66 | hwIntegratedPDUCabinet2QF17SwitchStatus | 2QF17 switch status(L2) | 2QF17 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF17 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.67 | hwIntegratedPDUCabinet2QF18SwitchStatus | 2QF18 switch status(L3) | 2QF18 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF18 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.68 | hwIntegratedPDUCabinet2QF19SwitchStatus | 2QF19 switch status(L1) | 2QF19 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF19 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.69 | hwIntegratedPDUCabinet2QF20SwitchStatus | 2QF20 switch status(L2) | 2QF20 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF20 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.70 | hwIntegratedPDUCabinet2QF21SwitchStatus | 2QF21 switch status(L3) | 2QF21 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF21 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.71 | hwIntegratedPDUCabinet2QF22SwitchStatus | 2QF22 switch status(L1) | 2QF22 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF22 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.72 | hwIntegratedPDUCabinet2QF23SwitchStatus | 2QF23 switch status(L2) | 2QF23 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF23 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.73 | hwIntegratedPDUCabinet2QF24SwitchStatus | 2QF24 switch status(L3) | 2QF24 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet2QF24 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.10.1.200 | hwIntegratedPDUCabinetRunning10RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11 | hwIntegratedPDUCabinetRunning11Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.1 | hwIntegratedPDUCabinetRunning11Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.2 | hwIntegratedPDUCabinet3QF1outputCurrent | 3QF1 current(L1) | 3QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF1L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.3 | hwIntegratedPDUCabinet3QF2outputCurrent | 3QF1 current(L2) | 3QF1 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF1L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.4 | hwIntegratedPDUCabinet3QF3outputCurrent | 3QF1 current(L3) | 3QF1 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF1L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.5 | hwIntegratedPDUCabinet3QF4outputCurrent | 3QF2 current(L1) | 3QF2 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF2L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.6 | hwIntegratedPDUCabinet3QF5outputCurrent | 3QF2 current(L2) | 3QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF2L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.7 | hwIntegratedPDUCabinet3QF6outputCurrent | 3QF2 current(L3) | 3QF2 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF2L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.8 | hwIntegratedPDUCabinet3QF7outputCurrent | 3QF3 current(L1) | 3QF3 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF3L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.9 | hwIntegratedPDUCabinet3QF8outputCurrent | 3QF3 current(L2) | 3QF3 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF3L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.10 | hwIntegratedPDUCabinet3QF9outputCurrent | 3QF3 current(L3) | 3QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF3L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.11 | hwIntegratedPDUCabinet3QF10outputCurrent | 3QF4 current(L1) | 3QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF4L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.12 | hwIntegratedPDUCabinet3QF11outputCurrent | 3QF4 current(L2) | 3QF4 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF4L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.13 | hwIntegratedPDUCabinet3QF12outputCurrent | 3QF4 current(L3) | 3QF4 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF4L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.14 | hwIntegratedPDUCabinet3QF13outputCurrent | 3QF5 current(L1) | 3QF5 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF5L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.15 | hwIntegratedPDUCabinet3QF14outputCurrent | 3QF5 current(L2) | 3QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF5L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.16 | hwIntegratedPDUCabinet3QF15outputCurrent | 3QF5 current(L3) | 3QF5 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF5L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.17 | hwIntegratedPDUCabinet3QF16outputCurrent | 3QF6 current(L1) | 3QF6 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF6L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.18 | hwIntegratedPDUCabinet3QF17outputCurrent | 3QF6 current(L2) | 3QF6 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF6L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.19 | hwIntegratedPDUCabinet3QF18outputCurrent | 3QF6 current(L3) | 3QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF6L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.20 | hwIntegratedPDUCabinet3QF19outputCurrent | 3QF7 current(L1) | 3QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF7L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.21 | hwIntegratedPDUCabinet3QF20outputCurrent | 3QF7 current(L2) | 3QF7 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF7L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.22 | hwIntegratedPDUCabinet3QF21outputCurrent | 3QF7 current(L3) | 3QF7 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF7L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.23 | hwIntegratedPDUCabinet3QF22outputCurrent | 3QF8 current(L1) | 3QF8 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF8L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.24 | hwIntegratedPDUCabinet3QF23outputCurrent | 3QF8 current(L2) | 3QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF8L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.25 | hwIntegratedPDUCabinet3QF24outputCurrent | 3QF8 current(L3) | 3QF8 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF8L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.26 | hwIntegratedPDUCabinet3QF25outputCurrent | 3QF9 current(L1) | 3QF9 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF9L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.27 | hwIntegratedPDUCabinet3QF26outputCurrent | 3QF9 current(L2) | 3QF9 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF9L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.28 | hwIntegratedPDUCabinet3QF27outputCurrent | 3QF9 current(L3) | 3QF9 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF9L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.29 | hwIntegratedPDUCabinet3QF28outputCurrent | 3QF10 current(L1) | 3QF10 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF10L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.30 | hwIntegratedPDUCabinet3QF29outputCurrent | 3QF10 current(L2) | 3QF10 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF10L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.31 | hwIntegratedPDUCabinet3QF30outputCurrent | 3QF10 current(L3) | 3QF10 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF10L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.32 | hwIntegratedPDUCabinet3QF31outputCurrent | 3QF11 current(L1) | 3QF11 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF11L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.33 | hwIntegratedPDUCabinet3QF32outputCurrent | 3QF11 current(L2) | 3QF11 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF11L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.34 | hwIntegratedPDUCabinet3QF33outputCurrent | 3QF11 current(L3) | 3QF11 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF11L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.35 | hwIntegratedPDUCabinet3QF34outputCurrent | 3QF12 current(L1) | 3QF12 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF12L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.36 | hwIntegratedPDUCabinet3QF35outputCurrent | 3QF12 current(L2) | 3QF12 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF12L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.37 | hwIntegratedPDUCabinet3QF36outputCurrent | 3QF12 current(L3) | 3QF12 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF12L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.38 | hwIntegratedPDUCabinet3QF37outputCurrent | 3QF13 current(L1) | 3QF13 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF13L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.39 | hwIntegratedPDUCabinet3QF38outputCurrent | 3QF13 current(L2) | 3QF13 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF13L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.40 | hwIntegratedPDUCabinet3QF39outputCurrent | 3QF13 current(L3) | 3QF13 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF13L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.41 | hwIntegratedPDUCabinet3QF40outputCurrent | 3QF14 current(L1) | 3QF14 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF14L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.42 | hwIntegratedPDUCabinet3QF41outputCurrent | 3QF14 current(L2) | 3QF14 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF14L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.43 | hwIntegratedPDUCabinet3QF42outputCurrent | 3QF14 current(L3) | 3QF14 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF14L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.44 | hwIntegratedPDUCabinet3QF43outputCurrent | 3QF15 current(L1) | 3QF15 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF15L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.45 | hwIntegratedPDUCabinet3QF44outputCurrent | 3QF15 current(L2) | 3QF15 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF15L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.46 | hwIntegratedPDUCabinet3QF45outputCurrent | 3QF15 current(L3) | 3QF15 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF15L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.47 | hwIntegratedPDUCabinet3QF46outputCurrent | 3QF16 current(L1) | 3QF16 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF16L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.48 | hwIntegratedPDUCabinet3QF47outputCurrent | 3QF16 current(L2) | 3QF16 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF16L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.49 | hwIntegratedPDUCabinet3QF48outputCurrent | 3QF16 current(L3) | 3QF16 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet3QF16L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.50 | hwIntegratedPDUCabinet3QF1LoadFactor | 3QF1 load factor(L1) | 3QF1 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF1L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.51 | hwIntegratedPDUCabinet3QF2LoadFactor | 3QF1 load factor(L2) | 3QF1 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF1L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.52 | hwIntegratedPDUCabinet3QF3LoadFactor | 3QF1 load factor(L3) | 3QF1 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF1L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.53 | hwIntegratedPDUCabinet3QF4LoadFactor | 3QF2 load factor(L1) | 3QF2 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF2L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.54 | hwIntegratedPDUCabinet3QF5LoadFactor | 3QF2 load factor(L2) | 3QF2 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF2L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.55 | hwIntegratedPDUCabinet3QF6LoadFactor | 3QF2 load factor(L3) | 3QF2 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF2L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.56 | hwIntegratedPDUCabinet3QF7LoadFactor | 3QF3 load factor(L1) | 3QF3 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF3L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.57 | hwIntegratedPDUCabinet3QF8LoadFactor | 3QF3 load factor(L2) | 3QF3 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF3L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.58 | hwIntegratedPDUCabinet3QF9LoadFactor | 3QF3 load factor(L3) | 3QF3 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF3L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.59 | hwIntegratedPDUCabinet3QF10LoadFactor | 3QF4 load factor(L1) | 3QF4 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF4L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.60 | hwIntegratedPDUCabinet3QF11LoadFactor | 3QF4 load factor(L2) | 3QF4 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF4L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.61 | hwIntegratedPDUCabinet3QF12LoadFactor | 3QF4 load factor(L3) | 3QF4 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF4L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.62 | hwIntegratedPDUCabinet3QF13LoadFactor | 3QF5 load factor(L1) | 3QF5 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF5L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.63 | hwIntegratedPDUCabinet3QF14LoadFactor | 3QF5 load factor(L2) | 3QF5 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF5L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.64 | hwIntegratedPDUCabinet3QF15LoadFactor | 3QF5 load factor(L3) | 3QF5 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF5L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.65 | hwIntegratedPDUCabinet3QF16LoadFactor | 3QF6 load factor(L1) | 3QF6 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF6L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.66 | hwIntegratedPDUCabinet3QF17LoadFactor | 3QF6 load factor(L2) | 3QF6 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF6L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.67 | hwIntegratedPDUCabinet3QF18LoadFactor | 3QF6 load factor(L3) | 3QF6 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF6L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.68 | hwIntegratedPDUCabinet3QF19LoadFactor | 3QF7 load factor(L1) | 3QF7 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF7L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.69 | hwIntegratedPDUCabinet3QF20LoadFactor | 3QF7 load factor(L2) | 3QF7 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF7L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.70 | hwIntegratedPDUCabinet3QF21LoadFactor | 3QF7 load factor(L3) | 3QF7 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF7L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.71 | hwIntegratedPDUCabinet3QF22LoadFactor | 3QF8 load factor(L1) | 3QF8 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF8L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.72 | hwIntegratedPDUCabinet3QF23LoadFactor | 3QF8 load factor(L2) | 3QF8 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF8L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.73 | hwIntegratedPDUCabinet3QF24LoadFactor | 3QF8 load factor(L3) | 3QF8 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF8L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.74 | hwIntegratedPDUCabinet3QF25LoadFactor | 3QF9 load factor(L1) | 3QF9 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF9L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.75 | hwIntegratedPDUCabinet3QF26LoadFactor | 3QF9 load factor(L2) | 3QF9 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF9L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.76 | hwIntegratedPDUCabinet3QF27LoadFactor | 3QF9 load factor(L3) | 3QF9 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF9L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.77 | hwIntegratedPDUCabinet3QF28LoadFactor | 3QF10 load factor(L1) | 3QF10 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF10L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.78 | hwIntegratedPDUCabinet3QF29LoadFactor | 3QF10 load factor(L2) | 3QF10 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF10L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.79 | hwIntegratedPDUCabinet3QF30LoadFactor | 3QF10 load factor(L3) | 3QF10 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF10L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.80 | hwIntegratedPDUCabinet3QF31LoadFactor | 3QF11 load factor(L1) | 3QF11 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF11L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.81 | hwIntegratedPDUCabinet3QF32LoadFactor | 3QF11 load factor(L2) | 3QF11 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF11L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.82 | hwIntegratedPDUCabinet3QF33LoadFactor | 3QF11 load factor(L3) | 3QF11 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF11L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.83 | hwIntegratedPDUCabinet3QF34LoadFactor | 3QF12 load factor(L1) | 3QF12 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF12L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.84 | hwIntegratedPDUCabinet3QF35LoadFactor | 3QF12 load factor(L2) | 3QF12 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF12L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.85 | hwIntegratedPDUCabinet3QF36LoadFactor | 3QF12 load factor(L3) | 3QF12 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF12L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.86 | hwIntegratedPDUCabinet3QF37LoadFactor | 3QF13 load factor(L1) | 3QF13 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF13L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.87 | hwIntegratedPDUCabinet3QF38LoadFactor | 3QF13 load factor(L2) | 3QF13 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF13L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.88 | hwIntegratedPDUCabinet3QF39LoadFactor | 3QF13 load factor(L3) | 3QF13 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF13L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.89 | hwIntegratedPDUCabinet3QF40LoadFactor | 3QF14 load factor(L1) | 3QF14 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF14L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.90 | hwIntegratedPDUCabinet3QF41LoadFactor | 3QF14 load factor(L2) | 3QF14 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF14L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.91 | hwIntegratedPDUCabinet3QF42LoadFactor | 3QF14 load factor(L3) | 3QF14 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF14L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.92 | hwIntegratedPDUCabinet3QF43LoadFactor | 3QF15 load factor(L1) | 3QF15 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF15L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.93 | hwIntegratedPDUCabinet3QF44LoadFactor | 3QF15 load factor(L2) | 3QF15 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF15L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.94 | hwIntegratedPDUCabinet3QF45LoadFactor | 3QF15 load factor(L3) | 3QF15 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF15L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.95 | hwIntegratedPDUCabinet3QF46LoadFactor | 3QF16 load factor(L1) | 3QF16 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF16L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.96 | hwIntegratedPDUCabinet3QF47LoadFactor | 3QF16 load factor(L2) | 3QF16 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF16L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.97 | hwIntegratedPDUCabinet3QF48LoadFactor | 3QF16 load factor(L3) | 3QF16 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet3QF16L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.98 | hwIntegratedPDUCabinet3QF1SwitchStatus | 3QF1 switch status(L1) | 3QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF1L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.99 | hwIntegratedPDUCabinet3QF2SwitchStatus | 3QF1 switch status(L2) | 3QF1 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF1L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.100 | hwIntegratedPDUCabinet3QF3SwitchStatus | 3QF1 switch status(L3) | 3QF1 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF1L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.101 | hwIntegratedPDUCabinet3QF4SwitchStatus | 3QF2 switch status(L1) | 3QF2 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF2L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.102 | hwIntegratedPDUCabinet3QF5SwitchStatus | 3QF2 switch status(L2) | 3QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF2L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.103 | hwIntegratedPDUCabinet3QF6SwitchStatus | 3QF2 switch status(L3) | 3QF2 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF2L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.104 | hwIntegratedPDUCabinet3QF7SwitchStatus | 3QF3 switch status(L1) | 3QF3 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF3L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.105 | hwIntegratedPDUCabinet3QF8SwitchStatus | 3QF3 switch status(L2) | 3QF3 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF3L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.106 | hwIntegratedPDUCabinet3QF9SwitchStatus | 3QF3 switch status(L3) | 3QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF3L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.107 | hwIntegratedPDUCabinet3QF10SwitchStatus | 3QF4 switch status(L1) | 3QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF4L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.108 | hwIntegratedPDUCabinet3QF11SwitchStatus | 3QF4 switch status(L2) | 3QF4 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF4L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.109 | hwIntegratedPDUCabinet3QF12SwitchStatus | 3QF4 switch status(L3) | 3QF4 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF4L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.110 | hwIntegratedPDUCabinet3QF13SwitchStatus | 3QF5 switch status(L1) | 3QF5 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF5L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.111 | hwIntegratedPDUCabinet3QF14SwitchStatus | 3QF5 switch status(L2) | 3QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF5L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.112 | hwIntegratedPDUCabinet3QF15SwitchStatus | 3QF5 switch status(L3) | 3QF5 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF5L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.113 | hwIntegratedPDUCabinet3QF16SwitchStatus | 3QF6 switch status(L1) | 3QF6 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF6L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.114 | hwIntegratedPDUCabinet3QF17SwitchStatus | 3QF6 switch status(L2) | 3QF6 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF6L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.115 | hwIntegratedPDUCabinet3QF18SwitchStatus | 3QF6 switch status(L3) | 3QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF6L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.116 | hwIntegratedPDUCabinet3QF19SwitchStatus | 3QF7 switch status(L1) | 3QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF7L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.117 | hwIntegratedPDUCabinet3QF20SwitchStatus | 3QF7 switch status(L2) | 3QF7 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF7L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.118 | hwIntegratedPDUCabinet3QF21SwitchStatus | 3QF7 switch status(L3) | 3QF7 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF7L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.119 | hwIntegratedPDUCabinet3QF22SwitchStatus | 3QF8 switch status(L1) | 3QF8 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF8L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.120 | hwIntegratedPDUCabinet3QF23SwitchStatus | 3QF8 switch status(L2) | 3QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF8L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.121 | hwIntegratedPDUCabinet3QF24SwitchStatus | 3QF8 switch status(L3) | 3QF8 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF8L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.122 | hwIntegratedPDUCabinet3QF25SwitchStatus | 3QF9 switch status(L1) | 3QF9 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF9L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.123 | hwIntegratedPDUCabinet3QF26SwitchStatus | 3QF9 switch status(L2) | 3QF9 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF9L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.124 | hwIntegratedPDUCabinet3QF27SwitchStatus | 3QF9 switch status(L3) | 3QF9 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF9L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.125 | hwIntegratedPDUCabinet3QF28SwitchStatus | 3QF10 switch status(L1) | 3QF10 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF10L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.126 | hwIntegratedPDUCabinet3QF29SwitchStatus | 3QF10 switch status(L2) | 3QF10 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF10L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.127 | hwIntegratedPDUCabinet3QF30SwitchStatus | 3QF10 switch status(L3) | 3QF10 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF10L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.128 | hwIntegratedPDUCabinet3QF31SwitchStatus | 3QF11 switch status(L1) | 3QF11 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF11L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.129 | hwIntegratedPDUCabinet3QF32SwitchStatus | 3QF11 switch status(L2) | 3QF11 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF11L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.130 | hwIntegratedPDUCabinet3QF33SwitchStatus | 3QF11 switch status(L3) | 3QF11 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF11L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.131 | hwIntegratedPDUCabinet3QF34SwitchStatus | 3QF12 switch status(L1) | 3QF12 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF12L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.132 | hwIntegratedPDUCabinet3QF35SwitchStatus | 3QF12 switch status(L2) | 3QF12 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF12L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.133 | hwIntegratedPDUCabinet3QF36SwitchStatus | 3QF12 switch status(L3) | 3QF12 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF12L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.134 | hwIntegratedPDUCabinet3QF37SwitchStatus | 3QF13 switch status(L1) | 3QF13 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF13L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.135 | hwIntegratedPDUCabinet3QF38SwitchStatus | 3QF13 switch status(L2) | 3QF13 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF13L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.136 | hwIntegratedPDUCabinet3QF39SwitchStatus | 3QF13 switch status(L3) | 3QF13 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF13L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.137 | hwIntegratedPDUCabinet3QF40SwitchStatus | 3QF14 switch status(L1) | 3QF14 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF14L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.138 | hwIntegratedPDUCabinet3QF41SwitchStatus | 3QF14 switch status(L2) | 3QF14 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF14L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.139 | hwIntegratedPDUCabinet3QF42SwitchStatus | 3QF14 switch status(L3) | 3QF14 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF14L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.140 | hwIntegratedPDUCabinet3QF43SwitchStatus | 3QF15 switch status(L1) | 3QF15 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF15L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.141 | hwIntegratedPDUCabinet3QF44SwitchStatus | 3QF15 switch status(L2) | 3QF15 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF15L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.142 | hwIntegratedPDUCabinet3QF45SwitchStatus | 3QF15 switch status(L3) | 3QF15 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF15L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.143 | hwIntegratedPDUCabinet3QF46SwitchStatus | 3QF16 switch status(L1) | 3QF16 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF16L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.144 | hwIntegratedPDUCabinet3QF47SwitchStatus | 3QF16 switch status(L2) | 3QF16 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF16L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.145 | hwIntegratedPDUCabinet3QF48SwitchStatus | 3QF16 switch status(L3) | 3QF16 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet3QF16L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.11.1.200 | hwIntegratedPDUCabinetRunning11RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12 | hwIntegratedPDUCabinetRunning12Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.1 | hwIntegratedPDUCabinetRunning12Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.2 | hwIntegratedPDUCabinet4QF1outputCurrent | 4QF1 current(L1) | 4QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF1L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.3 | hwIntegratedPDUCabinet4QF2outputCurrent | 4QF1 current(L2) | 4QF1 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF1L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.4 | hwIntegratedPDUCabinet4QF3outputCurrent | 4QF1 current(L3) | 4QF1 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF1L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.5 | hwIntegratedPDUCabinet4QF4outputCurrent | 4QF2 current(L1) | 4QF2 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF2L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.6 | hwIntegratedPDUCabinet4QF5outputCurrent | 4QF2 current(L2) | 4QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF2L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.7 | hwIntegratedPDUCabinet4QF6outputCurrent | 4QF2 current(L3) | 4QF2 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF2L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.8 | hwIntegratedPDUCabinet4QF7outputCurrent | 4QF3 current(L1) | 4QF3 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF3L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.9 | hwIntegratedPDUCabinet4QF8outputCurrent | 4QF3 current(L2) | 4QF3 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF3L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.10 | hwIntegratedPDUCabinet4QF9outputCurrent | 4QF3 current(L3) | 4QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF3L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.11 | hwIntegratedPDUCabinet4QF10outputCurrent | 4QF4 current(L1) | 4QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF4L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.12 | hwIntegratedPDUCabinet4QF11outputCurrent | 4QF4 current(L2) | 4QF4 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF4L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.13 | hwIntegratedPDUCabinet4QF12outputCurrent | 4QF4 current(L3) | 4QF4 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF4L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.14 | hwIntegratedPDUCabinet4QF13outputCurrent | 4QF5 current(L1) | 4QF5 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF5L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.15 | hwIntegratedPDUCabinet4QF14outputCurrent | 4QF5 current(L2) | 4QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF5L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.16 | hwIntegratedPDUCabinet4QF15outputCurrent | 4QF5 current(L3) | 4QF5 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF5L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.17 | hwIntegratedPDUCabinet4QF16outputCurrent | 4QF6 current(L1) | 4QF6 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF6L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.18 | hwIntegratedPDUCabinet4QF17outputCurrent | 4QF6 current(L2) | 4QF6 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF6L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.19 | hwIntegratedPDUCabinet4QF18outputCurrent | 4QF6 current(L3) | 4QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF6L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.20 | hwIntegratedPDUCabinet4QF19outputCurrent | 4QF7 current(L1) | 4QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF7L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.21 | hwIntegratedPDUCabinet4QF20outputCurrent | 4QF7 current(L2) | 4QF7 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF7L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.22 | hwIntegratedPDUCabinet4QF21outputCurrent | 4QF7 current(L3) | 4QF7 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF7L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.23 | hwIntegratedPDUCabinet4QF22outputCurrent | 4QF8 current(L1) | 4QF8 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF8L1outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.24 | hwIntegratedPDUCabinet4QF23outputCurrent | 4QF8 current(L2) | 4QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF8L2outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.25 | hwIntegratedPDUCabinet4QF24outputCurrent | 4QF8 current(L3) | 4QF8 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinet4QF8L3outputCurrent Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.50 | hwIntegratedPDUCabinet4QF1LoadFactor | 4QF1 load factor(L1) | 4QF1 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF1L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.51 | hwIntegratedPDUCabinet4QF2LoadFactor | 4QF1 load factor(L2) | 4QF1 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF1L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.52 | hwIntegratedPDUCabinet4QF3LoadFactor | 4QF1 load factor(L3) | 4QF1 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF1L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.53 | hwIntegratedPDUCabinet4QF4LoadFactor | 4QF2 load factor(L1) | 4QF2 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF2L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.54 | hwIntegratedPDUCabinet4QF5LoadFactor | 4QF2 load factor(L2) | 4QF2 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF2L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.55 | hwIntegratedPDUCabinet4QF6LoadFactor | 4QF2 load factor(L3) | 4QF2 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF2L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.56 | hwIntegratedPDUCabinet4QF7LoadFactor | 4QF3 load factor(L1) | 4QF3 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF3L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.57 | hwIntegratedPDUCabinet4QF8LoadFactor | 4QF3 load factor(L2) | 4QF3 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF3L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.58 | hwIntegratedPDUCabinet4QF9LoadFactor | 4QF3 load factor(L3) | 4QF3 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF3L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.59 | hwIntegratedPDUCabinet4QF10LoadFactor | 4QF4 load factor(L1) | 4QF4 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF4L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.60 | hwIntegratedPDUCabinet4QF11LoadFactor | 4QF4 load factor(L2) | 4QF4 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF4L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.61 | hwIntegratedPDUCabinet4QF12LoadFactor | 4QF4 load factor(L3) | 4QF4 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF4L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.62 | hwIntegratedPDUCabinet4QF13LoadFactor | 4QF5 load factor(L1) | 4QF5 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF5L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.63 | hwIntegratedPDUCabinet4QF14LoadFactor | 4QF5 load factor(L2) | 4QF5 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF5L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.64 | hwIntegratedPDUCabinet4QF15LoadFactor | 4QF5 load factor(L3) | 4QF5 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF5L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.65 | hwIntegratedPDUCabinet4QF16LoadFactor | 4QF6 load factor(L1) | 4QF6 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF6L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.66 | hwIntegratedPDUCabinet4QF17LoadFactor | 4QF6 load factor(L2) | 4QF6 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF6L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.67 | hwIntegratedPDUCabinet4QF18LoadFactor | 4QF6 load factor(L3) | 4QF6 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF6L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.68 | hwIntegratedPDUCabinet4QF19LoadFactor | 4QF7 load factor(L1) | 4QF7 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF7L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.69 | hwIntegratedPDUCabinet4QF20LoadFactor | 4QF7 load factor(L2) | 4QF7 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF7L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.70 | hwIntegratedPDUCabinet4QF21LoadFactor | 4QF7 load factor(L3) | 4QF7 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF7L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.71 | hwIntegratedPDUCabinet4QF22LoadFactor | 4QF8 load factor(L1) | 4QF8 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF8L1LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.72 | hwIntegratedPDUCabinet4QF23LoadFactor | 4QF8 load factor(L2) | 4QF8 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF8L2LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.73 | hwIntegratedPDUCabinet4QF24LoadFactor | 4QF8 load factor(L3) | 4QF8 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinet4QF8L3LoadFactor SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.98 | hwIntegratedPDUCabinet4QF1SwitchStatus | 4QF1 switch status(L1) | 4QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF1L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.99 | hwIntegratedPDUCabinet4QF2SwitchStatus | 4QF1 switch status(L2) | 4QF1 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF1L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.100 | hwIntegratedPDUCabinet4QF3SwitchStatus | 4QF1 switch status(L3) | 4QF1 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF1L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.101 | hwIntegratedPDUCabinet4QF4SwitchStatus | 4QF2 switch status(L1) | 4QF2 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF2L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.102 | hwIntegratedPDUCabinet4QF5SwitchStatus | 4QF2 switch status(L2) | 4QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF2L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.103 | hwIntegratedPDUCabinet4QF6SwitchStatus | 4QF2 switch status(L3) | 4QF2 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF2L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.104 | hwIntegratedPDUCabinet4QF7SwitchStatus | 4QF3 switch status(L1) | 4QF3 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF3L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.105 | hwIntegratedPDUCabinet4QF8SwitchStatus | 4QF3 switch status(L2) | 4QF3 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF3L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.106 | hwIntegratedPDUCabinet4QF9SwitchStatus | 4QF3 switch status(L3) | 4QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF3L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.107 | hwIntegratedPDUCabinet4QF10SwitchStatus | 4QF4 switch status(L1) | 4QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF4L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.108 | hwIntegratedPDUCabinet4QF11SwitchStatus | 4QF4 switch status(L2) | 4QF4 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF4L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.109 | hwIntegratedPDUCabinet4QF12SwitchStatus | 4QF4 switch status(L3) | 4QF4 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF4L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.110 | hwIntegratedPDUCabinet4QF13SwitchStatus | 4QF5 switch status(L1) | 4QF5 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF5L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.111 | hwIntegratedPDUCabinet4QF14SwitchStatus | 4QF5 switch status(L2) | 4QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF5L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.112 | hwIntegratedPDUCabinet4QF15SwitchStatus | 4QF5 switch status(L3) | 4QF5 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF5L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.113 | hwIntegratedPDUCabinet4QF16SwitchStatus | 4QF6 switch status(L1) | 4QF6 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF6L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.114 | hwIntegratedPDUCabinet4QF17SwitchStatus | 4QF6 switch status(L2) | 4QF6 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF6L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.115 | hwIntegratedPDUCabinet4QF18SwitchStatus | 4QF6 switch status(L3) | 4QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF6L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.116 | hwIntegratedPDUCabinet4QF19SwitchStatus | 4QF7 switch status(L1) | 4QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF7L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.117 | hwIntegratedPDUCabinet4QF20SwitchStatus | 4QF7 switch status(L2) | 4QF7 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF7L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.118 | hwIntegratedPDUCabinet4QF21SwitchStatus | 4QF7 switch status(L3) | 4QF7 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF7L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.119 | hwIntegratedPDUCabinet4QF22SwitchStatus | 4QF8 switch status(L1) | 4QF8 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF8L1SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.120 | hwIntegratedPDUCabinet4QF23SwitchStatus | 4QF8 switch status(L2) | 4QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF8L2SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.121 | hwIntegratedPDUCabinet4QF24SwitchStatus | 4QF8 switch status(L3) | 4QF8 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinet4QF8L3SwitchStatus Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.12.1.200 | hwIntegratedPDUCabinetRunning12RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13 | hwIntegratedPDUCabinetRunning13Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.1 | hwIntegratedPDUCabinetRunning13Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.2 | hwIntegratedPDUCabinetQF25outputCurrent | 1QF25 current(L1) | 1QF25 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF25 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.3 | hwIntegratedPDUCabinetQF26outputCurrent | 1QF26 current(L2) | 1QF26 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF26 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.4 | hwIntegratedPDUCabinetQF27outputCurrent | 1QF27 current(L3) | 1QF27 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF27 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.5 | hwIntegratedPDUCabinetQF28outputCurrent | 1QF28 current(L1) | 1QF28 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF28 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.6 | hwIntegratedPDUCabinetQF29outputCurrent | 1QF29 current(L2) | 1QF29 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF29 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.7 | hwIntegratedPDUCabinetQF30outputCurrent | 1QF30 current(L3) | 1QF30 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF30 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.8 | hwIntegratedPDUCabinetQF31outputCurrent | 1QF31 current(L1) | 1QF31 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF31 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.9 | hwIntegratedPDUCabinetQF32outputCurrent | 1QF32 current(L2) | 1QF32 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF32 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.10 | hwIntegratedPDUCabinetQF33outputCurrent | 1QF33 current(L3) | 1QF33 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF33 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.11 | hwIntegratedPDUCabinetQF34outputCurrent | 1QF34 current(L1) | 1QF34 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF34 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.12 | hwIntegratedPDUCabinetQF35outputCurrent | 1QF35 current(L2) | 1QF35 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF35 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.13 | hwIntegratedPDUCabinetQF36outputCurrent | 1QF36 current(L3) | 1QF36 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF36 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.14 | hwIntegratedPDUCabinetQF37outputCurrent | 1QF37 current(L1) | 1QF37 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF37 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.15 | hwIntegratedPDUCabinetQF38outputCurrent | 1QF38 current(L2) | 1QF38 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF38 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.16 | hwIntegratedPDUCabinetQF39outputCurrent | 1QF39 current(L3) | 1QF39 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF39 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.17 | hwIntegratedPDUCabinetQF40outputCurrent | 1QF40 current(L1) | 1QF40 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF40 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.18 | hwIntegratedPDUCabinetQF41outputCurrent | 1QF41 current(L2) | 1QF41 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF41 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.19 | hwIntegratedPDUCabinetQF42outputCurrent | 1QF42 current(L3) | 1QF42 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF42 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.20 | hwIntegratedPDUCabinetQF43outputCurrent | 1QF43 current(L1) | 1QF43 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF43 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.21 | hwIntegratedPDUCabinetQF44outputCurrent | 1QF44 current(L2) | 1QF44 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF44 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.22 | hwIntegratedPDUCabinetQF45outputCurrent | 1QF45 current(L3) | 1QF45 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF45 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.23 | hwIntegratedPDUCabinetQF46outputCurrent | 1QF46 current(L1) | 1QF46 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF46 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.24 | hwIntegratedPDUCabinetQF47outputCurrent | 1QF47 current(L2) | 1QF47 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF47 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.25 | hwIntegratedPDUCabinetQF48outputCurrent | 1QF48 current(L3) | 1QF48 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | hwIntegratedPDUCabinetQF48 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.26 | hwIntegratedPDUCabinetQF25PowerLoadFactor | 1QF25 load factor(L1) | 1QF25 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF25 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.27 | hwIntegratedPDUCabinetQF26PowerLoadFactor | 1QF26 load factor(L2) | 1QF26 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF26 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.28 | hwIntegratedPDUCabinetQF27PowerLoadFactor | 1QF27 load factor(L3) | 1QF27 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF27 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.29 | hwIntegratedPDUCabinetQF28PowerLoadFactor | 1QF28 load factor(L1) | 1QF28 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF28 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.30 | hwIntegratedPDUCabinetQF29PowerLoadFactor | 1QF29 load factor(L2) | 1QF29 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF29 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.31 | hwIntegratedPDUCabinetQF30PowerLoadFactor | 1QF30 load factor(L3) | 1QF30 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF30 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.32 | hwIntegratedPDUCabinetQF31PowerLoadFactor | 1QF31 load factor(L1) | 1QF31 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF31 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.33 | hwIntegratedPDUCabinetQF32PowerLoadFactor | 1QF32 load factor(L2) | 1QF32 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF32 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.34 | hwIntegratedPDUCabinetQF33PowerLoadFactor | 1QF33 load factor(L3) | 1QF33 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF33 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.35 | hwIntegratedPDUCabinetQF34PowerLoadFactor | 1QF34 load factor(L1) | 1QF34 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF34 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.36 | hwIntegratedPDUCabinetQF35PowerLoadFactor | 1QF35 load factor(L2) | 1QF35 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF35 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.37 | hwIntegratedPDUCabinetQF36PowerLoadFactor | 1QF36 load factor(L3) | 1QF36 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF36 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.38 | hwIntegratedPDUCabinetQF37PowerLoadFactor | 1QF37 load factor(L1) | 1QF37 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF37 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.39 | hwIntegratedPDUCabinetQF38PowerLoadFactor | 1QF38 load factor(L2) | 1QF38 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF38 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.40 | hwIntegratedPDUCabinetQF39PowerLoadFactor | 1QF39 load factor(L3) | 1QF39 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF39 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.41 | hwIntegratedPDUCabinetQF40PowerLoadFactor | 1QF40 load factor(L1) | 1QF40 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF40 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.42 | hwIntegratedPDUCabinetQF41PowerLoadFactor | 1QF41 load factor(L2) | 1QF41 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF41 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.43 | hwIntegratedPDUCabinetQF42PowerLoadFactor | 1QF42 load factor(L3) | 1QF42 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF42 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.44 | hwIntegratedPDUCabinetQF43PowerLoadFactor | 1QF43 load factor(L1) | 1QF43 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF43 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.45 | hwIntegratedPDUCabinetQF44PowerLoadFactor | 1QF44 load factor(L2) | 1QF44 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF44 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.46 | hwIntegratedPDUCabinetQF45PowerLoadFactor | 1QF45 load factor(L3) | 1QF45 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF45 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.47 | hwIntegratedPDUCabinetQF46PowerLoadFactor | 1QF46 load factor(L1) | 1QF46 负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF46 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.48 | hwIntegratedPDUCabinetQF47PowerLoadFactor | 1QF47 load factor(L2) | 1QF47 负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF47 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.49 | hwIntegratedPDUCabinetQF48PowerLoadFactor | 1QF48 load factor(L3) | 1QF48 负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | hwIntegratedPDUCabinetQF48 power loadfactor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.50 | hwIntegratedPDUCabinetQF25SwitchStatus | 1QF25 switch status(L1) | 1QF25 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF25 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.51 | hwIntegratedPDUCabinetQF26SwitchStatus | 1QF26 switch status(L2) | 1QF26 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF26 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.52 | hwIntegratedPDUCabinetQF27SwitchStatus | 1QF27 switch status(L3) | 1QF27 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF27 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.53 | hwIntegratedPDUCabinetQF28SwitchStatus | 1QF28 switch status(L1) | 1QF28 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF28 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.54 | hwIntegratedPDUCabinetQF29SwitchStatus | 1QF29 switch status(L2) | 1QF29 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF29 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.55 | hwIntegratedPDUCabinetQF30SwitchStatus | 1QF30 switch status(L3) | 1QF30 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF30 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.56 | hwIntegratedPDUCabinetQF31SwitchStatus | 1QF31 switch status(L1) | 1QF31 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF31 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.57 | hwIntegratedPDUCabinetQF32SwitchStatus | 1QF32 switch status(L2) | 1QF32 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF32 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.58 | hwIntegratedPDUCabinetQF33SwitchStatus | 1QF33 switch status(L3) | 1QF33 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF33 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.59 | hwIntegratedPDUCabinetQF34SwitchStatus | 1QF34 switch status(L1) | 1QF34 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF34 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.60 | hwIntegratedPDUCabinetQF35SwitchStatus | 1QF35 switch status(L2) | 1QF35 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF35 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.61 | hwIntegratedPDUCabinetQF36SwitchStatus | 1QF36 switch status(L3) | 1QF36 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF36 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.62 | hwIntegratedPDUCabinetQF37SwitchStatus | 1QF37 switch status(L1) | 1QF37 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF37 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.63 | hwIntegratedPDUCabinetQF38SwitchStatus | 1QF38 switch status(L2) | 1QF38 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF38 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.64 | hwIntegratedPDUCabinetQF39SwitchStatus | 1QF39 switch status(L3) | 1QF39 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF39 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.65 | hwIntegratedPDUCabinetQF40SwitchStatus | 1QF40 switch status(L1) | 1QF40 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF40 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.66 | hwIntegratedPDUCabinetQF41SwitchStatus | 1QF41 switch status(L2) | 1QF41 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF41 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.67 | hwIntegratedPDUCabinetQF42SwitchStatus | 1QF42 switch status(L3) | 1QF42 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF42 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.68 | hwIntegratedPDUCabinetQF43SwitchStatus | 1QF43 switch status(L1) | 1QF43 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF43 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.69 | hwIntegratedPDUCabinetQF44SwitchStatus | 1QF44 switch status(L2) | 1QF44 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF44 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.70 | hwIntegratedPDUCabinetQF45SwitchStatus | 1QF45 switch status(L3) | 1QF45 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF45 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.71 | hwIntegratedPDUCabinetQF46SwitchStatus | 1QF46 switch status(L1) | 1QF46 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF46 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.72 | hwIntegratedPDUCabinetQF47SwitchStatus | 1QF47 switch status(L2) | 1QF47 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF47 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.73 | hwIntegratedPDUCabinetQF48SwitchStatus | 1QF48 switch status(L3) | 1QF48 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | hwIntegratedPDUCabinetQF48 switch status. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.4.13.1.200 | hwIntegratedPDUCabinetRunning13RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15 | hwIntegratedPDUCabinetRunning14Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.1 | hwIntegratedPDUCabinetRunning14Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.2 | hwIntegratedPDUCabinet1MainsPostOut1Temperature | 1 Mains post out 1 temperature | 1主路端子1温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 1 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.3 | hwIntegratedPDUCabinet1MainsPostOut2Temperature | 1 Mains post out 2 temperature | 1主路端子2温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 2 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.4 | hwIntegratedPDUCabinet1MainsPostOut3Temperature | 1 Mains post out 3 temperature | 1主路端子3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 3 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.5 | hwIntegratedPDUCabinet1MainsPostOut4Temperature | 1 Mains post out 4 temperature | 1主路端子4温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 4 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.6 | hwIntegratedPDUCabinet1MainsPostOut5Temperature | 1 Mains post out 5 temperature | 1主路端子5温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 5 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.7 | hwIntegratedPDUCabinet1MainsPostOut6Temperature | 1 Mains post out 6 temperature | 1主路端子6温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 6 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.8 | hwIntegratedPDUCabinet1MainsPostOut7Temperature | 1 Mains post out 7 temperature | 1主路端子7温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 7 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.9 | hwIntegratedPDUCabinet1MainsPostOut8Temperature | 1 Mains post out 8 temperature | 1主路端子8温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 8 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.10 | hwIntegratedPDUCabinet1MainsPostOut9Temperature | 1 Mains post out 9 temperature | 1主路端子9温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 9 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.11 | hwIntegratedPDUCabinet1MainsPostOut10Temperature | 1 Mains post out 10 temperature | 1主路端子10温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 10 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.12 | hwIntegratedPDUCabinet1MainsPostOut11Temperature | 1 Mains post out 11 temperature | 1主路端子11温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 11 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.13 | hwIntegratedPDUCabinet1MainsPostOut12Temperature | 1 Mains post out 12 temperature | 1主路端子12温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 12 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.14 | hwIntegratedPDUCabinet1MainsPostOut13Temperature | 1 Mains post out 13 temperature | 1主路端子13温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 13 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.15 | hwIntegratedPDUCabinet1MainsPostOut14Temperature | 1 Mains post out 14 temperature | 1主路端子14温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 14 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.16 | hwIntegratedPDUCabinet1MainsPostOut15Temperature | 1 Mains post out 15 temperature | 1主路端子15温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 15 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.17 | hwIntegratedPDUCabinet1MainsPostOut16Temperature | 1 Mains post out 16 temperature | 1主路端子16温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 16 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.18 | hwIntegratedPDUCabinet1MainsPostOut17Temperature | 1 Mains post out 17 temperature | 1主路端子17温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 17 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.19 | hwIntegratedPDUCabinet1MainsPostOut18Temperature | 1 Mains post out 18 temperature | 1主路端子18温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 18 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.20 | hwIntegratedPDUCabinet1MainsPostOut19Temperature | 1 Mains post out 19 temperature | 1主路端子19温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 19 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.21 | hwIntegratedPDUCabinet1MainsPostOut20Temperature | 1 Mains post out 20 temperature | 1主路端子20温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 20 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.22 | hwIntegratedPDUCabinet1MainsPostOut21Temperature | 1 Mains post out 21 temperature | 1主路端子21温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 21 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.23 | hwIntegratedPDUCabinet1MainsPostOut22Temperature | 1 Mains post out 22 temperature | 1主路端子22温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 22 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.24 | hwIntegratedPDUCabinet1MainsPostOut23Temperature | 1 Mains post out 23 temperature | 1主路端子23温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 23 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.25 | hwIntegratedPDUCabinet1MainsPostOut24Temperature | 1 Mains post out 24 temperature | 1主路端子24温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1 Mains post out 24 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.26 | hwIntegratedPDUCabinet2MainsPostOut1Temperature | 2 Mains post out 1 temperature | 2主路端子1温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 1 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.27 | hwIntegratedPDUCabinet2MainsPostOut2Temperature | 2 Mains post out 2 temperature | 2主路端子2温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 2 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.28 | hwIntegratedPDUCabinet2MainsPostOut3Temperature | 2 Mains post out 3 temperature | 2主路端子3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 3 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.29 | hwIntegratedPDUCabinet2MainsPostOut4Temperature | 2 Mains post out 4 temperature | 2主路端子4温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 4 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.30 | hwIntegratedPDUCabinet2MainsPostOut5Temperature | 2 Mains post out 5 temperature | 2主路端子5温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 5 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.31 | hwIntegratedPDUCabinet2MainsPostOut6Temperature | 2 Mains post out 6 temperature | 2主路端子6温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 6 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.32 | hwIntegratedPDUCabinet2MainsPostOut7Temperature | 2 Mains post out 7 temperature | 2主路端子7温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 7 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.33 | hwIntegratedPDUCabinet2MainsPostOut8Temperature | 2 Mains post out 8 temperature | 2主路端子8温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 8 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.34 | hwIntegratedPDUCabinet2MainsPostOut9Temperature | 2 Mains post out 9 temperature | 2主路端子9温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 9 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.35 | hwIntegratedPDUCabinet2MainsPostOut10Temperature | 2 Mains post out 10 temperature | 2主路端子10温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 10 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.36 | hwIntegratedPDUCabinet2MainsPostOut11Temperature | 2 Mains post out 11 temperature | 2主路端子11温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 11 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.37 | hwIntegratedPDUCabinet2MainsPostOut12Temperature | 2 Mains post out 12 temperature | 2主路端子12温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2 Mains post out 12 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.38 | hwIntegratedPDUCabinet3MainsPostOut1Temperature | 3 Mains post out 1 temperature | 3主路端子1温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 1 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.39 | hwIntegratedPDUCabinet3MainsPostOut2Temperature | 3 Mains post out 2 temperature | 3主路端子2温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 2 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.40 | hwIntegratedPDUCabinet3MainsPostOut3Temperature | 3 Mains post out 3 temperature | 3主路端子3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 3 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.41 | hwIntegratedPDUCabinet3MainsPostOut4Temperature | 3 Mains post out 4 temperature | 3主路端子4温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 4 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.42 | hwIntegratedPDUCabinet3MainsPostOut5Temperature | 3 Mains post out 5 temperature | 3主路端子5温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 5 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.43 | hwIntegratedPDUCabinet3MainsPostOut6Temperature | 3 Mains post out 6 temperature | 3主路端子6温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 6 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.44 | hwIntegratedPDUCabinet3MainsPostOut7Temperature | 3 Mains post out 7 temperature | 3主路端子7温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 7 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.45 | hwIntegratedPDUCabinet3MainsPostOut8Temperature | 3 Mains post out 8 temperature | 3主路端子8温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 8 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.46 | hwIntegratedPDUCabinet3MainsPostOut9Temperature | 3 Mains post out 9 temperature | 3主路端子9温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 9 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.47 | hwIntegratedPDUCabinet3MainsPostOut10Temperature | 3 Mains post out 10 temperature | 3主路端子10温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 10 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.48 | hwIntegratedPDUCabinet3MainsPostOut11Temperature | 3 Mains post out 11 temperature | 3主路端子11温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 11 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.49 | hwIntegratedPDUCabinet3MainsPostOut12Temperature | 3 Mains post out 12 temperature | 3主路端子12温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 12 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.50 | hwIntegratedPDUCabinet3MainsPostOut13Temperature | 3 Mains post out 13 temperature | 3主路端子13温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 13 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.51 | hwIntegratedPDUCabinet3MainsPostOut14Temperature | 3 Mains post out 14 temperature | 3主路端子14温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 14 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.52 | hwIntegratedPDUCabinet3MainsPostOut15Temperature | 3 Mains post out 15 temperature | 3主路端子15温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 15 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.53 | hwIntegratedPDUCabinet3MainsPostOut16Temperature | 3 Mains post out 16 temperature | 3主路端子16温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 16 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.54 | hwIntegratedPDUCabinet3MainsPostOut17Temperature | 3 Mains post out 17 temperature | 3主路端子17温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 17 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.55 | hwIntegratedPDUCabinet3MainsPostOut18Temperature | 3 Mains post out 18 temperature | 3主路端子18温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 18 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.56 | hwIntegratedPDUCabinet3MainsPostOut19Temperature | 3 Mains post out 19 temperature | 3主路端子19温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 19 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.57 | hwIntegratedPDUCabinet3MainsPostOut20Temperature | 3 Mains post out 20 temperature | 3主路端子20温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 20 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.58 | hwIntegratedPDUCabinet3MainsPostOut21Temperature | 3 Mains post out 21 temperature | 3主路端子21温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 21 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.59 | hwIntegratedPDUCabinet3MainsPostOut22Temperature | 3 Mains post out 22 temperature | 3主路端子22温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 22 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.60 | hwIntegratedPDUCabinet3MainsPostOut23Temperature | 3 Mains post out 23 temperature | 3主路端子23温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 23 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.61 | hwIntegratedPDUCabinet3MainsPostOut24Temperature | 3 Mains post out 24 temperature | 3主路端子24温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 3 Mains post out 24 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.62 | hwIntegratedPDUCabinet4MainsPostOut1Temperature | 4 Mains post out 1 temperature | 4主路端子1温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 1 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.63 | hwIntegratedPDUCabinet4MainsPostOut2Temperature | 4 Mains post out 2 temperature | 4主路端子2温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 2 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.64 | hwIntegratedPDUCabinet4MainsPostOut3Temperature | 4 Mains post out 3 temperature | 4主路端子3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 3 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.65 | hwIntegratedPDUCabinet4MainsPostOut4Temperature | 4 Mains post out 4 temperature | 4主路端子4温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 4 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.66 | hwIntegratedPDUCabinet4MainsPostOut5Temperature | 4 Mains post out 5 temperature | 4主路端子5温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 5 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.67 | hwIntegratedPDUCabinet4MainsPostOut6Temperature | 4 Mains post out 6 temperature | 4主路端子6温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 6 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.68 | hwIntegratedPDUCabinet4MainsPostOut7Temperature | 4 Mains post out 7 temperature | 4主路端子7温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 7 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.69 | hwIntegratedPDUCabinet4MainsPostOut8Temperature | 4 Mains post out 8 temperature | 4主路端子8温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 8 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.70 | hwIntegratedPDUCabinet4MainsPostOut9Temperature | 4 Mains post out 9 temperature | 4主路端子9温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 9 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.71 | hwIntegratedPDUCabinet4MainsPostOut10Temperature | 4 Mains post out 10 temperature | 4主路端子10温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 10 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.72 | hwIntegratedPDUCabinet4MainsPostOut11Temperature | 4 Mains post out 11 temperature | 4主路端子11温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 11 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.73 | hwIntegratedPDUCabinet4MainsPostOut12Temperature | 4 Mains post out 12 temperature | 4主路端子12温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 4 Mains post out 12 temperature of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.15.1.200 | hwIntegratedPDUCabinetRunning14RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16 | hwIntegratedPDUCabinetRunning15Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.1 | hwIntegratedPDUCabinetRunning15Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.2 | hwIntegratedPDUCabinetMaininputIIIfrequency | Main input 3-frequency | 主路3-频率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 3-AC Frequency of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.3 | hwIntegratedPDUCabinetMaininputIIIthreephaseaveglinevoltage | Main input 3-three phase aveg line voltage | 主路3-三相平均线电压 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | Main input 3-Three Phase Aveg Line Voltage of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.4 | hwIntegratedPDUCabinetMaininputIIIL1L2linevoltage | Main input 3-L1-L2 line voltage | 主路3-L1-L2线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 3-L1-L2 Line Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.5 | hwIntegratedPDUCabinetMaininputIIIL2L3linevoltage | Main input 3-L2-L3 line voltage | 主路3-L2-L3线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 3-L2-L3 Line Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.6 | hwIntegratedPDUCabinetMaininputIIIL3L1linevoltage | Main input 3-L3-L1 line voltage | 主路3-L3-L1线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 3-L3-L1 Line Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.7 | hwIntegratedPDUCabinetMaininputIIIthreephaseavegphasevoltage | Main input 3-three phase aveg phase voltage | 主路3-三相平均相电压 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | Main input 3-Three Phase Aveg Phase Voltage of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.8 | hwIntegratedPDUCabinetMaininputIIIphaseL1voltage | Main input 3-phase L1 voltage | 主路3-L1相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 3-Phase L1 Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.9 | hwIntegratedPDUCabinetMaininputIIIphaseL2voltage | Main input 3-phase L2 voltage | 主路3-L2相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 3-Phase L2 Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.10 | hwIntegratedPDUCabinetMaininputIIIphaseL3voltage | Main input 3-phase L3 voltage | 主路3-L3相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 3-Phase L3 Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.11 | hwIntegratedPDUCabinetMaininputIIIphaseL1angel | Main input 3-phase L1 angel | 主路3-L1相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 3-Phase L1 Angel of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.12 | hwIntegratedPDUCabinetMaininputIIIphaseL2angel | Main input 3-phase L2 angel | 主路3-L2相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 3-Phase L2 Angel of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.13 | hwIntegratedPDUCabinetMaininputIIIphaseL3angel | Main input 3-phase L3 angel | 主路3-L3相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 3-Phase L3 Angel of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.14 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL1current | Main input 3-channel 1 phase L1 current | 主路3-通道1 L1相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 3-Ch1 Ph L1 Current of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.15 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL2current | Main input 3-channel 1 phase L2 current | 主路3-通道1 L2相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 3-Ch1 Ph L2 Current of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.16 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL3current | Main input 3-channel 1 phase L3 current | 主路3-通道1 L3相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 3-Ch1 Ph L3 Current of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.17 | hwIntegratedPDUCabinetMaininputIIIchannel1activepower | Main input 3-channel1 active power | 主路3-通道1 有功功率 | 0-Read_Only | 只读 | -75000..75000 | -75000..75000 | Main input 3-Ch1 Active Power of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.18 | hwIntegratedPDUCabinetMaininputIIIchannel1reactpower | Main input 3-channel1 react power | 主路3-通道1 总无功功率 | 0-Read_Only | 只读 | -75000..75000 | -75000..75000 | Main input 3-Channel1 React Power of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.19 | hwIntegratedPDUCabinetMaininputIIIchannel1apparentpower | Main input 3-channel1 apparent power | 主路3-通道1 总视在功率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | Main input 3-Ch1 Apparent Power of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.20 | hwIntegratedPDUCabinetMaininputIIIchannel1powerfactor | Main input 3-channel1 power factor | 主路3-通道1 功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input 3-Ch1 Power Factor of the device config table for the Integrated PDU Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.21 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL1activepower | Main input 3-channel1 phase L1 active power | 主路3-通道1 L1相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 3-Ch1 Ph L1 Active P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.22 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL2activepower | Main input 3-channel1 phase L2 active power | 主路3-通道1 L2相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 3-Ch1 Ph L2 Active P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.23 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL3activepower | Main input 3-channel1 phase L3 active power | 主路3-通道1 L3相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 3-Ch1 Ph L3 Active P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.24 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL1reactpower | Main input 3-channel1 phase L1 react power | 主路3-通道1 L1相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 3-Ch1 Ph L1 React P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.25 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL2reactpower | Main input 3-channel1 phase L2 react power | 主路3-通道1 L2相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 3-Ch1 Ph L2 React P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.26 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL3reactpower | Main input 3-channel1 phase L3 react power | 主路3-通道1 L3相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 3-Ch1 Ph L3 React P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.27 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL1powerfactor | Main input 3-channel1 phase L1 power factor | 主路3-通道1 L1相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input 3-Ch1 Ph L1 P Factor of the device config table for the Integrated PDU Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.28 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL2powerfactor | Main input 3-channel1 phase L2 power factor | 主路3-通道1 L2相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input 3-Ch1 Ph L2 P Factor of the device config table for the Integrated PDU Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.29 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL3powerfactor | Main input 3-channel1 phase L3 power factor | 主路3-通道1 L3相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input 3-Ch1 Ph L3 P Factor of the device config table for the Integrated PDU Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.30 | hwIntegratedPDUCabinetMaininputIIIchannel1powerconsumption | Main input 3-channel1 power consumption | 主路3-通道1 有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Main input 3-Ch1 Power Consump of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.31 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL1actelect | Main input 3-channel1 phase L1 active electricity | 主路3-通道1 L1相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Main input 3-Ch1 Ph L1 Act Elect of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.32 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL2actelect | Main input 3-channel1 phase L2 active electricity | 主路3-通道1 L2相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Main input 3-Ch1 Ph L2 Act Elect of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.33 | hwIntegratedPDUCabinetMaininputIIIchannel1phaseL3actelect | Main input 3-channel1 phase L3 active electricity | 主路3-通道1 L3相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Main input 3-Ch1 Ph L3 Act Elect of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.34 | hwIntegratedPDUCabinetMaininputIIITHDVA | Main input 3-THD VA | 主路3-THD VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-THD VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.35 | hwIntegratedPDUCabinetMaininputIIIbasicwaveVA | Main input 3-basic wave VA | 主路3-基波 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-Basic Wave VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.36 | hwIntegratedPDUCabinetMaininputIII3thTHDVA | Main input 3-3th THD VA | 主路3-3次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-3th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.37 | hwIntegratedPDUCabinetMaininputIII5thTHDVA | Main input 3-5th THD VA | 主路3-5次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-5th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.38 | hwIntegratedPDUCabinetMaininputIII7thTHDVA | Main input 3-7th THD VA | 主路3-7次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-7th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.39 | hwIntegratedPDUCabinetMaininputIII9thTHDVA | Main input 3-9th THD VA | 主路3-9次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-9th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.40 | hwIntegratedPDUCabinetMaininputIII11thTHDVA | Main input 3-11th THD VA | 主路3-11次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-11th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.41 | hwIntegratedPDUCabinetMaininputIIITHDVB | Main input 3-THD VB | 主路3-THD VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-THD VB VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.42 | hwIntegratedPDUCabinetMaininputIIIbasicwaveVB | Main input 3-basic wave VB | 主路3-基波 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-basic Wave VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.43 | hwIntegratedPDUCabinetMaininputIII3thTHDVB | Main input 3-3th THD VB | 主路3-3次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-3th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.44 | hwIntegratedPDUCabinetMaininputIII5thTHDVB | Main input 3-5th THD VB | 主路3-5次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-5th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.45 | hwIntegratedPDUCabinetMaininputIII7thTHDVB | Main input 3-7th THD VB | 主路3-7次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-7th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.46 | hwIntegratedPDUCabinetMaininputIII9thTHDVB | Main input 3-9th THD VB | 主路3-9次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-9th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.47 | hwIntegratedPDUCabinetMaininputIII11thTHDVB | Main input 3-11th THD VB | 主路3-11次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-11th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.48 | hwIntegratedPDUCabinetMaininputIIITHDVC | Main input 3-THD VC | 主路3-THD VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-THD VC VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.49 | hwIntegratedPDUCabinetMaininputIIIbasicwaveVC | Main input 3-basic wave VC | 主路3-基波 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-basic Wave VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.50 | hwIntegratedPDUCabinetMaininputIII3thTHDVC | Main input 3-3th THD VC | 主路3-3次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-3th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.51 | hwIntegratedPDUCabinetMaininputIII5thTHDVC | Main input 3-5th THD VC | 主路3-5次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-5th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.52 | hwIntegratedPDUCabinetMaininputIII7thTHDVC | Main input 3-7th THD VC | 主路3-7次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-7th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.53 | hwIntegratedPDUCabinetMaininputIII9thTHDVC | Main input 3-9th THD VC | 主路3-9次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-9th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.54 | hwIntegratedPDUCabinetMaininputIII11thTHDVC | Main input 3-11th THD VC | 主路3-11次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-11th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.55 | hwIntegratedPDUCabinetMaininputIIITHDIA | Main input 3-THD IA | 主路3-THD IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.56 | hwIntegratedPDUCabinetMaininputIIIbasicwaveIA | Main input 3-basic wave IA | 主路3-基波 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-Basic Wave IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.57 | hwIntegratedPDUCabinetMaininputIII3thTHDIA | Main input 3-3th THD IA | 主路3-3次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-3th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.58 | hwIntegratedPDUCabinetMaininputIII5thTHDIA | Main input 3-5th THD IA | 主路3-5次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-5th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.59 | hwIntegratedPDUCabinetMaininputIII7thTHDIA | Main input 3-7th THD IA | 主路3-7次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-7th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.60 | hwIntegratedPDUCabinetMaininputIII9thTHDIA | Main input 3-9th THD IA | 主路3-9次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-9th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.61 | hwIntegratedPDUCabinetMaininputIII11thTHDIA | Main input 3-11th THD IA | 主路3-11次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-11th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.62 | hwIntegratedPDUCabinetMaininputIIITHDIB | Main input 3-THD IB | 主路3-THD IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.63 | hwIntegratedPDUCabinetMaininputIIIbasicwaveIB | Main input 3-basic wave IB | 主路3-基波 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-Basic Wave IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.64 | hwIntegratedPDUCabinetMaininputIII3thTHDIB | Main input 3-3th THD IB | 主路3-3次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-3th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.65 | hwIntegratedPDUCabinetMaininputIII5thTHDIB | Main input 3-5th THD IB | 主路3-5次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-5th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.66 | hwIntegratedPDUCabinetMaininputIII7thTHDIB | Main input 3-7th THD IB | 主路3-7次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-7th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.67 | hwIntegratedPDUCabinetMaininputIII9thTHDIB | Main input 3-9th THD IB | 主路3-9次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-9th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.68 | hwIntegratedPDUCabinetMaininputIII11thTHDIB | Main input 3-11th THD IB | 主路3-11次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-11th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.69 | hwIntegratedPDUCabinetMaininputIIITHDIC | Main input 3-THD IC | 主路3-THD IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.70 | hwIntegratedPDUCabinetMaininputIIIbasicwaveIC | Main input 3-basic wave IC | 主路3-基波 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-Basic Wave IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.71 | hwIntegratedPDUCabinetMaininputIII3thTHDIC | Main input 3-3th THD IC | 主路3-3次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-3th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.72 | hwIntegratedPDUCabinetMaininputIII5thTHDIC | Main input 3-5th THD IC | 主路3-5次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-5th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.73 | hwIntegratedPDUCabinetMaininputIII7thTHDIC | Main input 3-7th THD IC | 主路3-7次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-7th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.74 | hwIntegratedPDUCabinetMaininputIII9thTHDIC | Main input 3-9th THD IC | 主路3-9次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-9th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.75 | hwIntegratedPDUCabinetMaininputIII11thTHDIC | Main input 3-11th THD IC | 主路3-11次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 3-11th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.76 | hwIntegratedPDUCabinetMaininputIVfrequency | Main input 4-frequency | 主路4-频率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 4-AC Frequency of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.77 | hwIntegratedPDUCabinetMaininputIVthreephaseaveglinevoltage | Main input 4-three phase aveg line voltage | 主路4-三相平均线电压 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | Main input 4-Three Phase Aveg Line Voltage of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.78 | hwIntegratedPDUCabinetMaininputIVL1L2linevoltage | Main input 4-L1-L2 line voltage | 主路4-L1-L2线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 4-L1-L2 Line Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.79 | hwIntegratedPDUCabinetMaininputIVL2L3linevoltage | Main input 4-L2-L3 line voltage | 主路4-L2-L3线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 4-L2-L3 Line Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.80 | hwIntegratedPDUCabinetMaininputIVL3L1linevoltage | Main input 4-L3-L1 line voltage | 主路4-L3-L1线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 4-L3-L1 Line Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.81 | hwIntegratedPDUCabinetMaininputIVthreephaseavegphasevoltage | Main input 4-three phase aveg phase voltage | 主路4-三相平均相电压 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | Main input 4-Three Phase Aveg Phase Voltage of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.82 | hwIntegratedPDUCabinetMaininputIVphaseL1voltage | Main input 4-phase L1 voltage | 主路4-L1相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 4-Phase L1 Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.83 | hwIntegratedPDUCabinetMaininputIVphaseL2voltage | Main input 4-phase L2 voltage | 主路4-L2相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 4-Phase L2 Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.84 | hwIntegratedPDUCabinetMaininputIVphaseL3voltage | Main input 4-phase L3 voltage | 主路4-L3相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Main input 4-Phase L3 Voltage of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.85 | hwIntegratedPDUCabinetMaininputIVphaseL1angel | Main input 4-phase L1 angel | 主路4-L1相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 4-Phase L1 Angel of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.86 | hwIntegratedPDUCabinetMaininputIVphaseL2angel | Main input 4-phase L2 angel | 主路4-L2相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 4-Phase L2 Angel of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.87 | hwIntegratedPDUCabinetMaininputIVphaseL3angel | Main input 4-phase L3 angel | 主路4-L3相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 4-Phase L3 Angel of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.88 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL1current | Main input 4-channel 1 phase L1 current | 主路4-通道1 L1相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 4-Ch1 Ph L1 Current of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.89 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL2current | Main input 4-channel 1 phase L2 current | 主路4-通道1 L2相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 4-Ch1 Ph L2 Current of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.90 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL3current | Main input 4-channel 1 phase L3 current | 主路4-通道1 L3相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input 4-Ch1 Ph L3 Current of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.91 | hwIntegratedPDUCabinetMaininputIVchannel1activepower | Main input 4-channel1 active power | 主路4-通道1 有功功率 | 0-Read_Only | 只读 | -75000..75000 | -75000..75000 | Main input 4-Ch1 Active Power of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.92 | hwIntegratedPDUCabinetMaininputIVchannel1reactpower | Main input 4-channel1 react power | 主路4-通道1 总无功功率 | 0-Read_Only | 只读 | -75000..75000 | -75000..75000 | Main input 4-Channel1 React Power of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.93 | hwIntegratedPDUCabinetMaininputIVchannel1apparentpower | Main input 4-channel1 apparent power | 主路4-通道1 总视在功率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | Main input 4-Ch1 Apparent Power of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.94 | hwIntegratedPDUCabinetMaininputIVchannel1powerfactor | Main input 4-channel1 power factor | 主路4-通道1 功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input 4-Ch1 Power Factor of the device config table for the Integrated PDU Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.95 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL1activepower | Main input 4-channel1 phase L1 active power | 主路4-通道1 L1相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 4-Ch1 Ph L1 Active P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.96 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL2activepower | Main input 4-channel1 phase L2 active power | 主路4-通道1 L2相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 4-Ch1 Ph L2 Active P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.97 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL3activepower | Main input 4-channel1 phase L3 active power | 主路4-通道1 L3相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 4-Ch1 Ph L3 Active P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.98 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL1reactpower | Main input 4-channel1 phase L1 react power | 主路4-通道1 L1相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 4-Ch1 Ph L1 React P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.99 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL2reactpower | Main input 4-channel1 phase L2 react power | 主路4-通道1 L2相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 4-Ch1 Ph L2 React P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.100 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL3reactpower | Main input 4-channel1 phase L3 react power | 主路4-通道1 L3相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Main input 4-Ch1 Ph L3 React P of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.101 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL1powerfactor | Main input 4-channel1 phase L1 power factor | 主路4-通道1 L1相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input 4-Ch1 Ph L1 P Factor of the device config table for the Integrated PDU Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.102 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL2powerfactor | Main input 4-channel1 phase L2 power factor | 主路4-通道1 L2相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input 4-Ch1 Ph L2 P Factor of the device config table for the Integrated PDU Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.103 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL3powerfactor | Main input 4-channel1 phase L3 power factor | 主路4-通道1 L3相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input 4-Ch1 Ph L3 P Factor of the device config table for the Integrated PDU Cabinet.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.104 | hwIntegratedPDUCabinetMaininputIVchannel1powerconsumption | Main input 4-channel1 power consumption | 主路4-通道1 有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Main input 4-Ch1 Power Consump of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.105 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL1actelect | Main input 4-channel1 phase L1 active electricity | 主路4-通道1 L1相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Main input 4-Ch1 Ph L1 Act Elect of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.106 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL2actelect | Main input 4-channel1 phase L2 active electricity | 主路4-通道1 L2相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Main input 4-Ch1 Ph L2 Act Elect of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.107 | hwIntegratedPDUCabinetMaininputIVchannel1phaseL3actelect | Main input 4-channel1 phase L3 active electricity | 主路4-通道1 L3相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Main input 4-Ch1 Ph L3 Act Elect of the device config table for the Integrated PDU Cabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.108 | hwIntegratedPDUCabinetMaininputIVTHDVA | Main input 4-THD VA | 主路4-THD VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-THD VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.109 | hwIntegratedPDUCabinetMaininputIVbasicwaveVA | Main input 4-basic wave VA | 主路4-基波 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-Basic Wave VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.110 | hwIntegratedPDUCabinetMaininputIV3thTHDVA | Main input 4-3th THD VA | 主路4-3次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-3th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.111 | hwIntegratedPDUCabinetMaininputIV5thTHDVA | Main input 4-5th THD VA | 主路4-5次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-5th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.112 | hwIntegratedPDUCabinetMaininputIV7thTHDVA | Main input 4-7th THD VA | 主路4-7次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-7th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.113 | hwIntegratedPDUCabinetMaininputIV9thTHDVA | Main input 4-9th THD VA | 主路4-9次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-9th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.114 | hwIntegratedPDUCabinetMaininputIV11thTHDVA | Main input 4-11th THD VA | 主路4-11次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-11th Thd VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.115 | hwIntegratedPDUCabinetMaininputIVTHDVB | Main input 4-THD VB | 主路4-THD VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-THD VB VA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.116 | hwIntegratedPDUCabinetMaininputIVbasicwaveVB | Main input 4-basic wave VB | 主路4-基波 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-basic Wave VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.117 | hwIntegratedPDUCabinetMaininputIV3thTHDVB | Main input 4-3th THD VB | 主路4-3次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-3th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.118 | hwIntegratedPDUCabinetMaininputIV5thTHDVB | Main input 4-5th THD VB | 主路4-5次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-5th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.119 | hwIntegratedPDUCabinetMaininputIV7thTHDVB | Main input 4-7th THD VB | 主路4-7次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-7th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.120 | hwIntegratedPDUCabinetMaininputIV9thTHDVB | Main input 4-9th THD VB | 主路4-9次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-9th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.121 | hwIntegratedPDUCabinetMaininputIV11thTHDVB | Main input 4-11th THD VB | 主路4-11次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-11th Thd VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.122 | hwIntegratedPDUCabinetMaininputIVTHDVC | Main input 4-THD VC | 主路4-THD VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-THD VC VB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.123 | hwIntegratedPDUCabinetMaininputIVbasicwaveVC | Main input 4-basic wave VC | 主路4-基波 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-basic Wave VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.124 | hwIntegratedPDUCabinetMaininputIV3thTHDVC | Main input 4-3th THD VC | 主路4-3次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-3th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.125 | hwIntegratedPDUCabinetMaininputIV5thTHDVC | Main input 4-5th THD VC | 主路4-5次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-5th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.126 | hwIntegratedPDUCabinetMaininputIV7thTHDVC | Main input 4-7th THD VC | 主路4-7次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-7th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.127 | hwIntegratedPDUCabinetMaininputIV9thTHDVC | Main input 4-9th THD VC | 主路4-9次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-9th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.128 | hwIntegratedPDUCabinetMaininputIV11thTHDVC | Main input 4-11th THD VC | 主路4-11次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-11th Thd VC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.129 | hwIntegratedPDUCabinetMaininputIVTHDIA | Main input 4-THD IA | 主路4-THD IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.130 | hwIntegratedPDUCabinetMaininputIVbasicwaveIA | Main input 4-basic wave IA | 主路4-基波 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-Basic Wave IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.131 | hwIntegratedPDUCabinetMaininputIV3thTHDIA | Main input 4-3th THD IA | 主路4-3次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-3th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.132 | hwIntegratedPDUCabinetMaininputIV5thTHDIA | Main input 4-5th THD IA | 主路4-5次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-5th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.133 | hwIntegratedPDUCabinetMaininputIV7thTHDIA | Main input 4-7th THD IA | 主路4-7次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-7th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.134 | hwIntegratedPDUCabinetMaininputIV9thTHDIA | Main input 4-9th THD IA | 主路4-9次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-9th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.135 | hwIntegratedPDUCabinetMaininputIV11thTHDIA | Main input 4-11th THD IA | 主路4-11次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-11th Thd IA of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.136 | hwIntegratedPDUCabinetMaininputIVTHDIB | Main input 4-THD IB | 主路4-THD IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.137 | hwIntegratedPDUCabinetMaininputIVbasicwaveIB | Main input 4-basic wave IB | 主路4-基波 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-Basic Wave IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.138 | hwIntegratedPDUCabinetMaininputIV3thTHDIB | Main input 4-3th THD IB | 主路4-3次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-3th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.139 | hwIntegratedPDUCabinetMaininputIV5thTHDIB | Main input 4-5th THD IB | 主路4-5次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-5th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.140 | hwIntegratedPDUCabinetMaininputIV7thTHDIB | Main input 4-7th THD IB | 主路4-7次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-7th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.141 | hwIntegratedPDUCabinetMaininputIV9thTHDIB | Main input 4-9th THD IB | 主路4-9次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-9th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.142 | hwIntegratedPDUCabinetMaininputIV11thTHDIB | Main input 4-11th THD IB | 主路4-11次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-11th Thd IB of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.143 | hwIntegratedPDUCabinetMaininputIVTHDIC | Main input 4-THD IC | 主路4-THD IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.144 | hwIntegratedPDUCabinetMaininputIVbasicwaveIC | Main input 4-basic wave IC | 主路4-基波 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-Basic Wave IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.145 | hwIntegratedPDUCabinetMaininputIV3thTHDIC | Main input 4-3th THD IC | 主路4-3次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-3th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.146 | hwIntegratedPDUCabinetMaininputIV5thTHDIC | Main input 4-5th THD IC | 主路4-5次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-5th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.147 | hwIntegratedPDUCabinetMaininputIV7thTHDIC | Main input 4-7th THD IC | 主路4-7次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-7th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.148 | hwIntegratedPDUCabinetMaininputIV9thTHDIC | Main input 4-9th THD IC | 主路4-9次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-9th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.149 | hwIntegratedPDUCabinetMaininputIV11thTHDIC | Main input 4-11th THD IC | 主路4-11次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input 4-11th Thd IC of the device config table for the Integrated PDU Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.4.16.1.200 | hwIntegratedPDUCabinetRunning15RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17 | hwIntegratedPDUCabinetRunning16Table | / | / |  |  | / | / | The running table of Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.1 | hwIntegratedPDUCabinetRunning16Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated PDU Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.2 | hwIntegratedPDUCabinetIL1busbarjointtemperature | Main input 1-L1 busbar temperature | 主路1-L1母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 1-L1 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.3 | hwIntegratedPDUCabinetIL2busbarjointtemperature | Main input 1-L2 busbar temperature | 主路1-L2母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 1-L2 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.4 | hwIntegratedPDUCabinetIL3busbarjointtemperature | Main input 1-L3 busbar temperature | 主路1-L3母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 1-L3 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.5 | hwIntegratedPDUCabinetIIL1busbarjointtemperature | Main input 2-L1 busbar temperature | 主路2-L1母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 2-L1 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.6 | hwIntegratedPDUCabinetIIL2busbarjointtemperature | Main input 2-L2 busbar temperature | 主路2-L2母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 2-L2 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.7 | hwIntegratedPDUCabinetIIL3busbarjointtemperature | Main input 2-L3 busbar temperature | 主路2-L3母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 2-L3 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.8 | hwIntegratedPDUCabinetIIIL1busbarjointtemperature | Main input 3-L1 busbar temperature | 主路3-L1母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 3-L1 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.9 | hwIntegratedPDUCabinetIIIL2busbarjointtemperature | Main input 3-L2 busbar temperature | 主路3-L2母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 3-L2 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.10 | hwIntegratedPDUCabinetIIIL3busbarjointtemperature | Main input 3-L3 busbar temperature | 主路3-L3母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 3-L3 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.11 | hwIntegratedPDUCabinetIVL1busbarjointtemperature | Main input 4-L1 busbar temperature | 主路4-L1母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 4-L1 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.12 | hwIntegratedPDUCabinetIVL2busbarjointtemperature | Main input 4-L2 busbar temperature | 主路4-L2母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 4-L2 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.13 | hwIntegratedPDUCabinetIVL3busbarjointtemperature | Main input 4-L3 busbar temperature | 主路4-L3母排连接处温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 4-L3 busbar temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.14 | hwIntegratedPDUCabinetIL1busbartemperature | Main input 1-L1 temperature | 主路1-L1母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 1-L1 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.15 | hwIntegratedPDUCabinetIL2busbartemperature | Main input 1-L2 temperature | 主路1-L2母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 1-L2 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.16 | hwIntegratedPDUCabinetIL3busbartemperature | Main input 1-L3 temperature | 主路1-L3母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 1-L3 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.17 | hwIntegratedPDUCabinetIIL1busbartemperature | Main input 2-L1 temperature | 主路2-L1母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 2-L1 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.18 | hwIntegratedPDUCabinetIIL2busbartemperature | Main input 2-L2 temperature | 主路2-L2母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 2-L2 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.19 | hwIntegratedPDUCabinetIIL3busbartemperature | Main input 2-L3 temperature | 主路2-L3母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 2-L3 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.20 | hwIntegratedPDUCabinetIIIL1busbartemperature | Main input 3-L1 temperature | 主路3-L1母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 3-L1 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.21 | hwIntegratedPDUCabinetIIIL2busbartemperature | Main input 3-L2 temperature | 主路3-L2母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 3-L2 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.22 | hwIntegratedPDUCabinetIIIL3busbartemperature | Main input 3-L3 temperature | 主路3-L3母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 3-L3 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.23 | hwIntegratedPDUCabinetIVL1busbartemperature | Main input 4-L1 temperature | 主路4-L1母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 4-L1 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.24 | hwIntegratedPDUCabinetIVL2busbartemperature | Main input 4-L2 temperature | 主路4-L2母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 4-L2 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.25 | hwIntegratedPDUCabinetIVL3busbartemperature | Main input 4-L3 temperature | 主路4-L3母排温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The main input 4-L3 temperature of Integrated PDU Cabinet. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.26 | hwIntegratedPDUMains1AmbientTemperature1 | Mains 1 ambient temperature 1 | 主路1-环境温度1 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 1 ambient temperature 1 of the device config table for the Integrated PDU.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.27 | hwIntegratedPDUMains1AmbientTemperature2 | Mains 1 ambient temperature 2 | 主路1-环境温度2 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 1 ambient temperature 2 of the device config table for the Integrated PDU.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.28 | hwIntegratedPDUMains2AmbientTemperature1 | Mains 2 ambient temperature 1 | 主路2-环境温度1 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 2 ambient temperature 1 of the device config table for the Integrated PDU.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.29 | hwIntegratedPDUMains3AmbientTemperature1 | Mains 3 ambient temperature 1 | 主路3-环境温度1 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 3 ambient temperature 1 of the device config table for the Integrated PDU.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.30 | hwIntegratedPDUMains3AmbientTemperature2 | Mains 3 ambient temperature 2 | 主路3-环境温度2 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 3 ambient temperature 2 of the device config table for the Integrated PDU.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.31 | hwIntegratedPDUMains4AmbientTemperature1 | Mains 4 ambient temperature 1 | 主路4-环境温度1 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 4 ambient temperature 1 of the device config table for the Integrated PDU.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.32 | hwIntegratedPDUWhetherToSupportTemperaturePrediction | Whether to support temperature prediction | 是否支持温度预测 | 0-Read_Only | 只读 | notsupported(1), support(2), unknown(255) | [不支持=1]/[支持=2] | Whether to support temperature prediction of the device config table for the Integrated PDU. Value 1 indicate not supported Value 2 indicate support
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.33 | hwIntegratedPDUMains1InputSwitchStatus | Mains 1 input switch status | 主路1-输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Mains 1 input switch status of the device config table for the Integrated PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.34 | hwIntegratedPDUMains2InputSwitchStatus | Mains 2 input switch status | 主路2-输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Mains 2 input switch status of the device config table for the Integrated PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.35 | hwIntegratedPDUMains3InputSwitchStatus | Mains 3 input switch status | 主路3-输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Mains 3 input switch status of the device config table for the Integrated PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.36 | hwIntegratedPDUMains4InputSwitchStatus | Mains 4 input switch status | 主路4-输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Mains 4 input switch status of the device config table for the Integrated PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.37 | hwIntegratedPDUMains1InputSpdStatus | Mains 1 input SPD status | 主路1-输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Mains 1 input SPD status of the device config table for the Integrated PDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.38 | hwIntegratedPDUMains2InputSpdStatus | Mains 2 input SPD status | 主路2-输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Mains 2 input SPD status of the device config table for the Integrated PDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.39 | hwIntegratedPDUMains3InputSpdStatus | Mains 3 input SPD status | 主路3-输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Mains 3 input SPD status of the device config table for the Integrated PDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.40 | hwIntegratedPDUMains4InputSpdStatus | Mains 4 input SPD status | 主路4-输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Mains 4 input SPD status of the device config table for the Integrated PDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.41 | hwIntegratedPDUMains1InputSwitchStatusNew | Mains 1 input switch status | 主路1-输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Mains 1 input switch status of the device config table for the Integrated PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.42 | hwIntegratedPDUMains2InputSwitchStatusNew | Mains 2 input switch status | 主路2-输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Mains 2 input switch status of the device config table for the Integrated PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.43 | hwIntegratedPDUMains3InputSwitchStatusNew | Mains 3 input switch status | 主路3-输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Mains 3 input switch status of the device config table for the Integrated PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.44 | hwIntegratedPDUMains4InputSwitchStatusNew | Mains 4 input switch status | 主路4-输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Mains 4 input switch status of the device config table for the Integrated PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.45 | hwIntegratedPDUMains1InputSpdStatusNew | Mains 1 input SPD status | 主路1-输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Mains 1 input SPD status of the device config table for the Integrated PDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.46 | hwIntegratedPDUMains2InputSpdStatusNew | Mains 2 input SPD status | 主路2-输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Mains 2 input SPD status of the device config table for the Integrated PDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.47 | hwIntegratedPDUMains3InputSpdStatusNew | Mains 3 input SPD status | 主路3-输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Mains 3 input SPD status of the device config table for the Integrated PDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.48 | hwIntegratedPDUMains4InputSpdStatusNew | Mains 4 input SPD status | 主路4-输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Mains 4 input SPD status of the device config table for the Integrated PDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.4.17.1.200 | hwIntegratedPDUCabinetRunning16RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Integrated PDU Cabinet.

## PDU8000
PDU8000
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.5 | PDU8000 | PDU8000 | PDU8000 | / | / | / | / | The PDU800 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1 | hwPDU8000Running1Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.1 | hwPDU8000Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.2 | hwPDU8000CommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | pdu8000 comm status: Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.3 | hwPDU8000SlotNo | Slot No. | 槽位号 | 0-Read_Only | 只读 | 0..6 | 0..6 | pdu8000 slot no.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.4 | hwPDU8000PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | pdu8000 port no.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.5 | hwPDU8000ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | pdu8000 modbus addr.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.6 | hwPDU8000SoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | pdu8000 software ver.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.7 | hwPDU8000ESN | ESN | ESN | 0-Read_Only | 只读 | 0..20 | 0..20 | pdu8000 esn.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.8 | hwPDU8000InputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | singlemode(1), dualmode(2), dual1way(3), dual2way(4), transformer380to380(5), transformer480to208(6), unknown(255) | [单路输入=1]/[双路输入=2]/[双路输入-1=3]/[双路输入-2=4]/[380/380变压器=5]/[480/208变压器=6] | pdu8000 pdu input mode: value 1 indicates Single-Mode. value 2 indicates Dual-Mode. value 3 indicates Dual-1-Way. value 4 indicates Dual-2-Way. value 5 indicates 380/380-Transformer. value 6 indicates 480/208-Transformer.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.9 | hwPDU8000TotalInputElectricEnergy | Total input electric energy | 总输入电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 total input energy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.11 | hwPDU8000TotalInputPower | Total input power | 总输入功率 | 0-Read_Only | 只读 | -100000..100000 | -100000..100000 | pdu8000 total input power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.13 | hwPDU8000MIL1InputPhaseVoltage | L1 input voltage | L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mi l1 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.14 | hwPDU8000MIL2InputPhaseVoltage | L2 input voltage | L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mi l2 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.15 | hwPDU8000MIL3InputPhaseVoltage | L3 input voltage | L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mi l3 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.16 | hwPDU8000MIL1L2InputLineVoltage | L1-L2 input line voltage | L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mi l1l2 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.17 | hwPDU8000MIL2L3InputLineVoltage | L2-L3 input line voltage | L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mi l2l3 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.18 | hwPDU8000MIL3L1InputLineVoltage | L3-L1 input line voltage | L1-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mi l1l3 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.19 | hwPDU8000MIL1InputPhaseCurrent | L1 input current | L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 mi l1 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.20 | hwPDU8000MIL2InputPhaseCurrent | L2 input current | L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 mi l2 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.21 | hwPDU8000MIL3InputPhaseCurrent | L3 input current | L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 mi l3 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.22 | hwPDU8000MIInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mi input freq. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.32 | hwPDU8000MIL1InputPowerFactor | L1 input power factor | L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 mi l1 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.33 | hwPDU8000MIL2InputPowerFactor | L2 input power factor | L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 mi l2 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.34 | hwPDU8000MIL3InputPowerFactor | L3 input power factor | L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 mi l3 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.35 | hwPDU8000MIInputActiveElectricEnergy | Input active electric energy | 输入有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 mi input act energy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.36 | hwPDU8000MIL1InputPowerLoadRate | L1 input power load rate | L1输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 mi l1 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.37 | hwPDU8000MIL2InputPowerLoadRate | L2 input power load rate | L2输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 mi l2 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.38 | hwPDU8000MIL3InputPowerLoadRate | L3 input power load rate | L3输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 mi l3 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.39 | hwPDU8000MINWireCurrent | Input neutral wire current | 输入N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mi input n line cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.40 | hwPDU8000MIL1THDuRate | L1 THDu | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mi l1 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.41 | hwPDU8000MIL2THDuRate | L2 THDu | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mi l2 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.42 | hwPDU8000MIL3THDuRate | L3 THDu | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mi l3 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.43 | hwPDU8000MIL1THDiRate | L1 THDi | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mi l1 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.44 | hwPDU8000MIL2THDiRate | L2 THDi | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mi l2 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.45 | hwPDU8000MIL3THDiRate | L3 THDi | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mi l3 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.46 | hwPDU8000MITotalInputActivePower | Total input active power | 总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 mi total input act power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.47 | hwPDU8000MITotalInputApparentPower | Total input apparent power | 总输入视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 mi total input app power. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.48 | hwPDU8000MITotalInputReactivePower | Total input reactive power | 总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 mi total input invalid power. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.49 | hwPDU8000L1PhaseVoltage | L1 phase voltage | L1相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mo l1 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.50 | hwPDU8000L2PhaseVoltage | L2 phase voltage | L2相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mo l2 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.51 | hwPDU8000L3PhaseVoltage | L3 phase voltage | L3相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mo l3 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.52 | hwPDU8000L1L2LineVoltage | L1-L2 line voltage | L1-L2线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mo l1l2 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.53 | hwPDU8000L2L3LineVoltage | L2-L3 line voltage | L2-L3线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mo l2l3 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.54 | hwPDU8000L3L1LineVoltage | L3-L1 line voltage | L1-L3线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mo l1l3 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.55 | hwPDU8000L1Current | L1 current | L1电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 mo l1 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.56 | hwPDU8000L2Current | L2 current | L2电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 mo l2 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.57 | hwPDU8000L3Current | L3 current | L3电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 mo l3 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.58 | hwPDU8000Frequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mo input freq. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.68 | hwPDU8000L1PowerFactor | L1 power factor | L1功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 mo l1 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.69 | hwPDU8000L2PowerFactor | L2 power factor | L2功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 mo l2 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.70 | hwPDU8000L3PowerFactor | L3 power factor | L3功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 mo l3 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.71 | hwPDU8000ActiveElectricEnergy | Active electric energy | 有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 mo input act energy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.72 | hwPDU8000L1PowerLoadRate | L1 power load rate | L1电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 mo l1 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.73 | hwPDU8000L2PowerLoadRate | L2 power load rate | L2电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 mo l2 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.74 | hwPDU8000L3PowerLoadRate | L3 power load rate | L3电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 mo l3 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.75 | hwPDU8000NWireCurrent | N wire current | N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 mo input n line cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.76 | hwPDU8000L1THDuRate | L1 THDu | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mo l1 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.77 | hwPDU8000L2THDuRate | L2 THDu | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mo l2 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.78 | hwPDU8000L3THDuRate | L3 THDu | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mo l3 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.79 | hwPDU8000L1THDiRate | L1 THDi | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mo l1 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.80 | hwPDU8000L2THDiRate | L2 THDi | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mo l2 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.81 | hwPDU8000L3THDiRate | L3 THDi | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 mo l3 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.82 | hwPDU8000TotalActivePower | Total active power | 总有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 mo total input act power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.83 | hwPDU8000TotalApparentPower | Total apparent power | 总视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 mo total input app power. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.84 | hwPDU8000TotalReactivePower | Total reactive power | 总无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 mo total input invalid power. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.85 | hwPDU8000M1IL1InputPhaseVoltage | L1 input voltage | L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main i l1 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.86 | hwPDU8000M1IL2InputPhaseVoltage | L2 input voltage | L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main i l2 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.87 | hwPDU8000M1IL3InputPhaseVoltage | L3 input voltage | L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main i l3 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.88 | hwPDU8000M1IL1L2InputLineVoltage | L1-L2 input line voltage | L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main i l1l2 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.89 | hwPDU8000M1IL2L3InputLineVoltage | L2-L3 input line voltage | L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main i l2l3 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.90 | hwPDU8000M1IL3L1InputLineVoltage | L3-L1 input line voltage | L1-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main i l1l3 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.91 | hwPDU8000M1IL1InputPhaseCurrent | L1 input current | L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 main i l1 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.92 | hwPDU8000M1IL2InputPhaseCurrent | L2 input current | L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 main i l2 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.93 | hwPDU8000M1IL3InputPhaseCurrent | L3 input current | L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 main i l3 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.94 | hwPDU8000M1IInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main i input freq. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.104 | hwPDU8000M1IL1InputPowerFactor | L1 input power factor | L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 main i l1 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.105 | hwPDU8000M1IL2InputPowerFactor | L2 input power factor | L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 main i l2 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.106 | hwPDU8000M1IL3InputPowerFactor | L3 input power factor | L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 main i l3 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.107 | hwPDU8000M1IInputActiveElectricEnergy | Input active electric energy | 输入有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 main i input act energy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.108 | hwPDU8000M1IL1InputPowerLoadRate | L1 input power load rate | L1输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 main i l1 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.109 | hwPDU8000M1IL2InputPowerLoadRate | L2 input power load rate | L2输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 main i l2 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.110 | hwPDU8000M1IL3InputPowerLoadRate | L3 input power load rate | L3输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 main i l3 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.111 | hwPDU8000M1IInputNWireCurrent | Input neutral wire current | 输入N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main i input n line cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.112 | hwPDU8000M1IL1THDuRate | L1 THDu | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main i l1 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.113 | hwPDU8000M1IL2THDuRate | L2 THDu | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main i l2 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.114 | hwPDU8000M1IL3THDuRate | L3 THDu | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main i l3 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.115 | hwPDU8000M1IL1THDiRate | L1 THDi | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main i l1 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.116 | hwPDU8000M1IL2THDiRate | L2 THDi | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main i l2 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.117 | hwPDU8000M1IL3THDiRate | L3 THDi | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main i l3 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.118 | hwPDU8000M1ITotalInputActivePower | Total input active power | 总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 main i total input act power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.119 | hwPDU8000M1ITotalInputApparentPower | Total input apparent power | 总输入视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 main i total input app power. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.120 | hwPDU8000M1ITotalInputReactivePower | Total input reactive power | 总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 main i total input invalid power. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.121 | hwPDU8000M2IL1InputPhaseVoltage | L1 input voltage | L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main ii l1 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.122 | hwPDU8000M2IL2InputPhaseVoltage | L2 input voltage | L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main ii l2 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.123 | hwPDU8000M2IL3InputPhaseVoltage | L3 input voltage | L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main ii l3 input volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.124 | hwPDU8000M2IL1L2InputLineVoltage | L1-L2 input line voltage | L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main ii l1l2 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.125 | hwPDU8000M2IL2L3InputLineVoltage | L2-L3 input line voltage | L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main ii l2l3 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.126 | hwPDU8000M2IL3L1InputLineVoltage | L3-L1 input line voltage | L1-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main ii l1l3 input line volt. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.127 | hwPDU8000M2IL1InputPhaseCurrent | L1 input current | L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 main ii l1 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.128 | hwPDU8000Mains1AmbientTemperature1 | Mains 1 ambient temperature 1 | 主路1环境温度1 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 1 ambient temperature 1 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.129 | hwPDU8000Mains1AmbientTemperature2 | Mains 1 ambient temperature 2 | 主路1环境温度2 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 1 ambient temperature 2 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.130 | hwPDU8000Mains1AmbientTemperature3 | Mains 1 ambient temperature 3 | 主路1环境温度3 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 1 ambient temperature 3 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.131 | hwPDU8000Mains1AmbientTemperature4 | Mains 1 ambient temperature 4 | 主路1环境温度4 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 1 ambient temperature 4 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.132 | hwPDU8000Mains1AmbientTemperature5 | Mains 1 ambient temperature 5 | 主路1环境温度5 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 1 ambient temperature 5 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.133 | hwPDU8000Mains1AmbientTemperature6 | Mains 1 ambient temperature 6 | 主路1环境温度6 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 1 ambient temperature 6 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.134 | hwPDU8000Mains2AmbientTemperature1 | Mains 2 ambient temperature 1 | 主路2环境温度1 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 2 ambient temperature 1 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.135 | hwPDU8000Mains2AmbientTemperature2 | Mains 2 ambient temperature 2 | 主路2环境温度2 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 2 ambient temperature 2 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.136 | hwPDU8000Mains2AmbientTemperature3 | Mains 2 ambient temperature 3 | 主路2环境温度3 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Mains 2 ambient temperature 3 of the device config table for the PDU8000.Multiple: 10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.137 | hwPDU8000WhetherToSupportTemperaturePrediction | Whether to support temperature prediction | 是否支持温度预测 | 0-Read_Only | 只读 | notsupported(1), support(2), unknown(255) | [不支持=1]/[支持=2] | Whether to support temperature prediction of the device config table for the PDU8000. Value 1 indicate not supported Value 2 indicate support
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.138 | hwPDU8000Mac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.139 | hwPDU8000Mains1InputSwitchStatus | Main input 1 switch status | 1路输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 Mains 1 input switch status: Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.140 | hwPDU8000Mains1InputSwitchTripStatus | Main input 1 SPD status | 1路输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | pdu8000 Mains 1 input switch trip status: Value 1 indicates Abnormal. Value 2 indicates Normal.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.141 | hwPDU8000Mains2InputSwitchStatus | Main input 2 switch status | 2路输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 Mains 2 input switch status: Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.142 | hwPDU8000Mains2InputSwitchTripStatus | Main input 2 SPD status | 2路输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | pdu8000 Mains 2 input switch trip status: Value 1 indicates Abnormal. Value 2 indicates Normal.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.143 | hwPDU8000PhaseOpenVoltage | Phase open voltage | 系统缺相电压 | 1-Read_Write | 读写 | 0..60 | 0..60 | pdu8000 phase open voltage.SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.144 | hwPDU8000EnableHarmonicAlarm | Enable harmonic alarm | 谐波告警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | pdu8000 enable harmonic alarm. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.145 | hwPDU8000VoltageHarmonicAlarm | Voltage harmonic alarm | 电压谐波告警 | 1-Read_Write | 读写 | 10..300 | 10..300 | pdu8000 voltage harmonic alarm. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.146 | hwPDU8000CurrentHarmonicAlarm | Current harmonic alarm | 电流谐波告警 | 1-Read_Write | 读写 | 0..300 | 0..300 | pdu8000 current harmonic alarm. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.147 | hwPDU8000OverVoltage | Overvoltage | 系统过压 | 1-Read_Write | 读写 | 1050..1250 | 1050..1250 | pdu8000 overvoltage. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.148 | hwPDU8000UnderVoltage | Undervoltage | 系统欠压 | 1-Read_Write | 读写 | 750..950 | 750..950 | pdu8000 undervoltage. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.149 | hwPDU8000OverLoad | Overload | 负载过载 | 1-Read_Write | 读写 | 1000..1200 | 1000..1200 | pdu8000 overload. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.150 | hwPDU8000OverFrequency | Overfrequency | 系统频率越限 | 1-Read_Write | 读写 | 10..100 | 10..100 | pdu8000 overfrequency. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.151 | hwPDU8000LoadOvercurrentThreshold | Load overcurrent threshold | 负载电流高阈值 | 1-Read_Write | 读写 | 400..1000 | 400..1000 | pdu8000 load overcurrent threshold. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.152 | hwPDU8000LoadundercurrentThreshold | Load undercurrent threshold | 负载电流低阈值 | 1-Read_Write | 读写 | 300..800 | 300..800 | pdu8000 load undercurrent threshold. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.153 | hwPDU8000ThreePhaseCurrentImbalance | Three-phase current imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..500 | 0..500 | pdu8000 threephase current imbalance. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.154 | hwPDU8000MainsInputSwitchStatusNew | Main input switch status | 主路输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 Mains input switch status: Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.155 | hwPDU8000MainsInputSwitchTripStatusNew | Main input SPD status | 主路输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | pdu8000 Mains input switch trip status: Value 1 indicates Abnormal. Value 2 indicates Normal.
1.3.6.1.4.1.2011.6.178.1.1.9.5.1.1.156 | hwPDU8000Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.2 | hwPDU8000Running2Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.1 | hwPDU8000Running2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.2 | hwPDU8000M2IL2InputPhaseCurrent | L2 input current | L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 main ii l2 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.3 | hwPDU8000M2IL3InputPhaseCurrent | L3 input current | L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | pdu8000 main ii l3 input cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.4 | hwPDU8000M2IInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main ii input freq. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.5 | hwPDU8000M2IL1InputActivePower | L1 input active power | L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l1 input act power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.6 | hwPDU8000M2IL2InputActivePower | L2 input active power | L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l2 input act power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.7 | hwPDU8000M2IL3InputActivePower | L3 input active power | L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l3 input act power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.8 | hwPDU8000M2IL1InputApparentPower | L1 input apparent power | L1输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l1 input app power. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.9 | hwPDU8000M2IL2InputApparentPower | L2 input apparent power | L2输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l2 input app power. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.10 | hwPDU8000M2IL3InputApparentPower | L3 input apparent power | L3输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l3 input app power. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.11 | hwPDU8000M2IL1InputReactivePower | L1 input reactive power | L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l1 input invalid power. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.12 | hwPDU8000M2IL2InputReactivePower | L2 input reactive power | L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l2 input invalid power. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.13 | hwPDU8000M2IL3InputReactivePower | L3 input reactive power | L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | pdu8000 main ii l3 input invalid power. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.14 | hwPDU8000M2IL1InputPowerFactor | L1 input power factor | L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 main ii l1 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.15 | hwPDU8000M2IL2InputPowerFactor | L2 input power factor | L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 main ii l2 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.16 | hwPDU8000M2IL3InputPowerFactor | L3 input power factor | L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | pdu8000 main ii l3 input power factor. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.17 | hwPDU8000M2IInputActiveElectricEnergy | Input active electric energy | 输入有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 main ii input act energy. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.18 | hwPDU8000M2IL1InputPowerLoadRate | L1 input power load rate | L1输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 main ii l1 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.19 | hwPDU8000M2IL2InputPowerLoadRate | L2 input power load rate | L2输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 main ii l2 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.20 | hwPDU8000M2IL3InputPowerLoadRate | L3 input power load rate | L3输入电源负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 main ii l3 input power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.21 | hwPDU8000M2IInputNWireCurrent | Input neutral wire current | 输入N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 main ii input n line cur. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.22 | hwPDU8000M2IL1THDuRate | L1 THDu | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main ii l1 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.23 | hwPDU8000M2IL2THDuRate | L2 THDu | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main ii l2 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.24 | hwPDU8000M2IL3THDuRate | L3 THDu | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main ii l3 volt harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.25 | hwPDU8000M2IL1THDiRate | L1 THDi | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main ii l1 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.26 | hwPDU8000M2IL2THDiRate | L2 THDi | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main ii l2 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.27 | hwPDU8000M2IL3THDiRate | L3 THDi | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | pdu8000 main ii l3 cur harmonic. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.28 | hwPDU8000M2ITotalInputActivePower | Total input active power | 总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 main ii total input act power. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.29 | hwPDU8000M2ITotalInputApparentPower | Total input apparent power | 总输入视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 main ii total input app power. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.30 | hwPDU8000M2ITotalInputReactivePower | Total input reactive power | 总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | pdu8000 main ii total input invalid power. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.31 | hwPDU8000QF1OutputPhaseCurrent | QF1 Output current(L1) | QF1 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf1 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.32 | hwPDU8000QF2OutputPhaseCurrent | QF2 Output current(L2) | QF2 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf2 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.33 | hwPDU8000QF3OutputPhaseCurrent | QF3 Output current(L3) | QF3 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf3 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.34 | hwPDU8000QF4OutputPhaseCurrent | QF4 Output current(L1) | QF4 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf4 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.35 | hwPDU8000QF5OutputPhaseCurrent | QF5 Output current(L2) | QF5 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf5 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.36 | hwPDU8000QF6OutputPhaseCurrent | QF6 Output current(L3) | QF6 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf6 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.37 | hwPDU8000QF7OutputPhaseCurrent | QF7 Output current(L1) | QF7 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf7 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.38 | hwPDU8000QF8OutputPhaseCurrent | QF8 Output current(L2) | QF8 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf8 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.39 | hwPDU8000QF9OutputPhaseCurrent | QF9 Output current(L3) | QF9 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf9 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.40 | hwPDU8000QF10OutputPhaseCurrent | QF10 Output current(L1) | QF10 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf10 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.41 | hwPDU8000QF11OutputPhaseCurrent | QF11 Output current(L2) | QF11 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf11 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.42 | hwPDU8000QF12OutputPhaseCurrent | QF12 Output current(L3) | QF12 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf12 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.43 | hwPDU8000QF13OutputPhaseCurrent | QF13 Output current(L1) | QF13 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf13 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.44 | hwPDU8000QF14OutputPhaseCurrent | QF14 Output current(L2) | QF14 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf14 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.45 | hwPDU8000QF15OutputPhaseCurrent | QF15 Output current(L3) | QF15 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf15 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.46 | hwPDU8000QF16OutputPhaseCurrent | QF16 Output current(L1) | QF16 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf16 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.47 | hwPDU8000QF17OutputPhaseCurrent | QF17 Output current(L2) | QF17 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf17 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.48 | hwPDU8000QF18OutputPhaseCurrent | QF18 Output current(L3) | QF18 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf18 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.49 | hwPDU8000QF19OutputPhaseCurrent | QF19 Output current(L1) | QF19 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf19 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.50 | hwPDU8000QF20OutputPhaseCurrent | QF20 Output current(L2) | QF20 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf20 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.51 | hwPDU8000QF21OutputPhaseCurrent | QF21 Output current(L3) | QF21 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf21 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.52 | hwPDU8000QF22OutputPhaseCurrent | QF22 Output current(L1) | QF22 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf22 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.53 | hwPDU8000QF23OutputPhaseCurrent | QF23 Output current(L2) | QF23 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf23 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.54 | hwPDU8000QF24OutputPhaseCurrent | QF24 Output current(L3) | QF24 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf24 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.55 | hwPDU8000QF25OutputPhaseCurrent | QF25 Output current(L1) | QF25 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf25 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.56 | hwPDU8000QF26OutputPhaseCurrent | QF26 Output current(L2) | QF26 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf26 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.57 | hwPDU8000QF27OutputPhaseCurrent | QF27 Output current(L3) | QF27 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf27 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.58 | hwPDU8000QF28OutputPhaseCurrent | QF28 Output current(L1) | QF28 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf28 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.59 | hwPDU8000QF29OutputPhaseCurrent | QF29 Output current(L2) | QF29 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf29 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.60 | hwPDU8000QF30OutputPhaseCurrent | QF30 Output current(L3) | QF30 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf30 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.61 | hwPDU8000QF31OutputPhaseCurrent | QF31 Output current(L1) | QF31 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf31 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.62 | hwPDU8000QF32OutputPhaseCurrent | QF32 Output current(L2) | QF32 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf32 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.63 | hwPDU8000QF33OutputPhaseCurrent | QF33 Output current(L3) | QF33 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf33 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.64 | hwPDU8000QF34OutputPhaseCurrent | QF34 Output current(L1) | QF34 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf34 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.65 | hwPDU8000QF35OutputPhaseCurrent | QF35 Output current(L2) | QF35 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf35 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.66 | hwPDU8000QF36OutputPhaseCurrent | QF36 Output current(L3) | QF36 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf36 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.67 | hwPDU8000QF37OutputPhaseCurrent | QF37 Output current(L1) | QF37 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf37 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.68 | hwPDU8000QF38OutputPhaseCurrent | QF38 Output current(L2) | QF38 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf38 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.69 | hwPDU8000QF39OutputPhaseCurrent | QF39 Output current(L3) | QF39 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf39 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.70 | hwPDU8000QF40OutputPhaseCurrent | QF40 Output current(L1) | QF40 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf40 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.71 | hwPDU8000QF41OutputPhaseCurrent | QF41 Output current(L2) | QF41 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf41 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.72 | hwPDU8000QF42OutputPhaseCurrent | QF42 Output current(L3) | QF42 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf42 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.73 | hwPDU8000QF43OutputPhaseCurrent | QF43 Output current(L1) | QF43 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf43 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.74 | hwPDU8000QF44OutputPhaseCurrent | QF44 Output current(L2) | QF44 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf44 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.75 | hwPDU8000QF45OutputPhaseCurrent | QF45 Output current(L3) | QF45 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf45 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.76 | hwPDU8000QF46OutputPhaseCurrent | QF46 Output current(L1) | QF46 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf46 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.77 | hwPDU8000QF47OutputPhaseCurrent | QF47 Output current(L2) | QF47 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf47 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.78 | hwPDU8000QF48OutputPhaseCurrent | QF48 Output current(L3) | QF48 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf48 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.79 | hwPDU8000QF49OutputPhaseCurrent | QF49 Output current(L1) | QF49 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf49 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.80 | hwPDU8000QF50OutputPhaseCurrent | QF50 Output current(L2) | QF50 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf50 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.81 | hwPDU8000QF51OutputPhaseCurrent | QF51 Output current(L3) | QF51 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf51 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.82 | hwPDU8000QF52OutputPhaseCurrent | QF52 Output current(L1) | QF52 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf52 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.83 | hwPDU8000QF53OutputPhaseCurrent | QF53 Output current(L2) | QF53 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf53 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.84 | hwPDU8000QF54OutputPhaseCurrent | QF54 Output current(L3) | QF54 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf54 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.85 | hwPDU8000QF55OutputPhaseCurrent | QF55 Output current(L1) | QF55 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf55 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.86 | hwPDU8000QF56OutputPhaseCurrent | QF56 Output current(L2) | QF56 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf56 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.87 | hwPDU8000QF57OutputPhaseCurrent | QF57 Output current(L3) | QF57 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf57 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.88 | hwPDU8000QF58OutputPhaseCurrent | QF58 Output current(L1) | QF58 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf58 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.89 | hwPDU8000QF59OutputPhaseCurrent | QF59 Output current(L2) | QF59 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf59 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.90 | hwPDU8000QF60OutputPhaseCurrent | QF60 Output current(L3) | QF60 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf60 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.91 | hwPDU8000QF61OutputPhaseCurrent | QF61 Output current(L1) | QF61 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf61 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.92 | hwPDU8000QF62OutputPhaseCurrent | QF62 Output current(L2) | QF62 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf62 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.93 | hwPDU8000QF63OutputPhaseCurrent | QF63 Output current(L3) | QF63 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf63 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.94 | hwPDU8000QF64OutputPhaseCurrent | QF64 Output current(L1) | QF64 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf64 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.95 | hwPDU8000QF65OutputPhaseCurrent | QF65 Output current(L2) | QF65 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf65 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.96 | hwPDU8000QF66OutputPhaseCurrent | QF66 Output current(L3) | QF66 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf66 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.97 | hwPDU8000QF67OutputPhaseCurrent | QF67 Output current(L1) | QF67 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf67 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.98 | hwPDU8000QF68OutputPhaseCurrent | QF68 Output current(L2) | QF68 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf68 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.99 | hwPDU8000QF69OutputPhaseCurrent | QF69 Output current(L3) | QF69 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf69 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.100 | hwPDU8000QF70OutputPhaseCurrent | QF70 Output current(L1) | QF70 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf70 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.101 | hwPDU8000QF71OutputPhaseCurrent | QF71 Output current(L2) | QF71 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf71 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.102 | hwPDU8000QF72OutputPhaseCurrent | QF72 Output current(L3) | QF72 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf72 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.103 | hwPDU8000QF73OutputPhaseCurrent | QF73 Output current(L1) | QF73 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf73 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.104 | hwPDU8000QF74OutputPhaseCurrent | QF74 Output current(L2) | QF74 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf74 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.105 | hwPDU8000QF75OutputPhaseCurrent | QF75 Output current(L3) | QF75 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf75 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.106 | hwPDU8000QF76OutputPhaseCurrent | QF76 Output current(L1) | QF76 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf76 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.107 | hwPDU8000QF77OutputPhaseCurrent | QF77 Output current(L2) | QF77 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf77 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.108 | hwPDU8000QF78OutputPhaseCurrent | QF78 Output current(L3) | QF78 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf78 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.109 | hwPDU8000QF79OutputPhaseCurrent | QF79 Output current(L1) | QF79 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf79 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.110 | hwPDU8000QF80OutputPhaseCurrent | QF80 Output current(L2) | QF80 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf80 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.111 | hwPDU8000QF81OutputPhaseCurrent | QF81 Output current(L3) | QF81 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf81 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.112 | hwPDU8000QF82OutputPhaseCurrent | QF82 Output current(L1) | QF82 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf82 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.113 | hwPDU8000QF83OutputPhaseCurrent | QF83 Output current(L2) | QF83 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf83 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.114 | hwPDU8000QF84OutputPhaseCurrent | QF84 Output current(L3) | QF84 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf84 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.115 | hwPDU8000QF85OutputPhaseCurrent | QF85 Output current(L1) | QF85 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf85 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.116 | hwPDU8000QF86OutputPhaseCurrent | QF86 Output current(L2) | QF86 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf86 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.117 | hwPDU8000QF87OutputPhaseCurrent | QF87 Output current(L3) | QF87 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf87 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.118 | hwPDU8000QF88OutputPhaseCurrent | QF88 Output current(L1) | QF88 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf88 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.119 | hwPDU8000QF89OutputPhaseCurrent | QF89 Output current(L2) | QF89 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf89 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.120 | hwPDU8000QF90OutputPhaseCurrent | QF90 Output current(L3) | QF90 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf90 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.121 | hwPDU8000QF91OutputPhaseCurrent | QF91 Output current(L1) | QF91 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf91 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.122 | hwPDU8000QF92OutputPhaseCurrent | QF92 Output current(L2) | QF92 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf92 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.123 | hwPDU8000QF93OutputPhaseCurrent | QF93 Output current(L3) | QF93 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf93 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.124 | hwPDU8000QF94OutputPhaseCurrent | QF94 Output current(L1) | QF94 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf94 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.125 | hwPDU8000QF95OutputPhaseCurrent | QF95 Output current(L2) | QF95 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf95 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.126 | hwPDU8000QF96OutputPhaseCurrent | QF96 Output current(L3) | QF96 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf96 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.127 | hwPDU8000QF97OutputPhaseCurrent | QF97 Output current(L1) | QF97 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf97 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.2.1.128 | hwPDU8000Running2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.3 | hwPDU8000Running3Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.1 | hwPDU8000Running3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.2 | hwPDU8000QF98OutputPhaseCurrent | QF98 Output current(L2) | QF98 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf98 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.3 | hwPDU8000QF99OutputPhaseCurrent | QF99 Output current(L3) | QF99 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf99 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.4 | hwPDU8000QF100OutputPhaseCurrent | QF100 Output current(L1) | QF100 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf100 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.5 | hwPDU8000QF101OutputPhaseCurrent | QF101 Output current(L2) | QF101 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf101 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.6 | hwPDU8000QF102OutputPhaseCurrent | QF102 Output current(L3) | QF102 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf102 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.7 | hwPDU8000QF103OutputPhaseCurrent | QF103 Output current(L1) | QF103 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf103 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.8 | hwPDU8000QF104OutputPhaseCurrent | QF104 Output current(L2) | QF104 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf104 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.9 | hwPDU8000QF105OutputPhaseCurrent | QF105 Output current(L3) | QF105 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf105 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.10 | hwPDU8000QF106OutputPhaseCurrent | QF106 Output current(L1) | QF106 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf106 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.11 | hwPDU8000QF107OutputPhaseCurrent | QF107 Output current(L2) | QF107 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf107 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.12 | hwPDU8000QF108OutputPhaseCurrent | QF108 Output current(L3) | QF108 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf108 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.13 | hwPDU8000QF109OutputPhaseCurrent | QF109 Output current(L1) | QF109 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf109 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.14 | hwPDU8000QF110OutputPhaseCurrent | QF110 Output current(L2) | QF110 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf110 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.15 | hwPDU8000QF111OutputPhaseCurrent | QF111 Output current(L3) | QF111 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf111 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.16 | hwPDU8000QF112OutputPhaseCurrent | QF112 Output current(L1) | QF112 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf112 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.17 | hwPDU8000QF113OutputPhaseCurrent | QF113 Output current(L2) | QF113 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf113 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.18 | hwPDU8000QF114OutputPhaseCurrent | QF114 Output current(L3) | QF114 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf114 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.19 | hwPDU8000QF115OutputPhaseCurrent | QF115 Output current(L1) | QF115 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf115 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.20 | hwPDU8000QF116OutputPhaseCurrent | QF116 Output current(L2) | QF116 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf116 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.21 | hwPDU8000QF117OutputPhaseCurrent | QF117 Output current(L3) | QF117 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf117 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.22 | hwPDU8000QF118OutputPhaseCurrent | QF118 Output current(L1) | QF118 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf118 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.23 | hwPDU8000QF119OutputPhaseCurrent | QF119 Output current(L2) | QF119 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf119 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.24 | hwPDU8000QF120OutputPhaseCurrent | QF120 Output current(L3) | QF120 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf120 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.25 | hwPDU8000QF121OutputPhaseCurrent | QF121 Output current(L1) | QF121 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf121 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.26 | hwPDU8000QF122OutputPhaseCurrent | QF122 Output current(L2) | QF122 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf122 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.27 | hwPDU8000QF123OutputPhaseCurrent | QF123 Output current(L3) | QF123 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf123 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.28 | hwPDU8000QF124OutputPhaseCurrent | QF124 Output current(L1) | QF124 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf124 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.29 | hwPDU8000QF125OutputPhaseCurrent | QF125 Output current(L2) | QF125 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf125 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.30 | hwPDU8000QF126OutputPhaseCurrent | QF126 Output current(L3) | QF126 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf126 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.31 | hwPDU8000QF127OutputPhaseCurrent | QF127 Output current(L1) | QF127 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf127 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.32 | hwPDU8000QF128OutputPhaseCurrent | QF128 Output current(L2) | QF128 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf128 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.33 | hwPDU8000QF129OutputPhaseCurrent | QF129 Output current(L3) | QF129 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf129 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.34 | hwPDU8000QF130OutputPhaseCurrent | QF130 Output current(L1) | QF130 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf130 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.35 | hwPDU8000QF131OutputPhaseCurrent | QF131 Output current(L2) | QF131 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf131 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.36 | hwPDU8000QF132OutputPhaseCurrent | QF132 Output current(L3) | QF132 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf132 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.37 | hwPDU8000QF133OutputPhaseCurrent | QF133 Output current(L1) | QF133 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf133 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.38 | hwPDU8000QF134OutputPhaseCurrent | QF134 Output current(L2) | QF134 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf134 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.39 | hwPDU8000QF135OutputPhaseCurrent | QF135 Output current(L3) | QF135 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf135 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.40 | hwPDU8000QF136OutputPhaseCurrent | QF136 Output current(L1) | QF136 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf136 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.41 | hwPDU8000QF137OutputPhaseCurrent | QF137 Output current(L2) | QF137 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf137 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.42 | hwPDU8000QF138OutputPhaseCurrent | QF138 Output current(L3) | QF138 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf138 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.43 | hwPDU8000QF139OutputPhaseCurrent | QF139 Output current(L1) | QF139 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf139 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.44 | hwPDU8000QF140OutputPhaseCurrent | QF140 Output current(L2) | QF140 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf140 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.45 | hwPDU8000QF141OutputPhaseCurrent | QF141 Output current(L3) | QF141 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf141 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.46 | hwPDU8000QF142OutputPhaseCurrent | QF142 Output current(L1) | QF142 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf142 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.47 | hwPDU8000QF143OutputPhaseCurrent | QF143 Output current(L2) | QF143 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf143 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.48 | hwPDU8000QF144OutputPhaseCurrent | QF144 Output current(L3) | QF144 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 qf144 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.49 | hwPDU8000QF1OutputActiveElectricEnergy | QF1 Output active electric energy(L1) | QF1 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf1 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.50 | hwPDU8000QF2OutputActiveElectricEnergy | QF2 Output active electric energy(L2) | QF2 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf2 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.51 | hwPDU8000QF3OutputActiveElectricEnergy | QF3 Output active electric energy(L3) | QF3 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf3 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.52 | hwPDU8000QF4OutputActiveElectricEnergy | QF4 Output active electric energy(L1) | QF4 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf4 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.53 | hwPDU8000QF5OutputActiveElectricEnergy | QF5 Output active electric energy(L2) | QF5 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf5 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.54 | hwPDU8000QF6OutputActiveElectricEnergy | QF6 Output active electric energy(L3) | QF6 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf6 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.55 | hwPDU8000QF7OutputActiveElectricEnergy | QF7 Output active electric energy(L1) | QF7 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf7 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.56 | hwPDU8000QF8OutputActiveElectricEnergy | QF8 Output active electric energy(L2) | QF8 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf8 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.57 | hwPDU8000QF9OutputActiveElectricEnergy | QF9 Output active electric energy(L3) | QF9 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf9 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.58 | hwPDU8000QF10OutputActiveElectricEnergy | QF10 Output active electric energy(L1) | QF10 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf10 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.59 | hwPDU8000QF11OutputActiveElectricEnergy | QF11 Output active electric energy(L2) | QF11 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf11 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.60 | hwPDU8000QF12OutputActiveElectricEnergy | QF12 Output active electric energy(L3) | QF12 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf12 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.61 | hwPDU8000QF13OutputActiveElectricEnergy | QF13 Output active electric energy(L1) | QF13 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf13 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.62 | hwPDU8000QF14OutputActiveElectricEnergy | QF14 Output active electric energy(L2) | QF14 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf14 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.63 | hwPDU8000QF15OutputActiveElectricEnergy | QF15 Output active electric energy(L3) | QF15 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf15 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.64 | hwPDU8000QF16OutputActiveElectricEnergy | QF16 Output active electric energy(L1) | QF16 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf16 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.65 | hwPDU8000QF17OutputActiveElectricEnergy | QF17 Output active electric energy(L2) | QF17 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf17 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.66 | hwPDU8000QF18OutputActiveElectricEnergy | QF18 Output active electric energy(L3) | QF18 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf18 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.67 | hwPDU8000QF19OutputActiveElectricEnergy | QF19 Output active electric energy(L1) | QF19 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf19 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.68 | hwPDU8000QF20OutputActiveElectricEnergy | QF20 Output active electric energy(L2) | QF20 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf20 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.69 | hwPDU8000QF21OutputActiveElectricEnergy | QF21 Output active electric energy(L3) | QF21 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf21 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.70 | hwPDU8000QF22OutputActiveElectricEnergy | QF22 Output active electric energy(L1) | QF22 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf22 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.71 | hwPDU8000QF23OutputActiveElectricEnergy | QF23 Output active electric energy(L2) | QF23 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf23 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.72 | hwPDU8000QF24OutputActiveElectricEnergy | QF24 Output active electric energy(L3) | QF24 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf24 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.73 | hwPDU8000QF25OutputActiveElectricEnergy | QF25 Output active electric energy(L1) | QF25 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf25 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.74 | hwPDU8000QF26OutputActiveElectricEnergy | QF26 Output active electric energy(L2) | QF26 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf26 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.75 | hwPDU8000QF27OutputActiveElectricEnergy | QF27 Output active electric energy(L3) | QF27 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf27 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.76 | hwPDU8000QF28OutputActiveElectricEnergy | QF28 Output active electric energy(L1) | QF28 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf28 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.77 | hwPDU8000QF29OutputActiveElectricEnergy | QF29 Output active electric energy(L2) | QF29 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf29 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.78 | hwPDU8000QF30OutputActiveElectricEnergy | QF30 Output active electric energy(L3) | QF30 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf30 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.79 | hwPDU8000QF31OutputActiveElectricEnergy | QF31 Output active electric energy(L1) | QF31 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf31 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.80 | hwPDU8000QF32OutputActiveElectricEnergy | QF32 Output active electric energy(L2) | QF32 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf32 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.81 | hwPDU8000QF33OutputActiveElectricEnergy | QF33 Output active electric energy(L3) | QF33 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf33 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.82 | hwPDU8000QF34OutputActiveElectricEnergy | QF34 Output active electric energy(L1) | QF34 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf34 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.83 | hwPDU8000QF35OutputActiveElectricEnergy | QF35 Output active electric energy(L2) | QF35 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf35 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.84 | hwPDU8000QF36OutputActiveElectricEnergy | QF36 Output active electric energy(L3) | QF36 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf36 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.85 | hwPDU8000QF37OutputActiveElectricEnergy | QF37 Output active electric energy(L1) | QF37 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf37 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.86 | hwPDU8000QF38OutputActiveElectricEnergy | QF38 Output active electric energy(L2) | QF38 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf38 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.87 | hwPDU8000QF39OutputActiveElectricEnergy | QF39 Output active electric energy(L3) | QF39 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf39 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.88 | hwPDU8000QF40OutputActiveElectricEnergy | QF40 Output active electric energy(L1) | QF40 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf40 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.89 | hwPDU8000QF41OutputActiveElectricEnergy | QF41 Output active electric energy(L2) | QF41 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf41 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.90 | hwPDU8000QF42OutputActiveElectricEnergy | QF42 Output active electric energy(L3) | QF42 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf42 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.91 | hwPDU8000QF43OutputActiveElectricEnergy | QF43 Output active electric energy(L1) | QF43 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf43 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.92 | hwPDU8000QF44OutputActiveElectricEnergy | QF44 Output active electric energy(L2) | QF44 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf44 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.93 | hwPDU8000QF45OutputActiveElectricEnergy | QF45 Output active electric energy(L3) | QF45 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf45 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.94 | hwPDU8000QF46OutputActiveElectricEnergy | QF46 Output active electric energy(L1) | QF46 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf46 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.95 | hwPDU8000QF47OutputActiveElectricEnergy | QF47 Output active electric energy(L2) | QF47 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf47 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.96 | hwPDU8000QF48OutputActiveElectricEnergy | QF48 Output active electric energy(L3) | QF48 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf48 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.97 | hwPDU8000QF49OutputActiveElectricEnergy | QF49 Output active electric energy(L1) | QF49 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf49 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.98 | hwPDU8000QF50OutputActiveElectricEnergy | QF50 Output active electric energy(L2) | QF50 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf50 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.99 | hwPDU8000QF51OutputActiveElectricEnergy | QF51 Output active electric energy(L3) | QF51 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf51 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.100 | hwPDU8000QF52OutputActiveElectricEnergy | QF52 Output active electric energy(L1) | QF52 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf52 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.101 | hwPDU8000QF53OutputActiveElectricEnergy | QF53 Output active electric energy(L2) | QF53 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf53 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.102 | hwPDU8000QF54OutputActiveElectricEnergy | QF54 Output active electric energy(L3) | QF54 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf54 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.103 | hwPDU8000QF55OutputActiveElectricEnergy | QF55 Output active electric energy(L1) | QF55 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf55 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.104 | hwPDU8000QF56OutputActiveElectricEnergy | QF56 Output active electric energy(L2) | QF56 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf56 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.105 | hwPDU8000QF57OutputActiveElectricEnergy | QF57 Output active electric energy(L3) | QF57 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf57 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.106 | hwPDU8000QF58OutputActiveElectricEnergy | QF58 Output active electric energy(L1) | QF58 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf58 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.107 | hwPDU8000QF59OutputActiveElectricEnergy | QF59 Output active electric energy(L2) | QF59 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf59 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.108 | hwPDU8000QF60OutputActiveElectricEnergy | QF60 Output active electric energy(L3) | QF60 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf60 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.109 | hwPDU8000QF61OutputActiveElectricEnergy | QF61 Output active electric energy(L1) | QF61 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf61 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.110 | hwPDU8000QF62OutputActiveElectricEnergy | QF62 Output active electric energy(L2) | QF62 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf62 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.111 | hwPDU8000QF63OutputActiveElectricEnergy | QF63 Output active electric energy(L3) | QF63 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf63 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.112 | hwPDU8000QF64OutputActiveElectricEnergy | QF64 Output active electric energy(L1) | QF64 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf64 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.113 | hwPDU8000QF65OutputActiveElectricEnergy | QF65 Output active electric energy(L2) | QF65 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf65 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.114 | hwPDU8000QF66OutputActiveElectricEnergy | QF66 Output active electric energy(L3) | QF66 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf66 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.115 | hwPDU8000QF67OutputActiveElectricEnergy | QF67 Output active electric energy(L1) | QF67 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf67 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.116 | hwPDU8000QF68OutputActiveElectricEnergy | QF68 Output active electric energy(L2) | QF68 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf68 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.117 | hwPDU8000QF69OutputActiveElectricEnergy | QF69 Output active electric energy(L3) | QF69 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf69 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.118 | hwPDU8000QF70OutputActiveElectricEnergy | QF70 Output active electric energy(L1) | QF70 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf70 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.119 | hwPDU8000QF71OutputActiveElectricEnergy | QF71 Output active electric energy(L2) | QF71 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf71 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.120 | hwPDU8000QF72OutputActiveElectricEnergy | QF72 Output active electric energy(L3) | QF72 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf72 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.121 | hwPDU8000QF73OutputActiveElectricEnergy | QF73 Output active electric energy(L1) | QF73 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf73 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.122 | hwPDU8000QF74OutputActiveElectricEnergy | QF74 Output active electric energy(L2) | QF74 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf74 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.123 | hwPDU8000QF75OutputActiveElectricEnergy | QF75 Output active electric energy(L3) | QF75 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf75 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.124 | hwPDU8000QF76OutputActiveElectricEnergy | QF76 Output active electric energy(L1) | QF76 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf76 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.125 | hwPDU8000QF77OutputActiveElectricEnergy | QF77 Output active electric energy(L2) | QF77 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf77 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.126 | hwPDU8000QF78OutputActiveElectricEnergy | QF78 Output active electric energy(L3) | QF78 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf78 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.127 | hwPDU8000QF79OutputActiveElectricEnergy | QF79 Output active electric energy(L1) | QF79 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf79 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.3.1.128 | hwPDU8000Running3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.4 | hwPDU8000Running4Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.1 | hwPDU8000Running4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.2 | hwPDU8000QF80OutputActiveElectricEnergy | QF80 Output active electric energy(L2) | QF80 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf80 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.3 | hwPDU8000QF81OutputActiveElectricEnergy | QF81 Output active electric energy(L3) | QF81 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf81 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.4 | hwPDU8000QF82OutputActiveElectricEnergy | QF82 Output active electric energy(L1) | QF82 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf82 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.5 | hwPDU8000QF83OutputActiveElectricEnergy | QF83 Output active electric energy(L2) | QF83 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf83 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.6 | hwPDU8000QF84OutputActiveElectricEnergy | QF84 Output active electric energy(L3) | QF84 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf84 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.7 | hwPDU8000QF85OutputActiveElectricEnergy | QF85 Output active electric energy(L1) | QF85 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf85 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.8 | hwPDU8000QF86OutputActiveElectricEnergy | QF86 Output active electric energy(L2) | QF86 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf86 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.9 | hwPDU8000QF87OutputActiveElectricEnergy | QF87 Output active electric energy(L3) | QF87 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf87 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.10 | hwPDU8000QF88OutputActiveElectricEnergy | QF88 Output active electric energy(L1) | QF88 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf88 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.11 | hwPDU8000QF89OutputActiveElectricEnergy | QF89 Output active electric energy(L2) | QF89 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf89 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.12 | hwPDU8000QF90OutputActiveElectricEnergy | QF90 Output active electric energy(L3) | QF90 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf90 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.13 | hwPDU8000QF91OutputActiveElectricEnergy | QF91 Output active electric energy(L1) | QF91 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf91 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.14 | hwPDU8000QF92OutputActiveElectricEnergy | QF92 Output active electric energy(L2) | QF92 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf92 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.15 | hwPDU8000QF93OutputActiveElectricEnergy | QF93 Output active electric energy(L3) | QF93 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf93 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.16 | hwPDU8000QF94OutputActiveElectricEnergy | QF94 Output active electric energy(L1) | QF94 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf94 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.17 | hwPDU8000QF95OutputActiveElectricEnergy | QF95 Output active electric energy(L2) | QF95 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf95 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.18 | hwPDU8000QF96OutputActiveElectricEnergy | QF96 Output active electric energy(L3) | QF96 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf96 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.19 | hwPDU8000QF97OutputActiveElectricEnergy | QF97 Output active electric energy(L1) | QF97 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf97 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.20 | hwPDU8000QF98OutputActiveElectricEnergy | QF98 Output active electric energy(L2) | QF98 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf98 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.21 | hwPDU8000QF99OutputActiveElectricEnergy | QF99 Output active electric energy(L3) | QF99 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf99 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.22 | hwPDU8000QF100OutputActiveElectricEnergy | QF100 Output active electric energy(L1) | QF100 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf100 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.23 | hwPDU8000QF101OutputActiveElectricEnergy | QF101 Output active electric energy(L2) | QF101 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf101 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.24 | hwPDU8000QF102OutputActiveElectricEnergy | QF102 Output active electric energy(L3) | QF102 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf102 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.25 | hwPDU8000QF103OutputActiveElectricEnergy | QF103 Output active electric energy(L1) | QF103 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf103 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.26 | hwPDU8000QF104OutputActiveElectricEnergy | QF104 Output active electric energy(L2) | QF104 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf104 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.27 | hwPDU8000QF105OutputActiveElectricEnergy | QF105 Output active electric energy(L3) | QF105 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf105 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.28 | hwPDU8000QF106OutputActiveElectricEnergy | QF106 Output active electric energy(L1) | QF106 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf106 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.29 | hwPDU8000QF107OutputActiveElectricEnergy | QF107 Output active electric energy(L2) | QF107 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf107 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.30 | hwPDU8000QF108OutputActiveElectricEnergy | QF108 Output active electric energy(L3) | QF108 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf108 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.31 | hwPDU8000QF109OutputActiveElectricEnergy | QF109 Output active electric energy(L1) | QF109 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf109 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.32 | hwPDU8000QF110OutputActiveElectricEnergy | QF110 Output active electric energy(L2) | QF110 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf110 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.33 | hwPDU8000QF111OutputActiveElectricEnergy | QF111 Output active electric energy(L3) | QF111 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf111 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.34 | hwPDU8000QF112OutputActiveElectricEnergy | QF112 Output active electric energy(L1) | QF112 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf112 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.35 | hwPDU8000QF113OutputActiveElectricEnergy | QF113 Output active electric energy(L2) | QF113 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf113 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.36 | hwPDU8000QF114OutputActiveElectricEnergy | QF114 Output active electric energy(L3) | QF114 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf114 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.37 | hwPDU8000QF115OutputActiveElectricEnergy | QF115 Output active electric energy(L1) | QF115 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf115 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.38 | hwPDU8000QF116OutputActiveElectricEnergy | QF116 Output active electric energy(L2) | QF116 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf116 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.39 | hwPDU8000QF117OutputActiveElectricEnergy | QF117 Output active electric energy(L3) | QF117 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf117 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.40 | hwPDU8000QF118OutputActiveElectricEnergy | QF118 Output active electric energy(L1) | QF118 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf118 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.41 | hwPDU8000QF119OutputActiveElectricEnergy | QF119 Output active electric energy(L2) | QF119 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf119 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.42 | hwPDU8000QF120OutputActiveElectricEnergy | QF120 Output active electric energy(L3) | QF120 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf120 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.43 | hwPDU8000QF121OutputActiveElectricEnergy | QF121 Output active electric energy(L1) | QF121 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf121 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.44 | hwPDU8000QF122OutputActiveElectricEnergy | QF122 Output active electric energy(L2) | QF122 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf122 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.45 | hwPDU8000QF123OutputActiveElectricEnergy | QF123 Output active electric energy(L3) | QF123 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf123 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.46 | hwPDU8000QF124OutputActiveElectricEnergy | QF124 Output active electric energy(L1) | QF124 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf124 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.47 | hwPDU8000QF125OutputActiveElectricEnergy | QF125 Output active electric energy(L2) | QF125 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf125 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.48 | hwPDU8000QF126OutputActiveElectricEnergy | QF126 Output active electric energy(L3) | QF126 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf126 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.49 | hwPDU8000QF127OutputActiveElectricEnergy | QF127 Output active electric energy(L1) | QF127 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf127 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.50 | hwPDU8000QF128OutputActiveElectricEnergy | QF128 Output active electric energy(L2) | QF128 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf128 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.51 | hwPDU8000QF129OutputActiveElectricEnergy | QF129 Output active electric energy(L3) | QF129 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf129 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.52 | hwPDU8000QF130OutputActiveElectricEnergy | QF130 Output active electric energy(L1) | QF130 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf130 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.53 | hwPDU8000QF131OutputActiveElectricEnergy | QF131 Output active electric energy(L2) | QF131 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf131 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.54 | hwPDU8000QF132OutputActiveElectricEnergy | QF132 Output active electric energy(L3) | QF132 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf132 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.55 | hwPDU8000QF133OutputActiveElectricEnergy | QF133 Output active electric energy(L1) | QF133 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf133 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.56 | hwPDU8000QF134OutputActiveElectricEnergy | QF134 Output active electric energy(L2) | QF134 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf134 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.57 | hwPDU8000QF135OutputActiveElectricEnergy | QF135 Output active electric energy(L3) | QF135 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf135 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.58 | hwPDU8000QF136OutputActiveElectricEnergy | QF136 Output active electric energy(L1) | QF136 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf136 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.59 | hwPDU8000QF137OutputActiveElectricEnergy | QF137 Output active electric energy(L2) | QF137 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf137 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.60 | hwPDU8000QF138OutputActiveElectricEnergy | QF138 Output active electric energy(L3) | QF138 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf138 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.61 | hwPDU8000QF139OutputActiveElectricEnergy | QF139 Output active electric energy(L1) | QF139 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf139 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.62 | hwPDU8000QF140OutputActiveElectricEnergy | QF140 Output active electric energy(L2) | QF140 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf140 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.63 | hwPDU8000QF141OutputActiveElectricEnergy | QF141 Output active electric energy(L3) | QF141 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf141 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.64 | hwPDU8000QF142OutputActiveElectricEnergy | QF142 Output active electric energy(L1) | QF142 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf142 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.65 | hwPDU8000QF143OutputActiveElectricEnergy | QF143 Output active electric energy(L2) | QF143 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf143 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.66 | hwPDU8000QF144OutputActiveElectricEnergy | QF144 Output active electric energy(L3) | QF144 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 qf144 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.67 | hwPDU80001QF1OutputPhaseCurrent | 1QF1 Output current(L1) | 1QF1 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf1 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.68 | hwPDU80001QF2OutputPhaseCurrent | 1QF2 Output current(L2) | 1QF2 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf2 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.69 | hwPDU80001QF3OutputPhaseCurrent | 1QF3 Output current(L3) | 1QF3 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf3 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.70 | hwPDU80001QF4OutputPhaseCurrent | 1QF4 Output current(L1) | 1QF4 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf4 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.71 | hwPDU80001QF5OutputPhaseCurrent | 1QF5 Output current(L2) | 1QF5 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf5 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.72 | hwPDU80001QF6OutputPhaseCurrent | 1QF6 Output current(L3) | 1QF6 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf6 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.73 | hwPDU80001QF7OutputPhaseCurrent | 1QF7 Output current(L1) | 1QF7 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf7 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.74 | hwPDU80001QF8OutputPhaseCurrent | 1QF8 Output current(L2) | 1QF8 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf8 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.75 | hwPDU80001QF9OutputPhaseCurrent | 1QF9 Output current(L3) | 1QF9 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf9 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.76 | hwPDU80001QF10OutputPhaseCurrent | 1QF10 Output current(L1) | 1QF10 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf10 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.77 | hwPDU80001QF11OutputPhaseCurrent | 1QF11 Output current(L2) | 1QF11 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf11 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.78 | hwPDU80001QF12OutputPhaseCurrent | 1QF12 Output current(L3) | 1QF12 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf12 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.79 | hwPDU80001QF13OutputPhaseCurrent | 1QF13 Output current(L1) | 1QF13 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf13 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.80 | hwPDU80001QF14OutputPhaseCurrent | 1QF14 Output current(L2) | 1QF14 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf14 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.81 | hwPDU80001QF15OutputPhaseCurrent | 1QF15 Output current(L3) | 1QF15 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf15 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.82 | hwPDU80001QF16OutputPhaseCurrent | 1QF16 Output current(L1) | 1QF16 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf16 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.83 | hwPDU80001QF17OutputPhaseCurrent | 1QF17 Output current(L2) | 1QF17 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf17 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.84 | hwPDU80001QF18OutputPhaseCurrent | 1QF18 Output current(L3) | 1QF18 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf18 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.85 | hwPDU80001QF19OutputPhaseCurrent | 1QF19 Output current(L1) | 1QF19 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf19 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.86 | hwPDU80001QF20OutputPhaseCurrent | 1QF20 Output current(L2) | 1QF20 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf20 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.87 | hwPDU80001QF21OutputPhaseCurrent | 1QF21 Output current(L3) | 1QF21 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf21 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.88 | hwPDU80001QF22OutputPhaseCurrent | 1QF22 Output current(L1) | 1QF22 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf22 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.89 | hwPDU80001QF23OutputPhaseCurrent | 1QF23 Output current(L2) | 1QF23 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf23 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.90 | hwPDU80001QF24OutputPhaseCurrent | 1QF24 Output current(L3) | 1QF24 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf24 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.91 | hwPDU80001QF25OutputPhaseCurrent | 1QF25 Output current(L1) | 1QF25 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf25 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.92 | hwPDU80001QF26OutputPhaseCurrent | 1QF26 Output current(L2) | 1QF26 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf26 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.93 | hwPDU80001QF27OutputPhaseCurrent | 1QF27 Output current(L3) | 1QF27 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf27 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.94 | hwPDU80001QF28OutputPhaseCurrent | 1QF28 Output current(L1) | 1QF28 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf28 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.95 | hwPDU80001QF29OutputPhaseCurrent | 1QF29 Output current(L2) | 1QF29 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf29 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.96 | hwPDU80001QF30OutputPhaseCurrent | 1QF30 Output current(L3) | 1QF30 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf30 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.97 | hwPDU80001QF31OutputPhaseCurrent | 1QF31 Output current(L1) | 1QF31 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf31 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.98 | hwPDU80001QF32OutputPhaseCurrent | 1QF32 Output current(L2) | 1QF32 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf32 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.99 | hwPDU80001QF33OutputPhaseCurrent | 1QF33 Output current(L3) | 1QF33 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf33 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.100 | hwPDU80001QF34OutputPhaseCurrent | 1QF34 Output current(L1) | 1QF34 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf34 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.101 | hwPDU80001QF35OutputPhaseCurrent | 1QF35 Output current(L2) | 1QF35 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf35 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.102 | hwPDU80001QF36OutputPhaseCurrent | 1QF36 Output current(L3) | 1QF36 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf36 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.103 | hwPDU80001QF37OutputPhaseCurrent | 1QF37 Output current(L1) | 1QF37 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf37 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.104 | hwPDU80001QF38OutputPhaseCurrent | 1QF38 Output current(L2) | 1QF38 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf38 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.105 | hwPDU80001QF39OutputPhaseCurrent | 1QF39 Output current(L3) | 1QF39 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf39 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.106 | hwPDU80001QF40OutputPhaseCurrent | 1QF40 Output current(L1) | 1QF40 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf40 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.107 | hwPDU80001QF41OutputPhaseCurrent | 1QF41 Output current(L2) | 1QF41 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf41 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.108 | hwPDU80001QF42OutputPhaseCurrent | 1QF42 Output current(L3) | 1QF42 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf42 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.109 | hwPDU80001QF43OutputPhaseCurrent | 1QF43 Output current(L1) | 1QF43 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf43 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.110 | hwPDU80001QF44OutputPhaseCurrent | 1QF44 Output current(L2) | 1QF44 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf44 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.111 | hwPDU80001QF45OutputPhaseCurrent | 1QF45 Output current(L3) | 1QF45 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf45 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.112 | hwPDU80001QF46OutputPhaseCurrent | 1QF46 Output current(L1) | 1QF46 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf46 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.113 | hwPDU80001QF47OutputPhaseCurrent | 1QF47 Output current(L2) | 1QF47 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf47 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.114 | hwPDU80001QF48OutputPhaseCurrent | 1QF48 Output current(L3) | 1QF48 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf48 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.115 | hwPDU80001QF49OutputPhaseCurrent | 1QF49 Output current(L1) | 1QF49 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf49 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.116 | hwPDU80001QF50OutputPhaseCurrent | 1QF50 Output current(L2) | 1QF50 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf50 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.117 | hwPDU80001QF51OutputPhaseCurrent | 1QF51 Output current(L3) | 1QF51 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf51 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.118 | hwPDU80001QF52OutputPhaseCurrent | 1QF52 Output current(L1) | 1QF52 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf52 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.119 | hwPDU80001QF53OutputPhaseCurrent | 1QF53 Output current(L2) | 1QF53 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf53 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.120 | hwPDU80001QF54OutputPhaseCurrent | 1QF54 Output current(L3) | 1QF54 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf54 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.121 | hwPDU80001QF55OutputPhaseCurrent | 1QF55 Output current(L1) | 1QF55 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf55 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.122 | hwPDU80001QF56OutputPhaseCurrent | 1QF56 Output current(L2) | 1QF56 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf56 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.123 | hwPDU80001QF57OutputPhaseCurrent | 1QF57 Output current(L3) | 1QF57 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf57 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.124 | hwPDU80001QF58OutputPhaseCurrent | 1QF58 Output current(L1) | 1QF58 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf58 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.125 | hwPDU80001QF59OutputPhaseCurrent | 1QF59 Output current(L2) | 1QF59 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf59 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.126 | hwPDU80001QF60OutputPhaseCurrent | 1QF60 Output current(L3) | 1QF60 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf60 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.127 | hwPDU80001QF61OutputPhaseCurrent | 1QF61 Output current(L1) | 1QF61 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf61 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.4.1.128 | hwPDU8000Running4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.5 | hwPDU8000Running5Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.1 | hwPDU8000Running5Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.2 | hwPDU80001QF62OutputPhaseCurrent | 1QF62 Output current(L2) | 1QF62 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf62 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.3 | hwPDU80001QF63OutputPhaseCurrent | 1QF63 Output current(L3) | 1QF63 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf63 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.4 | hwPDU80001QF64OutputPhaseCurrent | 1QF64 Output current(L1) | 1QF64 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf64 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.5 | hwPDU80001QF65OutputPhaseCurrent | 1QF65 Output current(L2) | 1QF65 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf65 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.6 | hwPDU80001QF66OutputPhaseCurrent | 1QF66 Output current(L3) | 1QF66 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf66 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.7 | hwPDU80001QF67OutputPhaseCurrent | 1QF67 Output current(L1) | 1QF67 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf67 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.8 | hwPDU80001QF68OutputPhaseCurrent | 1QF68 Output current(L2) | 1QF68 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf68 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.9 | hwPDU80001QF69OutputPhaseCurrent | 1QF69 Output current(L3) | 1QF69 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf69 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.10 | hwPDU80001QF70OutputPhaseCurrent | 1QF70 Output current(L1) | 1QF70 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf70 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.11 | hwPDU80001QF71OutputPhaseCurrent | 1QF71 Output current(L2) | 1QF71 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf71 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.12 | hwPDU80001QF72OutputPhaseCurrent | 1QF72 Output current(L3) | 1QF72 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 1qf72 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.13 | hwPDU80001QF1OutputActiveElectricEnergy | 1QF1 Output active electric energy(L1) | 1QF1 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf1 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.14 | hwPDU80001QF2OutputActiveElectricEnergy | 1QF2 Output active electric energy(L2) | 1QF2 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf2 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.15 | hwPDU80001QF3OutputActiveElectricEnergy | 1QF3 Output active electric energy(L3) | 1QF3 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf3 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.16 | hwPDU80001QF4OutputActiveElectricEnergy | 1QF4 Output active electric energy(L1) | 1QF4 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf4 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.17 | hwPDU80001QF5OutputActiveElectricEnergy | 1QF5 Output active electric energy(L2) | 1QF5 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf5 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.18 | hwPDU80001QF6OutputActiveElectricEnergy | 1QF6 Output active electric energy(L3) | 1QF6 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf6 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.19 | hwPDU80001QF7OutputActiveElectricEnergy | 1QF7 Output active electric energy(L1) | 1QF7 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf7 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.20 | hwPDU80001QF8OutputActiveElectricEnergy | 1QF8 Output active electric energy(L2) | 1QF8 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf8 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.21 | hwPDU80001QF9OutputActiveElectricEnergy | 1QF9 Output active electric energy(L3) | 1QF9 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf9 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.22 | hwPDU80001QF10OutputActiveElectricEnergy | 1QF10 Output active electric energy(L1) | 1QF10 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf10 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.23 | hwPDU80001QF11OutputActiveElectricEnergy | 1QF11 Output active electric energy(L2) | 1QF11 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf11 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.24 | hwPDU80001QF12OutputActiveElectricEnergy | 1QF12 Output active electric energy(L3) | 1QF12 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf12 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.25 | hwPDU80001QF13OutputActiveElectricEnergy | 1QF13 Output active electric energy(L1) | 1QF13 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf13 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.26 | hwPDU80001QF14OutputActiveElectricEnergy | 1QF14 Output active electric energy(L2) | 1QF14 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf14 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.27 | hwPDU80001QF15OutputActiveElectricEnergy | 1QF15 Output active electric energy(L3) | 1QF15 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf15 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.28 | hwPDU80001QF16OutputActiveElectricEnergy | 1QF16 Output active electric energy(L1) | 1QF16 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf16 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.29 | hwPDU80001QF17OutputActiveElectricEnergy | 1QF17 Output active electric energy(L2) | 1QF17 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf17 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.30 | hwPDU80001QF18OutputActiveElectricEnergy | 1QF18 Output active electric energy(L3) | 1QF18 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf18 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.31 | hwPDU80001QF19OutputActiveElectricEnergy | 1QF19 Output active electric energy(L1) | 1QF19 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf19 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.32 | hwPDU80001QF20OutputActiveElectricEnergy | 1QF20 Output active electric energy(L2) | 1QF20 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf20 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.33 | hwPDU80001QF21OutputActiveElectricEnergy | 1QF21 Output active electric energy(L3) | 1QF21 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf21 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.34 | hwPDU80001QF22OutputActiveElectricEnergy | 1QF22 Output active electric energy(L1) | 1QF22 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf22 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.35 | hwPDU80001QF23OutputActiveElectricEnergy | 1QF23 Output active electric energy(L2) | 1QF23 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf23 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.36 | hwPDU80001QF24OutputActiveElectricEnergy | 1QF24 Output active electric energy(L3) | 1QF24 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf24 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.37 | hwPDU80001QF25OutputActiveElectricEnergy | 1QF25 Output active electric energy(L1) | 1QF25 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf25 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.38 | hwPDU80001QF26OutputActiveElectricEnergy | 1QF26 Output active electric energy(L2) | 1QF26 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf26 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.39 | hwPDU80001QF27OutputActiveElectricEnergy | 1QF27 Output active electric energy(L3) | 1QF27 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf27 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.40 | hwPDU80001QF28OutputActiveElectricEnergy | 1QF28 Output active electric energy(L1) | 1QF28 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf28 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.41 | hwPDU80001QF29OutputActiveElectricEnergy | 1QF29 Output active electric energy(L2) | 1QF29 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf29 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.42 | hwPDU80001QF30OutputActiveElectricEnergy | 1QF30 Output active electric energy(L3) | 1QF30 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf30 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.43 | hwPDU80001QF31OutputActiveElectricEnergy | 1QF31 Output active electric energy(L1) | 1QF31 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf31 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.44 | hwPDU80001QF32OutputActiveElectricEnergy | 1QF32 Output active electric energy(L2) | 1QF32 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf32 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.45 | hwPDU80001QF33OutputActiveElectricEnergy | 1QF33 Output active electric energy(L3) | 1QF33 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf33 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.46 | hwPDU80001QF34OutputActiveElectricEnergy | 1QF34 Output active electric energy(L1) | 1QF34 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf34 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.47 | hwPDU80001QF35OutputActiveElectricEnergy | 1QF35 Output active electric energy(L2) | 1QF35 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf35 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.48 | hwPDU80001QF36OutputActiveElectricEnergy | 1QF36 Output active electric energy(L3) | 1QF36 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf36 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.49 | hwPDU80001QF37OutputActiveElectricEnergy | 1QF37 Output active electric energy(L1) | 1QF37 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf37 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.50 | hwPDU80001QF38OutputActiveElectricEnergy | 1QF38 Output active electric energy(L2) | 1QF38 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf38 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.51 | hwPDU80001QF39OutputActiveElectricEnergy | 1QF39 Output active electric energy(L3) | 1QF39 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf39 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.52 | hwPDU80001QF40OutputActiveElectricEnergy | 1QF40 Output active electric energy(L1) | 1QF40 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf40 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.53 | hwPDU80001QF41OutputActiveElectricEnergy | 1QF41 Output active electric energy(L2) | 1QF41 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf41 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.54 | hwPDU80001QF42OutputActiveElectricEnergy | 1QF42 Output active electric energy(L3) | 1QF42 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf42 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.55 | hwPDU80001QF43OutputActiveElectricEnergy | 1QF43 Output active electric energy(L1) | 1QF43 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf43 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.56 | hwPDU80001QF44OutputActiveElectricEnergy | 1QF44 Output active electric energy(L2) | 1QF44 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf44 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.57 | hwPDU80001QF45OutputActiveElectricEnergy | 1QF45 Output active electric energy(L3) | 1QF45 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf45 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.58 | hwPDU80001QF46OutputActiveElectricEnergy | 1QF46 Output active electric energy(L1) | 1QF46 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf46 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.59 | hwPDU80001QF47OutputActiveElectricEnergy | 1QF47 Output active electric energy(L2) | 1QF47 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf47 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.60 | hwPDU80001QF48OutputActiveElectricEnergy | 1QF48 Output active electric energy(L3) | 1QF48 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf48 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.61 | hwPDU80001QF49OutputActiveElectricEnergy | 1QF49 Output active electric energy(L1) | 1QF49 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf49 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.62 | hwPDU80001QF50OutputActiveElectricEnergy | 1QF50 Output active electric energy(L2) | 1QF50 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf50 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.63 | hwPDU80001QF51OutputActiveElectricEnergy | 1QF51 Output active electric energy(L3) | 1QF51 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf51 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.64 | hwPDU80001QF52OutputActiveElectricEnergy | 1QF52 Output active electric energy(L1) | 1QF52 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf52 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.65 | hwPDU80001QF53OutputActiveElectricEnergy | 1QF53 Output active electric energy(L2) | 1QF53 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf53 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.66 | hwPDU80001QF54OutputActiveElectricEnergy | 1QF54 Output active electric energy(L3) | 1QF54 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf54 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.67 | hwPDU80001QF55OutputActiveElectricEnergy | 1QF55 Output active electric energy(L1) | 1QF55 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf55 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.68 | hwPDU80001QF56OutputActiveElectricEnergy | 1QF56 Output active electric energy(L2) | 1QF56 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf56 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.69 | hwPDU80001QF57OutputActiveElectricEnergy | 1QF57 Output active electric energy(L3) | 1QF57 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf57 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.70 | hwPDU80001QF58OutputActiveElectricEnergy | 1QF58 Output active electric energy(L1) | 1QF58 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf58 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.71 | hwPDU80001QF59OutputActiveElectricEnergy | 1QF59 Output active electric energy(L2) | 1QF59 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf59 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.72 | hwPDU80001QF60OutputActiveElectricEnergy | 1QF60 Output active electric energy(L3) | 1QF60 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf60 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.73 | hwPDU80001QF61OutputActiveElectricEnergy | 1QF61 Output active electric energy(L1) | 1QF61 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf61 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.74 | hwPDU80001QF62OutputActiveElectricEnergy | 1QF62 Output active electric energy(L2) | 1QF62 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf62 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.75 | hwPDU80001QF63OutputActiveElectricEnergy | 1QF63 Output active electric energy(L3) | 1QF63 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf63 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.76 | hwPDU80001QF64OutputActiveElectricEnergy | 1QF64 Output active electric energy(L1) | 1QF64 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf64 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.77 | hwPDU80001QF65OutputActiveElectricEnergy | 1QF65 Output active electric energy(L2) | 1QF65 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf65 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.78 | hwPDU80001QF66OutputActiveElectricEnergy | 1QF66 Output active electric energy(L3) | 1QF66 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf66 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.79 | hwPDU80001QF67OutputActiveElectricEnergy | 1QF67 Output active electric energy(L1) | 1QF67 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf67 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.80 | hwPDU80001QF68OutputActiveElectricEnergy | 1QF68 Output active electric energy(L2) | 1QF68 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf68 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.81 | hwPDU80001QF69OutputActiveElectricEnergy | 1QF69 Output active electric energy(L3) | 1QF69 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf69 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.82 | hwPDU80001QF70OutputActiveElectricEnergy | 1QF70 Output active electric energy(L1) | 1QF70 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf70 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.83 | hwPDU80001QF71OutputActiveElectricEnergy | 1QF71 Output active electric energy(L2) | 1QF71 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf71 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.84 | hwPDU80001QF72OutputActiveElectricEnergy | 1QF72 Output active electric energy(L3) | 1QF72 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 1qf72 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.85 | hwPDU80002QF1OutputPhaseCurrent | 2QF1 Output current(L1) | 2QF1 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf1 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.86 | hwPDU80002QF2OutputPhaseCurrent | 2QF2 Output current(L2) | 2QF2 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf2 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.87 | hwPDU80002QF3OutputPhaseCurrent | 2QF3 Output current(L3) | 2QF3 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf3 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.88 | hwPDU80002QF4OutputPhaseCurrent | 2QF4 Output current(L1) | 2QF4 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf4 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.89 | hwPDU80002QF5OutputPhaseCurrent | 2QF5 Output current(L2) | 2QF5 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf5 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.90 | hwPDU80002QF6OutputPhaseCurrent | 2QF6 Output current(L3) | 2QF6 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf6 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.91 | hwPDU80002QF7OutputPhaseCurrent | 2QF7 Output current(L1) | 2QF7 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf7 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.92 | hwPDU80002QF8OutputPhaseCurrent | 2QF8 Output current(L2) | 2QF8 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf8 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.93 | hwPDU80002QF9OutputPhaseCurrent | 2QF9 Output current(L3) | 2QF9 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf9 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.94 | hwPDU80002QF10OutputPhaseCurrent | 2QF10 Output current(L1) | 2QF10 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf10 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.95 | hwPDU80002QF11OutputPhaseCurrent | 2QF11 Output current(L2) | 2QF11 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf11 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.96 | hwPDU80002QF12OutputPhaseCurrent | 2QF12 Output current(L3) | 2QF12 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf12 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.97 | hwPDU80002QF13OutputPhaseCurrent | 2QF13 Output current(L1) | 2QF13 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf13 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.98 | hwPDU80002QF14OutputPhaseCurrent | 2QF14 Output current(L2) | 2QF14 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf14 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.99 | hwPDU80002QF15OutputPhaseCurrent | 2QF15 Output current(L3) | 2QF15 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf15 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.100 | hwPDU80002QF16OutputPhaseCurrent | 2QF16 Output current(L1) | 2QF16 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf16 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.101 | hwPDU80002QF17OutputPhaseCurrent | 2QF17 Output current(L2) | 2QF17 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf17 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.102 | hwPDU80002QF18OutputPhaseCurrent | 2QF18 Output current(L3) | 2QF18 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf18 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.103 | hwPDU80002QF19OutputPhaseCurrent | 2QF19 Output current(L1) | 2QF19 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf19 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.104 | hwPDU80002QF20OutputPhaseCurrent | 2QF20 Output current(L2) | 2QF20 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf20 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.105 | hwPDU80002QF21OutputPhaseCurrent | 2QF21 Output current(L3) | 2QF21 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf21 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.106 | hwPDU80002QF22OutputPhaseCurrent | 2QF22 Output current(L1) | 2QF22 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf22 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.107 | hwPDU80002QF23OutputPhaseCurrent | 2QF23 Output current(L2) | 2QF23 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf23 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.108 | hwPDU80002QF24OutputPhaseCurrent | 2QF24 Output current(L3) | 2QF24 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf24 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.109 | hwPDU80002QF25OutputPhaseCurrent | 2QF25 Output current(L1) | 2QF25 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf25 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.110 | hwPDU80002QF26OutputPhaseCurrent | 2QF26 Output current(L2) | 2QF26 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf26 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.111 | hwPDU80002QF27OutputPhaseCurrent | 2QF27 Output current(L3) | 2QF27 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf27 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.112 | hwPDU80002QF28OutputPhaseCurrent | 2QF28 Output current(L1) | 2QF28 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf28 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.113 | hwPDU80002QF29OutputPhaseCurrent | 2QF29 Output current(L2) | 2QF29 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf29 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.114 | hwPDU80002QF30OutputPhaseCurrent | 2QF30 Output current(L3) | 2QF30 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf30 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.115 | hwPDU80002QF31OutputPhaseCurrent | 2QF31 Output current(L1) | 2QF31 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf31 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.116 | hwPDU80002QF32OutputPhaseCurrent | 2QF32 Output current(L2) | 2QF32 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf32 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.117 | hwPDU80002QF33OutputPhaseCurrent | 2QF33 Output current(L3) | 2QF33 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf33 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.118 | hwPDU80002QF34OutputPhaseCurrent | 2QF34 Output current(L1) | 2QF34 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf34 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.119 | hwPDU80002QF35OutputPhaseCurrent | 2QF35 Output current(L2) | 2QF35 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf35 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.120 | hwPDU80002QF36OutputPhaseCurrent | 2QF36 Output current(L3) | 2QF36 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf36 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.121 | hwPDU80002QF37OutputPhaseCurrent | 2QF37 Output current(L1) | 2QF37 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf37 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.122 | hwPDU80002QF38OutputPhaseCurrent | 2QF38 Output current(L2) | 2QF38 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf38 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.123 | hwPDU80002QF39OutputPhaseCurrent | 2QF39 Output current(L3) | 2QF39 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf39 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.124 | hwPDU80002QF40OutputPhaseCurrent | 2QF40 Output current(L1) | 2QF40 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf40 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.125 | hwPDU80002QF41OutputPhaseCurrent | 2QF41 Output current(L2) | 2QF41 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf41 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.126 | hwPDU80002QF42OutputPhaseCurrent | 2QF42 Output current(L3) | 2QF42 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf42 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.5.1.128 | hwPDU8000Running5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.6 | hwPDU8000Running6Table | / | / |  |  | / | / | The running table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.1 | hwPDU8000Running6Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.2 | hwPDU80002QF43OutputPhaseCurrent | 2QF43 Output current(L1) | 2QF43 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf43 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.3 | hwPDU80002QF44OutputPhaseCurrent | 2QF44 Output current(L2) | 2QF44 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf44 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.4 | hwPDU80002QF45OutputPhaseCurrent | 2QF45 Output current(L3) | 2QF45 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf45 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.5 | hwPDU80002QF46OutputPhaseCurrent | 2QF46 Output current(L1) | 2QF46 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf46 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.6 | hwPDU80002QF47OutputPhaseCurrent | 2QF47 Output current(L2) | 2QF47 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf47 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.7 | hwPDU80002QF48OutputPhaseCurrent | 2QF48 Output current(L3) | 2QF48 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf48 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.8 | hwPDU80002QF49OutputPhaseCurrent | 2QF49 Output current(L1) | 2QF49 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf49 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.9 | hwPDU80002QF50OutputPhaseCurrent | 2QF50 Output current(L2) | 2QF50 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf50 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.10 | hwPDU80002QF51OutputPhaseCurrent | 2QF51 Output current(L3) | 2QF51 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf51 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.11 | hwPDU80002QF52OutputPhaseCurrent | 2QF52 Output current(L1) | 2QF52 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf52 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.12 | hwPDU80002QF53OutputPhaseCurrent | 2QF53 Output current(L2) | 2QF53 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf53 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.13 | hwPDU80002QF54OutputPhaseCurrent | 2QF54 Output current(L3) | 2QF54 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf54 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.14 | hwPDU80002QF55OutputPhaseCurrent | 2QF55 Output current(L1) | 2QF55 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf55 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.15 | hwPDU80002QF56OutputPhaseCurrent | 2QF56 Output current(L2) | 2QF56 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf56 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.16 | hwPDU80002QF57OutputPhaseCurrent | 2QF57 Output current(L3) | 2QF57 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf57 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.17 | hwPDU80002QF58OutputPhaseCurrent | 2QF58 Output current(L1) | 2QF58 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf58 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.18 | hwPDU80002QF59OutputPhaseCurrent | 2QF59 Output current(L2) | 2QF59 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf59 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.19 | hwPDU80002QF60OutputPhaseCurrent | 2QF60 Output current(L3) | 2QF60 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf60 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.20 | hwPDU80002QF61OutputPhaseCurrent | 2QF61 Output current(L1) | 2QF61 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf61 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.21 | hwPDU80002QF62OutputPhaseCurrent | 2QF62 Output current(L2) | 2QF62 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf62 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.22 | hwPDU80002QF63OutputPhaseCurrent | 2QF63 Output current(L3) | 2QF63 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf63 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.23 | hwPDU80002QF64OutputPhaseCurrent | 2QF64 Output current(L1) | 2QF64 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf64 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.24 | hwPDU80002QF65OutputPhaseCurrent | 2QF65 Output current(L2) | 2QF65 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf65 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.25 | hwPDU80002QF66OutputPhaseCurrent | 2QF66 Output current(L3) | 2QF66 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf66 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.26 | hwPDU80002QF67OutputPhaseCurrent | 2QF67 Output current(L1) | 2QF67 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf67 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.27 | hwPDU80002QF68OutputPhaseCurrent | 2QF68 Output current(L2) | 2QF68 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf68 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.28 | hwPDU80002QF69OutputPhaseCurrent | 2QF69 Output current(L3) | 2QF69 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf69 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.29 | hwPDU80002QF70OutputPhaseCurrent | 2QF70 Output current(L1) | 2QF70 输出电流(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf70 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.30 | hwPDU80002QF71OutputPhaseCurrent | 2QF71 Output current(L2) | 2QF71 输出电流(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf71 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.31 | hwPDU80002QF72OutputPhaseCurrent | 2QF72 Output current(L3) | 2QF72 输出电流(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | pdu8000 2qf72 output cur. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.32 | hwPDU80002QF1OutputActiveElectricEnergy | 2QF1 Output active electric energy(L1) | 2QF1 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf1 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.33 | hwPDU80002QF2OutputActiveElectricEnergy | 2QF2 Output active electric energy(L2) | 2QF2 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf2 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.34 | hwPDU80002QF3OutputActiveElectricEnergy | 2QF3 Output active electric energy(L3) | 2QF3 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf3 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.35 | hwPDU80002QF4OutputActiveElectricEnergy | 2QF4 Output active electric energy(L1) | 2QF4 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf4 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.36 | hwPDU80002QF5OutputActiveElectricEnergy | 2QF5 Output active electric energy(L2) | 2QF5 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf5 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.37 | hwPDU80002QF6OutputActiveElectricEnergy | 2QF6 Output active electric energy(L3) | 2QF6 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf6 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.38 | hwPDU80002QF7OutputActiveElectricEnergy | 2QF7 Output active electric energy(L1) | 2QF7 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf7 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.39 | hwPDU80002QF8OutputActiveElectricEnergy | 2QF8 Output active electric energy(L2) | 2QF8 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf8 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.40 | hwPDU80002QF9OutputActiveElectricEnergy | 2QF9 Output active electric energy(L3) | 2QF9 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf9 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.41 | hwPDU80002QF10OutputActiveElectricEnergy | 2QF10 Output active electric energy(L1) | 2QF10 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf10 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.42 | hwPDU80002QF11OutputActiveElectricEnergy | 2QF11 Output active electric energy(L2) | 2QF11 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf11 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.43 | hwPDU80002QF12OutputActiveElectricEnergy | 2QF12 Output active electric energy(L3) | 2QF12 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf12 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.44 | hwPDU80002QF13OutputActiveElectricEnergy | 2QF13 Output active electric energy(L1) | 2QF13 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf13 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.45 | hwPDU80002QF14OutputActiveElectricEnergy | 2QF14 Output active electric energy(L2) | 2QF14 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf14 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.46 | hwPDU80002QF15OutputActiveElectricEnergy | 2QF15 Output active electric energy(L3) | 2QF15 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf15 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.47 | hwPDU80002QF16OutputActiveElectricEnergy | 2QF16 Output active electric energy(L1) | 2QF16 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf16 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.48 | hwPDU80002QF17OutputActiveElectricEnergy | 2QF17 Output active electric energy(L2) | 2QF17 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf17 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.49 | hwPDU80002QF18OutputActiveElectricEnergy | 2QF18 Output active electric energy(L3) | 2QF18 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf18 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.50 | hwPDU80002QF19OutputActiveElectricEnergy | 2QF19 Output active electric energy(L1) | 2QF19 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf19 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.51 | hwPDU80002QF20OutputActiveElectricEnergy | 2QF20 Output active electric energy(L2) | 2QF20 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf20 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.52 | hwPDU80002QF21OutputActiveElectricEnergy | 2QF21 Output active electric energy(L3) | 2QF21 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf21 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.53 | hwPDU80002QF22OutputActiveElectricEnergy | 2QF22 Output active electric energy(L1) | 2QF22 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf22 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.54 | hwPDU80002QF23OutputActiveElectricEnergy | 2QF23 Output active electric energy(L2) | 2QF23 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf23 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.55 | hwPDU80002QF24OutputActiveElectricEnergy | 2QF24 Output active electric energy(L3) | 2QF24 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf24 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.56 | hwPDU80002QF25OutputActiveElectricEnergy | 2QF25 Output active electric energy(L1) | 2QF25 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf25 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.57 | hwPDU80002QF26OutputActiveElectricEnergy | 2QF26 Output active electric energy(L2) | 2QF26 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf26 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.58 | hwPDU80002QF27OutputActiveElectricEnergy | 2QF27 Output active electric energy(L3) | 2QF27 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf27 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.59 | hwPDU80002QF28OutputActiveElectricEnergy | 2QF28 Output active electric energy(L1) | 2QF28 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf28 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.60 | hwPDU80002QF29OutputActiveElectricEnergy | 2QF29 Output active electric energy(L2) | 2QF29 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf29 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.61 | hwPDU80002QF30OutputActiveElectricEnergy | 2QF30 Output active electric energy(L3) | 2QF30 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf30 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.62 | hwPDU80002QF31OutputActiveElectricEnergy | 2QF31 Output active electric energy(L1) | 2QF31 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf31 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.63 | hwPDU80002QF32OutputActiveElectricEnergy | 2QF32 Output active electric energy(L2) | 2QF32 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf32 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.64 | hwPDU80002QF33OutputActiveElectricEnergy | 2QF33 Output active electric energy(L3) | 2QF33 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf33 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.65 | hwPDU80002QF34OutputActiveElectricEnergy | 2QF34 Output active electric energy(L1) | 2QF34 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf34 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.66 | hwPDU80002QF35OutputActiveElectricEnergy | 2QF35 Output active electric energy(L2) | 2QF35 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf35 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.67 | hwPDU80002QF36OutputActiveElectricEnergy | 2QF36 Output active electric energy(L3) | 2QF36 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf36 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.68 | hwPDU80002QF37OutputActiveElectricEnergy | 2QF37 Output active electric energy(L1) | 2QF37 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf37 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.69 | hwPDU80002QF38OutputActiveElectricEnergy | 2QF38 Output active electric energy(L2) | 2QF38 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf38 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.70 | hwPDU80002QF39OutputActiveElectricEnergy | 2QF39 Output active electric energy(L3) | 2QF39 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf39 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.71 | hwPDU80002QF40OutputActiveElectricEnergy | 2QF40 Output active electric energy(L1) | 2QF40 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf40 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.72 | hwPDU80002QF41OutputActiveElectricEnergy | 2QF41 Output active electric energy(L2) | 2QF41 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf41 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.73 | hwPDU80002QF42OutputActiveElectricEnergy | 2QF42 Output active electric energy(L3) | 2QF42 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf42 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.74 | hwPDU80002QF43OutputActiveElectricEnergy | 2QF43 Output active electric energy(L1) | 2QF43 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf43 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.75 | hwPDU80002QF44OutputActiveElectricEnergy | 2QF44 Output active electric energy(L2) | 2QF44 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf44 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.76 | hwPDU80002QF45OutputActiveElectricEnergy | 2QF45 Output active electric energy(L3) | 2QF45 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf45 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.77 | hwPDU80002QF46OutputActiveElectricEnergy | 2QF46 Output active electric energy(L1) | 2QF46 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf46 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.78 | hwPDU80002QF47OutputActiveElectricEnergy | 2QF47 Output active electric energy(L2) | 2QF47 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf47 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.79 | hwPDU80002QF48OutputActiveElectricEnergy | 2QF48 Output active electric energy(L3) | 2QF48 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf48 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.80 | hwPDU80002QF49OutputActiveElectricEnergy | 2QF49 Output active electric energy(L1) | 2QF49 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf49 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.81 | hwPDU80002QF50OutputActiveElectricEnergy | 2QF50 Output active electric energy(L2) | 2QF50 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf50 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.82 | hwPDU80002QF51OutputActiveElectricEnergy | 2QF51 Output active electric energy(L3) | 2QF51 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf51 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.83 | hwPDU80002QF52OutputActiveElectricEnergy | 2QF52 Output active electric energy(L1) | 2QF52 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf52 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.84 | hwPDU80002QF53OutputActiveElectricEnergy | 2QF53 Output active electric energy(L2) | 2QF53 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf53 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.85 | hwPDU80002QF54OutputActiveElectricEnergy | 2QF54 Output active electric energy(L3) | 2QF54 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf54 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.86 | hwPDU80002QF55OutputActiveElectricEnergy | 2QF55 Output active electric energy(L1) | 2QF55 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf55 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.87 | hwPDU80002QF56OutputActiveElectricEnergy | 2QF56 Output active electric energy(L2) | 2QF56 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf56 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.88 | hwPDU80002QF57OutputActiveElectricEnergy | 2QF57 Output active electric energy(L3) | 2QF57 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf57 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.89 | hwPDU80002QF58OutputActiveElectricEnergy | 2QF58 Output active electric energy(L1) | 2QF58 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf58 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.90 | hwPDU80002QF59OutputActiveElectricEnergy | 2QF59 Output active electric energy(L2) | 2QF59 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf59 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.91 | hwPDU80002QF60OutputActiveElectricEnergy | 2QF60 Output active electric energy(L3) | 2QF60 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf60 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.92 | hwPDU80002QF61OutputActiveElectricEnergy | 2QF61 Output active electric energy(L1) | 2QF61 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf61 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.93 | hwPDU80002QF62OutputActiveElectricEnergy | 2QF62 Output active electric energy(L2) | 2QF62 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf62 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.94 | hwPDU80002QF63OutputActiveElectricEnergy | 2QF63 Output active electric energy(L3) | 2QF63 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf63 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.95 | hwPDU80002QF64OutputActiveElectricEnergy | 2QF64 Output active electric energy(L1) | 2QF64 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf64 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.96 | hwPDU80002QF65OutputActiveElectricEnergy | 2QF65 Output active electric energy(L2) | 2QF65 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf65 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.97 | hwPDU80002QF66OutputActiveElectricEnergy | 2QF66 Output active electric energy(L3) | 2QF66 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf66 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.98 | hwPDU80002QF67OutputActiveElectricEnergy | 2QF67 Output active electric energy(L1) | 2QF67 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf67 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.99 | hwPDU80002QF68OutputActiveElectricEnergy | 2QF68 Output active electric energy(L2) | 2QF68 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf68 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.100 | hwPDU80002QF69OutputActiveElectricEnergy | 2QF69 Output active electric energy(L3) | 2QF69 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf69 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.101 | hwPDU80002QF70OutputActiveElectricEnergy | 2QF70 Output active electric energy(L1) | 2QF70 输出有功电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf70 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.102 | hwPDU80002QF71OutputActiveElectricEnergy | 2QF71 Output active electric energy(L2) | 2QF71 输出有功电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf71 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.103 | hwPDU80002QF72OutputActiveElectricEnergy | 2QF72 Output active electric energy(L3) | 2QF72 输出有功电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | pdu8000 2qf72 output act energy. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.104 | hwPDU8000DeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Virtual System Device Name.
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.105 | hwPDU8000IPAddr | IP address | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IP address of the device.
1.3.6.1.4.1.2011.6.178.1.1.9.5.6.1.128 | hwPDU8000Running6RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7 | hwPDU8000Running7Table | / | / |  |  | / | / | The running table of PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.1 | hwPDU8000Running7Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.2 | hwPDU8000MITemperature | Mains temperature | 主路温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The temperature of main input. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.3 | hwPDU8000MOTemperature | Temperature | 主路温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The temperature of main output. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.4 | hwPDU8000M1Temperature | Temperature | 主路温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The temperature of main 1. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.5 | hwPDU8000M2Temperature | Temperature | 主路温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | The temperature of main 2. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.6 | hwPDU8000QF1Temperature | QF1 Temperature(L1) | QF1 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF1 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.7 | hwPDU8000QF2Temperature | QF2 Temperature(L2) | QF2 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF2 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.8 | hwPDU8000QF3Temperature | QF3 Temperature(L3) | QF3 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF3 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.9 | hwPDU8000QF4Temperature | QF4 Temperature(L1) | QF4 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF4 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.10 | hwPDU8000QF5Temperature | QF5 Temperature(L2) | QF5 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF5 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.11 | hwPDU8000QF6Temperature | QF6 Temperature(L3) | QF6 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF6 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.12 | hwPDU8000QF7Temperature | QF7 Temperature(L1) | QF7 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF7 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.13 | hwPDU8000QF8Temperature | QF8 Temperature(L2) | QF8 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF8 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.14 | hwPDU8000QF9Temperature | QF9 Temperature(L3) | QF9 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF9 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.15 | hwPDU8000QF10Temperature | QF10 Temperature(L1) | QF10 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF10 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.16 | hwPDU8000QF11Temperature | QF11 Temperature(L2) | QF11 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF11 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.17 | hwPDU8000QF12Temperature | QF12 Temperature(L3) | QF12 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF12 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.18 | hwPDU8000QF13Temperature | QF13 Temperature(L1) | QF13 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF13 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.19 | hwPDU8000QF14Temperature | QF14 Temperature(L2) | QF14 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF14 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.20 | hwPDU8000QF15Temperature | QF15 Temperature(L3) | QF15 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF15 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.21 | hwPDU8000QF16Temperature | QF16 Temperature(L1) | QF16 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF16 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.22 | hwPDU8000QF17Temperature | QF17 Temperature(L2) | QF17 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF17 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.23 | hwPDU8000QF18Temperature | QF18 Temperature(L3) | QF18 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF18 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.24 | hwPDU8000QF19Temperature | QF19 Temperature(L1) | QF19 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF19 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.25 | hwPDU8000QF20Temperature | QF20 Temperature(L2) | QF20 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF20 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.26 | hwPDU8000QF21Temperature | QF21 Temperature(L3) | QF21 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF21 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.27 | hwPDU8000QF22Temperature | QF22 Temperature(L1) | QF22 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF22 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.28 | hwPDU8000QF23Temperature | QF23 Temperature(L2) | QF23 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF23 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.29 | hwPDU8000QF24Temperature | QF24 Temperature(L3) | QF24 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF24 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.30 | hwPDU8000QF25Temperature | QF25 Temperature(L1) | QF25 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF25 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.31 | hwPDU8000QF26Temperature | QF26 Temperature(L2) | QF26 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF26 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.32 | hwPDU8000QF27Temperature | QF27 Temperature(L3) | QF27 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF27 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.33 | hwPDU8000QF28Temperature | QF28 Temperature(L1) | QF28 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF28 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.34 | hwPDU8000QF29Temperature | QF29 Temperature(L2) | QF29 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF29 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.35 | hwPDU8000QF30Temperature | QF30 Temperature(L3) | QF30 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF30 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.36 | hwPDU8000QF31Temperature | QF31 Temperature(L1) | QF31 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF31 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.37 | hwPDU8000QF32Temperature | QF32 Temperature(L2) | QF32 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF32 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.38 | hwPDU8000QF33Temperature | QF33 Temperature(L3) | QF33 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF33 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.39 | hwPDU8000QF34Temperature | QF34 Temperature(L1) | QF34 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF34 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.40 | hwPDU8000QF35Temperature | QF35 Temperature(L2) | QF35 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF35 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.41 | hwPDU8000QF36Temperature | QF36 Temperature(L3) | QF36 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF36 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.42 | hwPDU8000QF37Temperature | QF37 Temperature(L1) | QF37 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF37 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.43 | hwPDU8000QF38Temperature | QF38 Temperature(L2) | QF38 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF38 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.44 | hwPDU8000QF39Temperature | QF39 Temperature(L3) | QF39 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF39 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.45 | hwPDU8000QF40Temperature | QF40 Temperature(L1) | QF40 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF40 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.46 | hwPDU8000QF41Temperature | QF41 Temperature(L2) | QF41 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF41 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.47 | hwPDU8000QF42Temperature | QF42 Temperature(L3) | QF42 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF42 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.48 | hwPDU8000QF43Temperature | QF43 Temperature(L1) | QF43 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF43 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.49 | hwPDU8000QF44Temperature | QF44 Temperature(L2) | QF44 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF44 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.50 | hwPDU8000QF45Temperature | QF45 Temperature(L3) | QF45 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF45 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.51 | hwPDU8000QF46Temperature | QF46 Temperature(L1) | QF46 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF46 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.52 | hwPDU8000QF47Temperature | QF47 Temperature(L2) | QF47 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF47 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.53 | hwPDU8000QF48Temperature | QF48 Temperature(L3) | QF48 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF48 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.54 | hwPDU8000QF49Temperature | QF49 Temperature(L1) | QF49 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF49 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.55 | hwPDU8000QF50Temperature | QF50 Temperature(L2) | QF50 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF50 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.56 | hwPDU8000QF51Temperature | QF51 Temperature(L3) | QF51 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF51 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.57 | hwPDU8000QF52Temperature | QF52 Temperature(L1) | QF52 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF52 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.58 | hwPDU8000QF53Temperature | QF53 Temperature(L2) | QF53 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF53 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.59 | hwPDU8000QF54Temperature | QF54 Temperature(L3) | QF54 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF54 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.60 | hwPDU8000QF55Temperature | QF55 Temperature(L1) | QF55 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF55 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.61 | hwPDU8000QF56Temperature | QF56 Temperature(L2) | QF56 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF56 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.62 | hwPDU8000QF57Temperature | QF57 Temperature(L3) | QF57 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF57 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.63 | hwPDU8000QF58Temperature | QF58 Temperature(L1) | QF58 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF58 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.64 | hwPDU8000QF59Temperature | QF59 Temperature(L2) | QF59 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF59 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.65 | hwPDU8000QF60Temperature | QF60 Temperature(L3) | QF60 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF60 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.66 | hwPDU8000QF61Temperature | QF61 Temperature(L1) | QF61 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF61 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.67 | hwPDU8000QF62Temperature | QF62 Temperature(L2) | QF62 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF62 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.68 | hwPDU8000QF63Temperature | QF63 Temperature(L3) | QF63 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF63 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.69 | hwPDU8000QF64Temperature | QF64 Temperature(L1) | QF64 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF64 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.70 | hwPDU8000QF65Temperature | QF65 Temperature(L2) | QF65 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF65 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.71 | hwPDU8000QF66Temperature | QF66 Temperature(L3) | QF66 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF66 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.72 | hwPDU8000QF67Temperature | QF67 Temperature(L1) | QF67 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF67 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.73 | hwPDU8000QF68Temperature | QF68 Temperature(L2) | QF68 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF68 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.74 | hwPDU8000QF69Temperature | QF69 Temperature(L3) | QF69 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF69 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.75 | hwPDU8000QF70Temperature | QF70 Temperature(L1) | QF70 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF70 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.76 | hwPDU8000QF71Temperature | QF71 Temperature(L2) | QF71 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF71 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.77 | hwPDU8000QF72Temperature | QF72 Temperature(L3) | QF72 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF72 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.78 | hwPDU8000QF73Temperature | QF73 Temperature(L1) | QF73 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF73 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.79 | hwPDU8000QF74Temperature | QF74 Temperature(L2) | QF74 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF74 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.80 | hwPDU8000QF75Temperature | QF75 Temperature(L3) | QF75 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF75 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.81 | hwPDU8000QF76Temperature | QF76 Temperature(L1) | QF76 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF76 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.82 | hwPDU8000QF77Temperature | QF77 Temperature(L2) | QF77 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF77 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.83 | hwPDU8000QF78Temperature | QF78 Temperature(L3) | QF78 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF78 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.84 | hwPDU8000QF79Temperature | QF79 Temperature(L1) | QF79 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF79 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.85 | hwPDU8000QF80Temperature | QF80 Temperature(L2) | QF80 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF80 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.86 | hwPDU8000QF81Temperature | QF81 Temperature(L3) | QF81 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF81 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.87 | hwPDU8000QF82Temperature | QF82 Temperature(L1) | QF82 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF82 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.88 | hwPDU8000QF83Temperature | QF83 Temperature(L2) | QF83 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF83 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.89 | hwPDU8000QF84Temperature | QF84 Temperature(L3) | QF84 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF84 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.90 | hwPDU8000QF85Temperature | QF85 Temperature(L1) | QF85 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF85 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.91 | hwPDU8000QF86Temperature | QF86 Temperature(L2) | QF86 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF86 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.92 | hwPDU8000QF87Temperature | QF87 Temperature(L3) | QF87 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF87 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.93 | hwPDU8000QF88Temperature | QF88 Temperature(L1) | QF88 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF88 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.94 | hwPDU8000QF89Temperature | QF89 Temperature(L2) | QF89 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF89 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.95 | hwPDU8000QF90Temperature | QF90 Temperature(L3) | QF90 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF90 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.96 | hwPDU8000QF91Temperature | QF91 Temperature(L1) | QF91 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF91 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.97 | hwPDU8000QF92Temperature | QF92 Temperature(L2) | QF92 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF92 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.98 | hwPDU8000QF93Temperature | QF93 Temperature(L3) | QF93 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF93 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.99 | hwPDU8000QF94Temperature | QF94 Temperature(L1) | QF94 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF94 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.100 | hwPDU8000QF95Temperature | QF95 Temperature(L2) | QF95 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF95 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.101 | hwPDU8000QF96Temperature | QF96 Temperature(L3) | QF96 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF96 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.102 | hwPDU8000QF97Temperature | QF97 Temperature(L1) | QF97 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF97 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.103 | hwPDU8000QF98Temperature | QF98 Temperature(L2) | QF98 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF98 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.104 | hwPDU8000QF99Temperature | QF99 Temperature(L3) | QF99 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF99 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.105 | hwPDU8000QF100Temperature | QF100 Temperature(L1) | QF100 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF100 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.106 | hwPDU8000QF101Temperature | QF101 Temperature(L2) | QF101 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF101 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.107 | hwPDU8000QF102Temperature | QF102 Temperature(L3) | QF102 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF102 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.108 | hwPDU8000QF103Temperature | QF103 Temperature(L1) | QF103 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF103 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.109 | hwPDU8000QF104Temperature | QF104 Temperature(L2) | QF104 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF104 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.110 | hwPDU8000QF105Temperature | QF105 Temperature(L3) | QF105 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF105 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.111 | hwPDU8000QF106Temperature | QF106 Temperature(L1) | QF106 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF106 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.112 | hwPDU8000QF107Temperature | QF107 Temperature(L2) | QF107 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF107 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.113 | hwPDU8000QF108Temperature | QF108 Temperature(L3) | QF108 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF108 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.114 | hwPDU8000QF109Temperature | QF109 Temperature(L1) | QF109 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF109 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.115 | hwPDU8000QF110Temperature | QF110 Temperature(L2) | QF110 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF110 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.116 | hwPDU8000QF111Temperature | QF111 Temperature(L3) | QF111 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF111 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.117 | hwPDU8000QF112Temperature | QF112 Temperature(L1) | QF112 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF112 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.118 | hwPDU8000QF113Temperature | QF113 Temperature(L2) | QF113 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF113 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.119 | hwPDU8000QF114Temperature | QF114 Temperature(L3) | QF114 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF114 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.120 | hwPDU8000QF115Temperature | QF115 Temperature(L1) | QF115 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF115 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.121 | hwPDU8000QF116Temperature | QF116 Temperature(L2) | QF116 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF116 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.122 | hwPDU8000QF117Temperature | QF117 Temperature(L3) | QF117 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF117 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.123 | hwPDU8000QF118Temperature | QF118 Temperature(L1) | QF118 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF118 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.124 | hwPDU8000QF119Temperature | QF119 Temperature(L2) | QF119 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF119 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.125 | hwPDU8000QF120Temperature | QF120 Temperature(L3) | QF120 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF120 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.126 | hwPDU8000QF121Temperature | QF121 Temperature(L1) | QF121 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF121 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.127 | hwPDU8000QF122Temperature | QF122 Temperature(L2) | QF122 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF122 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.128 | hwPDU8000QF123Temperature | QF123 Temperature(L3) | QF123 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF123 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.129 | hwPDU8000QF124Temperature | QF124 Temperature(L1) | QF124 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF124 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.130 | hwPDU8000QF125Temperature | QF125 Temperature(L2) | QF125 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF125 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.131 | hwPDU8000QF126Temperature | QF126 Temperature(L3) | QF126 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF126 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.132 | hwPDU8000QF127Temperature | QF127 Temperature(L1) | QF127 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF127 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.133 | hwPDU8000QF128Temperature | QF128 Temperature(L2) | QF128 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF128 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.134 | hwPDU8000QF129Temperature | QF129 Temperature(L3) | QF129 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF129 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.135 | hwPDU8000QF130Temperature | QF130 Temperature(L1) | QF130 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF130 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.136 | hwPDU8000QF131Temperature | QF131 Temperature(L2) | QF131 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF131 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.137 | hwPDU8000QF132Temperature | QF132 Temperature(L3) | QF132 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF132 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.138 | hwPDU8000QF133Temperature | QF133 Temperature(L1) | QF133 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF133 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.139 | hwPDU8000QF134Temperature | QF134 Temperature(L2) | QF134 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF134 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.140 | hwPDU8000QF135Temperature | QF135 Temperature(L3) | QF135 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF135 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.141 | hwPDU8000QF136Temperature | QF136 Temperature(L1) | QF136 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF136 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.142 | hwPDU8000QF137Temperature | QF137 Temperature(L2) | QF137 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF137 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.143 | hwPDU8000QF138Temperature | QF138 Temperature(L3) | QF138 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF138 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.144 | hwPDU8000QF139Temperature | QF139 Temperature(L1) | QF139 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF139 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.145 | hwPDU8000QF140Temperature | QF140 Temperature(L2) | QF140 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF140 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.146 | hwPDU8000QF141Temperature | QF141 Temperature(L3) | QF141 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF141 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.147 | hwPDU8000QF142Temperature | QF142 Temperature(L1) | QF142 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF142 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.148 | hwPDU8000QF143Temperature | QF143 Temperature(L2) | QF143 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF143 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.149 | hwPDU8000QF144Temperature | QF144 Temperature(L3) | QF144 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF144 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.150 | hwPDU80001QF1Temperature | 1QF1 Temperature(L1) | 1QF1 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF1 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.151 | hwPDU80001QF2Temperature | 1QF2 Temperature(L2) | 1QF2 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF2 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.152 | hwPDU80001QF3Temperature | 1QF3 Temperature(L3) | 1QF3 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF3 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.153 | hwPDU80001QF4Temperature | 1QF4 Temperature(L1) | 1QF4 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF4 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.154 | hwPDU80001QF5Temperature | 1QF5 Temperature(L2) | 1QF5 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF5 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.155 | hwPDU80001QF6Temperature | 1QF6 Temperature(L3) | 1QF6 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF6 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.156 | hwPDU80001QF7Temperature | 1QF7 Temperature(L1) | 1QF7 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF7 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.157 | hwPDU80001QF8Temperature | 1QF8 Temperature(L2) | 1QF8 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF8 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.158 | hwPDU80001QF9Temperature | 1QF9 Temperature(L3) | 1QF9 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF9 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.159 | hwPDU80001QF10Temperature | 1QF10 Temperature(L1) | 1QF10 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF10 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.160 | hwPDU80001QF11Temperature | 1QF11 Temperature(L2) | 1QF11 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF11 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.161 | hwPDU80001QF12Temperature | 1QF12 Temperature(L3) | 1QF12 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF12 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.162 | hwPDU80001QF13Temperature | 1QF13 Temperature(L1) | 1QF13 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF13 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.163 | hwPDU80001QF14Temperature | 1QF14 Temperature(L2) | 1QF14 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF14 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.164 | hwPDU80001QF15Temperature | 1QF15 Temperature(L3) | 1QF15 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF15 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.165 | hwPDU80001QF16Temperature | 1QF16 Temperature(L1) | 1QF16 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF16 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.166 | hwPDU80001QF17Temperature | 1QF17 Temperature(L2) | 1QF17 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF17 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.167 | hwPDU80001QF18Temperature | 1QF18 Temperature(L3) | 1QF18 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF18 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.168 | hwPDU80001QF19Temperature | 1QF19 Temperature(L1) | 1QF19 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF19 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.169 | hwPDU80001QF20Temperature | 1QF20 Temperature(L2) | 1QF20 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF20 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.170 | hwPDU80001QF21Temperature | 1QF21 Temperature(L3) | 1QF21 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF21 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.171 | hwPDU80001QF22Temperature | 1QF22 Temperature(L1) | 1QF22 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF22 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.172 | hwPDU80001QF23Temperature | 1QF23 Temperature(L2) | 1QF23 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF23 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.173 | hwPDU80001QF24Temperature | 1QF24 Temperature(L3) | 1QF24 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF24 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.174 | hwPDU80001QF25Temperature | 1QF25 Temperature(L1) | 1QF25 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF25 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.175 | hwPDU80001QF26Temperature | 1QF26 Temperature(L2) | 1QF26 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF26 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.176 | hwPDU80001QF27Temperature | 1QF27 Temperature(L3) | 1QF27 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF27 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.177 | hwPDU80001QF28Temperature | 1QF28 Temperature(L1) | 1QF28 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF28 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.178 | hwPDU80001QF29Temperature | 1QF29 Temperature(L2) | 1QF29 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF29 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.179 | hwPDU80001QF30Temperature | 1QF30 Temperature(L3) | 1QF30 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF30 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.180 | hwPDU80001QF31Temperature | 1QF31 Temperature(L1) | 1QF31 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF31 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.181 | hwPDU80001QF32Temperature | 1QF32 Temperature(L2) | 1QF32 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF32 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.182 | hwPDU80001QF33Temperature | 1QF33 Temperature(L3) | 1QF33 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF33 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.183 | hwPDU80001QF34Temperature | 1QF34 Temperature(L1) | 1QF34 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF34 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.184 | hwPDU80001QF35Temperature | 1QF35 Temperature(L2) | 1QF35 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF35 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.185 | hwPDU80001QF36Temperature | 1QF36 Temperature(L3) | 1QF36 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF36 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.186 | hwPDU80001QF37Temperature | 1QF37 Temperature(L1) | 1QF37 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF37 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.187 | hwPDU80001QF38Temperature | 1QF38 Temperature(L2) | 1QF38 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF38 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.188 | hwPDU80001QF39Temperature | 1QF39 Temperature(L3) | 1QF39 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF39 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.189 | hwPDU80001QF40Temperature | 1QF40 Temperature(L1) | 1QF40 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF40 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.190 | hwPDU80001QF41Temperature | 1QF41 Temperature(L2) | 1QF41 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF41 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.191 | hwPDU80001QF42Temperature | 1QF42 Temperature(L3) | 1QF42 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF42 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.192 | hwPDU80001QF43Temperature | 1QF43 Temperature(L1) | 1QF43 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF43 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.193 | hwPDU80001QF44Temperature | 1QF44 Temperature(L2) | 1QF44 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF44 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.194 | hwPDU80001QF45Temperature | 1QF45 Temperature(L3) | 1QF45 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF45 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.195 | hwPDU80001QF46Temperature | 1QF46 Temperature(L1) | 1QF46 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF46 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.196 | hwPDU80001QF47Temperature | 1QF47 Temperature(L2) | 1QF47 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF47 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.197 | hwPDU80001QF48Temperature | 1QF48 Temperature(L3) | 1QF48 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF48 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.198 | hwPDU80001QF49Temperature | 1QF49 Temperature(L1) | 1QF49 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF49 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.199 | hwPDU80001QF50Temperature | 1QF50 Temperature(L2) | 1QF50 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF50 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.200 | hwPDU80001QF51Temperature | 1QF51 Temperature(L3) | 1QF51 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF51 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.201 | hwPDU80001QF52Temperature | 1QF52 Temperature(L1) | 1QF52 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF52 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.202 | hwPDU80001QF53Temperature | 1QF53 Temperature(L2) | 1QF53 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF53 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.203 | hwPDU80001QF54Temperature | 1QF54 Temperature(L3) | 1QF54 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF54 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.204 | hwPDU80001QF55Temperature | 1QF55 Temperature(L1) | 1QF55 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF55 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.205 | hwPDU80001QF56Temperature | 1QF56 Temperature(L2) | 1QF56 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF56 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.206 | hwPDU80001QF57Temperature | 1QF57 Temperature(L3) | 1QF57 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF57 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.207 | hwPDU80001QF58Temperature | 1QF58 Temperature(L1) | 1QF58 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF58 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.208 | hwPDU80001QF59Temperature | 1QF59 Temperature(L2) | 1QF59 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF59 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.209 | hwPDU80001QF60Temperature | 1QF60 Temperature(L3) | 1QF60 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF60 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.210 | hwPDU80001QF61Temperature | 1QF61 Temperature(L1) | 1QF61 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF61 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.211 | hwPDU80001QF62Temperature | 1QF62 Temperature(L2) | 1QF62 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF62 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.212 | hwPDU80001QF63Temperature | 1QF63 Temperature(L3) | 1QF63 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF63 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.213 | hwPDU80001QF64Temperature | 1QF64 Temperature(L1) | 1QF64 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF64 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.214 | hwPDU80001QF65Temperature | 1QF65 Temperature(L2) | 1QF65 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF65 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.215 | hwPDU80001QF66Temperature | 1QF66 Temperature(L3) | 1QF66 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF66 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.216 | hwPDU80001QF67Temperature | 1QF67 Temperature(L1) | 1QF67 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF67 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.217 | hwPDU80001QF68Temperature | 1QF68 Temperature(L2) | 1QF68 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF68 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.218 | hwPDU80001QF69Temperature | 1QF69 Temperature(L3) | 1QF69 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF69 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.219 | hwPDU80001QF70Temperature | 1QF70 Temperature(L1) | 1QF70 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF70 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.220 | hwPDU80001QF71Temperature | 1QF71 Temperature(L2) | 1QF71 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF71 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.221 | hwPDU80001QF72Temperature | 1QF72 Temperature(L3) | 1QF72 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF72 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.7.1.225 | hwPDU8000Running7RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8 | hwPDU8000Running8Table | / | / |  |  | / | / | The running table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.1 | hwPDU8000Running8Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.2 | hwPDU80002QF1Temperature | 2QF1 Temperature(L1) | 2QF1 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF1 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.3 | hwPDU80002QF2Temperature | 2QF2 Temperature(L2) | 2QF2 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF2 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.4 | hwPDU80002QF3Temperature | 2QF3 Temperature(L3) | 2QF3 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF3 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.5 | hwPDU80002QF4Temperature | 2QF4 Temperature(L1) | 2QF4 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF4 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.6 | hwPDU80002QF5Temperature | 2QF5 Temperature(L2) | 2QF5 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF5 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.7 | hwPDU80002QF6Temperature | 2QF6 Temperature(L3) | 2QF6 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF6 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.8 | hwPDU80002QF7Temperature | 2QF7 Temperature(L1) | 2QF7 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF7 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.9 | hwPDU80002QF8Temperature | 2QF8 Temperature(L2) | 2QF8 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF8 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.10 | hwPDU80002QF9Temperature | 2QF9 Temperature(L3) | 2QF9 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF9 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.11 | hwPDU80002QF10Temperature | 2QF10 Temperature(L1) | 2QF10 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF10 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.12 | hwPDU80002QF11Temperature | 2QF11 Temperature(L2) | 2QF11 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF11 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.13 | hwPDU80002QF12Temperature | 2QF12 Temperature(L3) | 2QF12 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF12 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.14 | hwPDU80002QF13Temperature | 2QF13 Temperature(L1) | 2QF13 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF13 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.15 | hwPDU80002QF14Temperature | 2QF14 Temperature(L2) | 2QF14 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF14 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.16 | hwPDU80002QF15Temperature | 2QF15 Temperature(L3) | 2QF15 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF15 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.17 | hwPDU80002QF16Temperature | 2QF16 Temperature(L1) | 2QF16 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF16 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.18 | hwPDU80002QF17Temperature | 2QF17 Temperature(L2) | 2QF17 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF17 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.19 | hwPDU80002QF18Temperature | 2QF18 Temperature(L3) | 2QF18 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF18 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.20 | hwPDU80002QF19Temperature | 2QF19 Temperature(L1) | 2QF19 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF19 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.21 | hwPDU80002QF20Temperature | 2QF20 Temperature(L2) | 2QF20 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF20 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.22 | hwPDU80002QF21Temperature | 2QF21 Temperature(L3) | 2QF21 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF21 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.23 | hwPDU80002QF22Temperature | 2QF22 Temperature(L1) | 2QF22 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF22 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.24 | hwPDU80002QF23Temperature | 2QF23 Temperature(L2) | 2QF23 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF23 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.25 | hwPDU80002QF24Temperature | 2QF24 Temperature(L3) | 2QF24 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF24 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.26 | hwPDU80002QF25Temperature | 2QF25 Temperature(L1) | 2QF25 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF25 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.27 | hwPDU80002QF26Temperature | 2QF26 Temperature(L2) | 2QF26 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF26 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.28 | hwPDU80002QF27Temperature | 2QF27 Temperature(L3) | 2QF27 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF27 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.29 | hwPDU80002QF28Temperature | 2QF28 Temperature(L1) | 2QF28 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF28 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.30 | hwPDU80002QF29Temperature | 2QF29 Temperature(L2) | 2QF29 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF29 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.31 | hwPDU80002QF30Temperature | 2QF30 Temperature(L3) | 2QF30 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF30 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.32 | hwPDU80002QF31Temperature | 2QF31 Temperature(L1) | 2QF31 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF31 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.33 | hwPDU80002QF32Temperature | 2QF32 Temperature(L2) | 2QF32 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF32 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.34 | hwPDU80002QF33Temperature | 2QF33 Temperature(L3) | 2QF33 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF33 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.35 | hwPDU80002QF34Temperature | 2QF34 Temperature(L1) | 2QF34 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF34 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.36 | hwPDU80002QF35Temperature | 2QF35 Temperature(L2) | 2QF35 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF35 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.37 | hwPDU80002QF36Temperature | 2QF36 Temperature(L3) | 2QF36 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF36 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.38 | hwPDU80002QF37Temperature | 2QF37 Temperature(L1) | 2QF37 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF37 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.39 | hwPDU80002QF38Temperature | 2QF38 Temperature(L2) | 2QF38 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF38 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.40 | hwPDU80002QF39Temperature | 2QF39 Temperature(L3) | 2QF39 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF39 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.41 | hwPDU80002QF40Temperature | 2QF40 Temperature(L1) | 2QF40 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF40 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.42 | hwPDU80002QF41Temperature | 2QF41 Temperature(L2) | 2QF41 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF41 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.43 | hwPDU80002QF42Temperature | 2QF42 Temperature(L3) | 2QF42 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF42 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.44 | hwPDU80002QF43Temperature | 2QF43 Temperature(L1) | 2QF43 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF43 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.45 | hwPDU80002QF44Temperature | 2QF44 Temperature(L2) | 2QF44 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF44 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.46 | hwPDU80002QF45Temperature | 2QF45 Temperature(L3) | 2QF45 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF45 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.47 | hwPDU80002QF46Temperature | 2QF46 Temperature(L1) | 2QF46 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF46 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.48 | hwPDU80002QF47Temperature | 2QF47 Temperature(L2) | 2QF47 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF47 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.49 | hwPDU80002QF48Temperature | 2QF48 Temperature(L3) | 2QF48 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF48 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.50 | hwPDU80002QF49Temperature | 2QF49 Temperature(L1) | 2QF49 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF49 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.51 | hwPDU80002QF50Temperature | 2QF50 Temperature(L2) | 2QF50 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF50 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.52 | hwPDU80002QF51Temperature | 2QF51 Temperature(L3) | 2QF51 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF51 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.53 | hwPDU80002QF52Temperature | 2QF52 Temperature(L1) | 2QF52 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF52 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.54 | hwPDU80002QF53Temperature | 2QF53 Temperature(L2) | 2QF53 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF53 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.55 | hwPDU80002QF54Temperature | 2QF54 Temperature(L3) | 2QF54 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF54 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.56 | hwPDU80002QF55Temperature | 2QF55 Temperature(L1) | 2QF55 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF55 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.57 | hwPDU80002QF56Temperature | 2QF56 Temperature(L2) | 2QF56 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF56 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.58 | hwPDU80002QF57Temperature | 2QF57 Temperature(L3) | 2QF57 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF57 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.59 | hwPDU80002QF58Temperature | 2QF58 Temperature(L1) | 2QF58 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF58 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.60 | hwPDU80002QF59Temperature | 2QF59 Temperature(L2) | 2QF59 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF59 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.61 | hwPDU80002QF60Temperature | 2QF60 Temperature(L3) | 2QF60 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF60 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.62 | hwPDU80002QF61Temperature | 2QF61 Temperature(L1) | 2QF61 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF61 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.63 | hwPDU80002QF62Temperature | 2QF62 Temperature(L2) | 2QF62 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF62 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.64 | hwPDU80002QF63Temperature | 2QF63 Temperature(L3) | 2QF63 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF63 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.65 | hwPDU80002QF64Temperature | 2QF64 Temperature(L1) | 2QF64 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF64 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.66 | hwPDU80002QF65Temperature | 2QF65 Temperature(L2) | 2QF65 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF65 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.67 | hwPDU80002QF66Temperature | 2QF66 Temperature(L3) | 2QF66 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF66 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.68 | hwPDU80002QF67Temperature | 2QF67 Temperature(L1) | 2QF67 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF67 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.69 | hwPDU80002QF68Temperature | 2QF68 Temperature(L2) | 2QF68 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF68 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.70 | hwPDU80002QF69Temperature | 2QF69 Temperature(L3) | 2QF69 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF69 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.71 | hwPDU80002QF70Temperature | 2QF70 Temperature(L1) | 2QF70 温度(L1) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF70 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.72 | hwPDU80002QF71Temperature | 2QF71 Temperature(L2) | 2QF71 温度(L2) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF71 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.73 | hwPDU80002QF72Temperature | 2QF72 Temperature(L3) | 2QF72 温度(L3) | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF72 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.74 | hwPDU8000MIInputSwitchStatus | Main input switch status | 主路输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Main Input Switch Status: Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.75 | hwPDU8000MIInputLightningStatus | Main input SPD status | 主路输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Main Input Lightning Status: Value 1 indicates Abnormal. Value 2 indicates Normal.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.76 | hwPDU8000M1IInputSwitchStatus | Main input 1 switch status | 1路输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Main 1 Input Switch Status: Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.77 | hwPDU8000M1IInputLightningStatus | Main input 1 SPD status | 1路输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Main 1 Input Lightning Status: Value 1 indicates Abnormal. Value 2 indicates Normal.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.78 | hwPDU8000M2IInputSwitchStatus | Main input 2 switch status | 2路输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Main 2 Input Switch Status: Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.79 | hwPDU8000M2IInputLightningStatus | Main input 2 SPD status | 2路输入防雷器状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [异常=1]/[正常=2] | Main 2 Input Lightning Status: Value 1 indicates Abnormal. Value 2 indicates Normal.
1.3.6.1.4.1.2011.6.178.1.1.9.5.8.1.100 | hwPDU8000Running8RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.9 | hwPDU8000Running9Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.1 | hwPDU8000Running9Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.2 | hwPDU8000OutputBranch1NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 1 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.3 | hwPDU8000OutputBranch2NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 2 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.4 | hwPDU8000OutputBranch3NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 3 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.5 | hwPDU8000OutputBranch4NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 4 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.6 | hwPDU8000OutputBranch5NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 5 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.7 | hwPDU8000OutputBranch6NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 6 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.8 | hwPDU8000OutputBranch7NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 7 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.9 | hwPDU8000OutputBranch8NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 8 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.10 | hwPDU8000OutputBranch9NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 9 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.11 | hwPDU8000OutputBranch10NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 10 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.12 | hwPDU8000OutputBranch11NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 11 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.13 | hwPDU8000OutputBranch12NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 12 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.14 | hwPDU8000OutputBranch13NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 13 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.15 | hwPDU8000OutputBranch14NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 14 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.16 | hwPDU8000OutputBranch15NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 15 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.17 | hwPDU8000OutputBranch16NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 16 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.18 | hwPDU8000OutputBranch17NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 17 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.19 | hwPDU8000OutputBranch18NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 18 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.20 | hwPDU8000OutputBranch19NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 19 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.21 | hwPDU8000OutputBranch20NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 20 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.22 | hwPDU8000OutputBranch21NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 21 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.23 | hwPDU8000OutputBranch22NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 22 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.24 | hwPDU8000OutputBranch23NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 23 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.25 | hwPDU8000OutputBranch24NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 24 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.26 | hwPDU8000OutputBranch25NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 25 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.27 | hwPDU8000OutputBranch26NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 26 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.28 | hwPDU8000OutputBranch27NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 27 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.29 | hwPDU8000OutputBranch28NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 28 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.30 | hwPDU8000OutputBranch29NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 29 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.31 | hwPDU8000OutputBranch30NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 30 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.32 | hwPDU8000OutputBranch31NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 31 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.33 | hwPDU8000OutputBranch32NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 32 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.34 | hwPDU8000OutputBranch33NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 33 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.35 | hwPDU8000OutputBranch34NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 34 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.36 | hwPDU8000OutputBranch35NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 35 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.37 | hwPDU8000OutputBranch36NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 36 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.38 | hwPDU8000OutputBranch37NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 37 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.39 | hwPDU8000OutputBranch38NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 38 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.40 | hwPDU8000OutputBranch39NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 39 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.41 | hwPDU8000OutputBranch40NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 40 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.42 | hwPDU8000OutputBranch41NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 41 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.43 | hwPDU8000OutputBranch42NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 42 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.44 | hwPDU8000OutputBranch43NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 43 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.45 | hwPDU8000OutputBranch44NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 44 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.46 | hwPDU8000OutputBranch45NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 45 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.47 | hwPDU8000OutputBranch46NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 46 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.48 | hwPDU8000OutputBranch47NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 47 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.49 | hwPDU8000OutputBranch48NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 48 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.50 | hwPDU8000OutputBranch49NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 49 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.51 | hwPDU8000OutputBranch50NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 50 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.52 | hwPDU8000OutputBranch51NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 51 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.53 | hwPDU8000OutputBranch52NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 52 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.54 | hwPDU8000OutputBranch53NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 53 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.55 | hwPDU8000OutputBranch54NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 54 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.56 | hwPDU8000OutputBranch55NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 55 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.57 | hwPDU8000OutputBranch56NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 56 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.58 | hwPDU8000OutputBranch57NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 57 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.59 | hwPDU8000OutputBranch58NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 58 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.60 | hwPDU8000OutputBranch59NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 59 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.61 | hwPDU8000OutputBranch60NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 60 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.62 | hwPDU8000OutputBranch61NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 61 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.63 | hwPDU8000OutputBranch62NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 62 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.64 | hwPDU8000OutputBranch63NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 63 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.65 | hwPDU8000OutputBranch64NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 64 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.66 | hwPDU8000OutputBranch65NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 65 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.67 | hwPDU8000OutputBranch66NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 66 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.68 | hwPDU8000OutputBranch67NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 67 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.69 | hwPDU8000OutputBranch68NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 68 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.70 | hwPDU8000OutputBranch69NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 69 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.71 | hwPDU8000OutputBranch70NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 70 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.72 | hwPDU8000OutputBranch71NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 71 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.73 | hwPDU8000OutputBranch72NameOfMainInput1 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 72 Name Of Main Input 1
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.74 | hwPDU8000OutputBranch1NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 1 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.75 | hwPDU8000OutputBranch2NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 2 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.76 | hwPDU8000OutputBranch3NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 3 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.77 | hwPDU8000OutputBranch4NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 4 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.78 | hwPDU8000OutputBranch5NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 5 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.79 | hwPDU8000OutputBranch6NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 6 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.80 | hwPDU8000OutputBranch7NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 7 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.81 | hwPDU8000OutputBranch8NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 8 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.82 | hwPDU8000OutputBranch9NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 9 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.83 | hwPDU8000OutputBranch10NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 10 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.84 | hwPDU8000OutputBranch11NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 11 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.85 | hwPDU8000OutputBranch12NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 12 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.86 | hwPDU8000OutputBranch13NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 13 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.87 | hwPDU8000OutputBranch14NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 14 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.88 | hwPDU8000OutputBranch15NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 15 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.89 | hwPDU8000OutputBranch16NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 16 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.90 | hwPDU8000OutputBranch17NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 17 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.91 | hwPDU8000OutputBranch18NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 18 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.92 | hwPDU8000OutputBranch19NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 19 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.93 | hwPDU8000OutputBranch20NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 20 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.94 | hwPDU8000OutputBranch21NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 21 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.95 | hwPDU8000OutputBranch22NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 22 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.96 | hwPDU8000OutputBranch23NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 23 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.97 | hwPDU8000OutputBranch24NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 24 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.98 | hwPDU8000OutputBranch25NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 25 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.99 | hwPDU8000OutputBranch26NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 26 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.100 | hwPDU8000OutputBranch27NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 27 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.101 | hwPDU8000OutputBranch28NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 28 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.102 | hwPDU8000OutputBranch29NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 29 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.103 | hwPDU8000OutputBranch30NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 30 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.104 | hwPDU8000OutputBranch31NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 31 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.105 | hwPDU8000OutputBranch32NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 32 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.106 | hwPDU8000OutputBranch33NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 33 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.107 | hwPDU8000OutputBranch34NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 34 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.108 | hwPDU8000OutputBranch35NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 35 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.109 | hwPDU8000OutputBranch36NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 36 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.110 | hwPDU8000OutputBranch37NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 37 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.111 | hwPDU8000OutputBranch38NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 38 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.112 | hwPDU8000OutputBranch39NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 39 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.113 | hwPDU8000OutputBranch40NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 40 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.114 | hwPDU8000OutputBranch41NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 41 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.115 | hwPDU8000OutputBranch42NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 42 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.116 | hwPDU8000OutputBranch43NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 43 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.117 | hwPDU8000OutputBranch44NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 44 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.118 | hwPDU8000OutputBranch45NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 45 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.119 | hwPDU8000OutputBranch46NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 46 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.120 | hwPDU8000OutputBranch47NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 47 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.121 | hwPDU8000OutputBranch48NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 48 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.122 | hwPDU8000OutputBranch49NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 49 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.123 | hwPDU8000OutputBranch50NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 50 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.124 | hwPDU8000OutputBranch51NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 51 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.125 | hwPDU8000OutputBranch52NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 52 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.126 | hwPDU8000OutputBranch53NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 53 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.127 | hwPDU8000OutputBranch54NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 54 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.128 | hwPDU8000OutputBranch55NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 55 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.129 | hwPDU8000OutputBranch56NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 56 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.130 | hwPDU8000OutputBranch57NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 57 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.131 | hwPDU8000OutputBranch58NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 58 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.132 | hwPDU8000OutputBranch59NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 59 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.133 | hwPDU8000OutputBranch60NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 60 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.134 | hwPDU8000OutputBranch61NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 61 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.135 | hwPDU8000OutputBranch62NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 62 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.136 | hwPDU8000OutputBranch63NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 63 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.137 | hwPDU8000OutputBranch64NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 64 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.138 | hwPDU8000OutputBranch65NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 65 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.139 | hwPDU8000OutputBranch66NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 66 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.140 | hwPDU8000OutputBranch67NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 67 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.141 | hwPDU8000OutputBranch68NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 68 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.142 | hwPDU8000OutputBranch69NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 69 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.143 | hwPDU8000OutputBranch70NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 70 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.144 | hwPDU8000OutputBranch71NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 71 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.145 | hwPDU8000OutputBranch72NameOfMainInput2 | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 72 Name Of Main Input 2
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.150 | hwPDU8000TransformerOutputSwitchStatus | Transformer output switch status | 变压器输出开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Transformer output switch status: Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.151 | hwPDU8000TransformerInputSwitchStatus | Transformer input switch status | 变压器输入开关状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [断开=1]/[闭合=2] | Transformer input switch status: Value 1 indicates Abnormal. Value 2 indicates Normal.
1.3.6.1.4.1.2011.6.178.1.1.9.5.9.1.200 | hwPDU8000Running9RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.10 | hwPDU8000Running10Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.1 | hwPDU8000Running10Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.2 | hwPDU8000OutputBranch1Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 1 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.3 | hwPDU8000OutputBranch2Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 2 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.4 | hwPDU8000OutputBranch3Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 3 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.5 | hwPDU8000OutputBranch4Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 4 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.6 | hwPDU8000OutputBranch5Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 5 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.7 | hwPDU8000OutputBranch6Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 6 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.8 | hwPDU8000OutputBranch7Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 7 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.9 | hwPDU8000OutputBranch8Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 8 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.10 | hwPDU8000OutputBranch9Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 9 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.11 | hwPDU8000OutputBranch10Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 10 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.12 | hwPDU8000OutputBranch11Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 11 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.13 | hwPDU8000OutputBranch12Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 12 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.14 | hwPDU8000OutputBranch13Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 13 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.15 | hwPDU8000OutputBranch14Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 14 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.16 | hwPDU8000OutputBranch15Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 15 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.17 | hwPDU8000OutputBranch16Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 16 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.18 | hwPDU8000OutputBranch17Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 17 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.19 | hwPDU8000OutputBranch18Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 18 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.20 | hwPDU8000OutputBranch19Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 19 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.21 | hwPDU8000OutputBranch20Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 20 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.22 | hwPDU8000OutputBranch21Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 21 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.23 | hwPDU8000OutputBranch22Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 22 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.24 | hwPDU8000OutputBranch23Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 23 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.25 | hwPDU8000OutputBranch24Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 24 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.26 | hwPDU8000OutputBranch25Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 25 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.27 | hwPDU8000OutputBranch26Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 26 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.28 | hwPDU8000OutputBranch27Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 27 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.29 | hwPDU8000OutputBranch28Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 28 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.30 | hwPDU8000OutputBranch29Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 29 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.31 | hwPDU8000OutputBranch30Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 30 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.32 | hwPDU8000OutputBranch31Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 31 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.33 | hwPDU8000OutputBranch32Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 32 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.34 | hwPDU8000OutputBranch33Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 33 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.35 | hwPDU8000OutputBranch34Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 34 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.36 | hwPDU8000OutputBranch35Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 35 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.37 | hwPDU8000OutputBranch36Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 36 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.38 | hwPDU8000OutputBranch37Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 37 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.39 | hwPDU8000OutputBranch38Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 38 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.40 | hwPDU8000OutputBranch39Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 39 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.41 | hwPDU8000OutputBranch40Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 40 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.42 | hwPDU8000OutputBranch41Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 41 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.43 | hwPDU8000OutputBranch42Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 42 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.44 | hwPDU8000OutputBranch43Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 43 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.45 | hwPDU8000OutputBranch44Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 44 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.46 | hwPDU8000OutputBranch45Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 45 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.47 | hwPDU8000OutputBranch46Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 46 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.48 | hwPDU8000OutputBranch47Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 47 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.49 | hwPDU8000OutputBranch48Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 48 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.50 | hwPDU8000OutputBranch49Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 49 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.51 | hwPDU8000OutputBranch50Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 50 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.52 | hwPDU8000OutputBranch51Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 51 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.53 | hwPDU8000OutputBranch52Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 52 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.54 | hwPDU8000OutputBranch53Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 53 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.55 | hwPDU8000OutputBranch54Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 54 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.56 | hwPDU8000OutputBranch55Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 55 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.57 | hwPDU8000OutputBranch56Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 56 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.58 | hwPDU8000OutputBranch57Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 57 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.59 | hwPDU8000OutputBranch58Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 58 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.60 | hwPDU8000OutputBranch59Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 59 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.61 | hwPDU8000OutputBranch60Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 60 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.62 | hwPDU8000OutputBranch61Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 61 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.63 | hwPDU8000OutputBranch62Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 62 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.64 | hwPDU8000OutputBranch63Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 63 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.65 | hwPDU8000OutputBranch64Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 64 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.66 | hwPDU8000OutputBranch65Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 65 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.67 | hwPDU8000OutputBranch66Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 66 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.68 | hwPDU8000OutputBranch67Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 67 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.69 | hwPDU8000OutputBranch68Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 68 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.70 | hwPDU8000OutputBranch69Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 69 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.71 | hwPDU8000OutputBranch70Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 70 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.72 | hwPDU8000OutputBranch71Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 71 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.73 | hwPDU8000OutputBranch72Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 72 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.74 | hwPDU8000OutputBranch73Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 73 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.75 | hwPDU8000OutputBranch74Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 74 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.76 | hwPDU8000OutputBranch75Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 75 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.77 | hwPDU8000OutputBranch76Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 76 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.78 | hwPDU8000OutputBranch77Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 77 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.79 | hwPDU8000OutputBranch78Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 78 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.80 | hwPDU8000OutputBranch79Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 79 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.81 | hwPDU8000OutputBranch80Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 80 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.82 | hwPDU8000OutputBranch81Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 81 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.83 | hwPDU8000OutputBranch82Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 82 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.84 | hwPDU8000OutputBranch83Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 83 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.85 | hwPDU8000OutputBranch84Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 84 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.86 | hwPDU8000OutputBranch85Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 85 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.87 | hwPDU8000OutputBranch86Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 86 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.88 | hwPDU8000OutputBranch87Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 87 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.89 | hwPDU8000OutputBranch88Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 88 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.90 | hwPDU8000OutputBranch89Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 89 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.91 | hwPDU8000OutputBranch90Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 90 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.92 | hwPDU8000OutputBranch91Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 91 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.93 | hwPDU8000OutputBranch92Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 92 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.94 | hwPDU8000OutputBranch93Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 93 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.95 | hwPDU8000OutputBranch94Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 94 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.96 | hwPDU8000OutputBranch95Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 95 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.97 | hwPDU8000OutputBranch96Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 96 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.98 | hwPDU8000OutputBranch97Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 97 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.99 | hwPDU8000OutputBranch98Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 98 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.100 | hwPDU8000OutputBranch99Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 99 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.101 | hwPDU8000OutputBranch100Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 100 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.102 | hwPDU8000OutputBranch101Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 101 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.103 | hwPDU8000OutputBranch102Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 102 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.104 | hwPDU8000OutputBranch103Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 103 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.105 | hwPDU8000OutputBranch104Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 104 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.106 | hwPDU8000OutputBranch105Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 105 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.107 | hwPDU8000OutputBranch106Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 106 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.108 | hwPDU8000OutputBranch107Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 107 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.109 | hwPDU8000OutputBranch108Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 108 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.110 | hwPDU8000OutputBranch109Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 109 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.111 | hwPDU8000OutputBranch110Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 110 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.112 | hwPDU8000OutputBranch111Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 111 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.113 | hwPDU8000OutputBranch112Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 112 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.114 | hwPDU8000OutputBranch113Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 113 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.115 | hwPDU8000OutputBranch114Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 114 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.116 | hwPDU8000OutputBranch115Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 115 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.117 | hwPDU8000OutputBranch116Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 116 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.118 | hwPDU8000OutputBranch117Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 117 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.119 | hwPDU8000OutputBranch118Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 118 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.120 | hwPDU8000OutputBranch119Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 119 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.121 | hwPDU8000OutputBranch120Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 120 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.122 | hwPDU8000OutputBranch121Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 121 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.123 | hwPDU8000OutputBranch122Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 122 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.124 | hwPDU8000OutputBranch123Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 123 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.125 | hwPDU8000OutputBranch124Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 124 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.126 | hwPDU8000OutputBranch125Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 125 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.127 | hwPDU8000OutputBranch126Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 126 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.128 | hwPDU8000OutputBranch127Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 127 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.129 | hwPDU8000OutputBranch128Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 128 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.130 | hwPDU8000OutputBranch129Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 129 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.131 | hwPDU8000OutputBranch130Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 130 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.132 | hwPDU8000OutputBranch131Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 131 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.133 | hwPDU8000OutputBranch132Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 132 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.134 | hwPDU8000OutputBranch133Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 133 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.135 | hwPDU8000OutputBranch134Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 134 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.136 | hwPDU8000OutputBranch135Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 135 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.137 | hwPDU8000OutputBranch136Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 136 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.138 | hwPDU8000OutputBranch137Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 137 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.139 | hwPDU8000OutputBranch138Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 138 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.140 | hwPDU8000OutputBranch139Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 139 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.141 | hwPDU8000OutputBranch140Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 140 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.142 | hwPDU8000OutputBranch141Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 141 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.143 | hwPDU8000OutputBranch142Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 142 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.144 | hwPDU8000OutputBranch143Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 143 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.145 | hwPDU8000OutputBranch144Name | QF | QF | 0-Read_Only | 只读 | 1..50 | 1..50 | Output Branch 144 Name
1.3.6.1.4.1.2011.6.178.1.1.9.5.10.1.150 | hwPDU8000Running10RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.11 | hwPDU8000Running11Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.1 | hwPDU8000Running11Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.2 | hwPDU8000QF1OutputActivePower | QF1 Output active power(L1) | QF1 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF1 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.3 | hwPDU8000QF2OutputActivePower | QF2 Output active power(L2) | QF2 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF2 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.4 | hwPDU8000QF3OutputActivePower | QF3 Output active power(L3) | QF3 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF3 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.5 | hwPDU8000QF4OutputActivePower | QF4 Output active power(L1) | QF4 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF4 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.6 | hwPDU8000QF5OutputActivePower | QF5 Output active power(L2) | QF5 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF5 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.7 | hwPDU8000QF6OutputActivePower | QF6 Output active power(L3) | QF6 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF6 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.8 | hwPDU8000QF7OutputActivePower | QF7 Output active power(L1) | QF7 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF7 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.9 | hwPDU8000QF8OutputActivePower | QF8 Output active power(L2) | QF8 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF8 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.10 | hwPDU8000QF9OutputActivePower | QF9 Output active power(L3) | QF9 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF9 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.11 | hwPDU8000QF10OutputActivePower | QF10 Output active power(L1) | QF10 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF10 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.12 | hwPDU8000QF11OutputActivePower | QF11 Output active power(L2) | QF11 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF11 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.13 | hwPDU8000QF12OutputActivePower | QF12 Output active power(L3) | QF12 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF12 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.14 | hwPDU8000QF13OutputActivePower | QF13 Output active power(L1) | QF13 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF13 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.15 | hwPDU8000QF14OutputActivePower | QF14 Output active power(L2) | QF14 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF14 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.16 | hwPDU8000QF15OutputActivePower | QF15 Output active power(L3) | QF15 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF15 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.17 | hwPDU8000QF16OutputActivePower | QF16 Output active power(L1) | QF16 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF16 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.18 | hwPDU8000QF17OutputActivePower | QF17 Output active power(L2) | QF17 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF17 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.19 | hwPDU8000QF18OutputActivePower | QF18 Output active power(L3) | QF18 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF18 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.20 | hwPDU8000QF19OutputActivePower | QF19 Output active power(L1) | QF19 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF19 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.21 | hwPDU8000QF20OutputActivePower | QF20 Output active power(L2) | QF20 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF20 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.22 | hwPDU8000QF21OutputActivePower | QF21 Output active power(L3) | QF21 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF21 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.23 | hwPDU8000QF22OutputActivePower | QF22 Output active power(L1) | QF22 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF22 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.24 | hwPDU8000QF23OutputActivePower | QF23 Output active power(L2) | QF23 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF23 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.25 | hwPDU8000QF24OutputActivePower | QF24 Output active power(L3) | QF24 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF24 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.26 | hwPDU8000QF25OutputActivePower | QF25 Output active power(L1) | QF25 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF25 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.27 | hwPDU8000QF26OutputActivePower | QF26 Output active power(L2) | QF26 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF26 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.28 | hwPDU8000QF27OutputActivePower | QF27 Output active power(L3) | QF27 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF27 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.29 | hwPDU8000QF28OutputActivePower | QF28 Output active power(L1) | QF28 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF28 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.30 | hwPDU8000QF29OutputActivePower | QF29 Output active power(L2) | QF29 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF29 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.31 | hwPDU8000QF30OutputActivePower | QF30 Output active power(L3) | QF30 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF30 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.32 | hwPDU8000QF31OutputActivePower | QF31 Output active power(L1) | QF31 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF31 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.33 | hwPDU8000QF32OutputActivePower | QF32 Output active power(L2) | QF32 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF32 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.34 | hwPDU8000QF33OutputActivePower | QF33 Output active power(L3) | QF33 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF33 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.35 | hwPDU8000QF34OutputActivePower | QF34 Output active power(L1) | QF34 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF34 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.36 | hwPDU8000QF35OutputActivePower | QF35 Output active power(L2) | QF35 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF35 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.37 | hwPDU8000QF36OutputActivePower | QF36 Output active power(L3) | QF36 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF36 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.38 | hwPDU8000QF37OutputActivePower | QF37 Output active power(L1) | QF37 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF37 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.39 | hwPDU8000QF38OutputActivePower | QF38 Output active power(L2) | QF38 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF38 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.40 | hwPDU8000QF39OutputActivePower | QF39 Output active power(L3) | QF39 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF39 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.41 | hwPDU8000QF40OutputActivePower | QF40 Output active power(L1) | QF40 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF40 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.42 | hwPDU8000QF41OutputActivePower | QF41 Output active power(L2) | QF41 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF41 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.43 | hwPDU8000QF42OutputActivePower | QF42 Output active power(L3) | QF42 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF42 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.44 | hwPDU8000QF43OutputActivePower | QF43 Output active power(L1) | QF43 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF43 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.45 | hwPDU8000QF44OutputActivePower | QF44 Output active power(L2) | QF44 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF44 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.46 | hwPDU8000QF45OutputActivePower | QF45 Output active power(L3) | QF45 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF45 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.47 | hwPDU8000QF46OutputActivePower | QF46 Output active power(L1) | QF46 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF46 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.48 | hwPDU8000QF47OutputActivePower | QF47 Output active power(L2) | QF47 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF47 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.49 | hwPDU8000QF48OutputActivePower | QF48 Output active power(L3) | QF48 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF48 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.50 | hwPDU8000QF49OutputActivePower | QF49 Output active power(L1) | QF49 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF49 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.51 | hwPDU8000QF50OutputActivePower | QF50 Output active power(L2) | QF50 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF50 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.52 | hwPDU8000QF51OutputActivePower | QF51 Output active power(L3) | QF51 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF51 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.53 | hwPDU8000QF52OutputActivePower | QF52 Output active power(L1) | QF52 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF52 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.54 | hwPDU8000QF53OutputActivePower | QF53 Output active power(L2) | QF53 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF53 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.55 | hwPDU8000QF54OutputActivePower | QF54 Output active power(L3) | QF54 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF54 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.56 | hwPDU8000QF55OutputActivePower | QF55 Output active power(L1) | QF55 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF55 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.57 | hwPDU8000QF56OutputActivePower | QF56 Output active power(L2) | QF56 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF56 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.58 | hwPDU8000QF57OutputActivePower | QF57 Output active power(L3) | QF57 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF57 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.59 | hwPDU8000QF58OutputActivePower | QF58 Output active power(L1) | QF58 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF58 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.60 | hwPDU8000QF59OutputActivePower | QF59 Output active power(L2) | QF59 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF59 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.61 | hwPDU8000QF60OutputActivePower | QF60 Output active power(L3) | QF60 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF60 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.62 | hwPDU8000QF61OutputActivePower | QF61 Output active power(L1) | QF61 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF61 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.63 | hwPDU8000QF62OutputActivePower | QF62 Output active power(L2) | QF62 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF62 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.64 | hwPDU8000QF63OutputActivePower | QF63 Output active power(L3) | QF63 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF63 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.65 | hwPDU8000QF64OutputActivePower | QF64 Output active power(L1) | QF64 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF64 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.66 | hwPDU8000QF65OutputActivePower | QF65 Output active power(L2) | QF65 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF65 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.67 | hwPDU8000QF66OutputActivePower | QF66 Output active power(L3) | QF66 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF66 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.68 | hwPDU8000QF67OutputActivePower | QF67 Output active power(L1) | QF67 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF67 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.69 | hwPDU8000QF68OutputActivePower | QF68 Output active power(L2) | QF68 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF68 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.70 | hwPDU8000QF69OutputActivePower | QF69 Output active power(L3) | QF69 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF69 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.71 | hwPDU8000QF70OutputActivePower | QF70 Output active power(L1) | QF70 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF70 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.72 | hwPDU8000QF71OutputActivePower | QF71 Output active power(L2) | QF71 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF71 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.73 | hwPDU8000QF72OutputActivePower | QF72 Output active power(L3) | QF72 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF72 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.74 | hwPDU8000QF73OutputActivePower | QF73 Output active power(L1) | QF73 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF73 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.75 | hwPDU8000QF74OutputActivePower | QF74 Output active power(L2) | QF74 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF74 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.76 | hwPDU8000QF75OutputActivePower | QF75 Output active power(L3) | QF75 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF75 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.77 | hwPDU8000QF76OutputActivePower | QF76 Output active power(L1) | QF76 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF76 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.78 | hwPDU8000QF77OutputActivePower | QF77 Output active power(L2) | QF77 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF77 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.79 | hwPDU8000QF78OutputActivePower | QF78 Output active power(L3) | QF78 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF78 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.80 | hwPDU8000QF79OutputActivePower | QF79 Output active power(L1) | QF79 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF79 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.81 | hwPDU8000QF80OutputActivePower | QF80 Output active power(L2) | QF80 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF80 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.82 | hwPDU8000QF81OutputActivePower | QF81 Output active power(L3) | QF81 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF81 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.83 | hwPDU8000QF82OutputActivePower | QF82 Output active power(L1) | QF82 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF82 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.84 | hwPDU8000QF83OutputActivePower | QF83 Output active power(L2) | QF83 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF83 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.85 | hwPDU8000QF84OutputActivePower | QF84 Output active power(L3) | QF84 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF84 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.86 | hwPDU8000QF85OutputActivePower | QF85 Output active power(L1) | QF85 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF85 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.87 | hwPDU8000QF86OutputActivePower | QF86 Output active power(L2) | QF86 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF86 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.88 | hwPDU8000QF87OutputActivePower | QF87 Output active power(L3) | QF87 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF87 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.89 | hwPDU8000QF88OutputActivePower | QF88 Output active power(L1) | QF88 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF88 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.90 | hwPDU8000QF89OutputActivePower | QF89 Output active power(L2) | QF89 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF89 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.91 | hwPDU8000QF90OutputActivePower | QF90 Output active power(L3) | QF90 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF90 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.92 | hwPDU8000QF91OutputActivePower | QF91 Output active power(L1) | QF91 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF91 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.93 | hwPDU8000QF92OutputActivePower | QF92 Output active power(L2) | QF92 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF92 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.94 | hwPDU8000QF93OutputActivePower | QF93 Output active power(L3) | QF93 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF93 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.95 | hwPDU8000QF94OutputActivePower | QF94 Output active power(L1) | QF94 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF94 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.96 | hwPDU8000QF95OutputActivePower | QF95 Output active power(L2) | QF95 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF95 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.97 | hwPDU8000QF96OutputActivePower | QF96 Output active power(L3) | QF96 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF96 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.98 | hwPDU8000QF97OutputActivePower | QF97 Output active power(L1) | QF97 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF97 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.99 | hwPDU8000QF98OutputActivePower | QF98 Output active power(L2) | QF98 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF98 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.100 | hwPDU8000QF99OutputActivePower | QF99 Output active power(L3) | QF99 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF99 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.101 | hwPDU8000QF100OutputActivePower | QF100 Output active power(L1) | QF100 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF100 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.102 | hwPDU8000QF101OutputActivePower | QF101 Output active power(L2) | QF101 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF101 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.103 | hwPDU8000QF102OutputActivePower | QF102 Output active power(L3) | QF102 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF102 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.104 | hwPDU8000QF103OutputActivePower | QF103 Output active power(L1) | QF103 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF103 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.105 | hwPDU8000QF104OutputActivePower | QF104 Output active power(L2) | QF104 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF104 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.106 | hwPDU8000QF105OutputActivePower | QF105 Output active power(L3) | QF105 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF105 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.107 | hwPDU8000QF106OutputActivePower | QF106 Output active power(L1) | QF106 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF106 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.108 | hwPDU8000QF107OutputActivePower | QF107 Output active power(L2) | QF107 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF107 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.109 | hwPDU8000QF108OutputActivePower | QF108 Output active power(L3) | QF108 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF108 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.110 | hwPDU8000QF109OutputActivePower | QF109 Output active power(L1) | QF109 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF109 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.111 | hwPDU8000QF110OutputActivePower | QF110 Output active power(L2) | QF110 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF110 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.112 | hwPDU8000QF111OutputActivePower | QF111 Output active power(L3) | QF111 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF111 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.113 | hwPDU8000QF112OutputActivePower | QF112 Output active power(L1) | QF112 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF112 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.114 | hwPDU8000QF113OutputActivePower | QF113 Output active power(L2) | QF113 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF113 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.115 | hwPDU8000QF114OutputActivePower | QF114 Output active power(L3) | QF114 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF114 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.116 | hwPDU8000QF115OutputActivePower | QF115 Output active power(L1) | QF115 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF115 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.117 | hwPDU8000QF116OutputActivePower | QF116 Output active power(L2) | QF116 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF116 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.118 | hwPDU8000QF117OutputActivePower | QF117 Output active power(L3) | QF117 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF117 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.119 | hwPDU8000QF118OutputActivePower | QF118 Output active power(L1) | QF118 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF118 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.120 | hwPDU8000QF119OutputActivePower | QF119 Output active power(L2) | QF119 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF119 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.121 | hwPDU8000QF120OutputActivePower | QF120 Output active power(L3) | QF120 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF120 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.122 | hwPDU8000QF121OutputActivePower | QF121 Output active power(L1) | QF121 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF121 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.123 | hwPDU8000QF122OutputActivePower | QF122 Output active power(L2) | QF122 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF122 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.124 | hwPDU8000QF123OutputActivePower | QF123 Output active power(L3) | QF123 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF123 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.125 | hwPDU8000QF124OutputActivePower | QF124 Output active power(L1) | QF124 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF124 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.126 | hwPDU8000QF125OutputActivePower | QF125 Output active power(L2) | QF125 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF125 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.127 | hwPDU8000QF126OutputActivePower | QF126 Output active power(L3) | QF126 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF126 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.128 | hwPDU8000QF127OutputActivePower | QF127 Output active power(L1) | QF127 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF127 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.129 | hwPDU8000QF128OutputActivePower | QF128 Output active power(L2) | QF128 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF128 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.130 | hwPDU8000QF129OutputActivePower | QF129 Output active power(L3) | QF129 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF129 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.131 | hwPDU8000QF130OutputActivePower | QF130 Output active power(L1) | QF130 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF130 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.132 | hwPDU8000QF131OutputActivePower | QF131 Output active power(L2) | QF131 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF131 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.133 | hwPDU8000QF132OutputActivePower | QF132 Output active power(L3) | QF132 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF132 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.134 | hwPDU8000QF133OutputActivePower | QF133 Output active power(L1) | QF133 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF133 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.135 | hwPDU8000QF134OutputActivePower | QF134 Output active power(L2) | QF134 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF134 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.136 | hwPDU8000QF135OutputActivePower | QF135 Output active power(L3) | QF135 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF135 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.137 | hwPDU8000QF136OutputActivePower | QF136 Output active power(L1) | QF136 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF136 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.138 | hwPDU8000QF137OutputActivePower | QF137 Output active power(L2) | QF137 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF137 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.139 | hwPDU8000QF138OutputActivePower | QF138 Output active power(L3) | QF138 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF138 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.140 | hwPDU8000QF139OutputActivePower | QF139 Output active power(L1) | QF139 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF139 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.141 | hwPDU8000QF140OutputActivePower | QF140 Output active power(L2) | QF140 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF140 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.142 | hwPDU8000QF141OutputActivePower | QF141 Output active power(L3) | QF141 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF141 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.143 | hwPDU8000QF142OutputActivePower | QF142 Output active power(L1) | QF142 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF142 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.144 | hwPDU8000QF143OutputActivePower | QF143 Output active power(L2) | QF143 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF143 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.145 | hwPDU8000QF144OutputActivePower | QF144 Output active power(L3) | QF144 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 QF144 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.11.1.200 | hwPDU8000Running11RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.12 | hwPDU8000Running12Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.1 | hwPDU8000Running12Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.2 | hwPDU80001QF1OutputActivePower | 1QF1 Output active power(L1) | 1QF1 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF1 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.3 | hwPDU80001QF2OutputActivePower | 1QF2 Output active power(L2) | 1QF2 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF2 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.4 | hwPDU80001QF3OutputActivePower | 1QF3 Output active power(L3) | 1QF3 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF3 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.5 | hwPDU80001QF4OutputActivePower | 1QF4 Output active power(L1) | 1QF4 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF4 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.6 | hwPDU80001QF5OutputActivePower | 1QF5 Output active power(L2) | 1QF5 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF5 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.7 | hwPDU80001QF6OutputActivePower | 1QF6 Output active power(L3) | 1QF6 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF6 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.8 | hwPDU80001QF7OutputActivePower | 1QF7 Output active power(L1) | 1QF7 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF7 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.9 | hwPDU80001QF8OutputActivePower | 1QF8 Output active power(L2) | 1QF8 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF8 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.10 | hwPDU80001QF9OutputActivePower | 1QF9 Output active power(L3) | 1QF9 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF9 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.11 | hwPDU80001QF10OutputActivePower | 1QF10 Output active power(L1) | 1QF10 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF10 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.12 | hwPDU80001QF11OutputActivePower | 1QF11 Output active power(L2) | 1QF11 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF11 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.13 | hwPDU80001QF12OutputActivePower | 1QF12 Output active power(L3) | 1QF12 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF12 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.14 | hwPDU80001QF13OutputActivePower | 1QF13 Output active power(L1) | 1QF13 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF13 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.15 | hwPDU80001QF14OutputActivePower | 1QF14 Output active power(L2) | 1QF14 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF14 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.16 | hwPDU80001QF15OutputActivePower | 1QF15 Output active power(L3) | 1QF15 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF15 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.17 | hwPDU80001QF16OutputActivePower | 1QF16 Output active power(L1) | 1QF16 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF16 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.18 | hwPDU80001QF17OutputActivePower | 1QF17 Output active power(L2) | 1QF17 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF17 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.19 | hwPDU80001QF18OutputActivePower | 1QF18 Output active power(L3) | 1QF18 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF18 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.20 | hwPDU80001QF19OutputActivePower | 1QF19 Output active power(L1) | 1QF19 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF19 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.21 | hwPDU80001QF20OutputActivePower | 1QF20 Output active power(L2) | 1QF20 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF20 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.22 | hwPDU80001QF21OutputActivePower | 1QF21 Output active power(L3) | 1QF21 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF21 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.23 | hwPDU80001QF22OutputActivePower | 1QF22 Output active power(L1) | 1QF22 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF22 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.24 | hwPDU80001QF23OutputActivePower | 1QF23 Output active power(L2) | 1QF23 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF23 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.25 | hwPDU80001QF24OutputActivePower | 1QF24 Output active power(L3) | 1QF24 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF24 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.26 | hwPDU80001QF25OutputActivePower | 1QF25 Output active power(L1) | 1QF25 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF25 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.27 | hwPDU80001QF26OutputActivePower | 1QF26 Output active power(L2) | 1QF26 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF26 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.28 | hwPDU80001QF27OutputActivePower | 1QF27 Output active power(L3) | 1QF27 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF27 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.29 | hwPDU80001QF28OutputActivePower | 1QF28 Output active power(L1) | 1QF28 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF28 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.30 | hwPDU80001QF29OutputActivePower | 1QF29 Output active power(L2) | 1QF29 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF29 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.31 | hwPDU80001QF30OutputActivePower | 1QF30 Output active power(L3) | 1QF30 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF30 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.32 | hwPDU80001QF31OutputActivePower | 1QF31 Output active power(L1) | 1QF31 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF31 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.33 | hwPDU80001QF32OutputActivePower | 1QF32 Output active power(L2) | 1QF32 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF32 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.34 | hwPDU80001QF33OutputActivePower | 1QF33 Output active power(L3) | 1QF33 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF33 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.35 | hwPDU80001QF34OutputActivePower | 1QF34 Output active power(L1) | 1QF34 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF34 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.36 | hwPDU80001QF35OutputActivePower | 1QF35 Output active power(L2) | 1QF35 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF35 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.37 | hwPDU80001QF36OutputActivePower | 1QF36 Output active power(L3) | 1QF36 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF36 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.38 | hwPDU80001QF37OutputActivePower | 1QF37 Output active power(L1) | 1QF37 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF37 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.39 | hwPDU80001QF38OutputActivePower | 1QF38 Output active power(L2) | 1QF38 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF38 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.40 | hwPDU80001QF39OutputActivePower | 1QF39 Output active power(L3) | 1QF39 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF39 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.41 | hwPDU80001QF40OutputActivePower | 1QF40 Output active power(L1) | 1QF40 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF40 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.42 | hwPDU80001QF41OutputActivePower | 1QF41 Output active power(L2) | 1QF41 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF41 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.43 | hwPDU80001QF42OutputActivePower | 1QF42 Output active power(L3) | 1QF42 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF42 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.44 | hwPDU80001QF43OutputActivePower | 1QF43 Output active power(L1) | 1QF43 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF43 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.45 | hwPDU80001QF44OutputActivePower | 1QF44 Output active power(L2) | 1QF44 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF44 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.46 | hwPDU80001QF45OutputActivePower | 1QF45 Output active power(L3) | 1QF45 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF45 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.47 | hwPDU80001QF46OutputActivePower | 1QF46 Output active power(L1) | 1QF46 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF46 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.48 | hwPDU80001QF47OutputActivePower | 1QF47 Output active power(L2) | 1QF47 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF47 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.49 | hwPDU80001QF48OutputActivePower | 1QF48 Output active power(L3) | 1QF48 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF48 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.50 | hwPDU80001QF49OutputActivePower | 1QF49 Output active power(L1) | 1QF49 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF49 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.51 | hwPDU80001QF50OutputActivePower | 1QF50 Output active power(L2) | 1QF50 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF50 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.52 | hwPDU80001QF51OutputActivePower | 1QF51 Output active power(L3) | 1QF51 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF51 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.53 | hwPDU80001QF52OutputActivePower | 1QF52 Output active power(L1) | 1QF52 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF52 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.54 | hwPDU80001QF53OutputActivePower | 1QF53 Output active power(L2) | 1QF53 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF53 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.55 | hwPDU80001QF54OutputActivePower | 1QF54 Output active power(L3) | 1QF54 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF54 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.56 | hwPDU80001QF55OutputActivePower | 1QF55 Output active power(L1) | 1QF55 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF55 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.57 | hwPDU80001QF56OutputActivePower | 1QF56 Output active power(L2) | 1QF56 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF56 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.58 | hwPDU80001QF57OutputActivePower | 1QF57 Output active power(L3) | 1QF57 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF57 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.59 | hwPDU80001QF58OutputActivePower | 1QF58 Output active power(L1) | 1QF58 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF58 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.60 | hwPDU80001QF59OutputActivePower | 1QF59 Output active power(L2) | 1QF59 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF59 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.61 | hwPDU80001QF60OutputActivePower | 1QF60 Output active power(L3) | 1QF60 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF60 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.62 | hwPDU80001QF61OutputActivePower | 1QF61 Output active power(L1) | 1QF61 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF61 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.63 | hwPDU80001QF62OutputActivePower | 1QF62 Output active power(L2) | 1QF62 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF62 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.64 | hwPDU80001QF63OutputActivePower | 1QF63 Output active power(L3) | 1QF63 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF63 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.65 | hwPDU80001QF64OutputActivePower | 1QF64 Output active power(L1) | 1QF64 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF64 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.66 | hwPDU80001QF65OutputActivePower | 1QF65 Output active power(L2) | 1QF65 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF65 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.67 | hwPDU80001QF66OutputActivePower | 1QF66 Output active power(L3) | 1QF66 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF66 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.68 | hwPDU80001QF67OutputActivePower | 1QF67 Output active power(L1) | 1QF67 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF67 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.69 | hwPDU80001QF68OutputActivePower | 1QF68 Output active power(L2) | 1QF68 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF68 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.70 | hwPDU80001QF69OutputActivePower | 1QF69 Output active power(L3) | 1QF69 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF69 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.71 | hwPDU80001QF70OutputActivePower | 1QF70 Output active power(L1) | 1QF70 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF70 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.72 | hwPDU80001QF71OutputActivePower | 1QF71 Output active power(L2) | 1QF71 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF71 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.73 | hwPDU80001QF72OutputActivePower | 1QF72 Output active power(L3) | 1QF72 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 1QF72 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.12.1.200 | hwPDU8000Running12RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.13 | hwPDU8000Running13Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.1 | hwPDU8000Running13Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.2 | hwPDU80002QF1OutputActivePower | 2QF1 Output active power(L1) | 2QF1 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF1 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.3 | hwPDU80002QF2OutputActivePower | 2QF2 Output active power(L2) | 2QF2 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF2 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.4 | hwPDU80002QF3OutputActivePower | 2QF3 Output active power(L3) | 2QF3 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF3 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.5 | hwPDU80002QF4OutputActivePower | 2QF4 Output active power(L1) | 2QF4 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF4 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.6 | hwPDU80002QF5OutputActivePower | 2QF5 Output active power(L2) | 2QF5 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF5 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.7 | hwPDU80002QF6OutputActivePower | 2QF6 Output active power(L3) | 2QF6 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF6 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.8 | hwPDU80002QF7OutputActivePower | 2QF7 Output active power(L1) | 2QF7 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF7 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.9 | hwPDU80002QF8OutputActivePower | 2QF8 Output active power(L2) | 2QF8 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF8 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.10 | hwPDU80002QF9OutputActivePower | 2QF9 Output active power(L3) | 2QF9 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF9 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.11 | hwPDU80002QF10OutputActivePower | 2QF10 Output active power(L1) | 2QF10 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF10 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.12 | hwPDU80002QF11OutputActivePower | 2QF11 Output active power(L2) | 2QF11 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF11 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.13 | hwPDU80002QF12OutputActivePower | 2QF12 Output active power(L3) | 2QF12 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF12 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.14 | hwPDU80002QF13OutputActivePower | 2QF13 Output active power(L1) | 2QF13 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF13 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.15 | hwPDU80002QF14OutputActivePower | 2QF14 Output active power(L2) | 2QF14 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF14 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.16 | hwPDU80002QF15OutputActivePower | 2QF15 Output active power(L3) | 2QF15 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF15 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.17 | hwPDU80002QF16OutputActivePower | 2QF16 Output active power(L1) | 2QF16 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF16 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.18 | hwPDU80002QF17OutputActivePower | 2QF17 Output active power(L2) | 2QF17 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF17 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.19 | hwPDU80002QF18OutputActivePower | 2QF18 Output active power(L3) | 2QF18 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF18 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.20 | hwPDU80002QF19OutputActivePower | 2QF19 Output active power(L1) | 2QF19 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF19 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.21 | hwPDU80002QF20OutputActivePower | 2QF20 Output active power(L2) | 2QF20 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF20 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.22 | hwPDU80002QF21OutputActivePower | 2QF21 Output active power(L3) | 2QF21 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF21 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.23 | hwPDU80002QF22OutputActivePower | 2QF22 Output active power(L1) | 2QF22 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF22 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.24 | hwPDU80002QF23OutputActivePower | 2QF23 Output active power(L2) | 2QF23 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF23 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.25 | hwPDU80002QF24OutputActivePower | 2QF24 Output active power(L3) | 2QF24 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF24 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.26 | hwPDU80002QF25OutputActivePower | 2QF25 Output active power(L1) | 2QF25 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF25 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.27 | hwPDU80002QF26OutputActivePower | 2QF26 Output active power(L2) | 2QF26 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF26 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.28 | hwPDU80002QF27OutputActivePower | 2QF27 Output active power(L3) | 2QF27 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF27 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.29 | hwPDU80002QF28OutputActivePower | 2QF28 Output active power(L1) | 2QF28 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF28 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.30 | hwPDU80002QF29OutputActivePower | 2QF29 Output active power(L2) | 2QF29 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF29 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.31 | hwPDU80002QF30OutputActivePower | 2QF30 Output active power(L3) | 2QF30 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF30 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.32 | hwPDU80002QF31OutputActivePower | 2QF31 Output active power(L1) | 2QF31 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF31 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.33 | hwPDU80002QF32OutputActivePower | 2QF32 Output active power(L2) | 2QF32 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF32 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.34 | hwPDU80002QF33OutputActivePower | 2QF33 Output active power(L3) | 2QF33 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF33 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.35 | hwPDU80002QF34OutputActivePower | 2QF34 Output active power(L1) | 2QF34 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF34 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.36 | hwPDU80002QF35OutputActivePower | 2QF35 Output active power(L2) | 2QF35 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF35 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.37 | hwPDU80002QF36OutputActivePower | 2QF36 Output active power(L3) | 2QF36 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF36 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.38 | hwPDU80002QF37OutputActivePower | 2QF37 Output active power(L1) | 2QF37 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF37 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.39 | hwPDU80002QF38OutputActivePower | 2QF38 Output active power(L2) | 2QF38 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF38 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.40 | hwPDU80002QF39OutputActivePower | 2QF39 Output active power(L3) | 2QF39 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF39 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.41 | hwPDU80002QF40OutputActivePower | 2QF40 Output active power(L1) | 2QF40 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF40 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.42 | hwPDU80002QF41OutputActivePower | 2QF41 Output active power(L2) | 2QF41 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF41 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.43 | hwPDU80002QF42OutputActivePower | 2QF42 Output active power(L3) | 2QF42 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF42 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.44 | hwPDU80002QF43OutputActivePower | 2QF43 Output active power(L1) | 2QF43 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF43 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.45 | hwPDU80002QF44OutputActivePower | 2QF44 Output active power(L2) | 2QF44 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF44 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.46 | hwPDU80002QF45OutputActivePower | 2QF45 Output active power(L3) | 2QF45 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF45 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.47 | hwPDU80002QF46OutputActivePower | 2QF46 Output active power(L1) | 2QF46 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF46 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.48 | hwPDU80002QF47OutputActivePower | 2QF47 Output active power(L2) | 2QF47 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF47 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.49 | hwPDU80002QF48OutputActivePower | 2QF48 Output active power(L3) | 2QF48 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF48 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.50 | hwPDU80002QF49OutputActivePower | 2QF49 Output active power(L1) | 2QF49 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF49 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.51 | hwPDU80002QF50OutputActivePower | 2QF50 Output active power(L2) | 2QF50 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF50 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.52 | hwPDU80002QF51OutputActivePower | 2QF51 Output active power(L3) | 2QF51 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF51 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.53 | hwPDU80002QF52OutputActivePower | 2QF52 Output active power(L1) | 2QF52 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF52 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.54 | hwPDU80002QF53OutputActivePower | 2QF53 Output active power(L2) | 2QF53 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF53 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.55 | hwPDU80002QF54OutputActivePower | 2QF54 Output active power(L3) | 2QF54 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF54 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.56 | hwPDU80002QF55OutputActivePower | 2QF55 Output active power(L1) | 2QF55 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF55 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.57 | hwPDU80002QF56OutputActivePower | 2QF56 Output active power(L2) | 2QF56 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF56 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.58 | hwPDU80002QF57OutputActivePower | 2QF57 Output active power(L3) | 2QF57 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF57 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.59 | hwPDU80002QF58OutputActivePower | 2QF58 Output active power(L1) | 2QF58 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF58 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.60 | hwPDU80002QF59OutputActivePower | 2QF59 Output active power(L2) | 2QF59 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF59 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.61 | hwPDU80002QF60OutputActivePower | 2QF60 Output active power(L3) | 2QF60 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF60 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.62 | hwPDU80002QF61OutputActivePower | 2QF61 Output active power(L1) | 2QF61 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF61 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.63 | hwPDU80002QF62OutputActivePower | 2QF62 Output active power(L2) | 2QF62 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF62 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.64 | hwPDU80002QF63OutputActivePower | 2QF63 Output active power(L3) | 2QF63 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF63 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.65 | hwPDU80002QF64OutputActivePower | 2QF64 Output active power(L1) | 2QF64 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF64 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.66 | hwPDU80002QF65OutputActivePower | 2QF65 Output active power(L2) | 2QF65 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF65 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.67 | hwPDU80002QF66OutputActivePower | 2QF66 Output active power(L3) | 2QF66 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF66 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.68 | hwPDU80002QF67OutputActivePower | 2QF67 Output active power(L1) | 2QF67 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF67 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.69 | hwPDU80002QF68OutputActivePower | 2QF68 Output active power(L2) | 2QF68 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF68 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.70 | hwPDU80002QF69OutputActivePower | 2QF69 Output active power(L3) | 2QF69 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF69 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.71 | hwPDU80002QF70OutputActivePower | 2QF70 Output active power(L1) | 2QF70 输出有功功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF70 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.72 | hwPDU80002QF71OutputActivePower | 2QF71 Output active power(L2) | 2QF71 输出有功功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF71 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.73 | hwPDU80002QF72OutputActivePower | 2QF72 Output active power(L3) | 2QF72 输出有功功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | pdu8000 2QF72 output active power.Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.5.13.1.200 | hwPDU8000Running13RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.14 | hwPDU8000Running14Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.1 | hwPDU8000Running14Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.2 | hwPDU8000QF1outputPowerLoadFactor | QF1 Output load factor(L1) | QF1 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF1 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.3 | hwPDU8000QF2outputPowerLoadFactor | QF2 Output load factor(L2) | QF2 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF2 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.4 | hwPDU8000QF3outputPowerLoadFactor | QF3 Output load factor(L3) | QF3 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF3 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.5 | hwPDU8000QF4outputPowerLoadFactor | QF4 Output load factor(L1) | QF4 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF4 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.6 | hwPDU8000QF5outputPowerLoadFactor | QF5 Output load factor(L2) | QF5 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF5 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.7 | hwPDU8000QF6outputPowerLoadFactor | QF6 Output load factor(L3) | QF6 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF6 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.8 | hwPDU8000QF7outputPowerLoadFactor | QF7 Output load factor(L1) | QF7 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF7 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.9 | hwPDU8000QF8outputPowerLoadFactor | QF8 Output load factor(L2) | QF8 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF8 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.10 | hwPDU8000QF9outputPowerLoadFactor | QF9 Output load factor(L3) | QF9 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF9 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.11 | hwPDU8000QF10outputPowerLoadFactor | QF10 Output load factor(L1) | QF10 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF10 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.12 | hwPDU8000QF11outputPowerLoadFactor | QF11 Output load factor(L2) | QF11 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF11 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.13 | hwPDU8000QF12outputPowerLoadFactor | QF12 Output load factor(L3) | QF12 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF12 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.14 | hwPDU8000QF13outputPowerLoadFactor | QF13 Output load factor(L1) | QF13 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF13 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.15 | hwPDU8000QF14outputPowerLoadFactor | QF14 Output load factor(L2) | QF14 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF14 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.16 | hwPDU8000QF15outputPowerLoadFactor | QF15 Output load factor(L3) | QF15 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF15 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.17 | hwPDU8000QF16outputPowerLoadFactor | QF16 Output load factor(L1) | QF16 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF16 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.18 | hwPDU8000QF17outputPowerLoadFactor | QF17 Output load factor(L2) | QF17 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF17 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.19 | hwPDU8000QF18outputPowerLoadFactor | QF18 Output load factor(L3) | QF18 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF18 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.20 | hwPDU8000QF19outputPowerLoadFactor | QF19 Output load factor(L1) | QF19 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF19 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.21 | hwPDU8000QF20outputPowerLoadFactor | QF20 Output load factor(L2) | QF20 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF20 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.22 | hwPDU8000QF21outputPowerLoadFactor | QF21 Output load factor(L3) | QF21 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF21 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.23 | hwPDU8000QF22outputPowerLoadFactor | QF22 Output load factor(L1) | QF22 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF22 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.24 | hwPDU8000QF23outputPowerLoadFactor | QF23 Output load factor(L2) | QF23 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF23 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.25 | hwPDU8000QF24outputPowerLoadFactor | QF24 Output load factor(L3) | QF24 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF24 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.26 | hwPDU8000QF25outputPowerLoadFactor | QF25 Output load factor(L1) | QF25 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF25 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.27 | hwPDU8000QF26outputPowerLoadFactor | QF26 Output load factor(L2) | QF26 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF26 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.28 | hwPDU8000QF27outputPowerLoadFactor | QF27 Output load factor(L3) | QF27 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF27 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.29 | hwPDU8000QF28outputPowerLoadFactor | QF28 Output load factor(L1) | QF28 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF28 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.30 | hwPDU8000QF29outputPowerLoadFactor | QF29 Output load factor(L2) | QF29 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF29 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.31 | hwPDU8000QF30outputPowerLoadFactor | QF30 Output load factor(L3) | QF30 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF30 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.32 | hwPDU8000QF31outputPowerLoadFactor | QF31 Output load factor(L1) | QF31 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF31 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.33 | hwPDU8000QF32outputPowerLoadFactor | QF32 Output load factor(L2) | QF32 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF32 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.34 | hwPDU8000QF33outputPowerLoadFactor | QF33 Output load factor(L3) | QF33 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF33 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.35 | hwPDU8000QF34outputPowerLoadFactor | QF34 Output load factor(L1) | QF34 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF34 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.36 | hwPDU8000QF35outputPowerLoadFactor | QF35 Output load factor(L2) | QF35 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF35 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.37 | hwPDU8000QF36outputPowerLoadFactor | QF36 Output load factor(L3) | QF36 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF36 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.38 | hwPDU8000QF37outputPowerLoadFactor | QF37 Output load factor(L1) | QF37 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF37 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.39 | hwPDU8000QF38outputPowerLoadFactor | QF38 Output load factor(L2) | QF38 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF38 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.40 | hwPDU8000QF39outputPowerLoadFactor | QF39 Output load factor(L3) | QF39 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF39 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.41 | hwPDU8000QF40outputPowerLoadFactor | QF40 Output load factor(L1) | QF40 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF40 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.42 | hwPDU8000QF41outputPowerLoadFactor | QF41 Output load factor(L2) | QF41 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF41 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.43 | hwPDU8000QF42outputPowerLoadFactor | QF42 Output load factor(L3) | QF42 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF42 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.44 | hwPDU8000QF43outputPowerLoadFactor | QF43 Output load factor(L1) | QF43 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF43 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.45 | hwPDU8000QF44outputPowerLoadFactor | QF44 Output load factor(L2) | QF44 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF44 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.46 | hwPDU8000QF45outputPowerLoadFactor | QF45 Output load factor(L3) | QF45 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF45 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.47 | hwPDU8000QF46outputPowerLoadFactor | QF46 Output load factor(L1) | QF46 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF46 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.48 | hwPDU8000QF47outputPowerLoadFactor | QF47 Output load factor(L2) | QF47 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF47 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.49 | hwPDU8000QF48outputPowerLoadFactor | QF48 Output load factor(L3) | QF48 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF48 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.50 | hwPDU8000QF49outputPowerLoadFactor | QF49 Output load factor(L1) | QF49 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF49 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.51 | hwPDU8000QF50outputPowerLoadFactor | QF50 Output load factor(L2) | QF50 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF50 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.52 | hwPDU8000QF51outputPowerLoadFactor | QF51 Output load factor(L3) | QF51 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF51 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.53 | hwPDU8000QF52outputPowerLoadFactor | QF52 Output load factor(L1) | QF52 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF52 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.54 | hwPDU8000QF53outputPowerLoadFactor | QF53 Output load factor(L2) | QF53 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF53 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.55 | hwPDU8000QF54outputPowerLoadFactor | QF54 Output load factor(L3) | QF54 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF54 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.56 | hwPDU8000QF55outputPowerLoadFactor | QF55 Output load factor(L1) | QF55 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF55 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.57 | hwPDU8000QF56outputPowerLoadFactor | QF56 Output load factor(L2) | QF56 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF56 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.58 | hwPDU8000QF57outputPowerLoadFactor | QF57 Output load factor(L3) | QF57 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF57 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.59 | hwPDU8000QF58outputPowerLoadFactor | QF58 Output load factor(L1) | QF58 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF58 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.60 | hwPDU8000QF59outputPowerLoadFactor | QF59 Output load factor(L2) | QF59 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF59 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.61 | hwPDU8000QF60outputPowerLoadFactor | QF60 Output load factor(L3) | QF60 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF60 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.62 | hwPDU8000QF61outputPowerLoadFactor | QF61 Output load factor(L1) | QF61 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF61 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.63 | hwPDU8000QF62outputPowerLoadFactor | QF62 Output load factor(L2) | QF62 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF62 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.64 | hwPDU8000QF63outputPowerLoadFactor | QF63 Output load factor(L3) | QF63 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF63 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.65 | hwPDU8000QF64outputPowerLoadFactor | QF64 Output load factor(L1) | QF64 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF64 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.66 | hwPDU8000QF65outputPowerLoadFactor | QF65 Output load factor(L2) | QF65 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF65 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.67 | hwPDU8000QF66outputPowerLoadFactor | QF66 Output load factor(L3) | QF66 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF66 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.68 | hwPDU8000QF67outputPowerLoadFactor | QF67 Output load factor(L1) | QF67 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF67 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.69 | hwPDU8000QF68outputPowerLoadFactor | QF68 Output load factor(L2) | QF68 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF68 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.70 | hwPDU8000QF69outputPowerLoadFactor | QF69 Output load factor(L3) | QF69 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF69 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.71 | hwPDU8000QF70outputPowerLoadFactor | QF70 Output load factor(L1) | QF70 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF70 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.72 | hwPDU8000QF71outputPowerLoadFactor | QF71 Output load factor(L2) | QF71 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF71 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.73 | hwPDU8000QF72outputPowerLoadFactor | QF72 Output load factor(L3) | QF72 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF72 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.74 | hwPDU8000QF73outputPowerLoadFactor | QF73 Output load factor(L1) | QF73 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF73 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.75 | hwPDU8000QF74outputPowerLoadFactor | QF74 Output load factor(L2) | QF74 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF74 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.76 | hwPDU8000QF75outputPowerLoadFactor | QF75 Output load factor(L3) | QF75 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF75 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.77 | hwPDU8000QF76outputPowerLoadFactor | QF76 Output load factor(L1) | QF76 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF76 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.78 | hwPDU8000QF77outputPowerLoadFactor | QF77 Output load factor(L2) | QF77 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF77 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.79 | hwPDU8000QF78outputPowerLoadFactor | QF78 Output load factor(L3) | QF78 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF78 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.80 | hwPDU8000QF79outputPowerLoadFactor | QF79 Output load factor(L1) | QF79 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF79 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.81 | hwPDU8000QF80outputPowerLoadFactor | QF80 Output load factor(L2) | QF80 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF80 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.82 | hwPDU8000QF81outputPowerLoadFactor | QF81 Output load factor(L3) | QF81 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF81 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.83 | hwPDU8000QF82outputPowerLoadFactor | QF82 Output load factor(L1) | QF82 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF82 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.84 | hwPDU8000QF83outputPowerLoadFactor | QF83 Output load factor(L2) | QF83 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF83 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.85 | hwPDU8000QF84outputPowerLoadFactor | QF84 Output load factor(L3) | QF84 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF84 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.86 | hwPDU8000QF85outputPowerLoadFactor | QF85 Output load factor(L1) | QF85 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF85 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.87 | hwPDU8000QF86outputPowerLoadFactor | QF86 Output load factor(L2) | QF86 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF86 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.88 | hwPDU8000QF87outputPowerLoadFactor | QF87 Output load factor(L3) | QF87 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF87 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.89 | hwPDU8000QF88outputPowerLoadFactor | QF88 Output load factor(L1) | QF88 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF88 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.90 | hwPDU8000QF89outputPowerLoadFactor | QF89 Output load factor(L2) | QF89 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF89 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.91 | hwPDU8000QF90outputPowerLoadFactor | QF90 Output load factor(L3) | QF90 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF90 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.92 | hwPDU8000QF91outputPowerLoadFactor | QF91 Output load factor(L1) | QF91 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF91 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.93 | hwPDU8000QF92outputPowerLoadFactor | QF92 Output load factor(L2) | QF92 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF92 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.94 | hwPDU8000QF93outputPowerLoadFactor | QF93 Output load factor(L3) | QF93 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF93 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.95 | hwPDU8000QF94outputPowerLoadFactor | QF94 Output load factor(L1) | QF94 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF94 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.96 | hwPDU8000QF95outputPowerLoadFactor | QF95 Output load factor(L2) | QF95 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF95 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.97 | hwPDU8000QF96outputPowerLoadFactor | QF96 Output load factor(L3) | QF96 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF96 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.98 | hwPDU8000QF97outputPowerLoadFactor | QF97 Output load factor(L1) | QF97 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF97 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.99 | hwPDU8000QF98outputPowerLoadFactor | QF98 Output load factor(L2) | QF98 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF98 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.100 | hwPDU8000QF99outputPowerLoadFactor | QF99 Output load factor(L3) | QF99 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF99 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.101 | hwPDU8000QF100outputPowerLoadFactor | QF100 Output load factor(L1) | QF100 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF100 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.102 | hwPDU8000QF101outputPowerLoadFactor | QF101 Output load factor(L2) | QF101 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF101 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.103 | hwPDU8000QF102outputPowerLoadFactor | QF102 Output load factor(L3) | QF102 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF102 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.104 | hwPDU8000QF103outputPowerLoadFactor | QF103 Output load factor(L1) | QF103 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF103 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.105 | hwPDU8000QF104outputPowerLoadFactor | QF104 Output load factor(L2) | QF104 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF104 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.106 | hwPDU8000QF105outputPowerLoadFactor | QF105 Output load factor(L3) | QF105 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF105 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.107 | hwPDU8000QF106outputPowerLoadFactor | QF106 Output load factor(L1) | QF106 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF106 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.108 | hwPDU8000QF107outputPowerLoadFactor | QF107 Output load factor(L2) | QF107 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF107 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.109 | hwPDU8000QF108outputPowerLoadFactor | QF108 Output load factor(L3) | QF108 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF108 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.110 | hwPDU8000QF109outputPowerLoadFactor | QF109 Output load factor(L1) | QF109 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF109 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.111 | hwPDU8000QF110outputPowerLoadFactor | QF110 Output load factor(L2) | QF110 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF110 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.112 | hwPDU8000QF111outputPowerLoadFactor | QF111 Output load factor(L3) | QF111 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF111 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.113 | hwPDU8000QF112outputPowerLoadFactor | QF112 Output load factor(L1) | QF112 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF112 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.114 | hwPDU8000QF113outputPowerLoadFactor | QF113 Output load factor(L2) | QF113 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF113 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.115 | hwPDU8000QF114outputPowerLoadFactor | QF114 Output load factor(L3) | QF114 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF114 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.116 | hwPDU8000QF115outputPowerLoadFactor | QF115 Output load factor(L1) | QF115 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF115 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.117 | hwPDU8000QF116outputPowerLoadFactor | QF116 Output load factor(L2) | QF116 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF116 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.118 | hwPDU8000QF117outputPowerLoadFactor | QF117 Output load factor(L3) | QF117 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF117 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.119 | hwPDU8000QF118outputPowerLoadFactor | QF118 Output load factor(L1) | QF118 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF118 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.120 | hwPDU8000QF119outputPowerLoadFactor | QF119 Output load factor(L2) | QF119 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF119 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.121 | hwPDU8000QF120outputPowerLoadFactor | QF120 Output load factor(L3) | QF120 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF120 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.122 | hwPDU8000QF121outputPowerLoadFactor | QF121 Output load factor(L1) | QF121 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF121 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.123 | hwPDU8000QF122outputPowerLoadFactor | QF122 Output load factor(L2) | QF122 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF122 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.124 | hwPDU8000QF123outputPowerLoadFactor | QF123 Output load factor(L3) | QF123 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF123 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.125 | hwPDU8000QF124outputPowerLoadFactor | QF124 Output load factor(L1) | QF124 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF124 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.126 | hwPDU8000QF125outputPowerLoadFactor | QF125 Output load factor(L2) | QF125 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF125 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.127 | hwPDU8000QF126outputPowerLoadFactor | QF126 Output load factor(L3) | QF126 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF126 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.128 | hwPDU8000QF127outputPowerLoadFactor | QF127 Output load factor(L1) | QF127 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF127 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.129 | hwPDU8000QF128outputPowerLoadFactor | QF128 Output load factor(L2) | QF128 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF128 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.130 | hwPDU8000QF129outputPowerLoadFactor | QF129 Output load factor(L3) | QF129 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF129 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.131 | hwPDU8000QF130outputPowerLoadFactor | QF130 Output load factor(L1) | QF130 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF130 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.132 | hwPDU8000QF131outputPowerLoadFactor | QF131 Output load factor(L2) | QF131 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF131 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.133 | hwPDU8000QF132outputPowerLoadFactor | QF132 Output load factor(L3) | QF132 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF132 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.134 | hwPDU8000QF133outputPowerLoadFactor | QF133 Output load factor(L1) | QF133 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF133 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.135 | hwPDU8000QF134outputPowerLoadFactor | QF134 Output load factor(L2) | QF134 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF134 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.136 | hwPDU8000QF135outputPowerLoadFactor | QF135 Output load factor(L3) | QF135 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF135 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.137 | hwPDU8000QF136outputPowerLoadFactor | QF136 Output load factor(L1) | QF136 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF136 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.138 | hwPDU8000QF137outputPowerLoadFactor | QF137 Output load factor(L2) | QF137 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF137 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.139 | hwPDU8000QF138outputPowerLoadFactor | QF138 Output load factor(L3) | QF138 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF138 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.140 | hwPDU8000QF139outputPowerLoadFactor | QF139 Output load factor(L1) | QF139 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF139 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.141 | hwPDU8000QF140outputPowerLoadFactor | QF140 Output load factor(L2) | QF140 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF140 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.142 | hwPDU8000QF141outputPowerLoadFactor | QF141 Output load factor(L3) | QF141 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF141 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.143 | hwPDU8000QF142outputPowerLoadFactor | QF142 Output load factor(L1) | QF142 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF142 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.144 | hwPDU8000QF143outputPowerLoadFactor | QF143 Output load factor(L2) | QF143 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF143 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.145 | hwPDU8000QF144outputPowerLoadFactor | QF144 Output load factor(L3) | QF144 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 QF144 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.14.1.200 | hwPDU8000Running14RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.15 | hwPDU8000Running15Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.1 | hwPDU8000Running15Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.2 | hwPDU80001QF1outputPowerLoadFactor | 1QF1 Output load factor(L1) | 1QF1 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF1 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.3 | hwPDU80001QF2outputPowerLoadFactor | 1QF2 Output load factor(L2) | 1QF2 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF2 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.4 | hwPDU80001QF3outputPowerLoadFactor | 1QF3 Output load factor(L3) | 1QF3 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF3 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.5 | hwPDU80001QF4outputPowerLoadFactor | 1QF4 Output load factor(L1) | 1QF4 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF4 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.6 | hwPDU80001QF5outputPowerLoadFactor | 1QF5 Output load factor(L2) | 1QF5 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF5 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.7 | hwPDU80001QF6outputPowerLoadFactor | 1QF6 Output load factor(L3) | 1QF6 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF6 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.8 | hwPDU80001QF7outputPowerLoadFactor | 1QF7 Output load factor(L1) | 1QF7 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF7 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.9 | hwPDU80001QF8outputPowerLoadFactor | 1QF8 Output load factor(L2) | 1QF8 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF8 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.10 | hwPDU80001QF9outputPowerLoadFactor | 1QF9 Output load factor(L3) | 1QF9 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF9 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.11 | hwPDU80001QF10outputPowerLoadFactor | 1QF10 Output load factor(L1) | 1QF10 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF10 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.12 | hwPDU80001QF11outputPowerLoadFactor | 1QF11 Output load factor(L2) | 1QF11 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF11 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.13 | hwPDU80001QF12outputPowerLoadFactor | 1QF12 Output load factor(L3) | 1QF12 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF12 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.14 | hwPDU80001QF13outputPowerLoadFactor | 1QF13 Output load factor(L1) | 1QF13 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF13 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.15 | hwPDU80001QF14outputPowerLoadFactor | 1QF14 Output load factor(L2) | 1QF14 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF14 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.16 | hwPDU80001QF15outputPowerLoadFactor | 1QF15 Output load factor(L3) | 1QF15 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF15 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.17 | hwPDU80001QF16outputPowerLoadFactor | 1QF16 Output load factor(L1) | 1QF16 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF16 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.18 | hwPDU80001QF17outputPowerLoadFactor | 1QF17 Output load factor(L2) | 1QF17 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF17 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.19 | hwPDU80001QF18outputPowerLoadFactor | 1QF18 Output load factor(L3) | 1QF18 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF18 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.20 | hwPDU80001QF19outputPowerLoadFactor | 1QF19 Output load factor(L1) | 1QF19 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF19 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.21 | hwPDU80001QF20outputPowerLoadFactor | 1QF20 Output load factor(L2) | 1QF20 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF20 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.22 | hwPDU80001QF21outputPowerLoadFactor | 1QF21 Output load factor(L3) | 1QF21 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF21 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.23 | hwPDU80001QF22outputPowerLoadFactor | 1QF22 Output load factor(L1) | 1QF22 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF22 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.24 | hwPDU80001QF23outputPowerLoadFactor | 1QF23 Output load factor(L2) | 1QF23 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF23 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.25 | hwPDU80001QF24outputPowerLoadFactor | 1QF24 Output load factor(L3) | 1QF24 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF24 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.26 | hwPDU80001QF25outputPowerLoadFactor | 1QF25 Output load factor(L1) | 1QF25 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF25 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.27 | hwPDU80001QF26outputPowerLoadFactor | 1QF26 Output load factor(L2) | 1QF26 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF26 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.28 | hwPDU80001QF27outputPowerLoadFactor | 1QF27 Output load factor(L3) | 1QF27 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF27 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.29 | hwPDU80001QF28outputPowerLoadFactor | 1QF28 Output load factor(L1) | 1QF28 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF28 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.30 | hwPDU80001QF29outputPowerLoadFactor | 1QF29 Output load factor(L2) | 1QF29 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF29 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.31 | hwPDU80001QF30outputPowerLoadFactor | 1QF30 Output load factor(L3) | 1QF30 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF30 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.32 | hwPDU80001QF31outputPowerLoadFactor | 1QF31 Output load factor(L1) | 1QF31 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF31 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.33 | hwPDU80001QF32outputPowerLoadFactor | 1QF32 Output load factor(L2) | 1QF32 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF32 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.34 | hwPDU80001QF33outputPowerLoadFactor | 1QF33 Output load factor(L3) | 1QF33 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF33 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.35 | hwPDU80001QF34outputPowerLoadFactor | 1QF34 Output load factor(L1) | 1QF34 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF34 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.36 | hwPDU80001QF35outputPowerLoadFactor | 1QF35 Output load factor(L2) | 1QF35 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF35 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.37 | hwPDU80001QF36outputPowerLoadFactor | 1QF36 Output load factor(L3) | 1QF36 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF36 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.38 | hwPDU80001QF37outputPowerLoadFactor | 1QF37 Output load factor(L1) | 1QF37 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF37 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.39 | hwPDU80001QF38outputPowerLoadFactor | 1QF38 Output load factor(L2) | 1QF38 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF38 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.40 | hwPDU80001QF39outputPowerLoadFactor | 1QF39 Output load factor(L3) | 1QF39 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF39 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.41 | hwPDU80001QF40outputPowerLoadFactor | 1QF40 Output load factor(L1) | 1QF40 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF40 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.42 | hwPDU80001QF41outputPowerLoadFactor | 1QF41 Output load factor(L2) | 1QF41 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF41 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.43 | hwPDU80001QF42outputPowerLoadFactor | 1QF42 Output load factor(L3) | 1QF42 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF42 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.44 | hwPDU80001QF43outputPowerLoadFactor | 1QF43 Output load factor(L1) | 1QF43 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF43 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.45 | hwPDU80001QF44outputPowerLoadFactor | 1QF44 Output load factor(L2) | 1QF44 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF44 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.46 | hwPDU80001QF45outputPowerLoadFactor | 1QF45 Output load factor(L3) | 1QF45 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF45 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.47 | hwPDU80001QF46outputPowerLoadFactor | 1QF46 Output load factor(L1) | 1QF46 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF46 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.48 | hwPDU80001QF47outputPowerLoadFactor | 1QF47 Output load factor(L2) | 1QF47 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF47 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.49 | hwPDU80001QF48outputPowerLoadFactor | 1QF48 Output load factor(L3) | 1QF48 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF48 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.50 | hwPDU80001QF49outputPowerLoadFactor | 1QF49 Output load factor(L1) | 1QF49 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF49 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.51 | hwPDU80001QF50outputPowerLoadFactor | 1QF50 Output load factor(L2) | 1QF50 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF50 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.52 | hwPDU80001QF51outputPowerLoadFactor | 1QF51 Output load factor(L3) | 1QF51 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF51 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.53 | hwPDU80001QF52outputPowerLoadFactor | 1QF52 Output load factor(L1) | 1QF52 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF52 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.54 | hwPDU80001QF53outputPowerLoadFactor | 1QF53 Output load factor(L2) | 1QF53 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF53 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.55 | hwPDU80001QF54outputPowerLoadFactor | 1QF54 Output load factor(L3) | 1QF54 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF54 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.56 | hwPDU80001QF55outputPowerLoadFactor | 1QF55 Output load factor(L1) | 1QF55 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF55 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.57 | hwPDU80001QF56outputPowerLoadFactor | 1QF56 Output load factor(L2) | 1QF56 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF56 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.58 | hwPDU80001QF57outputPowerLoadFactor | 1QF57 Output load factor(L3) | 1QF57 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF57 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.59 | hwPDU80001QF58outputPowerLoadFactor | 1QF58 Output load factor(L1) | 1QF58 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF58 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.60 | hwPDU80001QF59outputPowerLoadFactor | 1QF59 Output load factor(L2) | 1QF59 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF59 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.61 | hwPDU80001QF60outputPowerLoadFactor | 1QF60 Output load factor(L3) | 1QF60 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF60 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.62 | hwPDU80001QF61outputPowerLoadFactor | 1QF61 Output load factor(L1) | 1QF61 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF61 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.63 | hwPDU80001QF62outputPowerLoadFactor | 1QF62 Output load factor(L2) | 1QF62 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF62 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.64 | hwPDU80001QF63outputPowerLoadFactor | 1QF63 Output load factor(L3) | 1QF63 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF63 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.65 | hwPDU80001QF64outputPowerLoadFactor | 1QF64 Output load factor(L1) | 1QF64 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF64 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.66 | hwPDU80001QF65outputPowerLoadFactor | 1QF65 Output load factor(L2) | 1QF65 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF65 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.67 | hwPDU80001QF66outputPowerLoadFactor | 1QF66 Output load factor(L3) | 1QF66 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF66 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.68 | hwPDU80001QF67outputPowerLoadFactor | 1QF67 Output load factor(L1) | 1QF67 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF67 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.69 | hwPDU80001QF68outputPowerLoadFactor | 1QF68 Output load factor(L2) | 1QF68 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF68 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.70 | hwPDU80001QF69outputPowerLoadFactor | 1QF69 Output load factor(L3) | 1QF69 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF69 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.71 | hwPDU80001QF70outputPowerLoadFactor | 1QF70 Output load factor(L1) | 1QF70 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF70 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.72 | hwPDU80001QF71outputPowerLoadFactor | 1QF71 Output load factor(L2) | 1QF71 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF71 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.73 | hwPDU80001QF72outputPowerLoadFactor | 1QF72 Output load factor(L3) | 1QF72 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 1QF72 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.15.1.200 | hwPDU8000Running15RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.16 | hwPDU8000Running16Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.1 | hwPDU8000Running16Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.2 | hwPDU80002QF1outputPowerLoadFactor | 2QF1 Output load factor(L1) | 2QF1 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF1 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.3 | hwPDU80002QF2outputPowerLoadFactor | 2QF2 Output load factor(L2) | 2QF2 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF2 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.4 | hwPDU80002QF3outputPowerLoadFactor | 2QF3 Output load factor(L3) | 2QF3 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF3 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.5 | hwPDU80002QF4outputPowerLoadFactor | 2QF4 Output load factor(L1) | 2QF4 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF4 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.6 | hwPDU80002QF5outputPowerLoadFactor | 2QF5 Output load factor(L2) | 2QF5 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF5 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.7 | hwPDU80002QF6outputPowerLoadFactor | 2QF6 Output load factor(L3) | 2QF6 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF6 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.8 | hwPDU80002QF7outputPowerLoadFactor | 2QF7 Output load factor(L1) | 2QF7 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF7 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.9 | hwPDU80002QF8outputPowerLoadFactor | 2QF8 Output load factor(L2) | 2QF8 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF8 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.10 | hwPDU80002QF9outputPowerLoadFactor | 2QF9 Output load factor(L3) | 2QF9 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF9 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.11 | hwPDU80002QF10outputPowerLoadFactor | 2QF10 Output load factor(L1) | 2QF10 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF10 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.12 | hwPDU80002QF11outputPowerLoadFactor | 2QF11 Output load factor(L2) | 2QF11 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF11 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.13 | hwPDU80002QF12outputPowerLoadFactor | 2QF12 Output load factor(L3) | 2QF12 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF12 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.14 | hwPDU80002QF13outputPowerLoadFactor | 2QF13 Output load factor(L1) | 2QF13 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF13 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.15 | hwPDU80002QF14outputPowerLoadFactor | 2QF14 Output load factor(L2) | 2QF14 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF14 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.16 | hwPDU80002QF15outputPowerLoadFactor | 2QF15 Output load factor(L3) | 2QF15 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF15 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.17 | hwPDU80002QF16outputPowerLoadFactor | 2QF16 Output load factor(L1) | 2QF16 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF16 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.18 | hwPDU80002QF17outputPowerLoadFactor | 2QF17 Output load factor(L2) | 2QF17 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF17 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.19 | hwPDU80002QF18outputPowerLoadFactor | 2QF18 Output load factor(L3) | 2QF18 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF18 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.20 | hwPDU80002QF19outputPowerLoadFactor | 2QF19 Output load factor(L1) | 2QF19 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF19 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.21 | hwPDU80002QF20outputPowerLoadFactor | 2QF20 Output load factor(L2) | 2QF20 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF20 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.22 | hwPDU80002QF21outputPowerLoadFactor | 2QF21 Output load factor(L3) | 2QF21 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF21 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.23 | hwPDU80002QF22outputPowerLoadFactor | 2QF22 Output load factor(L1) | 2QF22 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF22 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.24 | hwPDU80002QF23outputPowerLoadFactor | 2QF23 Output load factor(L2) | 2QF23 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF23 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.25 | hwPDU80002QF24outputPowerLoadFactor | 2QF24 Output load factor(L3) | 2QF24 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF24 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.26 | hwPDU80002QF25outputPowerLoadFactor | 2QF25 Output load factor(L1) | 2QF25 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF25 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.27 | hwPDU80002QF26outputPowerLoadFactor | 2QF26 Output load factor(L2) | 2QF26 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF26 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.28 | hwPDU80002QF27outputPowerLoadFactor | 2QF27 Output load factor(L3) | 2QF27 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF27 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.29 | hwPDU80002QF28outputPowerLoadFactor | 2QF28 Output load factor(L1) | 2QF28 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF28 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.30 | hwPDU80002QF29outputPowerLoadFactor | 2QF29 Output load factor(L2) | 2QF29 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF29 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.31 | hwPDU80002QF30outputPowerLoadFactor | 2QF30 Output load factor(L3) | 2QF30 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF30 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.32 | hwPDU80002QF31outputPowerLoadFactor | 2QF31 Output load factor(L1) | 2QF31 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF31 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.33 | hwPDU80002QF32outputPowerLoadFactor | 2QF32 Output load factor(L2) | 2QF32 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF32 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.34 | hwPDU80002QF33outputPowerLoadFactor | 2QF33 Output load factor(L3) | 2QF33 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF33 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.35 | hwPDU80002QF34outputPowerLoadFactor | 2QF34 Output load factor(L1) | 2QF34 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF34 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.36 | hwPDU80002QF35outputPowerLoadFactor | 2QF35 Output load factor(L2) | 2QF35 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF35 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.37 | hwPDU80002QF36outputPowerLoadFactor | 2QF36 Output load factor(L3) | 2QF36 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF36 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.38 | hwPDU80002QF37outputPowerLoadFactor | 2QF37 Output load factor(L1) | 2QF37 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF37 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.39 | hwPDU80002QF38outputPowerLoadFactor | 2QF38 Output load factor(L2) | 2QF38 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF38 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.40 | hwPDU80002QF39outputPowerLoadFactor | 2QF39 Output load factor(L3) | 2QF39 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF39 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.41 | hwPDU80002QF40outputPowerLoadFactor | 2QF40 Output load factor(L1) | 2QF40 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF40 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.42 | hwPDU80002QF41outputPowerLoadFactor | 2QF41 Output load factor(L2) | 2QF41 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF41 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.43 | hwPDU80002QF42outputPowerLoadFactor | 2QF42 Output load factor(L3) | 2QF42 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF42 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.44 | hwPDU80002QF43outputPowerLoadFactor | 2QF43 Output load factor(L1) | 2QF43 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF43 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.45 | hwPDU80002QF44outputPowerLoadFactor | 2QF44 Output load factor(L2) | 2QF44 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF44 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.46 | hwPDU80002QF45outputPowerLoadFactor | 2QF45 Output load factor(L3) | 2QF45 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF45 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.47 | hwPDU80002QF46outputPowerLoadFactor | 2QF46 Output load factor(L1) | 2QF46 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF46 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.48 | hwPDU80002QF47outputPowerLoadFactor | 2QF47 Output load factor(L2) | 2QF47 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF47 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.49 | hwPDU80002QF48outputPowerLoadFactor | 2QF48 Output load factor(L3) | 2QF48 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF48 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.50 | hwPDU80002QF49outputPowerLoadFactor | 2QF49 Output load factor(L1) | 2QF49 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF49 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.51 | hwPDU80002QF50outputPowerLoadFactor | 2QF50 Output load factor(L2) | 2QF50 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF50 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.52 | hwPDU80002QF51outputPowerLoadFactor | 2QF51 Output load factor(L3) | 2QF51 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF51 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.53 | hwPDU80002QF52outputPowerLoadFactor | 2QF52 Output load factor(L1) | 2QF52 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF52 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.54 | hwPDU80002QF53outputPowerLoadFactor | 2QF53 Output load factor(L2) | 2QF53 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF53 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.55 | hwPDU80002QF54outputPowerLoadFactor | 2QF54 Output load factor(L3) | 2QF54 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF54 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.56 | hwPDU80002QF55outputPowerLoadFactor | 2QF55 Output load factor(L1) | 2QF55 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF55 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.57 | hwPDU80002QF56outputPowerLoadFactor | 2QF56 Output load factor(L2) | 2QF56 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF56 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.58 | hwPDU80002QF57outputPowerLoadFactor | 2QF57 Output load factor(L3) | 2QF57 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF57 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.59 | hwPDU80002QF58outputPowerLoadFactor | 2QF58 Output load factor(L1) | 2QF58 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF58 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.60 | hwPDU80002QF59outputPowerLoadFactor | 2QF59 Output load factor(L2) | 2QF59 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF59 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.61 | hwPDU80002QF60outputPowerLoadFactor | 2QF60 Output load factor(L3) | 2QF60 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF60 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.62 | hwPDU80002QF61outputPowerLoadFactor | 2QF61 Output load factor(L1) | 2QF61 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF61 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.63 | hwPDU80002QF62outputPowerLoadFactor | 2QF62 Output load factor(L2) | 2QF62 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF62 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.64 | hwPDU80002QF63outputPowerLoadFactor | 2QF63 Output load factor(L3) | 2QF63 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF63 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.65 | hwPDU80002QF64outputPowerLoadFactor | 2QF64 Output load factor(L1) | 2QF64 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF64 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.66 | hwPDU80002QF65outputPowerLoadFactor | 2QF65 Output load factor(L2) | 2QF65 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF65 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.67 | hwPDU80002QF66outputPowerLoadFactor | 2QF66 Output load factor(L3) | 2QF66 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF66 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.68 | hwPDU80002QF67outputPowerLoadFactor | 2QF67 Output load factor(L1) | 2QF67 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF67 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.69 | hwPDU80002QF68outputPowerLoadFactor | 2QF68 Output load factor(L2) | 2QF68 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF68 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.70 | hwPDU80002QF69outputPowerLoadFactor | 2QF69 Output load factor(L3) | 2QF69 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF69 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.71 | hwPDU80002QF70outputPowerLoadFactor | 2QF70 Output load factor(L1) | 2QF70 输出电源负载率(L1) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF70 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.72 | hwPDU80002QF71outputPowerLoadFactor | 2QF71 Output load factor(L2) | 2QF71 输出电源负载率(L2) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF71 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.73 | hwPDU80002QF72outputPowerLoadFactor | 2QF72 Output load factor(L3) | 2QF72 输出电源负载率(L3) | 0-Read_Only | 只读 | 0..300 | 0..300 | pdu8000 2QF72 output power load factor. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.9.5.16.1.200 | hwPDU8000Running16RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17 | hwPDU8000Running17Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.1 | hwPDU8000Running17Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.2 | hwPDU8000QF1SwitchStatus | QF1 switch status(L1) | QF1 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.3 | hwPDU8000QF2SwitchStatus | QF2 switch status(L2) | QF2 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.4 | hwPDU8000QF3SwitchStatus | QF3 switch status(L3) | QF3 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.5 | hwPDU8000QF4SwitchStatus | QF4 switch status(L1) | QF4 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.6 | hwPDU8000QF5SwitchStatus | QF5 switch status(L2) | QF5 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.7 | hwPDU8000QF6SwitchStatus | QF6 switch status(L3) | QF6 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.8 | hwPDU8000QF7SwitchStatus | QF7 switch status(L1) | QF7 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.9 | hwPDU8000QF8SwitchStatus | QF8 switch status(L2) | QF8 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.10 | hwPDU8000QF9SwitchStatus | QF9 switch status(L3) | QF9 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.11 | hwPDU8000QF10SwitchStatus | QF10 switch status(L1) | QF10 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.12 | hwPDU8000QF11SwitchStatus | QF11 switch status(L2) | QF11 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.13 | hwPDU8000QF12SwitchStatus | QF12 switch status(L3) | QF12 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.14 | hwPDU8000QF13SwitchStatus | QF13 switch status(L1) | QF13 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.15 | hwPDU8000QF14SwitchStatus | QF14 switch status(L2) | QF14 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.16 | hwPDU8000QF15SwitchStatus | QF15 switch status(L3) | QF15 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.17 | hwPDU8000QF16SwitchStatus | QF16 switch status(L1) | QF16 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.18 | hwPDU8000QF17SwitchStatus | QF17 switch status(L2) | QF17 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.19 | hwPDU8000QF18SwitchStatus | QF18 switch status(L3) | QF18 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.20 | hwPDU8000QF19SwitchStatus | QF19 switch status(L1) | QF19 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.21 | hwPDU8000QF20SwitchStatus | QF20 switch status(L2) | QF20 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.22 | hwPDU8000QF21SwitchStatus | QF21 switch status(L3) | QF21 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.23 | hwPDU8000QF22SwitchStatus | QF22 switch status(L1) | QF22 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.24 | hwPDU8000QF23SwitchStatus | QF23 switch status(L2) | QF23 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.25 | hwPDU8000QF24SwitchStatus | QF24 switch status(L3) | QF24 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.26 | hwPDU8000QF25SwitchStatus | QF25 switch status(L1) | QF25 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.27 | hwPDU8000QF26SwitchStatus | QF26 switch status(L2) | QF26 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.28 | hwPDU8000QF27SwitchStatus | QF27 switch status(L3) | QF27 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.29 | hwPDU8000QF28SwitchStatus | QF28 switch status(L1) | QF28 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.30 | hwPDU8000QF29SwitchStatus | QF29 switch status(L2) | QF29 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.31 | hwPDU8000QF30SwitchStatus | QF30 switch status(L3) | QF30 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.32 | hwPDU8000QF31SwitchStatus | QF31 switch status(L1) | QF31 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.33 | hwPDU8000QF32SwitchStatus | QF32 switch status(L2) | QF32 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.34 | hwPDU8000QF33SwitchStatus | QF33 switch status(L3) | QF33 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.35 | hwPDU8000QF34SwitchStatus | QF34 switch status(L1) | QF34 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.36 | hwPDU8000QF35SwitchStatus | QF35 switch status(L2) | QF35 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.37 | hwPDU8000QF36SwitchStatus | QF36 switch status(L3) | QF36 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.38 | hwPDU8000QF37SwitchStatus | QF37 switch status(L1) | QF37 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.39 | hwPDU8000QF38SwitchStatus | QF38 switch status(L2) | QF38 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.40 | hwPDU8000QF39SwitchStatus | QF39 switch status(L3) | QF39 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.41 | hwPDU8000QF40SwitchStatus | QF40 switch status(L1) | QF40 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.42 | hwPDU8000QF41SwitchStatus | QF41 switch status(L2) | QF41 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.43 | hwPDU8000QF42SwitchStatus | QF42 switch status(L3) | QF42 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.44 | hwPDU8000QF43SwitchStatus | QF43 switch status(L1) | QF43 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.45 | hwPDU8000QF44SwitchStatus | QF44 switch status(L2) | QF44 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.46 | hwPDU8000QF45SwitchStatus | QF45 switch status(L3) | QF45 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.47 | hwPDU8000QF46SwitchStatus | QF46 switch status(L1) | QF46 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.48 | hwPDU8000QF47SwitchStatus | QF47 switch status(L2) | QF47 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.49 | hwPDU8000QF48SwitchStatus | QF48 switch status(L3) | QF48 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.50 | hwPDU8000QF49SwitchStatus | QF49 switch status(L1) | QF49 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.51 | hwPDU8000QF50SwitchStatus | QF50 switch status(L2) | QF50 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.52 | hwPDU8000QF51SwitchStatus | QF51 switch status(L3) | QF51 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.53 | hwPDU8000QF52SwitchStatus | QF52 switch status(L1) | QF52 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.54 | hwPDU8000QF53SwitchStatus | QF53 switch status(L2) | QF53 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.55 | hwPDU8000QF54SwitchStatus | QF54 switch status(L3) | QF54 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.56 | hwPDU8000QF55SwitchStatus | QF55 switch status(L1) | QF55 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.57 | hwPDU8000QF56SwitchStatus | QF56 switch status(L2) | QF56 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.58 | hwPDU8000QF57SwitchStatus | QF57 switch status(L3) | QF57 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.59 | hwPDU8000QF58SwitchStatus | QF58 switch status(L1) | QF58 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.60 | hwPDU8000QF59SwitchStatus | QF59 switch status(L2) | QF59 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.61 | hwPDU8000QF60SwitchStatus | QF60 switch status(L3) | QF60 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.62 | hwPDU8000QF61SwitchStatus | QF61 switch status(L1) | QF61 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.63 | hwPDU8000QF62SwitchStatus | QF62 switch status(L2) | QF62 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.64 | hwPDU8000QF63SwitchStatus | QF63 switch status(L3) | QF63 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.65 | hwPDU8000QF64SwitchStatus | QF64 switch status(L1) | QF64 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.66 | hwPDU8000QF65SwitchStatus | QF65 switch status(L2) | QF65 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.67 | hwPDU8000QF66SwitchStatus | QF66 switch status(L3) | QF66 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.68 | hwPDU8000QF67SwitchStatus | QF67 switch status(L1) | QF67 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.69 | hwPDU8000QF68SwitchStatus | QF68 switch status(L2) | QF68 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.70 | hwPDU8000QF69SwitchStatus | QF69 switch status(L3) | QF69 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.71 | hwPDU8000QF70SwitchStatus | QF70 switch status(L1) | QF70 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.72 | hwPDU8000QF71SwitchStatus | QF71 switch status(L2) | QF71 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.73 | hwPDU8000QF72SwitchStatus | QF72 switch status(L3) | QF72 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.74 | hwPDU8000QF73SwitchStatus | QF73 switch status(L1) | QF73 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.75 | hwPDU8000QF74SwitchStatus | QF74 switch status(L2) | QF74 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.76 | hwPDU8000QF75SwitchStatus | QF75 switch status(L3) | QF75 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.77 | hwPDU8000QF76SwitchStatus | QF76 switch status(L1) | QF76 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.78 | hwPDU8000QF77SwitchStatus | QF77 switch status(L2) | QF77 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.79 | hwPDU8000QF78SwitchStatus | QF78 switch status(L3) | QF78 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.80 | hwPDU8000QF79SwitchStatus | QF79 switch status(L1) | QF79 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.81 | hwPDU8000QF80SwitchStatus | QF80 switch status(L2) | QF80 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.82 | hwPDU8000QF81SwitchStatus | QF81 switch status(L3) | QF81 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.83 | hwPDU8000QF82SwitchStatus | QF82 switch status(L1) | QF82 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.84 | hwPDU8000QF83SwitchStatus | QF83 switch status(L2) | QF83 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.85 | hwPDU8000QF84SwitchStatus | QF84 switch status(L3) | QF84 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.86 | hwPDU8000QF85SwitchStatus | QF85 switch status(L1) | QF85 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.87 | hwPDU8000QF86SwitchStatus | QF86 switch status(L2) | QF86 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.88 | hwPDU8000QF87SwitchStatus | QF87 switch status(L3) | QF87 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.89 | hwPDU8000QF88SwitchStatus | QF88 switch status(L1) | QF88 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.90 | hwPDU8000QF89SwitchStatus | QF89 switch status(L2) | QF89 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.91 | hwPDU8000QF90SwitchStatus | QF90 switch status(L3) | QF90 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.92 | hwPDU8000QF91SwitchStatus | QF91 switch status(L1) | QF91 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.93 | hwPDU8000QF92SwitchStatus | QF92 switch status(L2) | QF92 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.94 | hwPDU8000QF93SwitchStatus | QF93 switch status(L3) | QF93 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.95 | hwPDU8000QF94SwitchStatus | QF94 switch status(L1) | QF94 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.96 | hwPDU8000QF95SwitchStatus | QF95 switch status(L2) | QF95 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.97 | hwPDU8000QF96SwitchStatus | QF96 switch status(L3) | QF96 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.98 | hwPDU8000QF97SwitchStatus | QF97 switch status(L1) | QF97 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.99 | hwPDU8000QF98SwitchStatus | QF98 switch status(L2) | QF98 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.100 | hwPDU8000QF99SwitchStatus | QF99 switch status(L3) | QF99 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.101 | hwPDU8000QF100SwitchStatus | QF100 switch status(L1) | QF100 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.102 | hwPDU8000QF101SwitchStatus | QF101 switch status(L2) | QF101 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.103 | hwPDU8000QF102SwitchStatus | QF102 switch status(L3) | QF102 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.104 | hwPDU8000QF103SwitchStatus | QF103 switch status(L1) | QF103 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.105 | hwPDU8000QF104SwitchStatus | QF104 switch status(L2) | QF104 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.106 | hwPDU8000QF105SwitchStatus | QF105 switch status(L3) | QF105 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.107 | hwPDU8000QF106SwitchStatus | QF106 switch status(L1) | QF106 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.108 | hwPDU8000QF107SwitchStatus | QF107 switch status(L2) | QF107 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.109 | hwPDU8000QF108SwitchStatus | QF108 switch status(L3) | QF108 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.110 | hwPDU8000QF109SwitchStatus | QF109 switch status(L1) | QF109 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.111 | hwPDU8000QF110SwitchStatus | QF110 switch status(L2) | QF110 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.112 | hwPDU8000QF111SwitchStatus | QF111 switch status(L3) | QF111 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.113 | hwPDU8000QF112SwitchStatus | QF112 switch status(L1) | QF112 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.114 | hwPDU8000QF113SwitchStatus | QF113 switch status(L2) | QF113 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.115 | hwPDU8000QF114SwitchStatus | QF114 switch status(L3) | QF114 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.116 | hwPDU8000QF115SwitchStatus | QF115 switch status(L1) | QF115 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.117 | hwPDU8000QF116SwitchStatus | QF116 switch status(L2) | QF116 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.118 | hwPDU8000QF117SwitchStatus | QF117 switch status(L3) | QF117 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.119 | hwPDU8000QF118SwitchStatus | QF118 switch status(L1) | QF118 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.120 | hwPDU8000QF119SwitchStatus | QF119 switch status(L2) | QF119 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.121 | hwPDU8000QF120SwitchStatus | QF120 switch status(L3) | QF120 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.122 | hwPDU8000QF121SwitchStatus | QF121 switch status(L1) | QF121 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.123 | hwPDU8000QF122SwitchStatus | QF122 switch status(L2) | QF122 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.124 | hwPDU8000QF123SwitchStatus | QF123 switch status(L3) | QF123 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.125 | hwPDU8000QF124SwitchStatus | QF124 switch status(L1) | QF124 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.126 | hwPDU8000QF125SwitchStatus | QF125 switch status(L2) | QF125 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.127 | hwPDU8000QF126SwitchStatus | QF126 switch status(L3) | QF126 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.128 | hwPDU8000QF127SwitchStatus | QF127 switch status(L1) | QF127 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.129 | hwPDU8000QF128SwitchStatus | QF128 switch status(L2) | QF128 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.130 | hwPDU8000QF129SwitchStatus | QF129 switch status(L3) | QF129 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.131 | hwPDU8000QF130SwitchStatus | QF130 switch status(L1) | QF130 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.132 | hwPDU8000QF131SwitchStatus | QF131 switch status(L2) | QF131 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.133 | hwPDU8000QF132SwitchStatus | QF132 switch status(L3) | QF132 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.134 | hwPDU8000QF133SwitchStatus | QF133 switch status(L1) | QF133 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.135 | hwPDU8000QF134SwitchStatus | QF134 switch status(L2) | QF134 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.136 | hwPDU8000QF135SwitchStatus | QF135 switch status(L3) | QF135 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.137 | hwPDU8000QF136SwitchStatus | QF136 switch status(L1) | QF136 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.138 | hwPDU8000QF137SwitchStatus | QF137 switch status(L2) | QF137 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.139 | hwPDU8000QF138SwitchStatus | QF138 switch status(L3) | QF138 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.140 | hwPDU8000QF139SwitchStatus | QF139 switch status(L1) | QF139 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.141 | hwPDU8000QF140SwitchStatus | QF140 switch status(L2) | QF140 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.142 | hwPDU8000QF141SwitchStatus | QF141 switch status(L3) | QF141 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.143 | hwPDU8000QF142SwitchStatus | QF142 switch status(L1) | QF142 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.144 | hwPDU8000QF143SwitchStatus | QF143 switch status(L2) | QF143 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.145 | hwPDU8000QF144SwitchStatus | QF144 switch status(L3) | QF144 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.17.1.150 | hwPDU8000Running17RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18 | hwPDU8000Running18Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.1 | hwPDU8000Running18Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.2 | hwPDU80001QF1SwitchStatus | 1QF1 switch status(L1) | 1QF1 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.3 | hwPDU80001QF2SwitchStatus | 1QF2 switch status(L2) | 1QF2 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.4 | hwPDU80001QF3SwitchStatus | 1QF3 switch status(L3) | 1QF3 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.5 | hwPDU80001QF4SwitchStatus | 1QF4 switch status(L1) | 1QF4 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.6 | hwPDU80001QF5SwitchStatus | 1QF5 switch status(L2) | 1QF5 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.7 | hwPDU80001QF6SwitchStatus | 1QF6 switch status(L3) | 1QF6 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.8 | hwPDU80001QF7SwitchStatus | 1QF7 switch status(L1) | 1QF7 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.9 | hwPDU80001QF8SwitchStatus | 1QF8 switch status(L2) | 1QF8 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.10 | hwPDU80001QF9SwitchStatus | 1QF9 switch status(L3) | 1QF9 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.11 | hwPDU80001QF10SwitchStatus | 1QF10 switch status(L1) | 1QF10 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.12 | hwPDU80001QF11SwitchStatus | 1QF11 switch status(L2) | 1QF11 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.13 | hwPDU80001QF12SwitchStatus | 1QF12 switch status(L3) | 1QF12 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.14 | hwPDU80001QF13SwitchStatus | 1QF13 switch status(L1) | 1QF13 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.15 | hwPDU80001QF14SwitchStatus | 1QF14 switch status(L2) | 1QF14 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.16 | hwPDU80001QF15SwitchStatus | 1QF15 switch status(L3) | 1QF15 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.17 | hwPDU80001QF16SwitchStatus | 1QF16 switch status(L1) | 1QF16 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.18 | hwPDU80001QF17SwitchStatus | 1QF17 switch status(L2) | 1QF17 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.19 | hwPDU80001QF18SwitchStatus | 1QF18 switch status(L3) | 1QF18 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.20 | hwPDU80001QF19SwitchStatus | 1QF19 switch status(L1) | 1QF19 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.21 | hwPDU80001QF20SwitchStatus | 1QF20 switch status(L2) | 1QF20 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.22 | hwPDU80001QF21SwitchStatus | 1QF21 switch status(L3) | 1QF21 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.23 | hwPDU80001QF22SwitchStatus | 1QF22 switch status(L1) | 1QF22 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.24 | hwPDU80001QF23SwitchStatus | 1QF23 switch status(L2) | 1QF23 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.25 | hwPDU80001QF24SwitchStatus | 1QF24 switch status(L3) | 1QF24 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.26 | hwPDU80001QF25SwitchStatus | 1QF25 switch status(L1) | 1QF25 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.27 | hwPDU80001QF26SwitchStatus | 1QF26 switch status(L2) | 1QF26 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.28 | hwPDU80001QF27SwitchStatus | 1QF27 switch status(L3) | 1QF27 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.29 | hwPDU80001QF28SwitchStatus | 1QF28 switch status(L1) | 1QF28 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.30 | hwPDU80001QF29SwitchStatus | 1QF29 switch status(L2) | 1QF29 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.31 | hwPDU80001QF30SwitchStatus | 1QF30 switch status(L3) | 1QF30 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.32 | hwPDU80001QF31SwitchStatus | 1QF31 switch status(L1) | 1QF31 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.33 | hwPDU80001QF32SwitchStatus | 1QF32 switch status(L2) | 1QF32 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.34 | hwPDU80001QF33SwitchStatus | 1QF33 switch status(L3) | 1QF33 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.35 | hwPDU80001QF34SwitchStatus | 1QF34 switch status(L1) | 1QF34 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.36 | hwPDU80001QF35SwitchStatus | 1QF35 switch status(L2) | 1QF35 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.37 | hwPDU80001QF36SwitchStatus | 1QF36 switch status(L3) | 1QF36 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.38 | hwPDU80001QF37SwitchStatus | 1QF37 switch status(L1) | 1QF37 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.39 | hwPDU80001QF38SwitchStatus | 1QF38 switch status(L2) | 1QF38 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.40 | hwPDU80001QF39SwitchStatus | 1QF39 switch status(L3) | 1QF39 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.41 | hwPDU80001QF40SwitchStatus | 1QF40 switch status(L1) | 1QF40 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.42 | hwPDU80001QF41SwitchStatus | 1QF41 switch status(L2) | 1QF41 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.43 | hwPDU80001QF42SwitchStatus | 1QF42 switch status(L3) | 1QF42 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.44 | hwPDU80001QF43SwitchStatus | 1QF43 switch status(L1) | 1QF43 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.45 | hwPDU80001QF44SwitchStatus | 1QF44 switch status(L2) | 1QF44 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.46 | hwPDU80001QF45SwitchStatus | 1QF45 switch status(L3) | 1QF45 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.47 | hwPDU80001QF46SwitchStatus | 1QF46 switch status(L1) | 1QF46 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.48 | hwPDU80001QF47SwitchStatus | 1QF47 switch status(L2) | 1QF47 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.49 | hwPDU80001QF48SwitchStatus | 1QF48 switch status(L3) | 1QF48 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.50 | hwPDU80001QF49SwitchStatus | 1QF49 switch status(L1) | 1QF49 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.51 | hwPDU80001QF50SwitchStatus | 1QF50 switch status(L2) | 1QF50 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.52 | hwPDU80001QF51SwitchStatus | 1QF51 switch status(L3) | 1QF51 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.53 | hwPDU80001QF52SwitchStatus | 1QF52 switch status(L1) | 1QF52 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.54 | hwPDU80001QF53SwitchStatus | 1QF53 switch status(L2) | 1QF53 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.55 | hwPDU80001QF54SwitchStatus | 1QF54 switch status(L3) | 1QF54 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.56 | hwPDU80001QF55SwitchStatus | 1QF55 switch status(L1) | 1QF55 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.57 | hwPDU80001QF56SwitchStatus | 1QF56 switch status(L2) | 1QF56 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.58 | hwPDU80001QF57SwitchStatus | 1QF57 switch status(L3) | 1QF57 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.59 | hwPDU80001QF58SwitchStatus | 1QF58 switch status(L1) | 1QF58 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.60 | hwPDU80001QF59SwitchStatus | 1QF59 switch status(L2) | 1QF59 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.61 | hwPDU80001QF60SwitchStatus | 1QF60 switch status(L3) | 1QF60 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.62 | hwPDU80001QF61SwitchStatus | 1QF61 switch status(L1) | 1QF61 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.63 | hwPDU80001QF62SwitchStatus | 1QF62 switch status(L2) | 1QF62 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.64 | hwPDU80001QF63SwitchStatus | 1QF63 switch status(L3) | 1QF63 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.65 | hwPDU80001QF64SwitchStatus | 1QF64 switch status(L1) | 1QF64 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.66 | hwPDU80001QF65SwitchStatus | 1QF65 switch status(L2) | 1QF65 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.67 | hwPDU80001QF66SwitchStatus | 1QF66 switch status(L3) | 1QF66 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.68 | hwPDU80001QF67SwitchStatus | 1QF67 switch status(L1) | 1QF67 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.69 | hwPDU80001QF68SwitchStatus | 1QF68 switch status(L2) | 1QF68 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.70 | hwPDU80001QF69SwitchStatus | 1QF69 switch status(L3) | 1QF69 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.71 | hwPDU80001QF70SwitchStatus | 1QF70 switch status(L1) | 1QF70 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.72 | hwPDU80001QF71SwitchStatus | 1QF71 switch status(L2) | 1QF71 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.73 | hwPDU80001QF72SwitchStatus | 1QF72 switch status(L3) | 1QF72 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.74 | hwPDU80002QF1SwitchStatus | 2QF1 switch status(L1) | 2QF1 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.75 | hwPDU80002QF2SwitchStatus | 2QF2 switch status(L2) | 2QF2 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.76 | hwPDU80002QF3SwitchStatus | 2QF3 switch status(L3) | 2QF3 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.77 | hwPDU80002QF4SwitchStatus | 2QF4 switch status(L1) | 2QF4 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.78 | hwPDU80002QF5SwitchStatus | 2QF5 switch status(L2) | 2QF5 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.79 | hwPDU80002QF6SwitchStatus | 2QF6 switch status(L3) | 2QF6 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.80 | hwPDU80002QF7SwitchStatus | 2QF7 switch status(L1) | 2QF7 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.81 | hwPDU80002QF8SwitchStatus | 2QF8 switch status(L2) | 2QF8 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.82 | hwPDU80002QF9SwitchStatus | 2QF9 switch status(L3) | 2QF9 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.83 | hwPDU80002QF10SwitchStatus | 2QF10 switch status(L1) | 2QF10 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.84 | hwPDU80002QF11SwitchStatus | 2QF11 switch status(L2) | 2QF11 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.85 | hwPDU80002QF12SwitchStatus | 2QF12 switch status(L3) | 2QF12 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.86 | hwPDU80002QF13SwitchStatus | 2QF13 switch status(L1) | 2QF13 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.87 | hwPDU80002QF14SwitchStatus | 2QF14 switch status(L2) | 2QF14 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.88 | hwPDU80002QF15SwitchStatus | 2QF15 switch status(L3) | 2QF15 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.89 | hwPDU80002QF16SwitchStatus | 2QF16 switch status(L1) | 2QF16 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.90 | hwPDU80002QF17SwitchStatus | 2QF17 switch status(L2) | 2QF17 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.91 | hwPDU80002QF18SwitchStatus | 2QF18 switch status(L3) | 2QF18 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.92 | hwPDU80002QF19SwitchStatus | 2QF19 switch status(L1) | 2QF19 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.93 | hwPDU80002QF20SwitchStatus | 2QF20 switch status(L2) | 2QF20 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.94 | hwPDU80002QF21SwitchStatus | 2QF21 switch status(L3) | 2QF21 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.95 | hwPDU80002QF22SwitchStatus | 2QF22 switch status(L1) | 2QF22 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.96 | hwPDU80002QF23SwitchStatus | 2QF23 switch status(L2) | 2QF23 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.97 | hwPDU80002QF24SwitchStatus | 2QF24 switch status(L3) | 2QF24 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.98 | hwPDU80002QF25SwitchStatus | 2QF25 switch status(L1) | 2QF25 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.99 | hwPDU80002QF26SwitchStatus | 2QF26 switch status(L2) | 2QF26 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.100 | hwPDU80002QF27SwitchStatus | 2QF27 switch status(L3) | 2QF27 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.101 | hwPDU80002QF28SwitchStatus | 2QF28 switch status(L1) | 2QF28 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.102 | hwPDU80002QF29SwitchStatus | 2QF29 switch status(L2) | 2QF29 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.103 | hwPDU80002QF30SwitchStatus | 2QF30 switch status(L3) | 2QF30 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.104 | hwPDU80002QF31SwitchStatus | 2QF31 switch status(L1) | 2QF31 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.105 | hwPDU80002QF32SwitchStatus | 2QF32 switch status(L2) | 2QF32 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.106 | hwPDU80002QF33SwitchStatus | 2QF33 switch status(L3) | 2QF33 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.107 | hwPDU80002QF34SwitchStatus | 2QF34 switch status(L1) | 2QF34 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.108 | hwPDU80002QF35SwitchStatus | 2QF35 switch status(L2) | 2QF35 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.109 | hwPDU80002QF36SwitchStatus | 2QF36 switch status(L3) | 2QF36 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.110 | hwPDU80002QF37SwitchStatus | 2QF37 switch status(L1) | 2QF37 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.111 | hwPDU80002QF38SwitchStatus | 2QF38 switch status(L2) | 2QF38 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.112 | hwPDU80002QF39SwitchStatus | 2QF39 switch status(L3) | 2QF39 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.113 | hwPDU80002QF40SwitchStatus | 2QF40 switch status(L1) | 2QF40 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.114 | hwPDU80002QF41SwitchStatus | 2QF41 switch status(L2) | 2QF41 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.115 | hwPDU80002QF42SwitchStatus | 2QF42 switch status(L3) | 2QF42 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.116 | hwPDU80002QF43SwitchStatus | 2QF43 switch status(L1) | 2QF43 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.117 | hwPDU80002QF44SwitchStatus | 2QF44 switch status(L2) | 2QF44 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.118 | hwPDU80002QF45SwitchStatus | 2QF45 switch status(L3) | 2QF45 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.119 | hwPDU80002QF46SwitchStatus | 2QF46 switch status(L1) | 2QF46 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.120 | hwPDU80002QF47SwitchStatus | 2QF47 switch status(L2) | 2QF47 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.121 | hwPDU80002QF48SwitchStatus | 2QF48 switch status(L3) | 2QF48 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.122 | hwPDU80002QF49SwitchStatus | 2QF49 switch status(L1) | 2QF49 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.123 | hwPDU80002QF50SwitchStatus | 2QF50 switch status(L2) | 2QF50 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.124 | hwPDU80002QF51SwitchStatus | 2QF51 switch status(L3) | 2QF51 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.125 | hwPDU80002QF52SwitchStatus | 2QF52 switch status(L1) | 2QF52 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.126 | hwPDU80002QF53SwitchStatus | 2QF53 switch status(L2) | 2QF53 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.127 | hwPDU80002QF54SwitchStatus | 2QF54 switch status(L3) | 2QF54 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.128 | hwPDU80002QF55SwitchStatus | 2QF55 switch status(L1) | 2QF55 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.129 | hwPDU80002QF56SwitchStatus | 2QF56 switch status(L2) | 2QF56 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.130 | hwPDU80002QF57SwitchStatus | 2QF57 switch status(L3) | 2QF57 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.131 | hwPDU80002QF58SwitchStatus | 2QF58 switch status(L1) | 2QF58 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.132 | hwPDU80002QF59SwitchStatus | 2QF59 switch status(L2) | 2QF59 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.133 | hwPDU80002QF60SwitchStatus | 2QF60 switch status(L3) | 2QF60 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.134 | hwPDU80002QF61SwitchStatus | 2QF61 switch status(L1) | 2QF61 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.135 | hwPDU80002QF62SwitchStatus | 2QF62 switch status(L2) | 2QF62 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.136 | hwPDU80002QF63SwitchStatus | 2QF63 switch status(L3) | 2QF63 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.137 | hwPDU80002QF64SwitchStatus | 2QF64 switch status(L1) | 2QF64 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.138 | hwPDU80002QF65SwitchStatus | 2QF65 switch status(L2) | 2QF65 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.139 | hwPDU80002QF66SwitchStatus | 2QF66 switch status(L3) | 2QF66 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.140 | hwPDU80002QF67SwitchStatus | 2QF67 switch status(L1) | 2QF67 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.141 | hwPDU80002QF68SwitchStatus | 2QF68 switch status(L2) | 2QF68 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.142 | hwPDU80002QF69SwitchStatus | 2QF69 switch status(L3) | 2QF69 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.143 | hwPDU80002QF70SwitchStatus | 2QF70 switch status(L1) | 2QF70 空开状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.144 | hwPDU80002QF71SwitchStatus | 2QF71 switch status(L2) | 2QF71 空开状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.145 | hwPDU80002QF72SwitchStatus | 2QF72 switch status(L3) | 2QF72 空开状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | pdu8000 pdu Switch Status: value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.9.5.18.1.150 | hwPDU8000Running18RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19 | hwPDU8000Running19Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.1 | hwPDU8000Running19Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.2 | hwPDU8000MainInputL1Temp | L1 input temperature | L1输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main Input L1 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.3 | hwPDU8000MainInputL2Temp | L2 input temperature | L2输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main Input L2 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.4 | hwPDU8000MainInputL3Temp | L3 input temperature | L3输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main Input L3 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.5 | hwPDU8000MainTranInputL1Temp | L1 input temperature | L1输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main Tran Input L1 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.6 | hwPDU8000MainTranInputL2Temp | L2 input temperature | L2输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main Tran Input L2 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.7 | hwPDU8000MainTranInputL3Temp | L3 input temperature | L3输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main Tran Input L3 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.8 | hwPDU8000Main1InputL1Temp | L1 input temperature | L1输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main 1 Input L1 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.9 | hwPDU8000Main1InputL2Temp | L2 input temperature | L2输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main 1 Input L2 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.10 | hwPDU8000Main1InputL3Temp | L3 input temperature | L3输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main 1 Input L3 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.11 | hwPDU8000Main2InputL1Temp | L1 input temperature | L1输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main 2 Input L1 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.12 | hwPDU8000Main2InputL2Temp | L2 input temperature | L2输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main 2 Input L2 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.13 | hwPDU8000Main2InputL3Temp | L3 input temperature | L3输入温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main 2 Input L3 Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.19.1.100 | hwPDU8000Running19RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20 | hwPDU8000Running20Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.1 | hwPDU8000Running20Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.2 | hwPDU8000QF1PostTemp | Post out 1 temperature | 端子1温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF1 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.3 | hwPDU8000QF2PostTemp | Post out 2 temperature | 端子2温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF2 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.4 | hwPDU8000QF3PostTemp | Post out 3 temperature | 端子3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF3 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.5 | hwPDU8000QF4PostTemp | Post out 4 temperature | 端子4温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF4 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.6 | hwPDU8000QF5PostTemp | Post out 5 temperature | 端子5温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF5 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.7 | hwPDU8000QF6PostTemp | Post out 6 temperature | 端子6温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF6 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.8 | hwPDU8000QF7PostTemp | Post out 7 temperature | 端子7温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF7 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.9 | hwPDU8000QF8PostTemp | Post out 8 temperature | 端子8温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF8 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.10 | hwPDU8000QF9PostTemp | Post out 9 temperature | 端子9温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF9 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.11 | hwPDU8000QF10PostTemp | Post out 10 temperature | 端子10温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF10 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.12 | hwPDU8000QF11PostTemp | Post out 11 temperature | 端子11温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF11 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.13 | hwPDU8000QF12PostTemp | Post out 12 temperature | 端子12温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF12 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.14 | hwPDU8000QF13PostTemp | Post out 13 temperature | 端子13温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF13 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.15 | hwPDU8000QF14PostTemp | Post out 14 temperature | 端子14温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF14 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.16 | hwPDU8000QF15PostTemp | Post out 15 temperature | 端子15温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF15 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.17 | hwPDU8000QF16PostTemp | Post out 16 temperature | 端子16温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF16 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.18 | hwPDU8000QF17PostTemp | Post out 17 temperature | 端子17温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF17 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.19 | hwPDU8000QF18PostTemp | Post out 18 temperature | 端子18温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF18 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.20 | hwPDU8000QF19PostTemp | Post out 19 temperature | 端子19温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF19 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.21 | hwPDU8000QF20PostTemp | Post out 20 temperature | 端子20温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF20 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.22 | hwPDU8000QF21PostTemp | Post out 21 temperature | 端子21温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF21 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.23 | hwPDU8000QF22PostTemp | Post out 22 temperature | 端子22温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF22 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.24 | hwPDU8000QF23PostTemp | Post out 23 temperature | 端子23温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF23 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.25 | hwPDU8000QF24PostTemp | Post out 24 temperature | 端子24温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF24 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.26 | hwPDU8000QF25PostTemp | Post out 25 temperature | 端子25温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF25 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.27 | hwPDU8000QF26PostTemp | Post out 26 temperature | 端子26温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF26 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.28 | hwPDU8000QF27PostTemp | Post out 27 temperature | 端子27温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF27 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.29 | hwPDU8000QF28PostTemp | Post out 28 temperature | 端子28温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF28 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.30 | hwPDU8000QF29PostTemp | Post out 29 temperature | 端子29温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF29 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.31 | hwPDU8000QF30PostTemp | Post out 30 temperature | 端子30温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF30 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.32 | hwPDU8000QF31PostTemp | Post out 31 temperature | 端子31温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF31 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.33 | hwPDU8000QF32PostTemp | Post out 32 temperature | 端子32温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF32 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.34 | hwPDU8000QF33PostTemp | Post out 33 temperature | 端子33温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF33 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.35 | hwPDU8000QF34PostTemp | Post out 34 temperature | 端子34温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF34 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.36 | hwPDU8000QF35PostTemp | Post out 35 temperature | 端子35温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF35 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.37 | hwPDU8000QF36PostTemp | Post out 36 temperature | 端子36温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF36 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.38 | hwPDU8000QF37PostTemp | Post out 37 temperature | 端子37温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF37 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.39 | hwPDU8000QF38PostTemp | Post out 38 temperature | 端子38温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF38 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.40 | hwPDU8000QF39PostTemp | Post out 39 temperature | 端子39温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF39 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.41 | hwPDU8000QF40PostTemp | Post out 40 temperature | 端子40温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF40 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.42 | hwPDU8000QF41PostTemp | Post out 41 temperature | 端子41温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF41 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.43 | hwPDU8000QF42PostTemp | Post out 42 temperature | 端子42温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF42 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.44 | hwPDU8000QF43PostTemp | Post out 43 temperature | 端子43温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF43 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.45 | hwPDU8000QF44PostTemp | Post out 44 temperature | 端子44温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF44 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.46 | hwPDU8000QF45PostTemp | Post out 45 temperature | 端子45温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF45 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.47 | hwPDU8000QF46PostTemp | Post out 46 temperature | 端子46温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF46 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.48 | hwPDU8000QF47PostTemp | Post out 47 temperature | 端子47温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF47 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.49 | hwPDU8000QF48PostTemp | Post out 48 temperature | 端子48温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF48 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.50 | hwPDU8000QF49PostTemp | Post out 49 temperature | 端子49温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF49 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.51 | hwPDU8000QF50PostTemp | Post out 50 temperature | 端子50温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF50 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.52 | hwPDU8000QF51PostTemp | Post out 51 temperature | 端子51温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF51 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.53 | hwPDU8000QF52PostTemp | Post out 52 temperature | 端子52温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF52 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.54 | hwPDU8000QF53PostTemp | Post out 53 temperature | 端子53温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF53 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.55 | hwPDU8000QF54PostTemp | Post out 54 temperature | 端子54温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF54 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.56 | hwPDU8000QF55PostTemp | Post out 55 temperature | 端子55温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF55 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.57 | hwPDU8000QF56PostTemp | Post out 56 temperature | 端子56温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF56 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.58 | hwPDU8000QF57PostTemp | Post out 57 temperature | 端子57温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF57 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.59 | hwPDU8000QF58PostTemp | Post out 58 temperature | 端子58温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF58 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.60 | hwPDU8000QF59PostTemp | Post out 59 temperature | 端子59温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF59 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.61 | hwPDU8000QF60PostTemp | Post out 60 temperature | 端子60温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF60 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.62 | hwPDU8000QF61PostTemp | Post out 61 temperature | 端子61温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF61 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.63 | hwPDU8000QF62PostTemp | Post out 62 temperature | 端子62温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF62 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.64 | hwPDU8000QF63PostTemp | Post out 63 temperature | 端子63温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF63 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.65 | hwPDU8000QF64PostTemp | Post out 64 temperature | 端子64温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF64 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.66 | hwPDU8000QF65PostTemp | Post out 65 temperature | 端子65温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF65 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.67 | hwPDU8000QF66PostTemp | Post out 66 temperature | 端子66温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF66 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.68 | hwPDU8000QF67PostTemp | Post out 67 temperature | 端子67温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF67 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.69 | hwPDU8000QF68PostTemp | Post out 68 temperature | 端子68温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF68 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.70 | hwPDU8000QF69PostTemp | Post out 69 temperature | 端子69温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF69 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.71 | hwPDU8000QF70PostTemp | Post out 70 temperature | 端子70温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF70 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.72 | hwPDU8000QF71PostTemp | Post out 71 temperature | 端子71温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF71 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.73 | hwPDU8000QF72PostTemp | Post out 72 temperature | 端子72温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | QF72 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.20.1.80 | hwPDU8000Running20RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21 | hwPDU8000Running21Table | / | / |  |  | / | / | The running and config table of Huawei PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.1 | hwPDU8000Running21Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU8000.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.2 | hwPDU80001QF1PostTemp | 1 Mains post out 1 temperature | 1主路端子1温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF1 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.3 | hwPDU80001QF2PostTemp | 1 Mains post out 2 temperature | 1主路端子2温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF2 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.4 | hwPDU80001QF3PostTemp | 1 Mains post out 3 temperature | 1主路端子3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF3 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.5 | hwPDU80001QF4PostTemp | 1 Mains post out 4 temperature | 1主路端子4温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF4 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.6 | hwPDU80001QF5PostTemp | 1 Mains post out 5 temperature | 1主路端子5温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF5 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.7 | hwPDU80001QF6PostTemp | 1 Mains post out 6 temperature | 1主路端子6温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF6 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.8 | hwPDU80001QF7PostTemp | 1 Mains post out 7 temperature | 1主路端子7温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF7 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.9 | hwPDU80001QF8PostTemp | 1 Mains post out 8 temperature | 1主路端子8温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF8 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.10 | hwPDU80001QF9PostTemp | 1 Mains post out 9 temperature | 1主路端子9温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF9 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.11 | hwPDU80001QF10PostTemp | 1 Mains post out 10 temperature | 1主路端子10温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF10 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.12 | hwPDU80001QF11PostTemp | 1 Mains post out 11 temperature | 1主路端子11温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF11 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.13 | hwPDU80001QF12PostTemp | 1 Mains post out 12 temperature | 1主路端子12温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF12 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.14 | hwPDU80001QF13PostTemp | 1 Mains post out 13 temperature | 1主路端子13温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF13 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.15 | hwPDU80001QF14PostTemp | 1 Mains post out 14 temperature | 1主路端子14温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF14 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.16 | hwPDU80001QF15PostTemp | 1 Mains post out 15 temperature | 1主路端子15温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF15 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.17 | hwPDU80001QF16PostTemp | 1 Mains post out 16 temperature | 1主路端子16温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF16 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.18 | hwPDU80001QF17PostTemp | 1 Mains post out 17 temperature | 1主路端子17温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF17 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.19 | hwPDU80001QF18PostTemp | 1 Mains post out 18 temperature | 1主路端子18温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF18 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.20 | hwPDU80001QF19PostTemp | 1 Mains post out 19 temperature | 1主路端子19温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF19 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.21 | hwPDU80001QF20PostTemp | 1 Mains post out 20 temperature | 1主路端子20温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF20 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.22 | hwPDU80001QF21PostTemp | 1 Mains post out 21 temperature | 1主路端子21温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF21 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.23 | hwPDU80001QF22PostTemp | 1 Mains post out 22 temperature | 1主路端子22温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF22 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.24 | hwPDU80001QF23PostTemp | 1 Mains post out 23 temperature | 1主路端子23温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF23 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.25 | hwPDU80001QF24PostTemp | 1 Mains post out 24 temperature | 1主路端子24温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF24 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.26 | hwPDU80001QF25PostTemp | 1 Mains post out 25 temperature | 1主路端子25温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF25 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.27 | hwPDU80001QF26PostTemp | 1 Mains post out 26 temperature | 1主路端子26温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF26 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.28 | hwPDU80001QF27PostTemp | 1 Mains post out 27 temperature | 1主路端子27温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF27 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.29 | hwPDU80001QF28PostTemp | 1 Mains post out 28 temperature | 1主路端子28温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF28 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.30 | hwPDU80001QF29PostTemp | 1 Mains post out 29 temperature | 1主路端子29温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF29 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.31 | hwPDU80001QF30PostTemp | 1 Mains post out 30 temperature | 1主路端子30温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF30 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.32 | hwPDU80001QF31PostTemp | 1 Mains post out 31 temperature | 1主路端子31温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF31 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.33 | hwPDU80001QF32PostTemp | 1 Mains post out 32 temperature | 1主路端子32温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF32 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.34 | hwPDU80001QF33PostTemp | 1 Mains post out 33 temperature | 1主路端子33温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF33 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.35 | hwPDU80001QF34PostTemp | 1 Mains post out 34 temperature | 1主路端子34温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF34 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.36 | hwPDU80001QF35PostTemp | 1 Mains post out 35 temperature | 1主路端子35温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF35 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.37 | hwPDU80001QF36PostTemp | 1 Mains post out 36 temperature | 1主路端子36温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 1QF36 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.38 | hwPDU80002QF1PostTemp | 2 Mains post out 1 temperature | 2主路端子1温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF1 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.39 | hwPDU80002QF2PostTemp | 2 Mains post out 2 temperature | 2主路端子2温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF2 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.40 | hwPDU80002QF3PostTemp | 2 Mains post out 3 temperature | 2主路端子3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF3 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.41 | hwPDU80002QF4PostTemp | 2 Mains post out 4 temperature | 2主路端子4温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF4 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.42 | hwPDU80002QF5PostTemp | 2 Mains post out 5 temperature | 2主路端子5温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF5 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.43 | hwPDU80002QF6PostTemp | 2 Mains post out 6 temperature | 2主路端子6温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF6 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.44 | hwPDU80002QF7PostTemp | 2 Mains post out 7 temperature | 2主路端子7温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF7 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.45 | hwPDU80002QF8PostTemp | 2 Mains post out 8 temperature | 2主路端子8温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF8 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.46 | hwPDU80002QF9PostTemp | 2 Mains post out 9 temperature | 2主路端子9温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF9 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.47 | hwPDU80002QF10PostTemp | 2 Mains post out 10 temperature | 2主路端子10温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF10 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.48 | hwPDU80002QF11PostTemp | 2 Mains post out 11 temperature | 2主路端子11温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF11 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.49 | hwPDU80002QF12PostTemp | 2 Mains post out 12 temperature | 2主路端子12温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF12 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.50 | hwPDU80002QF13PostTemp | 2 Mains post out 13 temperature | 2主路端子13温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF13 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.51 | hwPDU80002QF14PostTemp | 2 Mains post out 14 temperature | 2主路端子14温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF14 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.52 | hwPDU80002QF15PostTemp | 2 Mains post out 15 temperature | 2主路端子15温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF15 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.53 | hwPDU80002QF16PostTemp | 2 Mains post out 16 temperature | 2主路端子16温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF16 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.54 | hwPDU80002QF17PostTemp | 2 Mains post out 17 temperature | 2主路端子17温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF17 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.55 | hwPDU80002QF18PostTemp | 2 Mains post out 18 temperature | 2主路端子18温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF18 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.56 | hwPDU80002QF19PostTemp | 2 Mains post out 19 temperature | 2主路端子19温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF19 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.57 | hwPDU80002QF20PostTemp | 2 Mains post out 20 temperature | 2主路端子20温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF20 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.58 | hwPDU80002QF21PostTemp | 2 Mains post out 21 temperature | 2主路端子21温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF21 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.59 | hwPDU80002QF22PostTemp | 2 Mains post out 22 temperature | 2主路端子22温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF22 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.60 | hwPDU80002QF23PostTemp | 2 Mains post out 23 temperature | 2主路端子23温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF23 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.61 | hwPDU80002QF24PostTemp | 2 Mains post out 24 temperature | 2主路端子24温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF24 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.62 | hwPDU80002QF25PostTemp | 2 Mains post out 25 temperature | 2主路端子25温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF25 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.63 | hwPDU80002QF26PostTemp | 2 Mains post out 26 temperature | 2主路端子26温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF26 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.64 | hwPDU80002QF27PostTemp | 2 Mains post out 27 temperature | 2主路端子27温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF27 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.65 | hwPDU80002QF28PostTemp | 2 Mains post out 28 temperature | 2主路端子28温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF28 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.66 | hwPDU80002QF29PostTemp | 2 Mains post out 29 temperature | 2主路端子29温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF29 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.67 | hwPDU80002QF30PostTemp | 2 Mains post out 30 temperature | 2主路端子30温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF30 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.68 | hwPDU80002QF31PostTemp | 2 Mains post out 31 temperature | 2主路端子31温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF31 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.69 | hwPDU80002QF32PostTemp | 2 Mains post out 32 temperature | 2主路端子32温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF32 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.70 | hwPDU80002QF33PostTemp | 2 Mains post out 33 temperature | 2主路端子33温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF33 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.71 | hwPDU80002QF34PostTemp | 2 Mains post out 34 temperature | 2主路端子34温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF34 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.72 | hwPDU80002QF35PostTemp | 2 Mains post out 35 temperature | 2主路端子35温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF35 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.73 | hwPDU80002QF36PostTemp | 2 Mains post out 36 temperature | 2主路端子36温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | 2QF36 Post Temperature. Multiple: 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.5.21.1.80 | hwPDU8000Running21RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the PDU8000.

## PDU2000-M(C)
PDU2000-M(C)
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.6 | PDU2000MC | PDU2000-M(C) | PDU2000-M(C) | / | / | / | / | The PDU2000_M_C Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.6.1 | hwPDU2000MCRunningAndConfigTable | / | / |  |  | / | / | The running and config table of PDU2000_M_C.
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.1 | hwPDU2000MCRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the PDU2000_M_C.
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.2 | hwPDU2000MCCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of PDU2000_M_C: value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.4 | hwPDU2000MCPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of PDU2000_M_C.
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.5 | hwPDU2000MCModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of PDU2000_M_C.
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.6 | hwPDU2000MCL1PhaseVoltage | L1 phase voltage | L1相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | L1 phase voltage of PDU2000_M_C. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.7 | hwPDU2000MCL2PhaseVoltage | L2 phase voltage | L2相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | L2 phase voltage of PDU2000_M_C. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.8 | hwPDU2000MCL3PhaseVoltage | L3 phase voltage | L3相电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | L3 phase voltage of PDU2000_M_C. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.9 | hwPDU2000MCL1PhaseCurrent | L1 phase current | L1相电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | L1 phase current of PDU2000_M_C. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.10 | hwPDU2000MCL2PhaseCurrent | L2 phase current | L2相电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | L2 phase current of PDU2000_M_C. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.11 | hwPDU2000MCL3PhaseCurrent | L3 phase current | L3相电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | L3 phase current of PDU2000_M_C. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.12 | hwPDU2000MCL1PhasePower | L1 phase power | L1相功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 phase power of PDU2000_M_C. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.13 | hwPDU2000MCL2PhasePower | L2 phase power | L2相功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 phase power of PDU2000_M_C. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.14 | hwPDU2000MCL3PhasePower | L3 phase power | L3相功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 phase power of PDU2000_M_C. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.15 | hwPDU2000MCL1PhaseFrequency | L1 phase frequency | L1相频率 | 0-Read_Only | 只读 | 0..100 | 0..100 | L1 phase frequency of PDU2000_M_C. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.16 | hwPDU2000MCL2PhaseFrequency | L2 phase frequency | L2相频率 | 0-Read_Only | 只读 | 0..100 | 0..100 | L2 phase frequency of PDU2000_M_C. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.17 | hwPDU2000MCL3PhaseFrequency | L3 phase frequency | L3相频率 | 0-Read_Only | 只读 | 0..100 | 0..100 | L3 phase frequency of PDU2000_M_C. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.18 | hwPDU2000MCL1PhaseElectricity | L1 phase electricity | L1相电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | L1 phase electricity of PDU2000_M_C. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.19 | hwPDU2000MCL2PhaseElectricity | L2 phase electricity | L2相电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | L2 phase electricity of PDU2000_M_C. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.20 | hwPDU2000MCL3PhaseElectricity | L3 phase electricity | L3相电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | L3 phase electricity of PDU2000_M_C. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.21 | hwPDU2000MCVoltage | Voltage | 电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Voltage of PDU2000_M_C. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.22 | hwPDU2000MCCurrent | Current | 电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Current of PDU2000_M_C. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.23 | hwPDU2000MCPower | Power | 功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power of PDU2000_M_C. SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.24 | hwPDU2000MCFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..100 | 0..100 | Frequency of PDU2000_M_C. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.25 | hwPDU2000MCElectricity | Electricity | 电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Electricity of PDU2000_M_C. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.26 | hwPDU2000MCLowerVoltageThreshold | Lower voltage threshold | 欠压告警阈值 | 1-Read_Write | 读写 | 176..276 | 176..276 | Lower voltage threshold of PDU2000_M_C. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.27 | hwPDU2000MCUpperVoltageThreshold | Upper voltage threshold | 过压告警阈值 | 1-Read_Write | 读写 | 176..276 | 176..276 | Upper voltage threshold of PDU2000_M_C. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.28 | hwPDU2000MCLowerCurrentThreshold | Lower current threshold | 电流过小告警阈值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Lower current threshold of PDU2000_M_C. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.29 | hwPDU2000MCUpperCurrentThreshold | Upper current threshold | 过流告警阈值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Upper current threshold of PDU2000_M_C. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.30 | hwPDU2000MCDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device name of PDU2000_M_C.
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.31 | hwPDU2000MCInputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | InputMode of PDU2000_M_C: value 1 indicates single phase. Value 2 indicates three phase.
1.3.6.1.4.1.2011.6.178.1.1.9.6.1.1.100 | hwPDU2000MCRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase PDU2000_M_C.

## PDU2000-M(H)
PDU2000-M(H)
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.8 | PDU2000MH | PDU2000-M(H) | PDU2000-M(H) | / | / | / | / | The PDU2000_M_C Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.8.1 | hwPDU2000MHRunningAndConfig1Table | / | / |  |  | / | / | The running and config table of PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.1 | hwPDU2000MHRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.2 | hwPDU2000MHCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Inamecommstate Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.3 | hwPDU2000MHPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Inameportno
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.4 | hwPDU2000MHModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Inamemodbusaddress
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.5 | hwPDU2000MHHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Inamehandversion
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.6 | hwPDU2000MHSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Inamesoftversion
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.7 | hwPDU2000MHRatedVoltage | Rated voltage | 额定电压 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Inameratedvoltage SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.8 | hwPDU2000MHRatedPower | Rated power | 额定功率 | 0-Read_Only | 只读 | 0..500 | 0..500 | Inameratedpower SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.9 | hwPDU2000MHRatedFrequency | Rated frequency | 额定频率 | 0-Read_Only | 只读 | 45..65 | 45..65 | Inameratedfrequency SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.10 | hwPDU2000MHInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 4500..6500 | 4500..6500 | Inameiputfrequency.Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.11 | hwPDU2000MHTotalActiveElectricity | Total active electricity | 总有功电度 | 0-Read_Only | 只读 | 0..99999999 | 0..99999999 | Inametotalactivepower.Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.12 | hwPDU2000MHTotalReactiveElectricity | Total reactive electricity | 总无功电度 | 0-Read_Only | 只读 | 0..99999999 | 0..99999999 | Inametotalinactivepower.Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.13 | hwPDU2000MHTotalEnergy | Total energy | 总电度 | 0-Read_Only | 只读 | 0..99999999 | 0..99999999 | Inametotalpower.Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.14 | hwPDU2000MHCurrentAccumulatedUpTimeOfIpdu | Current accumulated up-time of IPDU | 当前累计运行时间 | 0-Read_Only | 只读 | 0..99999999 | 0..99999999 | Inamecurrentcumelativeruntime SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.15 | hwPDU2000MHNeutralLineCurrentIn | Neutral line current In | 中线电流In | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inamecenterlinecurrentin.Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.16 | hwPDU2000MHPhaseAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inameapvoltageva.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.17 | hwPDU2000MHPhaseBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inamebpvoltagevb.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.18 | hwPDU2000MHPhaseCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inamecpvoltagevc.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.19 | hwPDU2000MHABLineVoltage | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inameablvoltagevab.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.20 | hwPDU2000MHBCLineVoltage | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inamebclvoltagevbc.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.21 | hwPDU2000MHCALineVoltage | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inamecalvoltagevca.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.22 | hwPDU2000MHPhaseACurrent | Phase A current | A相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inameapcurrentia.Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.23 | hwPDU2000MHPhaseBCurrent | Phase B current | B相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inamebpcurrentib.Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.24 | hwPDU2000MHPhaseCCurrent | Phase C current | C相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Inamecpcurrentic.Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.25 | hwPDU2000MHPhaseAActivePower | Phase A active power | A相有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Inameapactivepowerpa SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.26 | hwPDU2000MHPhaseBActivePower | Phase B active power | B相有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Inamebpactivepowerpb SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.27 | hwPDU2000MHPhaseCActivePower | Phase C active power | C相有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Inamecpactivepowerpc SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.28 | hwPDU2000MHPhaseAReactivePower | Phase A reactive power | A相无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Inameapinactivepowerqa SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.29 | hwPDU2000MHPhaseBReactivePower | Phase B reactive power | B相无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Inamebpinactivepowerqb SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.30 | hwPDU2000MHPhaseCReactivePower | Phase C reactive power | C相无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Inamecpinactivepowerqc SigUnitInfo:W
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.31 | hwPDU2000MHPhaseAApparentPower | Phase A apparent power | A相视在功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Inameapapparentpowersa SigUnitInfo:VA
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.32 | hwPDU2000MHPhaseBApparentPower | Phase B apparent power | B相视在功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Inamebpapparentpowersb SigUnitInfo:VA
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.33 | hwPDU2000MHPhaseCApparentPower | Phase C apparent power | C相视在功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Inamecpapparentpowersc SigUnitInfo:VA
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.34 | hwPDU2000MHPhaseAPowerFactor | Phase A power factor | A相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Inameapfactorpowerpfa.Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.35 | hwPDU2000MHPhaseBPowerFactor | Phase B power factor | B相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Inamebpfactorpowerpfb.Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.36 | hwPDU2000MHPhaseCPowerFactor | Phase C power factor | C相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Inamecpfactorpowerpfc.Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.37 | hwPDU2000MHDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Inamedevicename
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.38 | hwPDU2000MHHighFrequencyAlarmThreshold | High frequency alarm threshold | 频率过高告警点 | 1-Read_Write | 读写 | 45..65 | 45..65 | Inamehighfrequencyalarmpoint SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.39 | hwPDU2000MHLowFrequencyAlarmThreshold | Low frequency alarm threshold | 频率过低告警点 | 1-Read_Write | 读写 | 45..65 | 45..65 | Inamelowfrequencyalarmpoint SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.40 | hwPDU2000MHPhaseOvervoltageAlarmThreshold | Phase overvoltage alarm threshold | 相电压过压告警点 | 1-Read_Write | 读写 | 500..5000 | 500..5000 | Inamephasevolthighalarmpoint.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.41 | hwPDU2000MHPhaseUndervoltageAlarmThreshold | Phase undervoltage alarm threshold | 相电压欠压告警点 | 1-Read_Write | 读写 | 500..5000 | 500..5000 | Inamephasevoltlowalarmpoint.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.42 | hwPDU2000MHLineOvervoltageAlarmThreshold | Line overvoltage alarm threshold | 线电压过压告警点 | 1-Read_Write | 读写 | 500..5000 | 500..5000 | Inamelinevolthighalarmpoint.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.43 | hwPDU2000MHLineUndervoltageAlarmThreshold | Line undervoltage alarm threshold | 线电压欠压告警点 | 1-Read_Write | 读写 | 500..5000 | 500..5000 | Inamelinevoltlowalarmpoint.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.44 | hwPDU2000MHPhaseOvercurrentAlarmThreshold | Phase overcurrent alarm threshold | 相电流过流告警点 | 1-Read_Write | 读写 | 50..500 | 50..500 | Inamephasecurrhighalarm.Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.8.1.1.100 | hwPDU2000MHRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.2 | hwPDU2000MHRunningAndConfig2Table | / | / |  |  | / | / | The running and config table of PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.2.1.1 | hwPDU2000MHRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.2.1.2 | hwPDU2000MHPhaseVolt | Phase voltage | 相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase Volt for the PDU2000_M_H.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.2.1.3 | hwPDU2000MHLineVolt | Line voltage | 线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Line Volt for the PDU2000_M_H.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.8.2.1.100 | hwPDU2000MHRunningAndConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.3 | hwPDU2000MHRunningAndConfig3Table | / | / |  |  | / | / | The running and config table of PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.3.1.1 | hwPDU2000MHRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.3.1.2 | hwPDU2000MHInputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | InputMode of PDU2000_M_H: value 1 indicates single phase. Value 2 indicates three phase.
1.3.6.1.4.1.2011.6.178.1.1.9.8.3.1.100 | hwPDU2000MHRunningAndConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.4 | hwPDU2000MHRunningAndConfig4Table | / | / |  |  | / | / | The running and config table of PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.4.1.1 | hwPDU2000MHRunning4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table for the PDU2000_M_H.
1.3.6.1.4.1.2011.6.178.1.1.9.8.4.1.2 | hwPDU2000MHPhaseCurrent | Phase current | 相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | The Phase Current of PDU2000_M_H. Multiple 10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.8.4.1.3 | hwPDU2000MHActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Active Power of PDU2000_M_H. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.8.4.1.4 | hwPDU2000MHReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Reactive Power of PDU2000_M_H. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.9.8.4.1.5 | hwPDU2000MHApparentPower | Apparent power | 视在功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Apparent Power of PDU2000_M_H. SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.9.8.4.1.6 | hwPDU2000MHPowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Power Factor of PDU2000_M_H. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.9.8.4.1.100 | hwPDU2000MHRunningAndConfig4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Uniphase PDU2000_M_H.

## TP48202BDCEndCabinet
TP48202B直流列头柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.9 | dispanelboard | TP48202BDCEndCabinet | TP48202B直流列头柜 | / | / | / | / | The Summary of Monitor.
1.3.6.1.4.1.2011.6.178.1.1.9.9.1 | hwdispanelboardRunning1Table | / | / |  |  | / | / | The running table of dis_panelboard.
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.1 | hwdispanelboardRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the dis_panelboard.
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.2 | hwdispanelboardCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Communication Status of dis_panelboard: Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.3 | hwdispanelboardSoftAddr | Software version | 软件版本 | 0-Read_Only | 只读 | / | / | hwdis_panelboardSoftAddr
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.4 | hwdispanelboardComNumber | Port No. | 端口号 | 0-Read_Only | 只读 | / | / | hwdis_panelboardComNumber
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.5 | hwdispanelboardModbusAddr | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | / | / | hwdis_panelboardModbusAddr
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.6 | hwdispanelboardAmbientTemp | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardAmbientTemp SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.7 | hwdispanelboardDcVol | DC voltage | 直流电压 | 0-Read_Only | 只读 | / | / | hwdis_panelboardDcVol.Multiple 100 SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.8 | hwdispanelboardBattTemp1 | Battery 1 temperature | 电池1温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp1 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.9 | hwdispanelboardTotalLoadCur | Total load current | 负载总电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardTotalLoadCur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.10 | hwdispanelboardTotalLoadPower | Total load power | 负载总功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardTotalLoadPower.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.11 | hwdispanelboardTotalElecEnergy | Total electric energy of loads in the cabinet | 柜内负载总电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardTotalElecEnergy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.12 | hwdispanelboardLoad1Cur | Load 1 current | 负载1电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad1Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.13 | hwdispanelboardLoad2Cur | Load 2 current | 负载2电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad2Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.14 | hwdispanelboardLoad3Cur | Load 3 current | 负载3电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad3Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.15 | hwdispanelboardLoad4Cur | Load 4 current | 负载4电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad4Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.16 | hwdispanelboardLoad5Cur | Load 5 current | 负载5电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad5Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.17 | hwdispanelboardLoad6Cur | Load 6 current | 负载6电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad6Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.18 | hwdispanelboardLoad7Cur | Load 7 current | 负载7电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad7Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.19 | hwdispanelboardLoad8Cur | Load 8 current | 负载8电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad8Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.20 | hwdispanelboardLoad9Cur | Load 9 current | 负载9电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad9Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.21 | hwdispanelboardLoad10Cur | Load 10 current | 负载10电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad10Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.22 | hwdispanelboardLoad11Cur | Load 11 current | 负载11电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad11Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.23 | hwdispanelboardLoad12Cur | Load 12 current | 负载12电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad12Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.24 | hwdispanelboardLoad13Cur | Load 13 current | 负载13电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad13Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.25 | hwdispanelboardLoad14Cur | Load 14 current | 负载14电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad14Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.26 | hwdispanelboardLoad15Cur | Load 15 current | 负载15电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad15Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.27 | hwdispanelboardLoad16Cur | Load 16 current | 负载16电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad16Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.28 | hwdispanelboardLoad17Cur | Load 17 current | 负载17电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad17Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.29 | hwdispanelboardLoad18Cur | Load 18 current | 负载18电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad18Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.30 | hwdispanelboardLoad19Cur | Load 19 current | 负载19电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad19Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.31 | hwdispanelboardLoad20Cur | Load 20 current | 负载20电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad20Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.32 | hwdispanelboardLoad21Cur | Load 21 current | 负载21电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad21Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.33 | hwdispanelboardLoad22Cur | Load 22 current | 负载22电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad22Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.34 | hwdispanelboardLoad23Cur | Load 23 current | 负载23电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad23Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.35 | hwdispanelboardLoad24Cur | Load 24 current | 负载24电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad24Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.36 | hwdispanelboardLoad25Cur | Load 25 current | 负载25电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad25Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.37 | hwdispanelboardLoad26Cur | Load 26 current | 负载26电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad26Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.38 | hwdispanelboardLoad27Cur | Load 27 current | 负载27电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad27Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.39 | hwdispanelboardLoad28Cur | Load 28 current | 负载28电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad28Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.40 | hwdispanelboardLoad29Cur | Load 29 current | 负载29电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad29Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.41 | hwdispanelboardLoad30Cur | Load 30 current | 负载30电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad30Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.42 | hwdispanelboardLoad31Cur | Load 31 current | 负载31电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad31Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.43 | hwdispanelboardLoad32Cur | Load 32 current | 负载32电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad32Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.44 | hwdispanelboardLoad33Cur | Load 33 current | 负载33电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad33Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.45 | hwdispanelboardLoad34Cur | Load 34 current | 负载34电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad34Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.46 | hwdispanelboardLoad35Cur | Load 35 current | 负载35电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad35Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.47 | hwdispanelboardLoad36Cur | Load 36 current | 负载36电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad36Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.48 | hwdispanelboardLoad37Cur | Load 37 current | 负载37电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad37Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.49 | hwdispanelboardLoad38Cur | Load 38 current | 负载38电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad38Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.50 | hwdispanelboardLoad39Cur | Load 39 current | 负载39电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad39Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.51 | hwdispanelboardLoad40Cur | Load 40 current | 负载40电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad40Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.52 | hwdispanelboardLoad41Cur | Load 41 current | 负载41电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad41Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.53 | hwdispanelboardLoad42Cur | Load 42 current | 负载42电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad42Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.54 | hwdispanelboardLoad43Cur | Load 43 current | 负载43电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad43Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.55 | hwdispanelboardLoad44Cur | Load 44 current | 负载44电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad44Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.56 | hwdispanelboardLoad45Cur | Load 45 current | 负载45电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad45Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.57 | hwdispanelboardLoad46Cur | Load 46 current | 负载46电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad46Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.58 | hwdispanelboardLoad47Cur | Load 47 current | 负载47电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad47Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.59 | hwdispanelboardLoad48Cur | Load 48 current | 负载48电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad48Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.60 | hwdispanelboardLoad49Cur | Load 49 current | 负载49电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad49Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.61 | hwdispanelboardLoad50Cur | Load 50 current | 负载50电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad50Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.62 | hwdispanelboardLoad51Cur | Load 51 current | 负载51电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad51Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.63 | hwdispanelboardLoad52Cur | Load 52 current | 负载52电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad52Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.64 | hwdispanelboardLoad53Cur | Load 53 current | 负载53电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad53Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.65 | hwdispanelboardLoad54Cur | Load 54 current | 负载54电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad54Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.66 | hwdispanelboardLoad55Cur | Load 55 current | 负载55电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad55Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.67 | hwdispanelboardLoad56Cur | Load 56 current | 负载56电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad56Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.68 | hwdispanelboardLoad57Cur | Load 57 current | 负载57电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad57Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.69 | hwdispanelboardLoad58Cur | Load 58 current | 负载58电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad58Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.70 | hwdispanelboardLoad59Cur | Load 59 current | 负载59电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad59Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.71 | hwdispanelboardLoad60Cur | Load 60 current | 负载60电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad60Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.72 | hwdispanelboardLoad61Cur | Load 61 current | 负载61电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad61Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.73 | hwdispanelboardLoad62Cur | Load 62 current | 负载62电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad62Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.74 | hwdispanelboardLoad63Cur | Load 63 current | 负载63电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad63Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.75 | hwdispanelboardLoad64Cur | Load 64 current | 负载64电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad64Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.76 | hwdispanelboardLoad65Cur | Load 65 current | 负载65电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad65Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.77 | hwdispanelboardLoad66Cur | Load 66 current | 负载66电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad66Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.78 | hwdispanelboardLoad67Cur | Load 67 current | 负载67电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad67Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.79 | hwdispanelboardLoad68Cur | Load 68 current | 负载68电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad68Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.80 | hwdispanelboardLoad69Cur | Load 69 current | 负载69电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad69Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.81 | hwdispanelboardLoad70Cur | Load 70 current | 负载70电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad70Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.82 | hwdispanelboardLoad71Cur | Load 71 current | 负载71电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad71Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.83 | hwdispanelboardLoad72Cur | Load 72 current | 负载72电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad72Cur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.84 | hwdispanelboardLoad1Power | Load 1 power | 负载1功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad1Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.85 | hwdispanelboardLoad2Power | Load 2 power | 负载2功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad2Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.86 | hwdispanelboardLoad3Power | Load 3 power | 负载3功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad3Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.87 | hwdispanelboardLoad4Power | Load 4 power | 负载4功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad4Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.88 | hwdispanelboardLoad5Power | Load 5 power | 负载5功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad5Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.89 | hwdispanelboardLoad6Power | Load 6 power | 负载6功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad6Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.90 | hwdispanelboardLoad7Power | Load 7 power | 负载7功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad7Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.91 | hwdispanelboardLoad8Power | Load 8 power | 负载8功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad8Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.92 | hwdispanelboardLoad9Power | Load 9 power | 负载9功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad9Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.93 | hwdispanelboardLoad10Power | Load 10 power | 负载10功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad10Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.94 | hwdispanelboardLoad11Power | Load 11 power | 负载11功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad11Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.95 | hwdispanelboardLoad12Power | Load 12 power | 负载12功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad12Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.96 | hwdispanelboardLoad13Power | Load 13 power | 负载13功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad13Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.97 | hwdispanelboardLoad14Power | Load 14 power | 负载14功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad14Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.98 | hwdispanelboardLoad15Power | Load 15 power | 负载15功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad15Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.99 | hwdispanelboardLoad16Power | Load 16 power | 负载16功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad16Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.100 | hwdispanelboardLoad17Power | Load 17 power | 负载17功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad17Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.101 | hwdispanelboardLoad18Power | Load 18 power | 负载18功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad18Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.102 | hwdispanelboardLoad19Power | Load 19 power | 负载19功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad19Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.103 | hwdispanelboardLoad20Power | Load 20 power | 负载20功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad20Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.104 | hwdispanelboardLoad21Power | Load 21 power | 负载21功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad21Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.105 | hwdispanelboardLoad22Power | Load 22 power | 负载22功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad22Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.106 | hwdispanelboardLoad23Power | Load 23 power | 负载23功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad23Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.107 | hwdispanelboardLoad24Power | Load 24 power | 负载24功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad24Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.108 | hwdispanelboardLoad25Power | Load 25 power | 负载25功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad25Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.109 | hwdispanelboardLoad26Power | Load 26 power | 负载26功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad26Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.110 | hwdispanelboardLoad27Power | Load 27 power | 负载27功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad27Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.111 | hwdispanelboardLoad28Power | Load 28 power | 负载28功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad28Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.112 | hwdispanelboardLoad29Power | Load 29 power | 负载29功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad29Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.113 | hwdispanelboardLoad30Power | Load 30 power | 负载30功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad30Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.114 | hwdispanelboardLoad31Power | Load 31 power | 负载31功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad31Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.115 | hwdispanelboardLoad32Power | Load 32 power | 负载32功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad32Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.116 | hwdispanelboardLoad33Power | Load 33 power | 负载33功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad33Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.117 | hwdispanelboardLoad34Power | Load 34 power | 负载34功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad34Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.118 | hwdispanelboardLoad35Power | Load 35 power | 负载35功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad35Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.119 | hwdispanelboardLoad36Power | Load 36 power | 负载36功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad36Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.120 | hwdispanelboardLoad37Power | Load 37 power | 负载37功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad37Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.121 | hwdispanelboardLoad38Power | Load 38 power | 负载38功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad38Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.122 | hwdispanelboardLoad39Power | Load 39 power | 负载39功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad39Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.123 | hwdispanelboardLoad40Power | Load 40 power | 负载40功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad40Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.124 | hwdispanelboardLoad41Power | Load 41 power | 负载41功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad41Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.125 | hwdispanelboardLoad42Power | Load 42 power | 负载42功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad42Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.1.1.200 | hwdispanelboard1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the dis_panelboard.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2 | hwdispanelboardRunning2Table | / | / |  |  | / | / | The running table of dis_panelboard.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.1 | hwdispanelboardRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the dis_panelboard.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.2 | hwdispanelboardLoad43Power | Load 43 power | 负载43功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad43Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.3 | hwdispanelboardLoad44Power | Load 44 power | 负载44功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad44Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.4 | hwdispanelboardLoad45Power | Load 45 power | 负载45功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad45Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.5 | hwdispanelboardLoad46Power | Load 46 power | 负载46功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad46Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.6 | hwdispanelboardLoad47Power | Load 47 power | 负载47功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad47Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.7 | hwdispanelboardLoad48Power | Load 48 power | 负载48功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad48Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.8 | hwdispanelboardLoad49Power | Load 49 power | 负载49功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad49Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.9 | hwdispanelboardLoad50Power | Load 50 power | 负载50功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad50Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.10 | hwdispanelboardLoad51Power | Load 51 power | 负载51功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad51Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.11 | hwdispanelboardLoad52Power | Load 52 power | 负载52功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad52Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.12 | hwdispanelboardLoad53Power | Load 53 power | 负载53功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad53Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.13 | hwdispanelboardLoad54Power | Load 54 power | 负载54功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad54Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.14 | hwdispanelboardLoad55Power | Load 55 power | 负载55功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad55Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.15 | hwdispanelboardLoad56Power | Load 56 power | 负载56功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad56Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.16 | hwdispanelboardLoad57Power | Load 57 power | 负载57功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad57Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.17 | hwdispanelboardLoad58Power | Load 58 power | 负载58功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad58Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.18 | hwdispanelboardLoad59Power | Load 59 power | 负载59功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad59Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.19 | hwdispanelboardLoad60Power | Load 60 power | 负载60功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad60Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.20 | hwdispanelboardLoad61Power | Load 61 power | 负载61功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad61Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.21 | hwdispanelboardLoad62Power | Load 62 power | 负载62功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad62Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.22 | hwdispanelboardLoad63Power | Load 63 power | 负载63功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad63Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.23 | hwdispanelboardLoad64Power | Load 64 power | 负载64功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad64Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.24 | hwdispanelboardLoad65Power | Load 65 power | 负载65功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad65Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.25 | hwdispanelboardLoad66Power | Load 66 power | 负载66功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad66Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.26 | hwdispanelboardLoad67Power | Load 67 power | 负载67功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad67Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.27 | hwdispanelboardLoad68Power | Load 68 power | 负载68功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad68Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.28 | hwdispanelboardLoad69Power | Load 69 power | 负载69功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad69Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.29 | hwdispanelboardLoad70Power | Load 70 power | 负载70功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad70Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.30 | hwdispanelboardLoad71Power | Load 71 power | 负载71功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad71Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.31 | hwdispanelboardLoad72Power | Load 72 power | 负载72功率 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad72Power.Multiple 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.32 | hwdispanelboardLoad1ElecEnrgy | Electric energy of loads 1 | 负载1电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad1ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.33 | hwdispanelboardLoad2ElecEnrgy | Electric energy of loads 2 | 负载2电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad2ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.34 | hwdispanelboardLoad3ElecEnrgy | Electric energy of loads 3 | 负载3电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad3ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.35 | hwdispanelboardLoad4ElecEnrgy | Electric energy of loads 4 | 负载4电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad4ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.36 | hwdispanelboardLoad5ElecEnrgy | Electric energy of loads 5 | 负载5电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad5ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.37 | hwdispanelboardLoad6ElecEnrgy | Electric energy of loads 6 | 负载6电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad6ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.38 | hwdispanelboardLoad7ElecEnrgy | Electric energy of loads 7 | 负载7电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad7ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.39 | hwdispanelboardLoad8ElecEnrgy | Electric energy of loads 8 | 负载8电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad8ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.40 | hwdispanelboardLoad9ElecEnrgy | Electric energy of loads 9 | 负载9电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad9ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.41 | hwdispanelboardLoad10ElecEnrgy | Electric energy of loads 10 | 负载10电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad10ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.42 | hwdispanelboardLoad11ElecEnrgy | Electric energy of loads 11 | 负载11电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad11ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.43 | hwdispanelboardLoad12ElecEnrgy | Electric energy of loads 12 | 负载12电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad12ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.44 | hwdispanelboardLoad13ElecEnrgy | Electric energy of loads 13 | 负载13电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad13ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.45 | hwdispanelboardLoad14ElecEnrgy | Electric energy of loads 14 | 负载14电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad14ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.46 | hwdispanelboardLoad15ElecEnrgy | Electric energy of loads 15 | 负载15电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad15ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.47 | hwdispanelboardLoad16ElecEnrgy | Electric energy of loads 16 | 负载16电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad16ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.48 | hwdispanelboardLoad17ElecEnrgy | Electric energy of loads 17 | 负载17电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad17ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.49 | hwdispanelboardLoad18ElecEnrgy | Electric energy of loads 18 | 负载18电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad18ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.50 | hwdispanelboardLoad19ElecEnrgy | Electric energy of loads 19 | 负载19电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad19ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.51 | hwdispanelboardLoad20ElecEnrgy | Electric energy of loads 20 | 负载20电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad20ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.52 | hwdispanelboardLoad21ElecEnrgy | Electric energy of loads 21 | 负载21电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad21ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.53 | hwdispanelboardLoad22ElecEnrgy | Electric energy of loads 22 | 负载22电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad22ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.54 | hwdispanelboardLoad23ElecEnrgy | Electric energy of loads 23 | 负载23电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad23ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.55 | hwdispanelboardLoad24ElecEnrgy | Electric energy of loads 24 | 负载24电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad24ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.56 | hwdispanelboardLoad25ElecEnrgy | Electric energy of loads 25 | 负载25电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad25ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.57 | hwdispanelboardLoad26ElecEnrgy | Electric energy of loads 26 | 负载26电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad26ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.58 | hwdispanelboardLoad27ElecEnrgy | Electric energy of loads 27 | 负载27电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad27ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.59 | hwdispanelboardLoad28ElecEnrgy | Electric energy of loads 28 | 负载28电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad28ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.60 | hwdispanelboardLoad29ElecEnrgy | Electric energy of loads 29 | 负载29电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad29ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.61 | hwdispanelboardLoad30ElecEnrgy | Electric energy of loads 30 | 负载30电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad30ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.62 | hwdispanelboardLoad31ElecEnrgy | Electric energy of loads 31 | 负载31电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad31ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.63 | hwdispanelboardLoad32ElecEnrgy | Electric energy of loads 32 | 负载32电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad32ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.64 | hwdispanelboardLoad33ElecEnrgy | Electric energy of loads 33 | 负载33电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad33ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.65 | hwdispanelboardLoad34ElecEnrgy | Electric energy of loads 34 | 负载34电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad34ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.66 | hwdispanelboardLoad35ElecEnrgy | Electric energy of loads 35 | 负载35电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad35ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.67 | hwdispanelboardLoad36ElecEnrgy | Electric energy of loads 36 | 负载36电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad36ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.68 | hwdispanelboardLoad37ElecEnrgy | Electric energy of loads 37 | 负载37电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad37ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.69 | hwdispanelboardLoad38ElecEnrgy | Electric energy of loads 38 | 负载38电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad38ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.70 | hwdispanelboardLoad39ElecEnrgy | Electric energy of loads 39 | 负载39电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad39ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.71 | hwdispanelboardLoad40ElecEnrgy | Electric energy of loads 40 | 负载40电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad40ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.72 | hwdispanelboardLoad41ElecEnrgy | Electric energy of loads 41 | 负载41电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad41ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.73 | hwdispanelboardLoad42ElecEnrgy | Electric energy of loads 42 | 负载42电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad42ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.74 | hwdispanelboardLoad43ElecEnrgy | Electric energy of loads 43 | 负载43电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad43ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.75 | hwdispanelboardLoad44ElecEnrgy | Electric energy of loads 44 | 负载44电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad44ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.76 | hwdispanelboardLoad45ElecEnrgy | Electric energy of loads 45 | 负载45电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad45ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.77 | hwdispanelboardLoad46ElecEnrgy | Electric energy of loads 46 | 负载46电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad46ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.78 | hwdispanelboardLoad47ElecEnrgy | Electric energy of loads 47 | 负载47电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad47ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.79 | hwdispanelboardLoad48ElecEnrgy | Electric energy of loads 48 | 负载48电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad48ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.80 | hwdispanelboardLoad49ElecEnrgy | Electric energy of loads 49 | 负载49电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad49ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.81 | hwdispanelboardLoad50ElecEnrgy | Electric energy of loads 50 | 负载50电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad50ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.82 | hwdispanelboardLoad51ElecEnrgy | Electric energy of loads 51 | 负载51电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad51ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.83 | hwdispanelboardLoad52ElecEnrgy | Electric energy of loads 52 | 负载52电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad52ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.84 | hwdispanelboardLoad53ElecEnrgy | Electric energy of loads 53 | 负载53电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad53ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.85 | hwdispanelboardLoad54ElecEnrgy | Electric energy of loads 54 | 负载54电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad54ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.86 | hwdispanelboardLoad55ElecEnrgy | Electric energy of loads 55 | 负载55电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad55ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.87 | hwdispanelboardLoad56ElecEnrgy | Electric energy of loads 56 | 负载56电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad56ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.88 | hwdispanelboardLoad57ElecEnrgy | Electric energy of loads 57 | 负载57电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad57ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.89 | hwdispanelboardLoad58ElecEnrgy | Electric energy of loads 58 | 负载58电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad58ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.90 | hwdispanelboardLoad59ElecEnrgy | Electric energy of loads 59 | 负载59电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad59ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.91 | hwdispanelboardLoad60ElecEnrgy | Electric energy of loads 60 | 负载60电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad60ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.92 | hwdispanelboardLoad61ElecEnrgy | Electric energy of loads 61 | 负载61电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad61ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.93 | hwdispanelboardLoad62ElecEnrgy | Electric energy of loads 62 | 负载62电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad62ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.94 | hwdispanelboardLoad63ElecEnrgy | Electric energy of loads 63 | 负载63电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad63ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.95 | hwdispanelboardLoad64ElecEnrgy | Electric energy of loads 64 | 负载64电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad64ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.96 | hwdispanelboardLoad65ElecEnrgy | Electric energy of loads 65 | 负载65电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad65ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.97 | hwdispanelboardLoad66ElecEnrgy | Electric energy of loads 66 | 负载66电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad66ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.98 | hwdispanelboardLoad67ElecEnrgy | Electric energy of loads 67 | 负载67电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad67ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.99 | hwdispanelboardLoad68ElecEnrgy | Electric energy of loads 68 | 负载68电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad68ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.100 | hwdispanelboardLoad69ElecEnrgy | Electric energy of loads 69 | 负载69电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad69ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.101 | hwdispanelboardLoad70ElecEnrgy | Electric energy of loads 70 | 负载70电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad70ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.102 | hwdispanelboardLoad71ElecEnrgy | Electric energy of loads 71 | 负载71电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad71ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.103 | hwdispanelboardLoad72ElecEnrgy | Electric energy of loads 72 | 负载72电量 | 0-Read_Only | 只读 | / | / | hwdis_panelboardLoad72ElecEnrgy.Multiple 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.104 | hwdispanelboardDcSpd | DC SPD configuration | 直流防雷器配置有无 | 0-Read_Only | 只读 | yes(1), no(2), unknown(255) | [有=1]/[无=2] | hwdis_panelboardDcSpd Value 1 indicates yes. Value 2 indicates no.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.105 | hwdispanelboardBattTemp2 | Battery 2 temperature | 电池2温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp2 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.106 | hwdispanelboardBattTemp3 | Battery 3 temperature | 电池3温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp3 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.107 | hwdispanelboardBattTemp4 | Battery 4 temperature | 电池4温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp4 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.108 | hwdispanelboardBattTemp5 | Battery 5 temperature | 电池5温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp5 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.109 | hwdispanelboardBattTemp6 | Battery 6 temperature | 电池6温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp6 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.110 | hwdispanelboardBattTemp7 | Battery 7 temperature | 电池7温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp7 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.111 | hwdispanelboardBattTemp8 | Battery 8 temperature | 电池8温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp8 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.112 | hwdispanelboardBattTemp9 | Battery 9 temperature | 电池9温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp9 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.113 | hwdispanelboardBattTemp10 | Battery 10 temperature | 电池10温度 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattTemp10 SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.114 | hwdispanelboardBattCur1 | Battery 1 current | 电池1电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur1.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.115 | hwdispanelboardBattCur2 | Battery 2 current | 电池2电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur2.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.116 | hwdispanelboardBattCur3 | Battery 3 current | 电池3电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur3.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.117 | hwdispanelboardBattCur4 | Battery 4 current | 电池4电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur4.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.118 | hwdispanelboardBattCur5 | Battery 5 current | 电池5电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur5.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.119 | hwdispanelboardBattCur6 | Battery 6 current | 电池6电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur6.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.120 | hwdispanelboardBattCur7 | Battery 7 current | 电池7电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur7.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.121 | hwdispanelboardBattCur8 | Battery 8 current | 电池8电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur8.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.122 | hwdispanelboardBattCur9 | Battery 9 current | 电池9电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur9.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.123 | hwdispanelboardBattCur10 | Battery 10 current | 电池10电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur10.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.124 | hwdispanelboardBattCur11 | Battery 11 current | 电池11电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur11.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.2.1.200 | hwdispanelboard2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the dis_panelboard.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3 | hwdispanelboardRunning3Table | / | / |  |  | / | / | The running table of dis_panelboard.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.1 | hwdispanelboardRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the dis_panelboard.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.2 | hwdispanelboardBattCur12 | Battery 12 current | 电池12电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur12.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.3 | hwdispanelboardBattCur13 | Battery 13 current | 电池13电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur13.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.4 | hwdispanelboardBattCur14 | Battery 14 current | 电池14电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur14.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.5 | hwdispanelboardBattCur15 | Battery 15 current | 电池15电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur15.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.6 | hwdispanelboardBattCur16 | Battery 16 current | 电池16电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur16.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.7 | hwdispanelboardBattCur17 | Battery 17 current | 电池17电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur17.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.8 | hwdispanelboardBattCur18 | Battery 18 current | 电池18电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur18.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.9 | hwdispanelboardBattCur19 | Battery 19 current | 电池19电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur19.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.10 | hwdispanelboardBattCur20 | Battery 20 current | 电池20电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur20.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.11 | hwdispanelboardBattCur21 | Battery 21 current | 电池21电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur21.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.12 | hwdispanelboardBattCur22 | Battery 22 current | 电池22电流 | 0-Read_Only | 只读 | / | / | hwdis_panelboardBattCur22.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.13 | hwdispanelboardEsn | ESN | ESN号 | 0-Read_Only | 只读 | / | / | hwdis_panelboardEsn
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.14 | hwdispanelboardDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | hwdis_panelboardDeviceName
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.15 | hwdispanelboardSetDcOvervolThred | DC overvoltage threshold | 直流过压点 | 1-Read_Write | 读写 | 3500..6000 | 3500..6000 | hwdis_panelboardSetDcOvervolThred.Multiple 100. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.16 | hwdispanelboardSetDcUnvolThred | DC undervoltage threshold | 直流欠压点 | 1-Read_Write | 读写 | 3500..6000 | 3500..6000 | hwdis_panelboardSetDcUnvolThred.Multiple 100. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.17 | hwdispanelboardSerHighTempThred | High ambient temperature threshold | 环境温度过高点 | 1-Read_Write | 读写 | 25..80 | 25..80 | hwdis_panelboardSerHighTempThred SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.18 | hwdispanelboardSetLowTempThred | Low ambient temperature threshold | 环境温度过低点 | 1-Read_Write | 读写 | -20..20 | -20..20 | hwdis_panelboardSetLowTempThred SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.19 | hwdispanelboardSetTotalLoadOvercur | Total load overcurrent | 总负载过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetTotalLoadOvercur.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.20 | hwdispanelboardSetLoad1OvercurThred | Load 1 overcurrent threshold | 负载1过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad1OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.21 | hwdispanelboardSetLoad2OvercurThred | Load 2 overcurrent threshold | 负载2过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad2OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.22 | hwdispanelboardSetLoad3OvercurThred | Load 3 overcurrent threshold | 负载3过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad3OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.23 | hwdispanelboardSetLoad4OvercurThred | Load 4 overcurrent threshold | 负载4过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad4OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.24 | hwdispanelboardSetLoad5OvercurThred | Load 5 overcurrent threshold | 负载5过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad5OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.25 | hwdispanelboardSetLoad6OvercurThred | Load 6 overcurrent threshold | 负载6过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad6OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.26 | hwdispanelboardSetLoad7OvercurThred | Load 7 overcurrent threshold | 负载7过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad7OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.27 | hwdispanelboardSetLoad8OvercurThred | Load 8 overcurrent threshold | 负载8过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad8OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.28 | hwdispanelboardSetLoad9OvercurThred | Load 9 overcurrent threshold | 负载9过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad9OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.29 | hwdispanelboardSetLoad10OvercurThred | Load 10 overcurrent threshold | 负载10过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad10OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.30 | hwdispanelboardSetLoad11OvercurThred | Load 11 overcurrent threshold | 负载11过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad11OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.31 | hwdispanelboardSetLoad12OvercurThred | Load 12 overcurrent threshold | 负载12过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad12OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.32 | hwdispanelboardSetLoad13OvercurThred | Load 13 overcurrent threshold | 负载13过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad13OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.33 | hwdispanelboardSetLoad14OvercurThred | Load 14 overcurrent threshold | 负载14过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad14OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.34 | hwdispanelboardSetLoad15OvercurThred | Load 15 overcurrent threshold | 负载15过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad15OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.35 | hwdispanelboardSetLoad16OvercurThred | Load 16 overcurrent threshold | 负载16过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad16OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.36 | hwdispanelboardSetLoad17OvercurThred | Load 17 overcurrent threshold | 负载17过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad17OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.37 | hwdispanelboardSetLoad18OvercurThred | Load 18 overcurrent threshold | 负载18过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad18OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.38 | hwdispanelboardSetLoad19OvercurThred | Load 19 overcurrent threshold | 负载19过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad19OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.39 | hwdispanelboardSetLoad20OvercurThred | Load 20 overcurrent threshold | 负载20过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad20OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.40 | hwdispanelboardSetLoad21OvercurThred | Load 21 overcurrent threshold | 负载21过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad21OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.41 | hwdispanelboardSetLoad22OvercurThred | Load 22 overcurrent threshold | 负载22过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad22OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.42 | hwdispanelboardSetLoad23OvercurThred | Load 23 overcurrent threshold | 负载23过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad23OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.43 | hwdispanelboardSetLoad24OvercurThred | Load 24 overcurrent threshold | 负载24过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad24OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.44 | hwdispanelboardSetLoad25OvercurThred | Load 25 overcurrent threshold | 负载25过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad25OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.45 | hwdispanelboardSetLoad26OvercurThred | Load 26 overcurrent threshold | 负载26过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad26OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.46 | hwdispanelboardSetLoad27OvercurThred | Load 27 overcurrent threshold | 负载27过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad27OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.47 | hwdispanelboardSetLoad28OvercurThred | Load 28 overcurrent threshold | 负载28过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad28OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.48 | hwdispanelboardSetLoad29OvercurThred | Load 29 overcurrent threshold | 负载29过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad29OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.49 | hwdispanelboardSetLoad30OvercurThred | Load 30 overcurrent threshold | 负载30过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad30OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.50 | hwdispanelboardSetLoad31OvercurThred | Load 31 overcurrent threshold | 负载31过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad31OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.51 | hwdispanelboardSetLoad32OvercurThred | Load 32 overcurrent threshold | 负载32过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad32OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.52 | hwdispanelboardSetLoad33OvercurThred | Load 33 overcurrent threshold | 负载33过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad33OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.53 | hwdispanelboardSetLoad34OvercurThred | Load 34 overcurrent threshold | 负载34过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad34OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.54 | hwdispanelboardSetLoad35OvercurThred | Load 35 overcurrent threshold | 负载35过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad35OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.55 | hwdispanelboardSetLoad36OvercurThred | Load 36 overcurrent threshold | 负载36过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad36OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.56 | hwdispanelboardSetLoad37OvercurThred | Load 37 overcurrent threshold | 负载37过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad37OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.57 | hwdispanelboardSetLoad38OvercurThred | Load 38 overcurrent threshold | 负载38过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad38OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.58 | hwdispanelboardSetLoad39OvercurThred | Load 39 overcurrent threshold | 负载39过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad39OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.59 | hwdispanelboardSetLoad40OvercurThred | Load 40 overcurrent threshold | 负载40过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad40OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.60 | hwdispanelboardSetLoad41OvercurThred | Load 41 overcurrent threshold | 负载41过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad41OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.61 | hwdispanelboardSetLoad42OvercurThred | Load 42 overcurrent threshold | 负载42过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad42OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.62 | hwdispanelboardSetLoad43OvercurThred | Load 43 overcurrent threshold | 负载43过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad43OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.63 | hwdispanelboardSetLoad44OvercurThred | Load 44 overcurrent threshold | 负载44过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad44OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.64 | hwdispanelboardSetLoad45OvercurThred | Load 45 overcurrent threshold | 负载45过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad45OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.65 | hwdispanelboardSetLoad46OvercurThred | Load 46 overcurrent threshold | 负载46过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad46OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.66 | hwdispanelboardSetLoad47OvercurThred | Load 47 overcurrent threshold | 负载47过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad47OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.67 | hwdispanelboardSetLoad48OvercurThred | Load 48 overcurrent threshold | 负载48过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad48OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.68 | hwdispanelboardSetLoad49OvercurThred | Load 49 overcurrent threshold | 负载49过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad49OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.69 | hwdispanelboardSetLoad50OvercurThred | Load 50 overcurrent threshold | 负载50过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad50OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.70 | hwdispanelboardSetLoad51OvercurThred | Load 51 overcurrent threshold | 负载51过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad51OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.71 | hwdispanelboardSetLoad52OvercurThred | Load 52 overcurrent threshold | 负载52过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad52OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.72 | hwdispanelboardSetLoad53OvercurThred | Load 53 overcurrent threshold | 负载53过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad53OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.73 | hwdispanelboardSetLoad54OvercurThred | Load 54 overcurrent threshold | 负载54过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad54OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.74 | hwdispanelboardSetLoad55OvercurThred | Load 55 overcurrent threshold | 负载55过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad55OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.75 | hwdispanelboardSetLoad56OvercurThred | Load 56 overcurrent threshold | 负载56过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad56OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.76 | hwdispanelboardSetLoad57OvercurThred | Load 57 overcurrent threshold | 负载57过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad57OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.77 | hwdispanelboardSetLoad58OvercurThred | Load 58 overcurrent threshold | 负载58过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad58OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.78 | hwdispanelboardSetLoad59OvercurThred | Load 59 overcurrent threshold | 负载59过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad59OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.79 | hwdispanelboardSetLoad60OvercurThred | Load 60 overcurrent threshold | 负载60过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad60OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.80 | hwdispanelboardSetLoad61OvercurThred | Load 61 overcurrent threshold | 负载61过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad61OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.81 | hwdispanelboardSetLoad62OvercurThred | Load 62 overcurrent threshold | 负载62过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad62OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.82 | hwdispanelboardSetLoad63OvercurThred | Load 63 overcurrent threshold | 负载63过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad63OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.83 | hwdispanelboardSetLoad64OvercurThred | Load 64 overcurrent threshold | 负载64过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad64OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.84 | hwdispanelboardSetLoad65OvercurThred | Load 65 overcurrent threshold | 负载65过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad65OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.85 | hwdispanelboardSetLoad66OvercurThred | Load 66 overcurrent threshold | 负载66过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad66OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.86 | hwdispanelboardSetLoad67OvercurThred | Load 67 overcurrent threshold | 负载67过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad67OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.87 | hwdispanelboardSetLoad68OvercurThred | Load 68 overcurrent threshold | 负载68过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad68OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.88 | hwdispanelboardSetLoad69OvercurThred | Load 69 overcurrent threshold | 负载69过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad69OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.89 | hwdispanelboardSetLoad70OvercurThred | Load 70 overcurrent threshold | 负载70过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad70OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.90 | hwdispanelboardSetLoad71OvercurThred | Load 71 overcurrent threshold | 负载71过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad71OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.91 | hwdispanelboardSetLoad72OvercurThred | Load 72 overcurrent threshold | 负载72过流点 | 1-Read_Write | 读写 | 1000..1000000 | 1000..1000000 | hwdis_panelboardSetLoad72OvercurThrerd.Multiple 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.92 | hwdispanelboardSetDi1AlmCondition | DI1 alarm condition | DI1告警条件 | 1-Read_Write | 读写 | closeAlarm(1), breakAlarm(2), unknown(255) | [闭合告警=1]/[断开告警=2] | hwdis_panelboardSetDi1AlmCondition Value 1 indicates closeAlarm. Value 2 indicates breakAlarm.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.93 | hwdispanelboardSetDi2AlmCondition | DI2 alarm condition | DI2告警条件 | 1-Read_Write | 读写 | closeAlarm(1), breakAlarm(2), unknown(255) | [闭合告警=1]/[断开告警=2] | hwdis_panelboardSetDi2AlmCondition Value 1 indicates closeAlarm. Value 2 indicates breakAlarm.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.94 | hwdispanelboardSetDi3AlmCondition | DI3 alarm condition | DI3告警条件 | 1-Read_Write | 读写 | closeAlarm(1), breakAlarm(2), unknown(255) | [闭合告警=1]/[断开告警=2] | hwdis_panelboardSetDi3AlmCondition Value 1 indicates closeAlarm. Value 2 indicates breakAlarm.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.95 | hwdispanelboardSetDi4AlmCondition | DI4 alarm condition | DI4告警条件 | 1-Read_Write | 读写 | closeAlarm(1), breakAlarm(2), unknown(255) | [闭合告警=1]/[断开告警=2] | hwdis_panelboardSetDi4AlmCondition Value 1 indicates closeAlarm. Value 2 indicates breakAlarm.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.96 | hwdispanelboardSetDi5AlmCondition | DI5 alarm condition | DI5告警条件 | 1-Read_Write | 读写 | closeAlarm(1), breakAlarm(2), unknown(255) | [闭合告警=1]/[断开告警=2] | hwdis_panelboardSetDi5AlmCondition Value 1 indicates closeAlarm. Value 2 indicates breakAlarm.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.97 | hwdispanelboardSetDi6AlmCondition | DI6 alarm condition | DI6告警条件 | 1-Read_Write | 读写 | closeAlarm(1), breakAlarm(2), unknown(255) | [闭合告警=1]/[断开告警=2] | hwdis_panelboardSetDi6AlmCondition Value 1 indicates closeAlarm. Value 2 indicates breakAlarm.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.98 | hwdispanelboardSetDi7AlmCondition | DI7 alarm condition | DI7告警条件 | 1-Read_Write | 读写 | closeAlarm(1), breakAlarm(2), unknown(255) | [闭合告警=1]/[断开告警=2] | hwdis_panelboardSetDi7AlmCondition Value 1 indicates closeAlarm. Value 2 indicates breakAlarm.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.99 | hwdispanelboardSetBoardReset | / | / | 1-Read_Write | 读写 | reset(1), unknown(255) | / | hwdis_panelboardSetBoardReset Value 1 indicates reset. Value 2 indicates unknown.
1.3.6.1.4.1.2011.6.178.1.1.9.9.3.1.200 | hwdispanelboard3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the dis_panelboard.

## DC End Cabinet
直流列头柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.14 | DCEndCabinet | DC End Cabinet | 直流列头柜 | / | / | / | / | DC End Cabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1 | hwDCEndCabinetRunning1Table | / | / |  |  | / | / | The running table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.1 | hwDCEndCabinetRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.2 | hwDCEndCabinetRoute1DcCabinetStatus | DC cabinet status | 直流柜状态 | 0-Read_Only | 只读 | normal(1), faulty(2), unknown(255) | [正常=1]/[故障=2] | Route 1 DC cabinet status of the device config table for the DC End Cabinet. Value 1 indicate normal Value 2 indicate faulty
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.3 | hwDCEndCabinetRoute2DcCabinetStatus | DC cabinet status | 直流柜状态 | 0-Read_Only | 只读 | normal(1), faulty(2), unknown(255) | [正常=1]/[故障=2] | Route 2 DC cabinet status of the device config table for the DC End Cabinet. Value 1 indicate normal Value 2 indicate faulty
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.4 | hwDCEndCabinetRoute1Branch1Voltage | Route 1 branch 1 voltage | 1路支路1电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 DC cabinet status of the device config table for the DC End Cabinet. Value 1 indicate normal Value 2 indicate faulty
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.5 | hwDCEndCabinetRoute2Branch1Voltage | Route 2 branch 1 voltage | 2路支路1电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 1 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.6 | hwDCEndCabinetCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the DC End Cabinet. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.7 | hwDCEndCabinetEsn | ESN | ESN | 0-Read_Only | 只读 | 0..20 | 0..20 | ESN of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.8 | hwDCEndCabinetELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.9 | hwDCEndCabinetIpAddress | IP address | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IP address of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.10 | hwDCEndCabinetMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.11 | hwDCEndCabinetSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.12 | hwDCEndCabinetHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.13 | hwDCEndCabinetSystemType | System type | 系统类型 | 0-Read_Only | 只读 | twohundredandfortyV(1), threehundredandthirtysixV(2), unknown(255) | [240V=1]/[336V=2] | System type of the device config table for the DC End Cabinet. Value 1 indicate 240v Value 2 indicate 336v
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.14 | hwDCEndCabinetRoute1BusbarVoltage | Busbar voltage | 母排电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 Busbar voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.15 | hwDCEndCabinetRoute1DcLoadCurrent | DC load current | 直流负载电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 DC load current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.16 | hwDCEndCabinetRoute1TotalDcPower | Total DC power | 直流总功率 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Route 1 Total DC power of the device config table for the DC End Cabinet.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.17 | hwDCEndCabinetRoute1TotalLoadPercentage | Total load percentage | 总负载负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 Total load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.18 | hwDCEndCabinetRoute1RatedMainCurrent | Rated main current | 主路额定电流 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Route 1 Rated main current of the device config table for the DC End Cabinet.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.19 | hwDCEndCabinetRoute1TotalNumberOfBranchSwitches | Total number of branch switches | 支路开关总路数 | 0-Read_Only | 只读 | 0..88 | 0..88 | Route 1 Total number of branch switches of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.20 | hwDCEndCabinetRoute1NumberOfClosedBranchSwitches | Number of closed branch switches | 支路开关闭合路数 | 0-Read_Only | 只读 | 0..88 | 0..88 | Route 1 Number of closed branch switches of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.21 | hwDCEndCabinetRoute1NumberOfOpenBranchSwitches | Number of open branch switches | 支路开关断开路数 | 0-Read_Only | 只读 | 0..88 | 0..88 | Route 1 Number of open branch switches of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.22 | hwDCEndCabinetRoute1DcSpdSwitchStatus | DC SPD switch status | 直流防雷开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 DC SPD switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.23 | hwDCEndCabinetRoute1MainInputSwitchStatus | Main input switch status | 主路输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 Main input switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.24 | hwDCEndCabinetRoute1VoltageBetweenPositiveBusbarAndGround | Voltage between positive busbar and ground | 母排正对地电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Route 1 Voltage between positive busbar and ground of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.25 | hwDCEndCabinetRoute1VoltageBetweenNegativeBusbarAndGround | Voltage between negative busbar and ground | 母排负对地电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Route 1 Voltage between negative busbar and ground of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.26 | hwDCEndCabinetRoute1ResistanceBetweenPositiveBusbarAndGround | Resistance between positive busbar and ground | 母排正对地电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 Resistance between positive busbar and ground of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.27 | hwDCEndCabinetRoute1ResistanceBetweenNegativeBusbarAndGround | Resistance between negative busbar and ground | 母排负对地电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 Resistance between negative busbar and ground of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.28 | hwDCEndCabinetRoute1InsulationBetweenPositiveBusbarAndGround | Insulation between positive busbar and ground | 母排正对地绝缘状态 | 0-Read_Only | 只读 | normal(1), faulty(2), unknown(255) | [正常=1]/[故障=2] | Route 1 Insulation between positive busbar and ground of the device config table for the DC End Cabinet. Value 1 indicate normal Value 2 indicate faulty
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.29 | hwDCEndCabinetRoute1InsulationBetweenNegativeBusbarAndGround | Insulation between negative busbar and ground | 母排负对地绝缘状态 | 0-Read_Only | 只读 | normal(1), faulty(2), unknown(255) | [正常=1]/[故障=2] | Route 1 Insulation between negative busbar and ground of the device config table for the DC End Cabinet. Value 1 indicate normal Value 2 indicate faulty
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.30 | hwDCEndCabinetRoute1TotalLoadElectricity | Total load electricity | 负载总电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 Total load electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.31 | hwDCEndCabinetRoute1Branch1Current | Route 1 branch 1 current | 1路支路1电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 1 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.32 | hwDCEndCabinetRoute1Branch1Power | Route 1 branch 1 power | 1路支路1功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 1 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.33 | hwDCEndCabinetRoute1Branch1SwitchStatus | Route 1 branch 1 switch status | 1路支路1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 1 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.34 | hwDCEndCabinetRoute1Branch1LoadPercentage | Route 1 branch 1 load percentage | 1路支路1负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 1 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.35 | hwDCEndCabinetRoute1Branch1Electricity | Route 1 branch 1 electricity | 1路支路1电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 1 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.36 | hwDCEndCabinetRoute1Branch1PositiveInsulationResistance | Route 1 branch 1 positive insulation resistance | 1路支路1正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 1 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.37 | hwDCEndCabinetRoute1Branch1NegativeInsulationResistance | Route 1 branch 1 negative insulation resistance | 1路支路1负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 1 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.38 | hwDCEndCabinetRoute1Branch2Voltage | Route 1 branch 2 voltage | 1路支路2电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 2 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.39 | hwDCEndCabinetRoute1Branch2Current | Route 1 branch 2 current | 1路支路2电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 2 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.40 | hwDCEndCabinetRoute1Branch2Power | Route 1 branch 2 power | 1路支路2功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 2 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.41 | hwDCEndCabinetRoute1Branch2SwitchStatus | Route 1 branch 2 switch status | 1路支路2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 2 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.42 | hwDCEndCabinetRoute1Branch2LoadPercentage | Route 1 branch 2 load percentage | 1路支路2负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 2 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.43 | hwDCEndCabinetRoute1Branch2Electricity | Route 1 branch 2 electricity | 1路支路2电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 2 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.44 | hwDCEndCabinetRoute1Branch2PositiveInsulationResistance | Route 1 branch 2 positive insulation resistance | 1路支路2正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 2 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.45 | hwDCEndCabinetRoute1Branch2NegativeInsulationResistance | Route 1 branch 2 negative insulation resistance | 1路支路2负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 2 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.46 | hwDCEndCabinetRoute1Branch3Voltage | Route 1 branch 3 voltage | 1路支路3电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 3 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.47 | hwDCEndCabinetRoute1Branch3Current | Route 1 branch 3 current | 1路支路3电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 3 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.48 | hwDCEndCabinetRoute1Branch3Power | Route 1 branch 3 power | 1路支路3功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 3 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.49 | hwDCEndCabinetRoute1Branch3SwitchStatus | Route 1 branch 3 switch status | 1路支路3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 3 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.50 | hwDCEndCabinetRoute1Branch3LoadPercentage | Route 1 branch 3 load percentage | 1路支路3负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 3 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.51 | hwDCEndCabinetRoute1Branch3Electricity | Route 1 branch 3 electricity | 1路支路3电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 3 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.52 | hwDCEndCabinetRoute1Branch3PositiveInsulationResistance | Route 1 branch 3 positive insulation resistance | 1路支路3正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 3 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.53 | hwDCEndCabinetRoute1Branch3NegativeInsulationResistance | Route 1 branch 3 negative insulation resistance | 1路支路3负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 3 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.54 | hwDCEndCabinetRoute1Branch4Voltage | Route 1 branch 4 voltage | 1路支路4电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 4 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.55 | hwDCEndCabinetRoute1Branch4Current | Route 1 branch 4 current | 1路支路4电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 4 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.56 | hwDCEndCabinetRoute1Branch4Power | Route 1 branch 4 power | 1路支路4功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 4 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.57 | hwDCEndCabinetRoute1Branch4SwitchStatus | Route 1 branch 4 switch status | 1路支路4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 4 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.58 | hwDCEndCabinetRoute1Branch4LoadPercentage | Route 1 branch 4 load percentage | 1路支路4负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 4 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.59 | hwDCEndCabinetRoute1Branch4Electricity | Route 1 branch 4 electricity | 1路支路4电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 4 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.60 | hwDCEndCabinetRoute1Branch4PositiveInsulationResistance | Route 1 branch 4 positive insulation resistance | 1路支路4正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 4 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.61 | hwDCEndCabinetRoute1Branch4NegativeInsulationResistance | Route 1 branch 4 negative insulation resistance | 1路支路4负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 4 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.62 | hwDCEndCabinetRoute1Branch5Voltage | Route 1 branch 5 voltage | 1路支路5电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 5 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.63 | hwDCEndCabinetRoute1Branch5Current | Route 1 branch 5 current | 1路支路5电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 5 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.64 | hwDCEndCabinetRoute1Branch5Power | Route 1 branch 5 power | 1路支路5功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 5 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.65 | hwDCEndCabinetRoute1Branch5SwitchStatus | Route 1 branch 5 switch status | 1路支路5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 5 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.66 | hwDCEndCabinetRoute1Branch5LoadPercentage | Route 1 branch 5 load percentage | 1路支路5负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 5 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.67 | hwDCEndCabinetRoute1Branch5Electricity | Route 1 branch 5 electricity | 1路支路5电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 5 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.68 | hwDCEndCabinetRoute1Branch5PositiveInsulationResistance | Route 1 branch 5 positive insulation resistance | 1路支路5正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 5 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.69 | hwDCEndCabinetRoute1Branch5NegativeInsulationResistance | Route 1 branch 5 negative insulation resistance | 1路支路5负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 5 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.70 | hwDCEndCabinetRoute1Branch6Voltage | Route 1 branch 6 voltage | 1路支路6电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 6 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.71 | hwDCEndCabinetRoute1Branch6Current | Route 1 branch 6 current | 1路支路6电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 6 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.72 | hwDCEndCabinetRoute1Branch6Power | Route 1 branch 6 power | 1路支路6功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 6 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.73 | hwDCEndCabinetRoute1Branch6SwitchStatus | Route 1 branch 6 switch status | 1路支路6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 6 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.74 | hwDCEndCabinetRoute1Branch6LoadPercentage | Route 1 branch 6 load percentage | 1路支路6负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 6 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.75 | hwDCEndCabinetRoute1Branch6Electricity | Route 1 branch 6 electricity | 1路支路6电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 6 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.76 | hwDCEndCabinetRoute1Branch6PositiveInsulationResistance | Route 1 branch 6 positive insulation resistance | 1路支路6正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 6 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.77 | hwDCEndCabinetRoute1Branch6NegativeInsulationResistance | Route 1 branch 6 negative insulation resistance | 1路支路6负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 6 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.78 | hwDCEndCabinetRoute1Branch7Voltage | Route 1 branch 7 voltage | 1路支路7电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 7 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.79 | hwDCEndCabinetRoute1Branch7Current | Route 1 branch 7 current | 1路支路7电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 7 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.80 | hwDCEndCabinetRoute1Branch7Power | Route 1 branch 7 power | 1路支路7功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 7 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.81 | hwDCEndCabinetRoute1Branch7SwitchStatus | Route 1 branch 7 switch status | 1路支路7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 7 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.82 | hwDCEndCabinetRoute1Branch7LoadPercentage | Route 1 branch 7 load percentage | 1路支路7负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 7 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.83 | hwDCEndCabinetRoute1Branch7Electricity | Route 1 branch 7 electricity | 1路支路7电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 7 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.84 | hwDCEndCabinetRoute1Branch7PositiveInsulationResistance | Route 1 branch 7 positive insulation resistance | 1路支路7正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 7 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.85 | hwDCEndCabinetRoute1Branch7NegativeInsulationResistance | Route 1 branch 7 negative insulation resistance | 1路支路7负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 7 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.86 | hwDCEndCabinetRoute1Branch8Voltage | Route 1 branch 8 voltage | 1路支路8电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 8 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.87 | hwDCEndCabinetRoute1Branch8Current | Route 1 branch 8 current | 1路支路8电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 8 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.88 | hwDCEndCabinetRoute1Branch8Power | Route 1 branch 8 power | 1路支路8功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 8 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.89 | hwDCEndCabinetRoute1Branch8SwitchStatus | Route 1 branch 8 switch status | 1路支路8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 8 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.90 | hwDCEndCabinetRoute1Branch8LoadPercentage | Route 1 branch 8 load percentage | 1路支路8负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 8 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.91 | hwDCEndCabinetRoute1Branch8Electricity | Route 1 branch 8 electricity | 1路支路8电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 8 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.92 | hwDCEndCabinetRoute1Branch8PositiveInsulationResistance | Route 1 branch 8 positive insulation resistance | 1路支路8正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 8 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.93 | hwDCEndCabinetRoute1Branch8NegativeInsulationResistance | Route 1 branch 8 negative insulation resistance | 1路支路8负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 8 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.94 | hwDCEndCabinetRoute1Branch9Voltage | Route 1 branch 9 voltage | 1路支路9电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 9 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.95 | hwDCEndCabinetRoute1Branch9Current | Route 1 branch 9 current | 1路支路9电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 9 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.96 | hwDCEndCabinetRoute1Branch9Power | Route 1 branch 9 power | 1路支路9功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 9 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.97 | hwDCEndCabinetRoute1Branch9SwitchStatus | Route 1 branch 9 switch status | 1路支路9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 9 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.98 | hwDCEndCabinetRoute1Branch9LoadPercentage | Route 1 branch 9 load percentage | 1路支路9负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 9 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.99 | hwDCEndCabinetRoute1Branch9Electricity | Route 1 branch 9 electricity | 1路支路9电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 9 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.100 | hwDCEndCabinetRoute1Branch9PositiveInsulationResistance | Route 1 branch 9 positive insulation resistance | 1路支路9正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 9 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.101 | hwDCEndCabinetRoute1Branch9NegativeInsulationResistance | Route 1 branch 9 negative insulation resistance | 1路支路9负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 9 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.102 | hwDCEndCabinetRoute1Branch10Voltage | Route 1 branch 10 voltage | 1路支路10电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 10 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.103 | hwDCEndCabinetRoute1Branch10Current | Route 1 branch 10 current | 1路支路10电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 10 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.104 | hwDCEndCabinetRoute1Branch10Power | Route 1 branch 10 power | 1路支路10功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 10 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.105 | hwDCEndCabinetRoute1Branch10SwitchStatus | Route 1 branch 10 switch status | 1路支路10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 10 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.106 | hwDCEndCabinetRoute1Branch10LoadPercentage | Route 1 branch 10 load percentage | 1路支路10负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 10 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.107 | hwDCEndCabinetRoute1Branch10Electricity | Route 1 branch 10 electricity | 1路支路10电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 10 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.108 | hwDCEndCabinetRoute1Branch10PositiveInsulationResistance | Route 1 branch 10 positive insulation resistance | 1路支路10正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 10 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.109 | hwDCEndCabinetRoute1Branch10NegativeInsulationResistance | Route 1 branch 10 negative insulation resistance | 1路支路10负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 10 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.110 | hwDCEndCabinetRoute1Branch11Voltage | Route 1 branch 11 voltage | 1路支路11电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 11 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.111 | hwDCEndCabinetRoute1Branch11Current | Route 1 branch 11 current | 1路支路11电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 11 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.112 | hwDCEndCabinetRoute1Branch11Power | Route 1 branch 11 power | 1路支路11功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 11 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.113 | hwDCEndCabinetRoute1Branch11SwitchStatus | Route 1 branch 11 switch status | 1路支路11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 11 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.114 | hwDCEndCabinetRoute1Branch11LoadPercentage | Route 1 branch 11 load percentage | 1路支路11负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 11 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.115 | hwDCEndCabinetRoute1Branch11Electricity | Route 1 branch 11 electricity | 1路支路11电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 11 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.116 | hwDCEndCabinetRoute1Branch11PositiveInsulationResistance | Route 1 branch 11 positive insulation resistance | 1路支路11正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 11 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.117 | hwDCEndCabinetRoute1Branch11NegativeInsulationResistance | Route 1 branch 11 negative insulation resistance | 1路支路11负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 11 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.118 | hwDCEndCabinetRoute1Branch12Voltage | Route 1 branch 12 voltage | 1路支路12电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 12 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.119 | hwDCEndCabinetRoute1Branch12Current | Route 1 branch 12 current | 1路支路12电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 12 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.120 | hwDCEndCabinetRoute1Branch12Power | Route 1 branch 12 power | 1路支路12功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 12 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.121 | hwDCEndCabinetRoute1Branch12SwitchStatus | Route 1 branch 12 switch status | 1路支路12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 12 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.122 | hwDCEndCabinetRoute1Branch12LoadPercentage | Route 1 branch 12 load percentage | 1路支路12负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 12 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.123 | hwDCEndCabinetRoute1Branch12Electricity | Route 1 branch 12 electricity | 1路支路12电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 12 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.124 | hwDCEndCabinetRoute1Branch12PositiveInsulationResistance | Route 1 branch 12 positive insulation resistance | 1路支路12正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 12 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.125 | hwDCEndCabinetRoute1Branch12NegativeInsulationResistance | Route 1 branch 12 negative insulation resistance | 1路支路12负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 12 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.126 | hwDCEndCabinetRoute1Branch13Voltage | Route 1 branch 13 voltage | 1路支路13电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 13 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.127 | hwDCEndCabinetRoute1Branch13Current | Route 1 branch 13 current | 1路支路13电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 13 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.128 | hwDCEndCabinetRoute1Branch13Power | Route 1 branch 13 power | 1路支路13功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 13 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.129 | hwDCEndCabinetRoute1Branch13SwitchStatus | Route 1 branch 13 switch status | 1路支路13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 13 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.130 | hwDCEndCabinetRoute1Branch13LoadPercentage | Route 1 branch 13 load percentage | 1路支路13负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 13 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.131 | hwDCEndCabinetRoute1Branch13Electricity | Route 1 branch 13 electricity | 1路支路13电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 13 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.132 | hwDCEndCabinetRoute1Branch13PositiveInsulationResistance | Route 1 branch 13 positive insulation resistance | 1路支路13正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 13 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.133 | hwDCEndCabinetRoute1Branch13NegativeInsulationResistance | Route 1 branch 13 negative insulation resistance | 1路支路13负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 13 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.134 | hwDCEndCabinetRoute1Branch14Voltage | Route 1 branch 14 voltage | 1路支路14电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 14 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.135 | hwDCEndCabinetRoute1Branch14Current | Route 1 branch 14 current | 1路支路14电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 14 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.136 | hwDCEndCabinetRoute1Branch14Power | Route 1 branch 14 power | 1路支路14功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 14 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.137 | hwDCEndCabinetRoute1Branch14SwitchStatus | Route 1 branch 14 switch status | 1路支路14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 14 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.138 | hwDCEndCabinetRoute1Branch14LoadPercentage | Route 1 branch 14 load percentage | 1路支路14负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 14 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.139 | hwDCEndCabinetRoute1Branch14Electricity | Route 1 branch 14 electricity | 1路支路14电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 14 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.140 | hwDCEndCabinetRoute1Branch14PositiveInsulationResistance | Route 1 branch 14 positive insulation resistance | 1路支路14正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 14 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.141 | hwDCEndCabinetRoute1Branch14NegativeInsulationResistance | Route 1 branch 14 negative insulation resistance | 1路支路14负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 14 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.142 | hwDCEndCabinetRoute1Branch15Voltage | Route 1 branch 15 voltage | 1路支路15电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 15 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.143 | hwDCEndCabinetRoute1Branch15Current | Route 1 branch 15 current | 1路支路15电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 15 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.144 | hwDCEndCabinetRoute1Branch15Power | Route 1 branch 15 power | 1路支路15功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 15 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.145 | hwDCEndCabinetRoute1Branch15SwitchStatus | Route 1 branch 15 switch status | 1路支路15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 15 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.146 | hwDCEndCabinetRoute1Branch15LoadPercentage | Route 1 branch 15 load percentage | 1路支路15负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 15 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.147 | hwDCEndCabinetRoute1Branch15Electricity | Route 1 branch 15 electricity | 1路支路15电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 15 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.148 | hwDCEndCabinetRoute1Branch15PositiveInsulationResistance | Route 1 branch 15 positive insulation resistance | 1路支路15正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 15 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.149 | hwDCEndCabinetRoute1Branch15NegativeInsulationResistance | Route 1 branch 15 negative insulation resistance | 1路支路15负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 15 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.150 | hwDCEndCabinetRoute1Branch16Voltage | Route 1 branch 16 voltage | 1路支路16电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 16 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.151 | hwDCEndCabinetRoute1Branch16Current | Route 1 branch 16 current | 1路支路16电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 16 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.152 | hwDCEndCabinetRoute1Branch16Power | Route 1 branch 16 power | 1路支路16功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 16 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.153 | hwDCEndCabinetRoute1Branch16SwitchStatus | Route 1 branch 16 switch status | 1路支路16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 16 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.154 | hwDCEndCabinetRoute1Branch16LoadPercentage | Route 1 branch 16 load percentage | 1路支路16负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 16 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.155 | hwDCEndCabinetRoute1Branch16Electricity | Route 1 branch 16 electricity | 1路支路16电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 16 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.156 | hwDCEndCabinetRoute1Branch16PositiveInsulationResistance | Route 1 branch 16 positive insulation resistance | 1路支路16正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 16 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.157 | hwDCEndCabinetRoute1Branch16NegativeInsulationResistance | Route 1 branch 16 negative insulation resistance | 1路支路16负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 16 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.158 | hwDCEndCabinetRoute1Branch17Voltage | Route 1 branch 17 voltage | 1路支路17电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 17 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.159 | hwDCEndCabinetRoute1Branch17Current | Route 1 branch 17 current | 1路支路17电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 17 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.160 | hwDCEndCabinetRoute1Branch17Power | Route 1 branch 17 power | 1路支路17功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 17 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.161 | hwDCEndCabinetRoute1Branch17SwitchStatus | Route 1 branch 17 switch status | 1路支路17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 17 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.162 | hwDCEndCabinetRoute1Branch17LoadPercentage | Route 1 branch 17 load percentage | 1路支路17负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 17 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.163 | hwDCEndCabinetRoute1Branch17Electricity | Route 1 branch 17 electricity | 1路支路17电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 17 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.164 | hwDCEndCabinetRoute1Branch17PositiveInsulationResistance | Route 1 branch 17 positive insulation resistance | 1路支路17正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 17 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.165 | hwDCEndCabinetRoute1Branch17NegativeInsulationResistance | Route 1 branch 17 negative insulation resistance | 1路支路17负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 17 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.166 | hwDCEndCabinetRoute1Branch18Voltage | Route 1 branch 18 voltage | 1路支路18电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 18 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.167 | hwDCEndCabinetRoute1Branch18Current | Route 1 branch 18 current | 1路支路18电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 18 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.168 | hwDCEndCabinetRoute1Branch18Power | Route 1 branch 18 power | 1路支路18功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 18 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.169 | hwDCEndCabinetRoute1Branch18SwitchStatus | Route 1 branch 18 switch status | 1路支路18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 18 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.170 | hwDCEndCabinetRoute1Branch18LoadPercentage | Route 1 branch 18 load percentage | 1路支路18负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 18 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.171 | hwDCEndCabinetRoute1Branch18Electricity | Route 1 branch 18 electricity | 1路支路18电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 18 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.172 | hwDCEndCabinetRoute1Branch18PositiveInsulationResistance | Route 1 branch 18 positive insulation resistance | 1路支路18正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 18 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.173 | hwDCEndCabinetRoute1Branch18NegativeInsulationResistance | Route 1 branch 18 negative insulation resistance | 1路支路18负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 18 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.174 | hwDCEndCabinetRoute1Branch19Voltage | Route 1 branch 19 voltage | 1路支路19电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 19 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.175 | hwDCEndCabinetRoute1Branch19Current | Route 1 branch 19 current | 1路支路19电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 19 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.176 | hwDCEndCabinetRoute1Branch19Power | Route 1 branch 19 power | 1路支路19功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 19 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.177 | hwDCEndCabinetRoute1Branch19SwitchStatus | Route 1 branch 19 switch status | 1路支路19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 19 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.178 | hwDCEndCabinetRoute1Branch19LoadPercentage | Route 1 branch 19 load percentage | 1路支路19负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 19 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.179 | hwDCEndCabinetRoute1Branch19Electricity | Route 1 branch 19 electricity | 1路支路19电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 19 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.180 | hwDCEndCabinetRoute1Branch19PositiveInsulationResistance | Route 1 branch 19 positive insulation resistance | 1路支路19正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 19 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.181 | hwDCEndCabinetRoute1Branch19NegativeInsulationResistance | Route 1 branch 19 negative insulation resistance | 1路支路19负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 19 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.182 | hwDCEndCabinetRoute1Branch20Voltage | Route 1 branch 20 voltage | 1路支路20电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 20 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.183 | hwDCEndCabinetRoute1Branch20Current | Route 1 branch 20 current | 1路支路20电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 20 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.184 | hwDCEndCabinetRoute1Branch20Power | Route 1 branch 20 power | 1路支路20功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 20 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.185 | hwDCEndCabinetRoute1Branch20SwitchStatus | Route 1 branch 20 switch status | 1路支路20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 20 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.186 | hwDCEndCabinetRoute1Branch20LoadPercentage | Route 1 branch 20 load percentage | 1路支路20负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 20 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.187 | hwDCEndCabinetRoute1Branch20Electricity | Route 1 branch 20 electricity | 1路支路20电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 20 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.188 | hwDCEndCabinetRoute1Branch20PositiveInsulationResistance | Route 1 branch 20 positive insulation resistance | 1路支路20正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 20 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.189 | hwDCEndCabinetRoute1Branch20NegativeInsulationResistance | Route 1 branch 20 negative insulation resistance | 1路支路20负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 20 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.190 | hwDCEndCabinetRoute1Branch21Voltage | Route 1 branch 21 voltage | 1路支路21电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 21 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.191 | hwDCEndCabinetRoute1Branch21Current | Route 1 branch 21 current | 1路支路21电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 21 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.192 | hwDCEndCabinetRoute1Branch21Power | Route 1 branch 21 power | 1路支路21功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 21 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.193 | hwDCEndCabinetRoute1Branch21SwitchStatus | Route 1 branch 21 switch status | 1路支路21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 21 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.194 | hwDCEndCabinetRoute1Branch21LoadPercentage | Route 1 branch 21 load percentage | 1路支路21负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 21 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.195 | hwDCEndCabinetRoute1Branch21Electricity | Route 1 branch 21 electricity | 1路支路21电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 21 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.196 | hwDCEndCabinetRoute1Branch21PositiveInsulationResistance | Route 1 branch 21 positive insulation resistance | 1路支路21正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 21 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.197 | hwDCEndCabinetRoute1Branch21NegativeInsulationResistance | Route 1 branch 21 negative insulation resistance | 1路支路21负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 21 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.198 | hwDCEndCabinetRoute1Branch22Voltage | Route 1 branch 22 voltage | 1路支路22电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 22 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.199 | hwDCEndCabinetRoute1Branch22Current | Route 1 branch 22 current | 1路支路22电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 22 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.200 | hwDCEndCabinetRoute1Branch22Power | Route 1 branch 22 power | 1路支路22功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 22 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.1.1.201 | hwDCEndCabinetRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2 | hwDCEndCabinetRunning2Table | / | / |  |  | / | / | The running table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.1 | hwDCEndCabinetRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.2 | hwDCEndCabinetRoute1Branch22SwitchStatus | Route 1 branch 22 switch status | 1路支路22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 22 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.3 | hwDCEndCabinetRoute1Branch22LoadPercentage | Route 1 branch 22 load percentage | 1路支路22负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 22 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.4 | hwDCEndCabinetRoute1Branch22Electricity | Route 1 branch 22 electricity | 1路支路22电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 22 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.5 | hwDCEndCabinetRoute1Branch22PositiveInsulationResistance | Route 1 branch 22 positive insulation resistance | 1路支路22正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 22 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.6 | hwDCEndCabinetRoute1Branch22NegativeInsulationResistance | Route 1 branch 22 negative insulation resistance | 1路支路22负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 22 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.7 | hwDCEndCabinetRoute1Branch23Voltage | Route 1 branch 23 voltage | 1路支路23电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 23 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.8 | hwDCEndCabinetRoute1Branch23Current | Route 1 branch 23 current | 1路支路23电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 23 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.9 | hwDCEndCabinetRoute1Branch23Power | Route 1 branch 23 power | 1路支路23功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 23 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.10 | hwDCEndCabinetRoute1Branch23SwitchStatus | Route 1 branch 23 switch status | 1路支路23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 23 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.11 | hwDCEndCabinetRoute1Branch23LoadPercentage | Route 1 branch 23 load percentage | 1路支路23负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 23 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.12 | hwDCEndCabinetRoute1Branch23Electricity | Route 1 branch 23 electricity | 1路支路23电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 23 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.13 | hwDCEndCabinetRoute1Branch23PositiveInsulationResistance | Route 1 branch 23 positive insulation resistance | 1路支路23正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 23 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.14 | hwDCEndCabinetRoute1Branch23NegativeInsulationResistance | Route 1 branch 23 negative insulation resistance | 1路支路23负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 23 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.15 | hwDCEndCabinetRoute1Branch24Voltage | Route 1 branch 24 voltage | 1路支路24电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 24 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.16 | hwDCEndCabinetRoute1Branch24Current | Route 1 branch 24 current | 1路支路24电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 24 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.17 | hwDCEndCabinetRoute1Branch24Power | Route 1 branch 24 power | 1路支路24功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 24 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.18 | hwDCEndCabinetRoute1Branch24SwitchStatus | Route 1 branch 24 switch status | 1路支路24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 24 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.19 | hwDCEndCabinetRoute1Branch24LoadPercentage | Route 1 branch 24 load percentage | 1路支路24负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 24 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.20 | hwDCEndCabinetRoute1Branch24Electricity | Route 1 branch 24 electricity | 1路支路24电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 24 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.21 | hwDCEndCabinetRoute1Branch24PositiveInsulationResistance | Route 1 branch 24 positive insulation resistance | 1路支路24正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 24 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.22 | hwDCEndCabinetRoute1Branch24NegativeInsulationResistance | Route 1 branch 24 negative insulation resistance | 1路支路24负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 24 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.23 | hwDCEndCabinetRoute1Branch25Voltage | Route 1 branch 25 voltage | 1路支路25电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 25 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.24 | hwDCEndCabinetRoute1Branch25Current | Route 1 branch 25 current | 1路支路25电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 25 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.25 | hwDCEndCabinetRoute1Branch25Power | Route 1 branch 25 power | 1路支路25功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 25 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.26 | hwDCEndCabinetRoute1Branch25SwitchStatus | Route 1 branch 25 switch status | 1路支路25开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 25 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.27 | hwDCEndCabinetRoute1Branch25LoadPercentage | Route 1 branch 25 load percentage | 1路支路25负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 25 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.28 | hwDCEndCabinetRoute1Branch25Electricity | Route 1 branch 25 electricity | 1路支路25电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 25 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.29 | hwDCEndCabinetRoute1Branch25PositiveInsulationResistance | Route 1 branch 25 positive insulation resistance | 1路支路25正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 25 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.30 | hwDCEndCabinetRoute1Branch25NegativeInsulationResistance | Route 1 branch 25 negative insulation resistance | 1路支路25负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 25 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.31 | hwDCEndCabinetRoute1Branch26Voltage | Route 1 branch 26 voltage | 1路支路26电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 26 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.32 | hwDCEndCabinetRoute1Branch26Current | Route 1 branch 26 current | 1路支路26电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 26 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.33 | hwDCEndCabinetRoute1Branch26Power | Route 1 branch 26 power | 1路支路26功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 26 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.34 | hwDCEndCabinetRoute1Branch26SwitchStatus | Route 1 branch 26 switch status | 1路支路26开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 26 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.35 | hwDCEndCabinetRoute1Branch26LoadPercentage | Route 1 branch 26 load percentage | 1路支路26负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 26 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.36 | hwDCEndCabinetRoute1Branch26Electricity | Route 1 branch 26 electricity | 1路支路26电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 26 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.37 | hwDCEndCabinetRoute1Branch26PositiveInsulationResistance | Route 1 branch 26 positive insulation resistance | 1路支路26正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 26 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.38 | hwDCEndCabinetRoute1Branch26NegativeInsulationResistance | Route 1 branch 26 negative insulation resistance | 1路支路26负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 26 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.39 | hwDCEndCabinetRoute1Branch27Voltage | Route 1 branch 27 voltage | 1路支路27电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 27 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.40 | hwDCEndCabinetRoute1Branch27Current | Route 1 branch 27 current | 1路支路27电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 27 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.41 | hwDCEndCabinetRoute1Branch27Power | Route 1 branch 27 power | 1路支路27功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 27 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.42 | hwDCEndCabinetRoute1Branch27SwitchStatus | Route 1 branch 27 switch status | 1路支路27开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 27 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.43 | hwDCEndCabinetRoute1Branch27LoadPercentage | Route 1 branch 27 load percentage | 1路支路27负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 27 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.44 | hwDCEndCabinetRoute1Branch27Electricity | Route 1 branch 27 electricity | 1路支路27电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 27 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.45 | hwDCEndCabinetRoute1Branch27PositiveInsulationResistance | Route 1 branch 27 positive insulation resistance | 1路支路27正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 27 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.46 | hwDCEndCabinetRoute1Branch27NegativeInsulationResistance | Route 1 branch 27 negative insulation resistance | 1路支路27负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 27 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.47 | hwDCEndCabinetRoute1Branch28Voltage | Route 1 branch 28 voltage | 1路支路28电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 28 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.48 | hwDCEndCabinetRoute1Branch28Current | Route 1 branch 28 current | 1路支路28电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 28 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.49 | hwDCEndCabinetRoute1Branch28Power | Route 1 branch 28 power | 1路支路28功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 28 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.50 | hwDCEndCabinetRoute1Branch28SwitchStatus | Route 1 branch 28 switch status | 1路支路28开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 28 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.51 | hwDCEndCabinetRoute1Branch28LoadPercentage | Route 1 branch 28 load percentage | 1路支路28负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 28 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.52 | hwDCEndCabinetRoute1Branch28Electricity | Route 1 branch 28 electricity | 1路支路28电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 28 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.53 | hwDCEndCabinetRoute1Branch28PositiveInsulationResistance | Route 1 branch 28 positive insulation resistance | 1路支路28正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 28 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.54 | hwDCEndCabinetRoute1Branch28NegativeInsulationResistance | Route 1 branch 28 negative insulation resistance | 1路支路28负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 28 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.55 | hwDCEndCabinetRoute1Branch29Voltage | Route 1 branch 29 voltage | 1路支路29电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 29 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.56 | hwDCEndCabinetRoute1Branch29Current | Route 1 branch 29 current | 1路支路29电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 29 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.57 | hwDCEndCabinetRoute1Branch29Power | Route 1 branch 29 power | 1路支路29功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 29 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.58 | hwDCEndCabinetRoute1Branch29SwitchStatus | Route 1 branch 29 switch status | 1路支路29开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 29 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.59 | hwDCEndCabinetRoute1Branch29LoadPercentage | Route 1 branch 29 load percentage | 1路支路29负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 29 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.60 | hwDCEndCabinetRoute1Branch29Electricity | Route 1 branch 29 electricity | 1路支路29电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 29 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.61 | hwDCEndCabinetRoute1Branch29PositiveInsulationResistance | Route 1 branch 29 positive insulation resistance | 1路支路29正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 29 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.62 | hwDCEndCabinetRoute1Branch29NegativeInsulationResistance | Route 1 branch 29 negative insulation resistance | 1路支路29负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 29 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.63 | hwDCEndCabinetRoute1Branch30Voltage | Route 1 branch 30 voltage | 1路支路30电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 30 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.64 | hwDCEndCabinetRoute1Branch30Current | Route 1 branch 30 current | 1路支路30电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 30 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.65 | hwDCEndCabinetRoute1Branch30Power | Route 1 branch 30 power | 1路支路30功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 30 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.66 | hwDCEndCabinetRoute1Branch30SwitchStatus | Route 1 branch 30 switch status | 1路支路30开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 30 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.67 | hwDCEndCabinetRoute1Branch30LoadPercentage | Route 1 branch 30 load percentage | 1路支路30负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 30 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.68 | hwDCEndCabinetRoute1Branch30Electricity | Route 1 branch 30 electricity | 1路支路30电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 30 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.69 | hwDCEndCabinetRoute1Branch30PositiveInsulationResistance | Route 1 branch 30 positive insulation resistance | 1路支路30正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 30 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.70 | hwDCEndCabinetRoute1Branch30NegativeInsulationResistance | Route 1 branch 30 negative insulation resistance | 1路支路30负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 30 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.71 | hwDCEndCabinetRoute1Branch31Voltage | Route 1 branch 31 voltage | 1路支路31电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 31 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.72 | hwDCEndCabinetRoute1Branch31Current | Route 1 branch 31 current | 1路支路31电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 31 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.73 | hwDCEndCabinetRoute1Branch31Power | Route 1 branch 31 power | 1路支路31功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 31 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.74 | hwDCEndCabinetRoute1Branch31SwitchStatus | Route 1 branch 31 switch status | 1路支路31开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 31 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.75 | hwDCEndCabinetRoute1Branch31LoadPercentage | Route 1 branch 31 load percentage | 1路支路31负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 31 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.76 | hwDCEndCabinetRoute1Branch31Electricity | Route 1 branch 31 electricity | 1路支路31电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 31 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.77 | hwDCEndCabinetRoute1Branch31PositiveInsulationResistance | Route 1 branch 31 positive insulation resistance | 1路支路31正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 31 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.78 | hwDCEndCabinetRoute1Branch31NegativeInsulationResistance | Route 1 branch 31 negative insulation resistance | 1路支路31负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 31 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.79 | hwDCEndCabinetRoute1Branch32Voltage | Route 1 branch 32 voltage | 1路支路32电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 32 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.80 | hwDCEndCabinetRoute1Branch32Current | Route 1 branch 32 current | 1路支路32电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 32 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.81 | hwDCEndCabinetRoute1Branch32Power | Route 1 branch 32 power | 1路支路32功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 32 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.82 | hwDCEndCabinetRoute1Branch32SwitchStatus | Route 1 branch 32 switch status | 1路支路32开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 32 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.83 | hwDCEndCabinetRoute1Branch32LoadPercentage | Route 1 branch 32 load percentage | 1路支路32负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 32 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.84 | hwDCEndCabinetRoute1Branch32Electricity | Route 1 branch 32 electricity | 1路支路32电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 32 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.85 | hwDCEndCabinetRoute1Branch32PositiveInsulationResistance | Route 1 branch 32 positive insulation resistance | 1路支路32正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 32 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.86 | hwDCEndCabinetRoute1Branch32NegativeInsulationResistance | Route 1 branch 32 negative insulation resistance | 1路支路32负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 32 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.87 | hwDCEndCabinetRoute1Branch33Voltage | Route 1 branch 33 voltage | 1路支路33电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 33 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.88 | hwDCEndCabinetRoute1Branch33Current | Route 1 branch 33 current | 1路支路33电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 33 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.89 | hwDCEndCabinetRoute1Branch33Power | Route 1 branch 33 power | 1路支路33功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 33 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.90 | hwDCEndCabinetRoute1Branch33SwitchStatus | Route 1 branch 33 switch status | 1路支路33开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 33 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.91 | hwDCEndCabinetRoute1Branch33LoadPercentage | Route 1 branch 33 load percentage | 1路支路33负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 33 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.92 | hwDCEndCabinetRoute1Branch33Electricity | Route 1 branch 33 electricity | 1路支路33电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 33 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.93 | hwDCEndCabinetRoute1Branch33PositiveInsulationResistance | Route 1 branch 33 positive insulation resistance | 1路支路33正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 33 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.94 | hwDCEndCabinetRoute1Branch33NegativeInsulationResistance | Route 1 branch 33 negative insulation resistance | 1路支路33负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 33 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.95 | hwDCEndCabinetRoute1Branch34Voltage | Route 1 branch 34 voltage | 1路支路34电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 34 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.96 | hwDCEndCabinetRoute1Branch34Current | Route 1 branch 34 current | 1路支路34电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 34 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.97 | hwDCEndCabinetRoute1Branch34Power | Route 1 branch 34 power | 1路支路34功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 34 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.98 | hwDCEndCabinetRoute1Branch34SwitchStatus | Route 1 branch 34 switch status | 1路支路34开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 34 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.99 | hwDCEndCabinetRoute1Branch34LoadPercentage | Route 1 branch 34 load percentage | 1路支路34负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 34 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.100 | hwDCEndCabinetRoute1Branch34Electricity | Route 1 branch 34 electricity | 1路支路34电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 34 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.101 | hwDCEndCabinetRoute1Branch34PositiveInsulationResistance | Route 1 branch 34 positive insulation resistance | 1路支路34正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 34 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.102 | hwDCEndCabinetRoute1Branch34NegativeInsulationResistance | Route 1 branch 34 negative insulation resistance | 1路支路34负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 34 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.103 | hwDCEndCabinetRoute1Branch35Voltage | Route 1 branch 35 voltage | 1路支路35电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 35 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.104 | hwDCEndCabinetRoute1Branch35Current | Route 1 branch 35 current | 1路支路35电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 35 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.105 | hwDCEndCabinetRoute1Branch35Power | Route 1 branch 35 power | 1路支路35功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 35 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.106 | hwDCEndCabinetRoute1Branch35SwitchStatus | Route 1 branch 35 switch status | 1路支路35开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 35 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.107 | hwDCEndCabinetRoute1Branch35LoadPercentage | Route 1 branch 35 load percentage | 1路支路35负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 35 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.108 | hwDCEndCabinetRoute1Branch35Electricity | Route 1 branch 35 electricity | 1路支路35电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 35 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.109 | hwDCEndCabinetRoute1Branch35PositiveInsulationResistance | Route 1 branch 35 positive insulation resistance | 1路支路35正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 35 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.110 | hwDCEndCabinetRoute1Branch35NegativeInsulationResistance | Route 1 branch 35 negative insulation resistance | 1路支路35负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 35 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.111 | hwDCEndCabinetRoute1Branch36Voltage | Route 1 branch 36 voltage | 1路支路36电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 36 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.112 | hwDCEndCabinetRoute1Branch36Current | Route 1 branch 36 current | 1路支路36电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 36 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.113 | hwDCEndCabinetRoute1Branch36Power | Route 1 branch 36 power | 1路支路36功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 36 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.114 | hwDCEndCabinetRoute1Branch36SwitchStatus | Route 1 branch 36 switch status | 1路支路36开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 36 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.115 | hwDCEndCabinetRoute1Branch36LoadPercentage | Route 1 branch 36 load percentage | 1路支路36负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 36 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.116 | hwDCEndCabinetRoute1Branch36Electricity | Route 1 branch 36 electricity | 1路支路36电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 36 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.117 | hwDCEndCabinetRoute1Branch36PositiveInsulationResistance | Route 1 branch 36 positive insulation resistance | 1路支路36正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 36 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.118 | hwDCEndCabinetRoute1Branch36NegativeInsulationResistance | Route 1 branch 36 negative insulation resistance | 1路支路36负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 36 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.119 | hwDCEndCabinetRoute1Branch37Voltage | Route 1 branch 37 voltage | 1路支路37电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 37 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.120 | hwDCEndCabinetRoute1Branch37Current | Route 1 branch 37 current | 1路支路37电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 37 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.121 | hwDCEndCabinetRoute1Branch37Power | Route 1 branch 37 power | 1路支路37功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 37 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.122 | hwDCEndCabinetRoute1Branch37SwitchStatus | Route 1 branch 37 switch status | 1路支路37开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 37 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.123 | hwDCEndCabinetRoute1Branch37LoadPercentage | Route 1 branch 37 load percentage | 1路支路37负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 37 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.124 | hwDCEndCabinetRoute1Branch37Electricity | Route 1 branch 37 electricity | 1路支路37电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 37 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.125 | hwDCEndCabinetRoute1Branch37PositiveInsulationResistance | Route 1 branch 37 positive insulation resistance | 1路支路37正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 37 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.126 | hwDCEndCabinetRoute1Branch37NegativeInsulationResistance | Route 1 branch 37 negative insulation resistance | 1路支路37负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 37 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.127 | hwDCEndCabinetRoute1Branch38Voltage | Route 1 branch 38 voltage | 1路支路38电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 38 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.128 | hwDCEndCabinetRoute1Branch38Current | Route 1 branch 38 current | 1路支路38电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 38 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.129 | hwDCEndCabinetRoute1Branch38Power | Route 1 branch 38 power | 1路支路38功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 38 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.130 | hwDCEndCabinetRoute1Branch38SwitchStatus | Route 1 branch 38 switch status | 1路支路38开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 38 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.131 | hwDCEndCabinetRoute1Branch38LoadPercentage | Route 1 branch 38 load percentage | 1路支路38负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 38 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.132 | hwDCEndCabinetRoute1Branch38Electricity | Route 1 branch 38 electricity | 1路支路38电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 38 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.133 | hwDCEndCabinetRoute1Branch38PositiveInsulationResistance | Route 1 branch 38 positive insulation resistance | 1路支路38正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 38 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.134 | hwDCEndCabinetRoute1Branch38NegativeInsulationResistance | Route 1 branch 38 negative insulation resistance | 1路支路38负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 38 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.135 | hwDCEndCabinetRoute1Branch39Voltage | Route 1 branch 39 voltage | 1路支路39电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 39 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.136 | hwDCEndCabinetRoute1Branch39Current | Route 1 branch 39 current | 1路支路39电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 39 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.137 | hwDCEndCabinetRoute1Branch39Power | Route 1 branch 39 power | 1路支路39功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 39 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.138 | hwDCEndCabinetRoute1Branch39SwitchStatus | Route 1 branch 39 switch status | 1路支路39开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 39 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.139 | hwDCEndCabinetRoute1Branch39LoadPercentage | Route 1 branch 39 load percentage | 1路支路39负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 39 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.140 | hwDCEndCabinetRoute1Branch39Electricity | Route 1 branch 39 electricity | 1路支路39电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 39 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.141 | hwDCEndCabinetRoute1Branch39PositiveInsulationResistance | Route 1 branch 39 positive insulation resistance | 1路支路39正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 39 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.142 | hwDCEndCabinetRoute1Branch39NegativeInsulationResistance | Route 1 branch 39 negative insulation resistance | 1路支路39负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 39 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.143 | hwDCEndCabinetRoute1Branch40Voltage | Route 1 branch 40 voltage | 1路支路40电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 40 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.144 | hwDCEndCabinetRoute1Branch40Current | Route 1 branch 40 current | 1路支路40电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 40 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.145 | hwDCEndCabinetRoute1Branch40Power | Route 1 branch 40 power | 1路支路40功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 40 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.146 | hwDCEndCabinetRoute1Branch40SwitchStatus | Route 1 branch 40 switch status | 1路支路40开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 40 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.147 | hwDCEndCabinetRoute1Branch40LoadPercentage | Route 1 branch 40 load percentage | 1路支路40负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 40 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.148 | hwDCEndCabinetRoute1Branch40Electricity | Route 1 branch 40 electricity | 1路支路40电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 40 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.149 | hwDCEndCabinetRoute1Branch40PositiveInsulationResistance | Route 1 branch 40 positive insulation resistance | 1路支路40正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 40 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.150 | hwDCEndCabinetRoute1Branch40NegativeInsulationResistance | Route 1 branch 40 negative insulation resistance | 1路支路40负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 40 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.151 | hwDCEndCabinetRoute1Branch41Voltage | Route 1 branch 41 voltage | 1路支路41电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 41 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.152 | hwDCEndCabinetRoute1Branch41Current | Route 1 branch 41 current | 1路支路41电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 41 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.153 | hwDCEndCabinetRoute1Branch41Power | Route 1 branch 41 power | 1路支路41功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 41 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.154 | hwDCEndCabinetRoute1Branch41SwitchStatus | Route 1 branch 41 switch status | 1路支路41开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 41 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.155 | hwDCEndCabinetRoute1Branch41LoadPercentage | Route 1 branch 41 load percentage | 1路支路41负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 41 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.156 | hwDCEndCabinetRoute1Branch41Electricity | Route 1 branch 41 electricity | 1路支路41电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 41 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.157 | hwDCEndCabinetRoute1Branch41PositiveInsulationResistance | Route 1 branch 41 positive insulation resistance | 1路支路41正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 41 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.158 | hwDCEndCabinetRoute1Branch41NegativeInsulationResistance | Route 1 branch 41 negative insulation resistance | 1路支路41负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 41 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.159 | hwDCEndCabinetRoute1Branch42Voltage | Route 1 branch 42 voltage | 1路支路42电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 42 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.160 | hwDCEndCabinetRoute1Branch42Current | Route 1 branch 42 current | 1路支路42电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 42 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.161 | hwDCEndCabinetRoute1Branch42Power | Route 1 branch 42 power | 1路支路42功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 42 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.162 | hwDCEndCabinetRoute1Branch42SwitchStatus | Route 1 branch 42 switch status | 1路支路42开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 42 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.163 | hwDCEndCabinetRoute1Branch42LoadPercentage | Route 1 branch 42 load percentage | 1路支路42负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 42 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.164 | hwDCEndCabinetRoute1Branch42Electricity | Route 1 branch 42 electricity | 1路支路42电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 42 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.165 | hwDCEndCabinetRoute1Branch42PositiveInsulationResistance | Route 1 branch 42 positive insulation resistance | 1路支路42正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 42 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.166 | hwDCEndCabinetRoute1Branch42NegativeInsulationResistance | Route 1 branch 42 negative insulation resistance | 1路支路42负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 42 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.167 | hwDCEndCabinetRoute1Branch43Voltage | Route 1 branch 43 voltage | 1路支路43电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 43 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.168 | hwDCEndCabinetRoute1Branch43Current | Route 1 branch 43 current | 1路支路43电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 43 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.169 | hwDCEndCabinetRoute1Branch43Power | Route 1 branch 43 power | 1路支路43功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 43 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.170 | hwDCEndCabinetRoute1Branch43SwitchStatus | Route 1 branch 43 switch status | 1路支路43开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 43 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.171 | hwDCEndCabinetRoute1Branch43LoadPercentage | Route 1 branch 43 load percentage | 1路支路43负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 43 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.172 | hwDCEndCabinetRoute1Branch43Electricity | Route 1 branch 43 electricity | 1路支路43电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 43 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.173 | hwDCEndCabinetRoute1Branch43PositiveInsulationResistance | Route 1 branch 43 positive insulation resistance | 1路支路43正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 43 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.174 | hwDCEndCabinetRoute1Branch43NegativeInsulationResistance | Route 1 branch 43 negative insulation resistance | 1路支路43负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 43 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.175 | hwDCEndCabinetRoute1Branch44Voltage | Route 1 branch 44 voltage | 1路支路44电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 44 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.176 | hwDCEndCabinetRoute1Branch44Current | Route 1 branch 44 current | 1路支路44电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 44 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.177 | hwDCEndCabinetRoute1Branch44Power | Route 1 branch 44 power | 1路支路44功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 44 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.178 | hwDCEndCabinetRoute1Branch44SwitchStatus | Route 1 branch 44 switch status | 1路支路44开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 44 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.179 | hwDCEndCabinetRoute1Branch44LoadPercentage | Route 1 branch 44 load percentage | 1路支路44负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 44 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.180 | hwDCEndCabinetRoute1Branch44Electricity | Route 1 branch 44 electricity | 1路支路44电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 44 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.181 | hwDCEndCabinetRoute1Branch44PositiveInsulationResistance | Route 1 branch 44 positive insulation resistance | 1路支路44正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 44 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.182 | hwDCEndCabinetRoute1Branch44NegativeInsulationResistance | Route 1 branch 44 negative insulation resistance | 1路支路44负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 44 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.183 | hwDCEndCabinetRoute1Branch45Voltage | Route 1 branch 45 voltage | 1路支路45电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 45 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.184 | hwDCEndCabinetRoute1Branch45Current | Route 1 branch 45 current | 1路支路45电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 45 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.185 | hwDCEndCabinetRoute1Branch45Power | Route 1 branch 45 power | 1路支路45功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 45 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.186 | hwDCEndCabinetRoute1Branch45SwitchStatus | Route 1 branch 45 switch status | 1路支路45开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 45 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.187 | hwDCEndCabinetRoute1Branch45LoadPercentage | Route 1 branch 45 load percentage | 1路支路45负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 45 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.188 | hwDCEndCabinetRoute1Branch45Electricity | Route 1 branch 45 electricity | 1路支路45电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 45 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.189 | hwDCEndCabinetRoute1Branch45PositiveInsulationResistance | Route 1 branch 45 positive insulation resistance | 1路支路45正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 45 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.190 | hwDCEndCabinetRoute1Branch45NegativeInsulationResistance | Route 1 branch 45 negative insulation resistance | 1路支路45负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 45 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.191 | hwDCEndCabinetRoute1Branch46Voltage | Route 1 branch 46 voltage | 1路支路46电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 46 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.192 | hwDCEndCabinetRoute1Branch46Current | Route 1 branch 46 current | 1路支路46电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 46 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.193 | hwDCEndCabinetRoute1Branch46Power | Route 1 branch 46 power | 1路支路46功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 46 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.194 | hwDCEndCabinetRoute1Branch46SwitchStatus | Route 1 branch 46 switch status | 1路支路46开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 46 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.195 | hwDCEndCabinetRoute1Branch46LoadPercentage | Route 1 branch 46 load percentage | 1路支路46负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 46 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.196 | hwDCEndCabinetRoute1Branch46Electricity | Route 1 branch 46 electricity | 1路支路46电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 46 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.197 | hwDCEndCabinetRoute1Branch46PositiveInsulationResistance | Route 1 branch 46 positive insulation resistance | 1路支路46正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 46 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.198 | hwDCEndCabinetRoute1Branch46NegativeInsulationResistance | Route 1 branch 46 negative insulation resistance | 1路支路46负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 46 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.199 | hwDCEndCabinetRoute1Branch47Voltage | Route 1 branch 47 voltage | 1路支路47电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 47 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.200 | hwDCEndCabinetRoute1Branch47Current | Route 1 branch 47 current | 1路支路47电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 47 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.2.1.201 | hwDCEndCabinetRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3 | hwDCEndCabinetRunning3Table | / | / |  |  | / | / | The running table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.1 | hwDCEndCabinetRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.2 | hwDCEndCabinetRoute1Branch47Power | Route 1 branch 47 power | 1路支路47功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 47 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.3 | hwDCEndCabinetRoute1Branch47SwitchStatus | Route 1 branch 47 switch status | 1路支路47开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 47 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.4 | hwDCEndCabinetRoute1Branch47LoadPercentage | Route 1 branch 47 load percentage | 1路支路47负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 47 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.5 | hwDCEndCabinetRoute1Branch47Electricity | Route 1 branch 47 electricity | 1路支路47电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 47 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.6 | hwDCEndCabinetRoute1Branch47PositiveInsulationResistance | Route 1 branch 47 positive insulation resistance | 1路支路47正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 47 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.7 | hwDCEndCabinetRoute1Branch47NegativeInsulationResistance | Route 1 branch 47 negative insulation resistance | 1路支路47负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 47 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.8 | hwDCEndCabinetRoute1Branch48Voltage | Route 1 branch 48 voltage | 1路支路48电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 48 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.9 | hwDCEndCabinetRoute1Branch48Current | Route 1 branch 48 current | 1路支路48电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 48 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.10 | hwDCEndCabinetRoute1Branch48Power | Route 1 branch 48 power | 1路支路48功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 48 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.11 | hwDCEndCabinetRoute1Branch48SwitchStatus | Route 1 branch 48 switch status | 1路支路48开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 48 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.12 | hwDCEndCabinetRoute1Branch48LoadPercentage | Route 1 branch 48 load percentage | 1路支路48负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 48 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.13 | hwDCEndCabinetRoute1Branch48Electricity | Route 1 branch 48 electricity | 1路支路48电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 48 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.14 | hwDCEndCabinetRoute1Branch48PositiveInsulationResistance | Route 1 branch 48 positive insulation resistance | 1路支路48正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 48 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.15 | hwDCEndCabinetRoute1Branch48NegativeInsulationResistance | Route 1 branch 48 negative insulation resistance | 1路支路48负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 48 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.16 | hwDCEndCabinetRoute1Branch49Voltage | Route 1 branch 49 voltage | 1路支路49电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 49 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.17 | hwDCEndCabinetRoute1Branch49Current | Route 1 branch 49 current | 1路支路49电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 49 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.18 | hwDCEndCabinetRoute1Branch49Power | Route 1 branch 49 power | 1路支路49功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 49 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.19 | hwDCEndCabinetRoute1Branch49SwitchStatus | Route 1 branch 49 switch status | 1路支路49开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 49 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.20 | hwDCEndCabinetRoute1Branch49LoadPercentage | Route 1 branch 49 load percentage | 1路支路49负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 49 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.21 | hwDCEndCabinetRoute1Branch49Electricity | Route 1 branch 49 electricity | 1路支路49电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 49 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.22 | hwDCEndCabinetRoute1Branch49PositiveInsulationResistance | Route 1 branch 49 positive insulation resistance | 1路支路49正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 49 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.23 | hwDCEndCabinetRoute1Branch49NegativeInsulationResistance | Route 1 branch 49 negative insulation resistance | 1路支路49负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 49 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.24 | hwDCEndCabinetRoute1Branch50Voltage | Route 1 branch 50 voltage | 1路支路50电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 50 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.25 | hwDCEndCabinetRoute1Branch50Current | Route 1 branch 50 current | 1路支路50电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 50 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.26 | hwDCEndCabinetRoute1Branch50Power | Route 1 branch 50 power | 1路支路50功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 50 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.27 | hwDCEndCabinetRoute1Branch50SwitchStatus | Route 1 branch 50 switch status | 1路支路50开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 50 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.28 | hwDCEndCabinetRoute1Branch50LoadPercentage | Route 1 branch 50 load percentage | 1路支路50负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 50 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.29 | hwDCEndCabinetRoute1Branch50Electricity | Route 1 branch 50 electricity | 1路支路50电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 50 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.30 | hwDCEndCabinetRoute1Branch50PositiveInsulationResistance | Route 1 branch 50 positive insulation resistance | 1路支路50正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 50 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.31 | hwDCEndCabinetRoute1Branch50NegativeInsulationResistance | Route 1 branch 50 negative insulation resistance | 1路支路50负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 50 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.32 | hwDCEndCabinetRoute1Branch51Voltage | Route 1 branch 51 voltage | 1路支路51电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 51 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.33 | hwDCEndCabinetRoute1Branch51Current | Route 1 branch 51 current | 1路支路51电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 51 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.34 | hwDCEndCabinetRoute1Branch51Power | Route 1 branch 51 power | 1路支路51功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 51 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.35 | hwDCEndCabinetRoute1Branch51SwitchStatus | Route 1 branch 51 switch status | 1路支路51开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 51 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.36 | hwDCEndCabinetRoute1Branch51LoadPercentage | Route 1 branch 51 load percentage | 1路支路51负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 51 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.37 | hwDCEndCabinetRoute1Branch51Electricity | Route 1 branch 51 electricity | 1路支路51电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 51 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.38 | hwDCEndCabinetRoute1Branch51PositiveInsulationResistance | Route 1 branch 51 positive insulation resistance | 1路支路51正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 51 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.39 | hwDCEndCabinetRoute1Branch51NegativeInsulationResistance | Route 1 branch 51 negative insulation resistance | 1路支路51负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 51 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.40 | hwDCEndCabinetRoute1Branch52Voltage | Route 1 branch 52 voltage | 1路支路52电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 52 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.41 | hwDCEndCabinetRoute1Branch52Current | Route 1 branch 52 current | 1路支路52电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 52 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.42 | hwDCEndCabinetRoute1Branch52Power | Route 1 branch 52 power | 1路支路52功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 52 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.43 | hwDCEndCabinetRoute1Branch52SwitchStatus | Route 1 branch 52 switch status | 1路支路52开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 52 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.44 | hwDCEndCabinetRoute1Branch52LoadPercentage | Route 1 branch 52 load percentage | 1路支路52负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 52 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.45 | hwDCEndCabinetRoute1Branch52Electricity | Route 1 branch 52 electricity | 1路支路52电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 52 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.46 | hwDCEndCabinetRoute1Branch52PositiveInsulationResistance | Route 1 branch 52 positive insulation resistance | 1路支路52正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 52 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.47 | hwDCEndCabinetRoute1Branch52NegativeInsulationResistance | Route 1 branch 52 negative insulation resistance | 1路支路52负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 52 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.48 | hwDCEndCabinetRoute1Branch53Voltage | Route 1 branch 53 voltage | 1路支路53电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 53 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.49 | hwDCEndCabinetRoute1Branch53Current | Route 1 branch 53 current | 1路支路53电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 53 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.50 | hwDCEndCabinetRoute1Branch53Power | Route 1 branch 53 power | 1路支路53功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 53 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.51 | hwDCEndCabinetRoute1Branch53SwitchStatus | Route 1 branch 53 switch status | 1路支路53开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 53 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.52 | hwDCEndCabinetRoute1Branch53LoadPercentage | Route 1 branch 53 load percentage | 1路支路53负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 53 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.53 | hwDCEndCabinetRoute1Branch53Electricity | Route 1 branch 53 electricity | 1路支路53电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 53 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.54 | hwDCEndCabinetRoute1Branch53PositiveInsulationResistance | Route 1 branch 53 positive insulation resistance | 1路支路53正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 53 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.55 | hwDCEndCabinetRoute1Branch53NegativeInsulationResistance | Route 1 branch 53 negative insulation resistance | 1路支路53负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 53 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.56 | hwDCEndCabinetRoute1Branch54Voltage | Route 1 branch 54 voltage | 1路支路54电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 54 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.57 | hwDCEndCabinetRoute1Branch54Current | Route 1 branch 54 current | 1路支路54电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 54 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.58 | hwDCEndCabinetRoute1Branch54Power | Route 1 branch 54 power | 1路支路54功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 54 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.59 | hwDCEndCabinetRoute1Branch54SwitchStatus | Route 1 branch 54 switch status | 1路支路54开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 54 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.60 | hwDCEndCabinetRoute1Branch54LoadPercentage | Route 1 branch 54 load percentage | 1路支路54负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 54 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.61 | hwDCEndCabinetRoute1Branch54Electricity | Route 1 branch 54 electricity | 1路支路54电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 54 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.62 | hwDCEndCabinetRoute1Branch54PositiveInsulationResistance | Route 1 branch 54 positive insulation resistance | 1路支路54正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 54 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.63 | hwDCEndCabinetRoute1Branch54NegativeInsulationResistance | Route 1 branch 54 negative insulation resistance | 1路支路54负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 54 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.64 | hwDCEndCabinetRoute1Branch55Voltage | Route 1 branch 55 voltage | 1路支路55电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 55 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.65 | hwDCEndCabinetRoute1Branch55Current | Route 1 branch 55 current | 1路支路55电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 55 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.66 | hwDCEndCabinetRoute1Branch55Power | Route 1 branch 55 power | 1路支路55功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 55 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.67 | hwDCEndCabinetRoute1Branch55SwitchStatus | Route 1 branch 55 switch status | 1路支路55开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 55 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.68 | hwDCEndCabinetRoute1Branch55LoadPercentage | Route 1 branch 55 load percentage | 1路支路55负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 55 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.69 | hwDCEndCabinetRoute1Branch55Electricity | Route 1 branch 55 electricity | 1路支路55电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 55 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.70 | hwDCEndCabinetRoute1Branch55PositiveInsulationResistance | Route 1 branch 55 positive insulation resistance | 1路支路55正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 55 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.71 | hwDCEndCabinetRoute1Branch55NegativeInsulationResistance | Route 1 branch 55 negative insulation resistance | 1路支路55负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 55 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.72 | hwDCEndCabinetRoute1Branch56Voltage | Route 1 branch 56 voltage | 1路支路56电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 56 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.73 | hwDCEndCabinetRoute1Branch56Current | Route 1 branch 56 current | 1路支路56电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 56 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.74 | hwDCEndCabinetRoute1Branch56Power | Route 1 branch 56 power | 1路支路56功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 56 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.75 | hwDCEndCabinetRoute1Branch56SwitchStatus | Route 1 branch 56 switch status | 1路支路56开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 56 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.76 | hwDCEndCabinetRoute1Branch56LoadPercentage | Route 1 branch 56 load percentage | 1路支路56负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 56 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.77 | hwDCEndCabinetRoute1Branch56Electricity | Route 1 branch 56 electricity | 1路支路56电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 56 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.78 | hwDCEndCabinetRoute1Branch56PositiveInsulationResistance | Route 1 branch 56 positive insulation resistance | 1路支路56正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 56 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.79 | hwDCEndCabinetRoute1Branch56NegativeInsulationResistance | Route 1 branch 56 negative insulation resistance | 1路支路56负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 56 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.80 | hwDCEndCabinetRoute1Branch57Voltage | Route 1 branch 57 voltage | 1路支路57电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 57 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.81 | hwDCEndCabinetRoute1Branch57Current | Route 1 branch 57 current | 1路支路57电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 57 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.82 | hwDCEndCabinetRoute1Branch57Power | Route 1 branch 57 power | 1路支路57功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 57 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.83 | hwDCEndCabinetRoute1Branch57SwitchStatus | Route 1 branch 57 switch status | 1路支路57开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 57 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.84 | hwDCEndCabinetRoute1Branch57LoadPercentage | Route 1 branch 57 load percentage | 1路支路57负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 57 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.85 | hwDCEndCabinetRoute1Branch57Electricity | Route 1 branch 57 electricity | 1路支路57电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 57 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.86 | hwDCEndCabinetRoute1Branch57PositiveInsulationResistance | Route 1 branch 57 positive insulation resistance | 1路支路57正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 57 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.87 | hwDCEndCabinetRoute1Branch57NegativeInsulationResistance | Route 1 branch 57 negative insulation resistance | 1路支路57负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 57 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.88 | hwDCEndCabinetRoute1Branch58Voltage | Route 1 branch 58 voltage | 1路支路58电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 58 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.89 | hwDCEndCabinetRoute1Branch58Current | Route 1 branch 58 current | 1路支路58电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 58 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.90 | hwDCEndCabinetRoute1Branch58Power | Route 1 branch 58 power | 1路支路58功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 58 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.91 | hwDCEndCabinetRoute1Branch58SwitchStatus | Route 1 branch 58 switch status | 1路支路58开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 58 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.92 | hwDCEndCabinetRoute1Branch58LoadPercentage | Route 1 branch 58 load percentage | 1路支路58负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 58 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.93 | hwDCEndCabinetRoute1Branch58Electricity | Route 1 branch 58 electricity | 1路支路58电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 58 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.94 | hwDCEndCabinetRoute1Branch58PositiveInsulationResistance | Route 1 branch 58 positive insulation resistance | 1路支路58正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 58 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.95 | hwDCEndCabinetRoute1Branch58NegativeInsulationResistance | Route 1 branch 58 negative insulation resistance | 1路支路58负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 58 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.96 | hwDCEndCabinetRoute1Branch59Voltage | Route 1 branch 59 voltage | 1路支路59电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 59 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.97 | hwDCEndCabinetRoute1Branch59Current | Route 1 branch 59 current | 1路支路59电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 59 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.98 | hwDCEndCabinetRoute1Branch59Power | Route 1 branch 59 power | 1路支路59功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 59 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.99 | hwDCEndCabinetRoute1Branch59SwitchStatus | Route 1 branch 59 switch status | 1路支路59开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 59 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.100 | hwDCEndCabinetRoute1Branch59LoadPercentage | Route 1 branch 59 load percentage | 1路支路59负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 59 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.101 | hwDCEndCabinetRoute1Branch59Electricity | Route 1 branch 59 electricity | 1路支路59电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 59 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.102 | hwDCEndCabinetRoute1Branch59PositiveInsulationResistance | Route 1 branch 59 positive insulation resistance | 1路支路59正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 59 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.103 | hwDCEndCabinetRoute1Branch59NegativeInsulationResistance | Route 1 branch 59 negative insulation resistance | 1路支路59负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 59 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.104 | hwDCEndCabinetRoute1Branch60Voltage | Route 1 branch 60 voltage | 1路支路60电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 60 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.105 | hwDCEndCabinetRoute1Branch60Current | Route 1 branch 60 current | 1路支路60电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 60 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.106 | hwDCEndCabinetRoute1Branch60Power | Route 1 branch 60 power | 1路支路60功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 60 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.107 | hwDCEndCabinetRoute1Branch60SwitchStatus | Route 1 branch 60 switch status | 1路支路60开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 60 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.108 | hwDCEndCabinetRoute1Branch60LoadPercentage | Route 1 branch 60 load percentage | 1路支路60负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 60 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.109 | hwDCEndCabinetRoute1Branch60Electricity | Route 1 branch 60 electricity | 1路支路60电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 60 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.110 | hwDCEndCabinetRoute1Branch60PositiveInsulationResistance | Route 1 branch 60 positive insulation resistance | 1路支路60正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 60 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.111 | hwDCEndCabinetRoute1Branch60NegativeInsulationResistance | Route 1 branch 60 negative insulation resistance | 1路支路60负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 60 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.112 | hwDCEndCabinetRoute1Branch61Voltage | Route 1 branch 61 voltage | 1路支路61电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 61 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.113 | hwDCEndCabinetRoute1Branch61Current | Route 1 branch 61 current | 1路支路61电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 61 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.114 | hwDCEndCabinetRoute1Branch61Power | Route 1 branch 61 power | 1路支路61功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 61 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.115 | hwDCEndCabinetRoute1Branch61SwitchStatus | Route 1 branch 61 switch status | 1路支路61开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 61 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.116 | hwDCEndCabinetRoute1Branch61LoadPercentage | Route 1 branch 61 load percentage | 1路支路61负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 61 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.117 | hwDCEndCabinetRoute1Branch61Electricity | Route 1 branch 61 electricity | 1路支路61电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 61 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.118 | hwDCEndCabinetRoute1Branch61PositiveInsulationResistance | Route 1 branch 61 positive insulation resistance | 1路支路61正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 61 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.119 | hwDCEndCabinetRoute1Branch61NegativeInsulationResistance | Route 1 branch 61 negative insulation resistance | 1路支路61负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 61 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.120 | hwDCEndCabinetRoute1Branch62Voltage | Route 1 branch 62 voltage | 1路支路62电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 62 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.121 | hwDCEndCabinetRoute1Branch62Current | Route 1 branch 62 current | 1路支路62电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 62 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.122 | hwDCEndCabinetRoute1Branch62Power | Route 1 branch 62 power | 1路支路62功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 62 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.123 | hwDCEndCabinetRoute1Branch62SwitchStatus | Route 1 branch 62 switch status | 1路支路62开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 62 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.124 | hwDCEndCabinetRoute1Branch62LoadPercentage | Route 1 branch 62 load percentage | 1路支路62负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 62 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.125 | hwDCEndCabinetRoute1Branch62Electricity | Route 1 branch 62 electricity | 1路支路62电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 62 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.126 | hwDCEndCabinetRoute1Branch62PositiveInsulationResistance | Route 1 branch 62 positive insulation resistance | 1路支路62正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 62 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.127 | hwDCEndCabinetRoute1Branch62NegativeInsulationResistance | Route 1 branch 62 negative insulation resistance | 1路支路62负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 62 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.128 | hwDCEndCabinetRoute1Branch63Voltage | Route 1 branch 63 voltage | 1路支路63电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 63 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.129 | hwDCEndCabinetRoute1Branch63Current | Route 1 branch 63 current | 1路支路63电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 63 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.130 | hwDCEndCabinetRoute1Branch63Power | Route 1 branch 63 power | 1路支路63功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 63 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.131 | hwDCEndCabinetRoute1Branch63SwitchStatus | Route 1 branch 63 switch status | 1路支路63开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 63 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.132 | hwDCEndCabinetRoute1Branch63LoadPercentage | Route 1 branch 63 load percentage | 1路支路63负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 63 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.133 | hwDCEndCabinetRoute1Branch63Electricity | Route 1 branch 63 electricity | 1路支路63电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 63 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.134 | hwDCEndCabinetRoute1Branch63PositiveInsulationResistance | Route 1 branch 63 positive insulation resistance | 1路支路63正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 63 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.135 | hwDCEndCabinetRoute1Branch63NegativeInsulationResistance | Route 1 branch 63 negative insulation resistance | 1路支路63负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 63 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.136 | hwDCEndCabinetRoute1Branch64Voltage | Route 1 branch 64 voltage | 1路支路64电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 64 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.137 | hwDCEndCabinetRoute1Branch64Current | Route 1 branch 64 current | 1路支路64电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 64 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.138 | hwDCEndCabinetRoute1Branch64Power | Route 1 branch 64 power | 1路支路64功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 64 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.139 | hwDCEndCabinetRoute1Branch64SwitchStatus | Route 1 branch 64 switch status | 1路支路64开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 64 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.140 | hwDCEndCabinetRoute1Branch64LoadPercentage | Route 1 branch 64 load percentage | 1路支路64负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 64 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.141 | hwDCEndCabinetRoute1Branch64Electricity | Route 1 branch 64 electricity | 1路支路64电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 64 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.142 | hwDCEndCabinetRoute1Branch64PositiveInsulationResistance | Route 1 branch 64 positive insulation resistance | 1路支路64正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 64 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.143 | hwDCEndCabinetRoute1Branch64NegativeInsulationResistance | Route 1 branch 64 negative insulation resistance | 1路支路64负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 64 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.144 | hwDCEndCabinetRoute1Branch65Voltage | Route 1 branch 65 voltage | 1路支路65电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 65 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.145 | hwDCEndCabinetRoute1Branch65Current | Route 1 branch 65 current | 1路支路65电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 65 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.146 | hwDCEndCabinetRoute1Branch65Power | Route 1 branch 65 power | 1路支路65功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 65 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.147 | hwDCEndCabinetRoute1Branch65SwitchStatus | Route 1 branch 65 switch status | 1路支路65开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 65 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.148 | hwDCEndCabinetRoute1Branch65LoadPercentage | Route 1 branch 65 load percentage | 1路支路65负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 65 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.149 | hwDCEndCabinetRoute1Branch65Electricity | Route 1 branch 65 electricity | 1路支路65电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 65 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.150 | hwDCEndCabinetRoute1Branch65PositiveInsulationResistance | Route 1 branch 65 positive insulation resistance | 1路支路65正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 65 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.151 | hwDCEndCabinetRoute1Branch65NegativeInsulationResistance | Route 1 branch 65 negative insulation resistance | 1路支路65负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 65 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.152 | hwDCEndCabinetRoute1Branch66Voltage | Route 1 branch 66 voltage | 1路支路66电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 66 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.153 | hwDCEndCabinetRoute1Branch66Current | Route 1 branch 66 current | 1路支路66电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 66 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.154 | hwDCEndCabinetRoute1Branch66Power | Route 1 branch 66 power | 1路支路66功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 66 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.155 | hwDCEndCabinetRoute1Branch66SwitchStatus | Route 1 branch 66 switch status | 1路支路66开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 66 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.156 | hwDCEndCabinetRoute1Branch66LoadPercentage | Route 1 branch 66 load percentage | 1路支路66负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 66 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.157 | hwDCEndCabinetRoute1Branch66Electricity | Route 1 branch 66 electricity | 1路支路66电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 66 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.158 | hwDCEndCabinetRoute1Branch66PositiveInsulationResistance | Route 1 branch 66 positive insulation resistance | 1路支路66正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 66 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.159 | hwDCEndCabinetRoute1Branch66NegativeInsulationResistance | Route 1 branch 66 negative insulation resistance | 1路支路66负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 66 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.160 | hwDCEndCabinetRoute1Branch67Voltage | Route 1 branch 67 voltage | 1路支路67电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 67 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.161 | hwDCEndCabinetRoute1Branch67Current | Route 1 branch 67 current | 1路支路67电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 67 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.162 | hwDCEndCabinetRoute1Branch67Power | Route 1 branch 67 power | 1路支路67功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 67 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.163 | hwDCEndCabinetRoute1Branch67SwitchStatus | Route 1 branch 67 switch status | 1路支路67开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 67 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.164 | hwDCEndCabinetRoute1Branch67LoadPercentage | Route 1 branch 67 load percentage | 1路支路67负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 67 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.165 | hwDCEndCabinetRoute1Branch67Electricity | Route 1 branch 67 electricity | 1路支路67电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 67 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.166 | hwDCEndCabinetRoute1Branch67PositiveInsulationResistance | Route 1 branch 67 positive insulation resistance | 1路支路67正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 67 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.167 | hwDCEndCabinetRoute1Branch67NegativeInsulationResistance | Route 1 branch 67 negative insulation resistance | 1路支路67负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 67 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.168 | hwDCEndCabinetRoute1Branch68Voltage | Route 1 branch 68 voltage | 1路支路68电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 68 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.169 | hwDCEndCabinetRoute1Branch68Current | Route 1 branch 68 current | 1路支路68电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 68 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.170 | hwDCEndCabinetRoute1Branch68Power | Route 1 branch 68 power | 1路支路68功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 68 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.171 | hwDCEndCabinetRoute1Branch68SwitchStatus | Route 1 branch 68 switch status | 1路支路68开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 68 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.172 | hwDCEndCabinetRoute1Branch68LoadPercentage | Route 1 branch 68 load percentage | 1路支路68负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 68 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.173 | hwDCEndCabinetRoute1Branch68Electricity | Route 1 branch 68 electricity | 1路支路68电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 68 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.174 | hwDCEndCabinetRoute1Branch68PositiveInsulationResistance | Route 1 branch 68 positive insulation resistance | 1路支路68正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 68 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.175 | hwDCEndCabinetRoute1Branch68NegativeInsulationResistance | Route 1 branch 68 negative insulation resistance | 1路支路68负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 68 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.176 | hwDCEndCabinetRoute1Branch69Voltage | Route 1 branch 69 voltage | 1路支路69电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 69 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.177 | hwDCEndCabinetRoute1Branch69Current | Route 1 branch 69 current | 1路支路69电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 69 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.178 | hwDCEndCabinetRoute1Branch69Power | Route 1 branch 69 power | 1路支路69功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 69 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.179 | hwDCEndCabinetRoute1Branch69SwitchStatus | Route 1 branch 69 switch status | 1路支路69开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 69 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.180 | hwDCEndCabinetRoute1Branch69LoadPercentage | Route 1 branch 69 load percentage | 1路支路69负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 69 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.181 | hwDCEndCabinetRoute1Branch69Electricity | Route 1 branch 69 electricity | 1路支路69电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 69 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.182 | hwDCEndCabinetRoute1Branch69PositiveInsulationResistance | Route 1 branch 69 positive insulation resistance | 1路支路69正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 69 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.183 | hwDCEndCabinetRoute1Branch69NegativeInsulationResistance | Route 1 branch 69 negative insulation resistance | 1路支路69负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 69 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.184 | hwDCEndCabinetRoute1Branch70Voltage | Route 1 branch 70 voltage | 1路支路70电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 70 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.185 | hwDCEndCabinetRoute1Branch70Current | Route 1 branch 70 current | 1路支路70电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 70 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.186 | hwDCEndCabinetRoute1Branch70Power | Route 1 branch 70 power | 1路支路70功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 70 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.187 | hwDCEndCabinetRoute1Branch70SwitchStatus | Route 1 branch 70 switch status | 1路支路70开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 70 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.188 | hwDCEndCabinetRoute1Branch70LoadPercentage | Route 1 branch 70 load percentage | 1路支路70负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 70 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.189 | hwDCEndCabinetRoute1Branch70Electricity | Route 1 branch 70 electricity | 1路支路70电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 70 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.190 | hwDCEndCabinetRoute1Branch70PositiveInsulationResistance | Route 1 branch 70 positive insulation resistance | 1路支路70正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 70 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.191 | hwDCEndCabinetRoute1Branch70NegativeInsulationResistance | Route 1 branch 70 negative insulation resistance | 1路支路70负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 70 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.192 | hwDCEndCabinetRoute1Branch71Voltage | Route 1 branch 71 voltage | 1路支路71电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 71 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.193 | hwDCEndCabinetRoute1Branch71Current | Route 1 branch 71 current | 1路支路71电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 71 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.194 | hwDCEndCabinetRoute1Branch71Power | Route 1 branch 71 power | 1路支路71功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 71 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.195 | hwDCEndCabinetRoute1Branch71SwitchStatus | Route 1 branch 71 switch status | 1路支路71开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 71 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.196 | hwDCEndCabinetRoute1Branch71LoadPercentage | Route 1 branch 71 load percentage | 1路支路71负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 71 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.197 | hwDCEndCabinetRoute1Branch71Electricity | Route 1 branch 71 electricity | 1路支路71电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 71 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.198 | hwDCEndCabinetRoute1Branch71PositiveInsulationResistance | Route 1 branch 71 positive insulation resistance | 1路支路71正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 71 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.199 | hwDCEndCabinetRoute1Branch71NegativeInsulationResistance | Route 1 branch 71 negative insulation resistance | 1路支路71负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 71 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.200 | hwDCEndCabinetRoute1Branch72Voltage | Route 1 branch 72 voltage | 1路支路72电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 72 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.3.1.201 | hwDCEndCabinetRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4 | hwDCEndCabinetRunning4Table | / | / |  |  | / | / | The running table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.1 | hwDCEndCabinetRunning4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.2 | hwDCEndCabinetRoute1Branch72Current | Route 1 branch 72 current | 1路支路72电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 72 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.3 | hwDCEndCabinetRoute1Branch72Power | Route 1 branch 72 power | 1路支路72功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 72 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.4 | hwDCEndCabinetRoute1Branch72SwitchStatus | Route 1 branch 72 switch status | 1路支路72开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 72 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.5 | hwDCEndCabinetRoute1Branch72LoadPercentage | Route 1 branch 72 load percentage | 1路支路72负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 72 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.6 | hwDCEndCabinetRoute1Branch72Electricity | Route 1 branch 72 electricity | 1路支路72电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 72 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.7 | hwDCEndCabinetRoute1Branch72PositiveInsulationResistance | Route 1 branch 72 positive insulation resistance | 1路支路72正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 72 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.8 | hwDCEndCabinetRoute1Branch72NegativeInsulationResistance | Route 1 branch 72 negative insulation resistance | 1路支路72负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 72 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.9 | hwDCEndCabinetRoute1Branch73Voltage | Route 1 branch 73 voltage | 1路支路73电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 73 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.10 | hwDCEndCabinetRoute1Branch73Current | Route 1 branch 73 current | 1路支路73电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 73 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.11 | hwDCEndCabinetRoute1Branch73Power | Route 1 branch 73 power | 1路支路73功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 73 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.12 | hwDCEndCabinetRoute1Branch73SwitchStatus | Route 1 branch 73 switch status | 1路支路73开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 73 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.13 | hwDCEndCabinetRoute1Branch73LoadPercentage | Route 1 branch 73 load percentage | 1路支路73负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 73 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.14 | hwDCEndCabinetRoute1Branch73Electricity | Route 1 branch 73 electricity | 1路支路73电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 73 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.15 | hwDCEndCabinetRoute1Branch73PositiveInsulationResistance | Route 1 branch 73 positive insulation resistance | 1路支路73正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 73 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.16 | hwDCEndCabinetRoute1Branch73NegativeInsulationResistance | Route 1 branch 73 negative insulation resistance | 1路支路73负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 73 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.17 | hwDCEndCabinetRoute1Branch74Voltage | Route 1 branch 74 voltage | 1路支路74电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 74 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.18 | hwDCEndCabinetRoute1Branch74Current | Route 1 branch 74 current | 1路支路74电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 74 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.19 | hwDCEndCabinetRoute1Branch74Power | Route 1 branch 74 power | 1路支路74功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 74 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.20 | hwDCEndCabinetRoute1Branch74SwitchStatus | Route 1 branch 74 switch status | 1路支路74开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 74 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.21 | hwDCEndCabinetRoute1Branch74LoadPercentage | Route 1 branch 74 load percentage | 1路支路74负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 74 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.22 | hwDCEndCabinetRoute1Branch74Electricity | Route 1 branch 74 electricity | 1路支路74电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 74 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.23 | hwDCEndCabinetRoute1Branch74PositiveInsulationResistance | Route 1 branch 74 positive insulation resistance | 1路支路74正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 74 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.24 | hwDCEndCabinetRoute1Branch74NegativeInsulationResistance | Route 1 branch 74 negative insulation resistance | 1路支路74负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 74 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.25 | hwDCEndCabinetRoute1Branch75Voltage | Route 1 branch 75 voltage | 1路支路75电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 75 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.26 | hwDCEndCabinetRoute1Branch75Current | Route 1 branch 75 current | 1路支路75电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 75 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.27 | hwDCEndCabinetRoute1Branch75Power | Route 1 branch 75 power | 1路支路75功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 75 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.28 | hwDCEndCabinetRoute1Branch75SwitchStatus | Route 1 branch 75 switch status | 1路支路75开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 75 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.29 | hwDCEndCabinetRoute1Branch75LoadPercentage | Route 1 branch 75 load percentage | 1路支路75负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 75 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.30 | hwDCEndCabinetRoute1Branch75Electricity | Route 1 branch 75 electricity | 1路支路75电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 75 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.31 | hwDCEndCabinetRoute1Branch75PositiveInsulationResistance | Route 1 branch 75 positive insulation resistance | 1路支路75正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 75 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.32 | hwDCEndCabinetRoute1Branch75NegativeInsulationResistance | Route 1 branch 75 negative insulation resistance | 1路支路75负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 75 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.33 | hwDCEndCabinetRoute1Branch76Voltage | Route 1 branch 76 voltage | 1路支路76电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 76 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.34 | hwDCEndCabinetRoute1Branch76Current | Route 1 branch 76 current | 1路支路76电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 76 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.35 | hwDCEndCabinetRoute1Branch76Power | Route 1 branch 76 power | 1路支路76功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 76 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.36 | hwDCEndCabinetRoute1Branch76SwitchStatus | Route 1 branch 76 switch status | 1路支路76开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 76 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.37 | hwDCEndCabinetRoute1Branch76LoadPercentage | Route 1 branch 76 load percentage | 1路支路76负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 76 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.38 | hwDCEndCabinetRoute1Branch76Electricity | Route 1 branch 76 electricity | 1路支路76电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 76 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.39 | hwDCEndCabinetRoute1Branch76PositiveInsulationResistance | Route 1 branch 76 positive insulation resistance | 1路支路76正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 76 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.40 | hwDCEndCabinetRoute1Branch76NegativeInsulationResistance | Route 1 branch 76 negative insulation resistance | 1路支路76负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 76 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.41 | hwDCEndCabinetRoute1Branch77Voltage | Route 1 branch 77 voltage | 1路支路77电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 77 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.42 | hwDCEndCabinetRoute1Branch77Current | Route 1 branch 77 current | 1路支路77电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 77 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.43 | hwDCEndCabinetRoute1Branch77Power | Route 1 branch 77 power | 1路支路77功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 77 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.44 | hwDCEndCabinetRoute1Branch77SwitchStatus | Route 1 branch 77 switch status | 1路支路77开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 77 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.45 | hwDCEndCabinetRoute1Branch77LoadPercentage | Route 1 branch 77 load percentage | 1路支路77负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 77 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.46 | hwDCEndCabinetRoute1Branch77Electricity | Route 1 branch 77 electricity | 1路支路77电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 77 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.47 | hwDCEndCabinetRoute1Branch77PositiveInsulationResistance | Route 1 branch 77 positive insulation resistance | 1路支路77正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 77 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.48 | hwDCEndCabinetRoute1Branch77NegativeInsulationResistance | Route 1 branch 77 negative insulation resistance | 1路支路77负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 77 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.49 | hwDCEndCabinetRoute1Branch78Voltage | Route 1 branch 78 voltage | 1路支路78电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 78 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.50 | hwDCEndCabinetRoute1Branch78Current | Route 1 branch 78 current | 1路支路78电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 78 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.51 | hwDCEndCabinetRoute1Branch78Power | Route 1 branch 78 power | 1路支路78功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 78 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.52 | hwDCEndCabinetRoute1Branch78SwitchStatus | Route 1 branch 78 switch status | 1路支路78开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 78 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.53 | hwDCEndCabinetRoute1Branch78LoadPercentage | Route 1 branch 78 load percentage | 1路支路78负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 78 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.54 | hwDCEndCabinetRoute1Branch78Electricity | Route 1 branch 78 electricity | 1路支路78电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 78 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.55 | hwDCEndCabinetRoute1Branch78PositiveInsulationResistance | Route 1 branch 78 positive insulation resistance | 1路支路78正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 78 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.56 | hwDCEndCabinetRoute1Branch78NegativeInsulationResistance | Route 1 branch 78 negative insulation resistance | 1路支路78负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 78 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.57 | hwDCEndCabinetRoute1Branch79Voltage | Route 1 branch 79 voltage | 1路支路79电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 79 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.58 | hwDCEndCabinetRoute1Branch79Current | Route 1 branch 79 current | 1路支路79电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 79 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.59 | hwDCEndCabinetRoute1Branch79Power | Route 1 branch 79 power | 1路支路79功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 79 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.60 | hwDCEndCabinetRoute1Branch79SwitchStatus | Route 1 branch 79 switch status | 1路支路79开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 79 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.61 | hwDCEndCabinetRoute1Branch79LoadPercentage | Route 1 branch 79 load percentage | 1路支路79负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 79 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.62 | hwDCEndCabinetRoute1Branch79Electricity | Route 1 branch 79 electricity | 1路支路79电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 79 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.63 | hwDCEndCabinetRoute1Branch79PositiveInsulationResistance | Route 1 branch 79 positive insulation resistance | 1路支路79正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 79 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.64 | hwDCEndCabinetRoute1Branch79NegativeInsulationResistance | Route 1 branch 79 negative insulation resistance | 1路支路79负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 79 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.65 | hwDCEndCabinetRoute1Branch80Voltage | Route 1 branch 80 voltage | 1路支路80电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 80 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.66 | hwDCEndCabinetRoute1Branch80Current | Route 1 branch 80 current | 1路支路80电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 80 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.67 | hwDCEndCabinetRoute1Branch80Power | Route 1 branch 80 power | 1路支路80功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 80 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.68 | hwDCEndCabinetRoute1Branch80SwitchStatus | Route 1 branch 80 switch status | 1路支路80开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 80 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.69 | hwDCEndCabinetRoute1Branch80LoadPercentage | Route 1 branch 80 load percentage | 1路支路80负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 80 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.70 | hwDCEndCabinetRoute1Branch80Electricity | Route 1 branch 80 electricity | 1路支路80电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 80 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.71 | hwDCEndCabinetRoute1Branch80PositiveInsulationResistance | Route 1 branch 80 positive insulation resistance | 1路支路80正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 80 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.72 | hwDCEndCabinetRoute1Branch80NegativeInsulationResistance | Route 1 branch 80 negative insulation resistance | 1路支路80负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 80 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.73 | hwDCEndCabinetRoute1Branch81Voltage | Route 1 branch 81 voltage | 1路支路81电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 81 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.74 | hwDCEndCabinetRoute1Branch81Current | Route 1 branch 81 current | 1路支路81电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 81 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.75 | hwDCEndCabinetRoute1Branch81Power | Route 1 branch 81 power | 1路支路81功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 81 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.76 | hwDCEndCabinetRoute1Branch81SwitchStatus | Route 1 branch 81 switch status | 1路支路81开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 81 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.77 | hwDCEndCabinetRoute1Branch81LoadPercentage | Route 1 branch 81 load percentage | 1路支路81负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 81 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.78 | hwDCEndCabinetRoute1Branch81Electricity | Route 1 branch 81 electricity | 1路支路81电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 81 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.79 | hwDCEndCabinetRoute1Branch81PositiveInsulationResistance | Route 1 branch 81 positive insulation resistance | 1路支路81正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 81 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.80 | hwDCEndCabinetRoute1Branch81NegativeInsulationResistance | Route 1 branch 81 negative insulation resistance | 1路支路81负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 81 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.81 | hwDCEndCabinetRoute1Branch82Voltage | Route 1 branch 82 voltage | 1路支路82电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 82 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.82 | hwDCEndCabinetRoute1Branch82Current | Route 1 branch 82 current | 1路支路82电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 82 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.83 | hwDCEndCabinetRoute1Branch82Power | Route 1 branch 82 power | 1路支路82功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 82 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.84 | hwDCEndCabinetRoute1Branch82SwitchStatus | Route 1 branch 82 switch status | 1路支路82开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 82 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.85 | hwDCEndCabinetRoute1Branch82LoadPercentage | Route 1 branch 82 load percentage | 1路支路82负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 82 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.86 | hwDCEndCabinetRoute1Branch82Electricity | Route 1 branch 82 electricity | 1路支路82电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 82 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.87 | hwDCEndCabinetRoute1Branch82PositiveInsulationResistance | Route 1 branch 82 positive insulation resistance | 1路支路82正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 82 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.88 | hwDCEndCabinetRoute1Branch82NegativeInsulationResistance | Route 1 branch 82 negative insulation resistance | 1路支路82负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 82 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.89 | hwDCEndCabinetRoute1Branch83Voltage | Route 1 branch 83 voltage | 1路支路83电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 83 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.90 | hwDCEndCabinetRoute1Branch83Current | Route 1 branch 83 current | 1路支路83电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 83 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.91 | hwDCEndCabinetRoute1Branch83Power | Route 1 branch 83 power | 1路支路83功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 83 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.92 | hwDCEndCabinetRoute1Branch83SwitchStatus | Route 1 branch 83 switch status | 1路支路83开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 83 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.93 | hwDCEndCabinetRoute1Branch83LoadPercentage | Route 1 branch 83 load percentage | 1路支路83负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 83 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.94 | hwDCEndCabinetRoute1Branch83Electricity | Route 1 branch 83 electricity | 1路支路83电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 83 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.95 | hwDCEndCabinetRoute1Branch83PositiveInsulationResistance | Route 1 branch 83 positive insulation resistance | 1路支路83正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 83 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.96 | hwDCEndCabinetRoute1Branch83NegativeInsulationResistance | Route 1 branch 83 negative insulation resistance | 1路支路83负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 83 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.97 | hwDCEndCabinetRoute1Branch84Voltage | Route 1 branch 84 voltage | 1路支路84电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 84 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.98 | hwDCEndCabinetRoute1Branch84Current | Route 1 branch 84 current | 1路支路84电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 84 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.99 | hwDCEndCabinetRoute1Branch84Power | Route 1 branch 84 power | 1路支路84功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 84 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.100 | hwDCEndCabinetRoute1Branch84SwitchStatus | Route 1 branch 84 switch status | 1路支路84开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 84 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.101 | hwDCEndCabinetRoute1Branch84LoadPercentage | Route 1 branch 84 load percentage | 1路支路84负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 84 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.102 | hwDCEndCabinetRoute1Branch84Electricity | Route 1 branch 84 electricity | 1路支路84电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 84 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.103 | hwDCEndCabinetRoute1Branch84PositiveInsulationResistance | Route 1 branch 84 positive insulation resistance | 1路支路84正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 84 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.104 | hwDCEndCabinetRoute1Branch84NegativeInsulationResistance | Route 1 branch 84 negative insulation resistance | 1路支路84负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 84 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.105 | hwDCEndCabinetRoute1Branch85Voltage | Route 1 branch 85 voltage | 1路支路85电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 85 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.106 | hwDCEndCabinetRoute1Branch85Current | Route 1 branch 85 current | 1路支路85电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 85 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.107 | hwDCEndCabinetRoute1Branch85Power | Route 1 branch 85 power | 1路支路85功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 85 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.108 | hwDCEndCabinetRoute1Branch85SwitchStatus | Route 1 branch 85 switch status | 1路支路85开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 85 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.109 | hwDCEndCabinetRoute1Branch85LoadPercentage | Route 1 branch 85 load percentage | 1路支路85负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 85 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.110 | hwDCEndCabinetRoute1Branch85Electricity | Route 1 branch 85 electricity | 1路支路85电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 85 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.111 | hwDCEndCabinetRoute1Branch85PositiveInsulationResistance | Route 1 branch 85 positive insulation resistance | 1路支路85正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 85 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.112 | hwDCEndCabinetRoute1Branch85NegativeInsulationResistance | Route 1 branch 85 negative insulation resistance | 1路支路85负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 85 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.113 | hwDCEndCabinetRoute1Branch86Voltage | Route 1 branch 86 voltage | 1路支路86电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 86 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.114 | hwDCEndCabinetRoute1Branch86Current | Route 1 branch 86 current | 1路支路86电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 86 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.115 | hwDCEndCabinetRoute1Branch86Power | Route 1 branch 86 power | 1路支路86功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 86 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.116 | hwDCEndCabinetRoute1Branch86SwitchStatus | Route 1 branch 86 switch status | 1路支路86开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 86 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.117 | hwDCEndCabinetRoute1Branch86LoadPercentage | Route 1 branch 86 load percentage | 1路支路86负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 86 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.118 | hwDCEndCabinetRoute1Branch86Electricity | Route 1 branch 86 electricity | 1路支路86电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 86 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.119 | hwDCEndCabinetRoute1Branch86PositiveInsulationResistance | Route 1 branch 86 positive insulation resistance | 1路支路86正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 86 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.120 | hwDCEndCabinetRoute1Branch86NegativeInsulationResistance | Route 1 branch 86 negative insulation resistance | 1路支路86负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 86 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.121 | hwDCEndCabinetRoute1Branch87Voltage | Route 1 branch 87 voltage | 1路支路87电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 87 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.122 | hwDCEndCabinetRoute1Branch87Current | Route 1 branch 87 current | 1路支路87电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 87 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.123 | hwDCEndCabinetRoute1Branch87Power | Route 1 branch 87 power | 1路支路87功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 87 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.124 | hwDCEndCabinetRoute1Branch87SwitchStatus | Route 1 branch 87 switch status | 1路支路87开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 87 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.125 | hwDCEndCabinetRoute1Branch87LoadPercentage | Route 1 branch 87 load percentage | 1路支路87负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 87 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.126 | hwDCEndCabinetRoute1Branch87Electricity | Route 1 branch 87 electricity | 1路支路87电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 87 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.127 | hwDCEndCabinetRoute1Branch87PositiveInsulationResistance | Route 1 branch 87 positive insulation resistance | 1路支路87正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 87 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.128 | hwDCEndCabinetRoute1Branch87NegativeInsulationResistance | Route 1 branch 87 negative insulation resistance | 1路支路87负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 87 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.129 | hwDCEndCabinetRoute1Branch88Voltage | Route 1 branch 88 voltage | 1路支路88电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 1 branch 88 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.130 | hwDCEndCabinetRoute1Branch88Current | Route 1 branch 88 current | 1路支路88电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 1 branch 88 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.131 | hwDCEndCabinetRoute1Branch88Power | Route 1 branch 88 power | 1路支路88功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 1 branch 88 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.132 | hwDCEndCabinetRoute1Branch88SwitchStatus | Route 1 branch 88 switch status | 1路支路88开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 1 branch 88 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.133 | hwDCEndCabinetRoute1Branch88LoadPercentage | Route 1 branch 88 load percentage | 1路支路88负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 88 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.134 | hwDCEndCabinetRoute1Branch88Electricity | Route 1 branch 88 electricity | 1路支路88电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 1 branch 88 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.135 | hwDCEndCabinetRoute1Branch88PositiveInsulationResistance | Route 1 branch 88 positive insulation resistance | 1路支路88正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 88 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.136 | hwDCEndCabinetRoute1Branch88NegativeInsulationResistance | Route 1 branch 88 negative insulation resistance | 1路支路88负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 1 branch 88 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.137 | hwDCEndCabinetRoute2BusbarVoltage | Busbar voltage | 母排电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 Busbar voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.138 | hwDCEndCabinetRoute2DcLoadCurrent | DC load current | 直流负载电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 DC load current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.139 | hwDCEndCabinetRoute2TotalDcPower | Total DC power | 直流总功率 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Route 2 Total DC power of the device config table for the DC End Cabinet.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.140 | hwDCEndCabinetRoute2TotalLoadPercentage | Total load percentage | 总负载负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 Total load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.141 | hwDCEndCabinetRoute2RatedMainCurrent | Rated main current | 主路额定电流 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Route 2 Rated main current of the device config table for the DC End Cabinet.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.142 | hwDCEndCabinetRoute2TotalNumberOfBranchSwitches | Total number of branch switches | 支路开关总路数 | 0-Read_Only | 只读 | 0..88 | 0..88 | Route 2 Total number of branch switches of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.143 | hwDCEndCabinetRoute2NumberOfClosedBranchSwitches | Number of closed branch switches | 支路开关闭合路数 | 0-Read_Only | 只读 | 0..88 | 0..88 | Route 2 Number of closed branch switches of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.144 | hwDCEndCabinetRoute2NumberOfOpenBranchSwitches | Number of open branch switches | 支路开关断开路数 | 0-Read_Only | 只读 | 0..88 | 0..88 | Route 2 Number of open branch switches of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.145 | hwDCEndCabinetRoute2DcSpdSwitchStatus | DC SPD switch status | 直流防雷开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 DC SPD switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.146 | hwDCEndCabinetRoute2MainInputSwitchStatus | Main input switch status | 主路输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 Main input switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.147 | hwDCEndCabinetRoute2VoltageBetweenPositiveBusbarAndGround | Voltage between positive busbar and ground | 母排正对地电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Route 2 Voltage between positive busbar and ground of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.148 | hwDCEndCabinetRoute2VoltageBetweenNegativeBusbarAndGround | Voltage between negative busbar and ground | 母排负对地电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Route 2 Voltage between negative busbar and ground of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.149 | hwDCEndCabinetRoute2ResistanceBetweenPositiveBusbarAndGround | Resistance between positive busbar and ground | 母排正对地电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 Resistance between positive busbar and ground of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.150 | hwDCEndCabinetRoute2ResistanceBetweenNegativeBusbarAndGround | Resistance between negative busbar and ground | 母排负对地电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 Resistance between negative busbar and ground of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.151 | hwDCEndCabinetRoute2InsulationBetweenPositiveBusbarAndGround | Insulation between positive busbar and ground | 母排正对地绝缘状态 | 0-Read_Only | 只读 | normal(1), faulty(2), unknown(255) | [正常=1]/[故障=2] | Route 2 Insulation between positive busbar and ground of the device config table for the DC End Cabinet. Value 1 indicate normal Value 2 indicate faulty
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.152 | hwDCEndCabinetRoute2InsulationBetweenNegativeBusbarAndGround | Insulation between negative busbar and ground | 母排负对地绝缘状态 | 0-Read_Only | 只读 | normal(1), faulty(2), unknown(255) | [正常=1]/[故障=2] | Route 2 Insulation between negative busbar and ground of the device config table for the DC End Cabinet. Value 1 indicate normal Value 2 indicate faulty
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.153 | hwDCEndCabinetRoute2TotalLoadElectricity | Total load electricity | 负载总电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 Total load electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.154 | hwDCEndCabinetRoute2Branch1Current | Route 2 branch 1 current | 2路支路1电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 1 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.155 | hwDCEndCabinetRoute2Branch1Power | Route 2 branch 1 power | 2路支路1功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 1 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.156 | hwDCEndCabinetRoute2Branch1SwitchStatus | Route 2 branch 1 switch status | 2路支路1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 1 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.157 | hwDCEndCabinetRoute2Branch1LoadPercentage | Route 2 branch 1 load percentage | 2路支路1负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 1 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.158 | hwDCEndCabinetRoute2Branch1Electricity | Route 2 branch 1 electricity | 2路支路1电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 1 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.159 | hwDCEndCabinetRoute2Branch1PositiveInsulationResistance | Route 2 branch 1 positive insulation resistance | 2路支路1正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 1 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.160 | hwDCEndCabinetRoute2Branch1NegativeInsulationResistance | Route 2 branch 1 negative insulation resistance | 2路支路1负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 1 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.161 | hwDCEndCabinetRoute2Branch2Voltage | Route 2 branch 2 voltage | 2路支路2电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 2 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.162 | hwDCEndCabinetRoute2Branch2Current | Route 2 branch 2 current | 2路支路2电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 2 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.163 | hwDCEndCabinetRoute2Branch2Power | Route 2 branch 2 power | 2路支路2功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 2 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.164 | hwDCEndCabinetRoute2Branch2SwitchStatus | Route 2 branch 2 switch status | 2路支路2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 2 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.165 | hwDCEndCabinetRoute2Branch2LoadPercentage | Route 2 branch 2 load percentage | 2路支路2负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 2 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.166 | hwDCEndCabinetRoute2Branch2Electricity | Route 2 branch 2 electricity | 2路支路2电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 2 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.167 | hwDCEndCabinetRoute2Branch2PositiveInsulationResistance | Route 2 branch 2 positive insulation resistance | 2路支路2正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 2 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.168 | hwDCEndCabinetRoute2Branch2NegativeInsulationResistance | Route 2 branch 2 negative insulation resistance | 2路支路2负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 2 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.169 | hwDCEndCabinetRoute2Branch3Voltage | Route 2 branch 3 voltage | 2路支路3电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 3 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.170 | hwDCEndCabinetRoute2Branch3Current | Route 2 branch 3 current | 2路支路3电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 3 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.171 | hwDCEndCabinetRoute2Branch3Power | Route 2 branch 3 power | 2路支路3功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 3 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.172 | hwDCEndCabinetRoute2Branch3SwitchStatus | Route 2 branch 3 switch status | 2路支路3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 3 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.173 | hwDCEndCabinetRoute2Branch3LoadPercentage | Route 2 branch 3 load percentage | 2路支路3负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 3 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.174 | hwDCEndCabinetRoute2Branch3Electricity | Route 2 branch 3 electricity | 2路支路3电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 3 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.175 | hwDCEndCabinetRoute2Branch3PositiveInsulationResistance | Route 2 branch 3 positive insulation resistance | 2路支路3正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 3 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.176 | hwDCEndCabinetRoute2Branch3NegativeInsulationResistance | Route 2 branch 3 negative insulation resistance | 2路支路3负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 3 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.177 | hwDCEndCabinetRoute2Branch4Voltage | Route 2 branch 4 voltage | 2路支路4电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 4 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.178 | hwDCEndCabinetRoute2Branch4Current | Route 2 branch 4 current | 2路支路4电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 4 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.179 | hwDCEndCabinetRoute2Branch4Power | Route 2 branch 4 power | 2路支路4功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 4 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.180 | hwDCEndCabinetRoute2Branch4SwitchStatus | Route 2 branch 4 switch status | 2路支路4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 4 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.181 | hwDCEndCabinetRoute2Branch4LoadPercentage | Route 2 branch 4 load percentage | 2路支路4负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 4 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.182 | hwDCEndCabinetRoute2Branch4Electricity | Route 2 branch 4 electricity | 2路支路4电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 4 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.183 | hwDCEndCabinetRoute2Branch4PositiveInsulationResistance | Route 2 branch 4 positive insulation resistance | 2路支路4正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 4 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.184 | hwDCEndCabinetRoute2Branch4NegativeInsulationResistance | Route 2 branch 4 negative insulation resistance | 2路支路4负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 4 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.185 | hwDCEndCabinetRoute2Branch5Voltage | Route 2 branch 5 voltage | 2路支路5电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 5 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.186 | hwDCEndCabinetRoute2Branch5Current | Route 2 branch 5 current | 2路支路5电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 5 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.187 | hwDCEndCabinetRoute2Branch5Power | Route 2 branch 5 power | 2路支路5功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 5 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.188 | hwDCEndCabinetRoute2Branch5SwitchStatus | Route 2 branch 5 switch status | 2路支路5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 5 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.189 | hwDCEndCabinetRoute2Branch5LoadPercentage | Route 2 branch 5 load percentage | 2路支路5负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 5 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.190 | hwDCEndCabinetRoute2Branch5Electricity | Route 2 branch 5 electricity | 2路支路5电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 5 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.191 | hwDCEndCabinetRoute2Branch5PositiveInsulationResistance | Route 2 branch 5 positive insulation resistance | 2路支路5正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 5 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.192 | hwDCEndCabinetRoute2Branch5NegativeInsulationResistance | Route 2 branch 5 negative insulation resistance | 2路支路5负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 5 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.193 | hwDCEndCabinetRoute2Branch6Voltage | Route 2 branch 6 voltage | 2路支路6电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 6 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.194 | hwDCEndCabinetRoute2Branch6Current | Route 2 branch 6 current | 2路支路6电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 6 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.195 | hwDCEndCabinetRoute2Branch6Power | Route 2 branch 6 power | 2路支路6功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 6 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.196 | hwDCEndCabinetRoute2Branch6SwitchStatus | Route 2 branch 6 switch status | 2路支路6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 6 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.197 | hwDCEndCabinetRoute2Branch6LoadPercentage | Route 2 branch 6 load percentage | 2路支路6负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 6 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.198 | hwDCEndCabinetRoute2Branch6Electricity | Route 2 branch 6 electricity | 2路支路6电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 6 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.199 | hwDCEndCabinetRoute2Branch6PositiveInsulationResistance | Route 2 branch 6 positive insulation resistance | 2路支路6正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 6 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.200 | hwDCEndCabinetRoute2Branch6NegativeInsulationResistance | Route 2 branch 6 negative insulation resistance | 2路支路6负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 6 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.4.1.201 | hwDCEndCabinetRunning4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5 | hwDCEndCabinetRunning5Table | / | / |  |  | / | / | The running table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.1 | hwDCEndCabinetRunning5Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.2 | hwDCEndCabinetRoute2Branch7Voltage | Route 2 branch 7 voltage | 2路支路7电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 7 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.3 | hwDCEndCabinetRoute2Branch7Current | Route 2 branch 7 current | 2路支路7电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 7 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.4 | hwDCEndCabinetRoute2Branch7Power | Route 2 branch 7 power | 2路支路7功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 7 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.5 | hwDCEndCabinetRoute2Branch7SwitchStatus | Route 2 branch 7 switch status | 2路支路7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 7 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.6 | hwDCEndCabinetRoute2Branch7LoadPercentage | Route 2 branch 7 load percentage | 2路支路7负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 7 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.7 | hwDCEndCabinetRoute2Branch7Electricity | Route 2 branch 7 electricity | 2路支路7电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 7 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.8 | hwDCEndCabinetRoute2Branch7PositiveInsulationResistance | Route 2 branch 7 positive insulation resistance | 2路支路7正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 7 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.9 | hwDCEndCabinetRoute2Branch7NegativeInsulationResistance | Route 2 branch 7 negative insulation resistance | 2路支路7负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 7 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.10 | hwDCEndCabinetRoute2Branch8Voltage | Route 2 branch 8 voltage | 2路支路8电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 8 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.11 | hwDCEndCabinetRoute2Branch8Current | Route 2 branch 8 current | 2路支路8电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 8 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.12 | hwDCEndCabinetRoute2Branch8Power | Route 2 branch 8 power | 2路支路8功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 8 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.13 | hwDCEndCabinetRoute2Branch8SwitchStatus | Route 2 branch 8 switch status | 2路支路8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 8 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.14 | hwDCEndCabinetRoute2Branch8LoadPercentage | Route 2 branch 8 load percentage | 2路支路8负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 8 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.15 | hwDCEndCabinetRoute2Branch8Electricity | Route 2 branch 8 electricity | 2路支路8电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 8 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.16 | hwDCEndCabinetRoute2Branch8PositiveInsulationResistance | Route 2 branch 8 positive insulation resistance | 2路支路8正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 8 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.17 | hwDCEndCabinetRoute2Branch8NegativeInsulationResistance | Route 2 branch 8 negative insulation resistance | 2路支路8负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 8 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.18 | hwDCEndCabinetRoute2Branch9Voltage | Route 2 branch 9 voltage | 2路支路9电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 9 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.19 | hwDCEndCabinetRoute2Branch9Current | Route 2 branch 9 current | 2路支路9电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 9 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.20 | hwDCEndCabinetRoute2Branch9Power | Route 2 branch 9 power | 2路支路9功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 9 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.21 | hwDCEndCabinetRoute2Branch9SwitchStatus | Route 2 branch 9 switch status | 2路支路9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 9 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.22 | hwDCEndCabinetRoute2Branch9LoadPercentage | Route 2 branch 9 load percentage | 2路支路9负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 9 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.23 | hwDCEndCabinetRoute2Branch9Electricity | Route 2 branch 9 electricity | 2路支路9电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 9 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.24 | hwDCEndCabinetRoute2Branch9PositiveInsulationResistance | Route 2 branch 9 positive insulation resistance | 2路支路9正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 9 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.25 | hwDCEndCabinetRoute2Branch9NegativeInsulationResistance | Route 2 branch 9 negative insulation resistance | 2路支路9负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 9 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.26 | hwDCEndCabinetRoute2Branch10Voltage | Route 2 branch 10 voltage | 2路支路10电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 10 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.27 | hwDCEndCabinetRoute2Branch10Current | Route 2 branch 10 current | 2路支路10电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 10 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.28 | hwDCEndCabinetRoute2Branch10Power | Route 2 branch 10 power | 2路支路10功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 10 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.29 | hwDCEndCabinetRoute2Branch10SwitchStatus | Route 2 branch 10 switch status | 2路支路10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 10 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.30 | hwDCEndCabinetRoute2Branch10LoadPercentage | Route 2 branch 10 load percentage | 2路支路10负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 10 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.31 | hwDCEndCabinetRoute2Branch10Electricity | Route 2 branch 10 electricity | 2路支路10电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 10 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.32 | hwDCEndCabinetRoute2Branch10PositiveInsulationResistance | Route 2 branch 10 positive insulation resistance | 2路支路10正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 10 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.33 | hwDCEndCabinetRoute2Branch10NegativeInsulationResistance | Route 2 branch 10 negative insulation resistance | 2路支路10负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 10 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.34 | hwDCEndCabinetRoute2Branch11Voltage | Route 2 branch 11 voltage | 2路支路11电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 11 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.35 | hwDCEndCabinetRoute2Branch11Current | Route 2 branch 11 current | 2路支路11电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 11 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.36 | hwDCEndCabinetRoute2Branch11Power | Route 2 branch 11 power | 2路支路11功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 11 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.37 | hwDCEndCabinetRoute2Branch11SwitchStatus | Route 2 branch 11 switch status | 2路支路11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 11 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.38 | hwDCEndCabinetRoute2Branch11LoadPercentage | Route 2 branch 11 load percentage | 2路支路11负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 11 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.39 | hwDCEndCabinetRoute2Branch11Electricity | Route 2 branch 11 electricity | 2路支路11电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 11 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.40 | hwDCEndCabinetRoute2Branch11PositiveInsulationResistance | Route 2 branch 11 positive insulation resistance | 2路支路11正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 11 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.41 | hwDCEndCabinetRoute2Branch11NegativeInsulationResistance | Route 2 branch 11 negative insulation resistance | 2路支路11负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 11 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.42 | hwDCEndCabinetRoute2Branch12Voltage | Route 2 branch 12 voltage | 2路支路12电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 12 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.43 | hwDCEndCabinetRoute2Branch12Current | Route 2 branch 12 current | 2路支路12电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 12 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.44 | hwDCEndCabinetRoute2Branch12Power | Route 2 branch 12 power | 2路支路12功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 12 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.45 | hwDCEndCabinetRoute2Branch12SwitchStatus | Route 2 branch 12 switch status | 2路支路12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 12 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.46 | hwDCEndCabinetRoute2Branch12LoadPercentage | Route 2 branch 12 load percentage | 2路支路12负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 12 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.47 | hwDCEndCabinetRoute2Branch12Electricity | Route 2 branch 12 electricity | 2路支路12电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 12 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.48 | hwDCEndCabinetRoute2Branch12PositiveInsulationResistance | Route 2 branch 12 positive insulation resistance | 2路支路12正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 12 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.49 | hwDCEndCabinetRoute2Branch12NegativeInsulationResistance | Route 2 branch 12 negative insulation resistance | 2路支路12负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 12 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.50 | hwDCEndCabinetRoute2Branch13Voltage | Route 2 branch 13 voltage | 2路支路13电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 13 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.51 | hwDCEndCabinetRoute2Branch13Current | Route 2 branch 13 current | 2路支路13电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 13 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.52 | hwDCEndCabinetRoute2Branch13Power | Route 2 branch 13 power | 2路支路13功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 13 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.53 | hwDCEndCabinetRoute2Branch13SwitchStatus | Route 2 branch 13 switch status | 2路支路13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 13 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.54 | hwDCEndCabinetRoute2Branch13LoadPercentage | Route 2 branch 13 load percentage | 2路支路13负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 13 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.55 | hwDCEndCabinetRoute2Branch13Electricity | Route 2 branch 13 electricity | 2路支路13电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 13 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.56 | hwDCEndCabinetRoute2Branch13PositiveInsulationResistance | Route 2 branch 13 positive insulation resistance | 2路支路13正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 13 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.57 | hwDCEndCabinetRoute2Branch13NegativeInsulationResistance | Route 2 branch 13 negative insulation resistance | 2路支路13负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 13 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.58 | hwDCEndCabinetRoute2Branch14Voltage | Route 2 branch 14 voltage | 2路支路14电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 14 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.59 | hwDCEndCabinetRoute2Branch14Current | Route 2 branch 14 current | 2路支路14电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 14 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.60 | hwDCEndCabinetRoute2Branch14Power | Route 2 branch 14 power | 2路支路14功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 14 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.61 | hwDCEndCabinetRoute2Branch14SwitchStatus | Route 2 branch 14 switch status | 2路支路14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 14 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.62 | hwDCEndCabinetRoute2Branch14LoadPercentage | Route 2 branch 14 load percentage | 2路支路14负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 14 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.63 | hwDCEndCabinetRoute2Branch14Electricity | Route 2 branch 14 electricity | 2路支路14电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 14 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.64 | hwDCEndCabinetRoute2Branch14PositiveInsulationResistance | Route 2 branch 14 positive insulation resistance | 2路支路14正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 14 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.65 | hwDCEndCabinetRoute2Branch14NegativeInsulationResistance | Route 2 branch 14 negative insulation resistance | 2路支路14负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 14 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.66 | hwDCEndCabinetRoute2Branch15Voltage | Route 2 branch 15 voltage | 2路支路15电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 15 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.67 | hwDCEndCabinetRoute2Branch15Current | Route 2 branch 15 current | 2路支路15电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 15 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.68 | hwDCEndCabinetRoute2Branch15Power | Route 2 branch 15 power | 2路支路15功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 15 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.69 | hwDCEndCabinetRoute2Branch15SwitchStatus | Route 2 branch 15 switch status | 2路支路15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 15 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.70 | hwDCEndCabinetRoute2Branch15LoadPercentage | Route 2 branch 15 load percentage | 2路支路15负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 15 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.71 | hwDCEndCabinetRoute2Branch15Electricity | Route 2 branch 15 electricity | 2路支路15电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 15 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.72 | hwDCEndCabinetRoute2Branch15PositiveInsulationResistance | Route 2 branch 15 positive insulation resistance | 2路支路15正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 15 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.73 | hwDCEndCabinetRoute2Branch15NegativeInsulationResistance | Route 2 branch 15 negative insulation resistance | 2路支路15负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 15 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.74 | hwDCEndCabinetRoute2Branch16Voltage | Route 2 branch 16 voltage | 2路支路16电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 16 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.75 | hwDCEndCabinetRoute2Branch16Current | Route 2 branch 16 current | 2路支路16电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 16 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.76 | hwDCEndCabinetRoute2Branch16Power | Route 2 branch 16 power | 2路支路16功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 16 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.77 | hwDCEndCabinetRoute2Branch16SwitchStatus | Route 2 branch 16 switch status | 2路支路16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 16 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.78 | hwDCEndCabinetRoute2Branch16LoadPercentage | Route 2 branch 16 load percentage | 2路支路16负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 16 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.79 | hwDCEndCabinetRoute2Branch16Electricity | Route 2 branch 16 electricity | 2路支路16电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 16 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.80 | hwDCEndCabinetRoute2Branch16PositiveInsulationResistance | Route 2 branch 16 positive insulation resistance | 2路支路16正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 16 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.81 | hwDCEndCabinetRoute2Branch16NegativeInsulationResistance | Route 2 branch 16 negative insulation resistance | 2路支路16负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 16 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.82 | hwDCEndCabinetRoute2Branch17Voltage | Route 2 branch 17 voltage | 2路支路17电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 17 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.83 | hwDCEndCabinetRoute2Branch17Current | Route 2 branch 17 current | 2路支路17电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 17 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.84 | hwDCEndCabinetRoute2Branch17Power | Route 2 branch 17 power | 2路支路17功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 17 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.85 | hwDCEndCabinetRoute2Branch17SwitchStatus | Route 2 branch 17 switch status | 2路支路17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 17 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.86 | hwDCEndCabinetRoute2Branch17LoadPercentage | Route 2 branch 17 load percentage | 2路支路17负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 17 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.87 | hwDCEndCabinetRoute2Branch17Electricity | Route 2 branch 17 electricity | 2路支路17电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 17 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.88 | hwDCEndCabinetRoute2Branch17PositiveInsulationResistance | Route 2 branch 17 positive insulation resistance | 2路支路17正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 17 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.89 | hwDCEndCabinetRoute2Branch17NegativeInsulationResistance | Route 2 branch 17 negative insulation resistance | 2路支路17负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 17 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.90 | hwDCEndCabinetRoute2Branch18Voltage | Route 2 branch 18 voltage | 2路支路18电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 18 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.91 | hwDCEndCabinetRoute2Branch18Current | Route 2 branch 18 current | 2路支路18电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 18 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.92 | hwDCEndCabinetRoute2Branch18Power | Route 2 branch 18 power | 2路支路18功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 18 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.93 | hwDCEndCabinetRoute2Branch18SwitchStatus | Route 2 branch 18 switch status | 2路支路18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 18 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.94 | hwDCEndCabinetRoute2Branch18LoadPercentage | Route 2 branch 18 load percentage | 2路支路18负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 18 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.95 | hwDCEndCabinetRoute2Branch18Electricity | Route 2 branch 18 electricity | 2路支路18电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 18 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.96 | hwDCEndCabinetRoute2Branch18PositiveInsulationResistance | Route 2 branch 18 positive insulation resistance | 2路支路18正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 18 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.97 | hwDCEndCabinetRoute2Branch18NegativeInsulationResistance | Route 2 branch 18 negative insulation resistance | 2路支路18负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 18 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.98 | hwDCEndCabinetRoute2Branch19Voltage | Route 2 branch 19 voltage | 2路支路19电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 19 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.99 | hwDCEndCabinetRoute2Branch19Current | Route 2 branch 19 current | 2路支路19电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 19 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.100 | hwDCEndCabinetRoute2Branch19Power | Route 2 branch 19 power | 2路支路19功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 19 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.101 | hwDCEndCabinetRoute2Branch19SwitchStatus | Route 2 branch 19 switch status | 2路支路19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 19 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.102 | hwDCEndCabinetRoute2Branch19LoadPercentage | Route 2 branch 19 load percentage | 2路支路19负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 19 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.103 | hwDCEndCabinetRoute2Branch19Electricity | Route 2 branch 19 electricity | 2路支路19电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 19 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.104 | hwDCEndCabinetRoute2Branch19PositiveInsulationResistance | Route 2 branch 19 positive insulation resistance | 2路支路19正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 19 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.105 | hwDCEndCabinetRoute2Branch19NegativeInsulationResistance | Route 2 branch 19 negative insulation resistance | 2路支路19负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 19 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.106 | hwDCEndCabinetRoute2Branch20Voltage | Route 2 branch 20 voltage | 2路支路20电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 20 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.107 | hwDCEndCabinetRoute2Branch20Current | Route 2 branch 20 current | 2路支路20电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 20 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.108 | hwDCEndCabinetRoute2Branch20Power | Route 2 branch 20 power | 2路支路20功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 20 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.109 | hwDCEndCabinetRoute2Branch20SwitchStatus | Route 2 branch 20 switch status | 2路支路20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 20 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.110 | hwDCEndCabinetRoute2Branch20LoadPercentage | Route 2 branch 20 load percentage | 2路支路20负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 20 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.111 | hwDCEndCabinetRoute2Branch20Electricity | Route 2 branch 20 electricity | 2路支路20电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 20 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.112 | hwDCEndCabinetRoute2Branch20PositiveInsulationResistance | Route 2 branch 20 positive insulation resistance | 2路支路20正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 20 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.113 | hwDCEndCabinetRoute2Branch20NegativeInsulationResistance | Route 2 branch 20 negative insulation resistance | 2路支路20负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 20 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.114 | hwDCEndCabinetRoute2Branch21Voltage | Route 2 branch 21 voltage | 2路支路21电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 21 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.115 | hwDCEndCabinetRoute2Branch21Current | Route 2 branch 21 current | 2路支路21电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 21 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.116 | hwDCEndCabinetRoute2Branch21Power | Route 2 branch 21 power | 2路支路21功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 21 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.117 | hwDCEndCabinetRoute2Branch21SwitchStatus | Route 2 branch 21 switch status | 2路支路21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 21 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.118 | hwDCEndCabinetRoute2Branch21LoadPercentage | Route 2 branch 21 load percentage | 2路支路21负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 21 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.119 | hwDCEndCabinetRoute2Branch21Electricity | Route 2 branch 21 electricity | 2路支路21电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 21 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.120 | hwDCEndCabinetRoute2Branch21PositiveInsulationResistance | Route 2 branch 21 positive insulation resistance | 2路支路21正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 21 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.121 | hwDCEndCabinetRoute2Branch21NegativeInsulationResistance | Route 2 branch 21 negative insulation resistance | 2路支路21负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 21 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.122 | hwDCEndCabinetRoute2Branch22Voltage | Route 2 branch 22 voltage | 2路支路22电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 22 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.123 | hwDCEndCabinetRoute2Branch22Current | Route 2 branch 22 current | 2路支路22电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 22 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.124 | hwDCEndCabinetRoute2Branch22Power | Route 2 branch 22 power | 2路支路22功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 22 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.125 | hwDCEndCabinetRoute2Branch22SwitchStatus | Route 2 branch 22 switch status | 2路支路22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 22 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.126 | hwDCEndCabinetRoute2Branch22LoadPercentage | Route 2 branch 22 load percentage | 2路支路22负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 22 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.127 | hwDCEndCabinetRoute2Branch22Electricity | Route 2 branch 22 electricity | 2路支路22电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 22 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.128 | hwDCEndCabinetRoute2Branch22PositiveInsulationResistance | Route 2 branch 22 positive insulation resistance | 2路支路22正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 22 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.129 | hwDCEndCabinetRoute2Branch22NegativeInsulationResistance | Route 2 branch 22 negative insulation resistance | 2路支路22负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 22 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.130 | hwDCEndCabinetRoute2Branch23Voltage | Route 2 branch 23 voltage | 2路支路23电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 23 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.131 | hwDCEndCabinetRoute2Branch23Current | Route 2 branch 23 current | 2路支路23电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 23 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.132 | hwDCEndCabinetRoute2Branch23Power | Route 2 branch 23 power | 2路支路23功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 23 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.133 | hwDCEndCabinetRoute2Branch23SwitchStatus | Route 2 branch 23 switch status | 2路支路23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 23 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.134 | hwDCEndCabinetRoute2Branch23LoadPercentage | Route 2 branch 23 load percentage | 2路支路23负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 23 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.135 | hwDCEndCabinetRoute2Branch23Electricity | Route 2 branch 23 electricity | 2路支路23电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 23 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.136 | hwDCEndCabinetRoute2Branch23PositiveInsulationResistance | Route 2 branch 23 positive insulation resistance | 2路支路23正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 23 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.137 | hwDCEndCabinetRoute2Branch23NegativeInsulationResistance | Route 2 branch 23 negative insulation resistance | 2路支路23负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 23 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.138 | hwDCEndCabinetRoute2Branch24Voltage | Route 2 branch 24 voltage | 2路支路24电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 24 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.139 | hwDCEndCabinetRoute2Branch24Current | Route 2 branch 24 current | 2路支路24电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 24 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.140 | hwDCEndCabinetRoute2Branch24Power | Route 2 branch 24 power | 2路支路24功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 24 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.141 | hwDCEndCabinetRoute2Branch24SwitchStatus | Route 2 branch 24 switch status | 2路支路24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 24 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.142 | hwDCEndCabinetRoute2Branch24LoadPercentage | Route 2 branch 24 load percentage | 2路支路24负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 24 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.143 | hwDCEndCabinetRoute2Branch24Electricity | Route 2 branch 24 electricity | 2路支路24电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 24 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.144 | hwDCEndCabinetRoute2Branch24PositiveInsulationResistance | Route 2 branch 24 positive insulation resistance | 2路支路24正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 24 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.145 | hwDCEndCabinetRoute2Branch24NegativeInsulationResistance | Route 2 branch 24 negative insulation resistance | 2路支路24负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 24 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.146 | hwDCEndCabinetRoute2Branch25Voltage | Route 2 branch 25 voltage | 2路支路25电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 25 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.147 | hwDCEndCabinetRoute2Branch25Current | Route 2 branch 25 current | 2路支路25电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 25 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.148 | hwDCEndCabinetRoute2Branch25Power | Route 2 branch 25 power | 2路支路25功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 25 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.149 | hwDCEndCabinetRoute2Branch25SwitchStatus | Route 2 branch 25 switch status | 2路支路25开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 25 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.150 | hwDCEndCabinetRoute2Branch25LoadPercentage | Route 2 branch 25 load percentage | 2路支路25负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 25 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.151 | hwDCEndCabinetRoute2Branch25Electricity | Route 2 branch 25 electricity | 2路支路25电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 25 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.152 | hwDCEndCabinetRoute2Branch25PositiveInsulationResistance | Route 2 branch 25 positive insulation resistance | 2路支路25正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 25 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.153 | hwDCEndCabinetRoute2Branch25NegativeInsulationResistance | Route 2 branch 25 negative insulation resistance | 2路支路25负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 25 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.154 | hwDCEndCabinetRoute2Branch26Voltage | Route 2 branch 26 voltage | 2路支路26电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 26 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.155 | hwDCEndCabinetRoute2Branch26Current | Route 2 branch 26 current | 2路支路26电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 26 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.156 | hwDCEndCabinetRoute2Branch26Power | Route 2 branch 26 power | 2路支路26功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 26 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.157 | hwDCEndCabinetRoute2Branch26SwitchStatus | Route 2 branch 26 switch status | 2路支路26开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 26 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.158 | hwDCEndCabinetRoute2Branch26LoadPercentage | Route 2 branch 26 load percentage | 2路支路26负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 26 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.159 | hwDCEndCabinetRoute2Branch26Electricity | Route 2 branch 26 electricity | 2路支路26电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 26 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.160 | hwDCEndCabinetRoute2Branch26PositiveInsulationResistance | Route 2 branch 26 positive insulation resistance | 2路支路26正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 26 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.161 | hwDCEndCabinetRoute2Branch26NegativeInsulationResistance | Route 2 branch 26 negative insulation resistance | 2路支路26负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 26 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.162 | hwDCEndCabinetRoute2Branch27Voltage | Route 2 branch 27 voltage | 2路支路27电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 27 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.163 | hwDCEndCabinetRoute2Branch27Current | Route 2 branch 27 current | 2路支路27电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 27 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.164 | hwDCEndCabinetRoute2Branch27Power | Route 2 branch 27 power | 2路支路27功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 27 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.165 | hwDCEndCabinetRoute2Branch27SwitchStatus | Route 2 branch 27 switch status | 2路支路27开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 27 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.166 | hwDCEndCabinetRoute2Branch27LoadPercentage | Route 2 branch 27 load percentage | 2路支路27负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 27 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.167 | hwDCEndCabinetRoute2Branch27Electricity | Route 2 branch 27 electricity | 2路支路27电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 27 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.168 | hwDCEndCabinetRoute2Branch27PositiveInsulationResistance | Route 2 branch 27 positive insulation resistance | 2路支路27正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 27 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.169 | hwDCEndCabinetRoute2Branch27NegativeInsulationResistance | Route 2 branch 27 negative insulation resistance | 2路支路27负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 27 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.170 | hwDCEndCabinetRoute2Branch28Voltage | Route 2 branch 28 voltage | 2路支路28电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 28 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.171 | hwDCEndCabinetRoute2Branch28Current | Route 2 branch 28 current | 2路支路28电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 28 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.172 | hwDCEndCabinetRoute2Branch28Power | Route 2 branch 28 power | 2路支路28功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 28 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.173 | hwDCEndCabinetRoute2Branch28SwitchStatus | Route 2 branch 28 switch status | 2路支路28开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 28 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.174 | hwDCEndCabinetRoute2Branch28LoadPercentage | Route 2 branch 28 load percentage | 2路支路28负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 28 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.175 | hwDCEndCabinetRoute2Branch28Electricity | Route 2 branch 28 electricity | 2路支路28电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 28 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.176 | hwDCEndCabinetRoute2Branch28PositiveInsulationResistance | Route 2 branch 28 positive insulation resistance | 2路支路28正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 28 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.177 | hwDCEndCabinetRoute2Branch28NegativeInsulationResistance | Route 2 branch 28 negative insulation resistance | 2路支路28负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 28 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.178 | hwDCEndCabinetRoute2Branch29Voltage | Route 2 branch 29 voltage | 2路支路29电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 29 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.179 | hwDCEndCabinetRoute2Branch29Current | Route 2 branch 29 current | 2路支路29电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 29 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.180 | hwDCEndCabinetRoute2Branch29Power | Route 2 branch 29 power | 2路支路29功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 29 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.181 | hwDCEndCabinetRoute2Branch29SwitchStatus | Route 2 branch 29 switch status | 2路支路29开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 29 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.182 | hwDCEndCabinetRoute2Branch29LoadPercentage | Route 2 branch 29 load percentage | 2路支路29负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 29 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.183 | hwDCEndCabinetRoute2Branch29Electricity | Route 2 branch 29 electricity | 2路支路29电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 29 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.184 | hwDCEndCabinetRoute2Branch29PositiveInsulationResistance | Route 2 branch 29 positive insulation resistance | 2路支路29正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 29 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.185 | hwDCEndCabinetRoute2Branch29NegativeInsulationResistance | Route 2 branch 29 negative insulation resistance | 2路支路29负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 29 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.186 | hwDCEndCabinetRoute2Branch30Voltage | Route 2 branch 30 voltage | 2路支路30电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 30 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.187 | hwDCEndCabinetRoute2Branch30Current | Route 2 branch 30 current | 2路支路30电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 30 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.188 | hwDCEndCabinetRoute2Branch30Power | Route 2 branch 30 power | 2路支路30功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 30 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.189 | hwDCEndCabinetRoute2Branch30SwitchStatus | Route 2 branch 30 switch status | 2路支路30开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 30 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.190 | hwDCEndCabinetRoute2Branch30LoadPercentage | Route 2 branch 30 load percentage | 2路支路30负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 30 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.191 | hwDCEndCabinetRoute2Branch30Electricity | Route 2 branch 30 electricity | 2路支路30电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 30 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.192 | hwDCEndCabinetRoute2Branch30PositiveInsulationResistance | Route 2 branch 30 positive insulation resistance | 2路支路30正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 30 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.193 | hwDCEndCabinetRoute2Branch30NegativeInsulationResistance | Route 2 branch 30 negative insulation resistance | 2路支路30负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 30 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.194 | hwDCEndCabinetRoute2Branch31Voltage | Route 2 branch 31 voltage | 2路支路31电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 31 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.195 | hwDCEndCabinetRoute2Branch31Current | Route 2 branch 31 current | 2路支路31电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 31 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.196 | hwDCEndCabinetRoute2Branch31Power | Route 2 branch 31 power | 2路支路31功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 31 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.197 | hwDCEndCabinetRoute2Branch31SwitchStatus | Route 2 branch 31 switch status | 2路支路31开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 31 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.198 | hwDCEndCabinetRoute2Branch31LoadPercentage | Route 2 branch 31 load percentage | 2路支路31负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 31 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.199 | hwDCEndCabinetRoute2Branch31Electricity | Route 2 branch 31 electricity | 2路支路31电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 31 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.200 | hwDCEndCabinetRoute2Branch31PositiveInsulationResistance | Route 2 branch 31 positive insulation resistance | 2路支路31正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 31 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.5.1.201 | hwDCEndCabinetRunning5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6 | hwDCEndCabinetRunning6Table | / | / |  |  | / | / | The running table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.1 | hwDCEndCabinetRunning6Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.2 | hwDCEndCabinetRoute2Branch31NegativeInsulationResistance | Route 2 branch 31 negative insulation resistance | 2路支路31负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 31 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.3 | hwDCEndCabinetRoute2Branch32Voltage | Route 2 branch 32 voltage | 2路支路32电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 32 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.4 | hwDCEndCabinetRoute2Branch32Current | Route 2 branch 32 current | 2路支路32电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 32 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.5 | hwDCEndCabinetRoute2Branch32Power | Route 2 branch 32 power | 2路支路32功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 32 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.6 | hwDCEndCabinetRoute2Branch32SwitchStatus | Route 2 branch 32 switch status | 2路支路32开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 32 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.7 | hwDCEndCabinetRoute2Branch32LoadPercentage | Route 2 branch 32 load percentage | 2路支路32负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 32 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.8 | hwDCEndCabinetRoute2Branch32Electricity | Route 2 branch 32 electricity | 2路支路32电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 32 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.9 | hwDCEndCabinetRoute2Branch32PositiveInsulationResistance | Route 2 branch 32 positive insulation resistance | 2路支路32正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 32 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.10 | hwDCEndCabinetRoute2Branch32NegativeInsulationResistance | Route 2 branch 32 negative insulation resistance | 2路支路32负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 32 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.11 | hwDCEndCabinetRoute2Branch33Voltage | Route 2 branch 33 voltage | 2路支路33电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 33 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.12 | hwDCEndCabinetRoute2Branch33Current | Route 2 branch 33 current | 2路支路33电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 33 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.13 | hwDCEndCabinetRoute2Branch33Power | Route 2 branch 33 power | 2路支路33功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 33 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.14 | hwDCEndCabinetRoute2Branch33SwitchStatus | Route 2 branch 33 switch status | 2路支路33开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 33 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.15 | hwDCEndCabinetRoute2Branch33LoadPercentage | Route 2 branch 33 load percentage | 2路支路33负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 33 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.16 | hwDCEndCabinetRoute2Branch33Electricity | Route 2 branch 33 electricity | 2路支路33电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 33 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.17 | hwDCEndCabinetRoute2Branch33PositiveInsulationResistance | Route 2 branch 33 positive insulation resistance | 2路支路33正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 33 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.18 | hwDCEndCabinetRoute2Branch33NegativeInsulationResistance | Route 2 branch 33 negative insulation resistance | 2路支路33负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 33 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.19 | hwDCEndCabinetRoute2Branch34Voltage | Route 2 branch 34 voltage | 2路支路34电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 34 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.20 | hwDCEndCabinetRoute2Branch34Current | Route 2 branch 34 current | 2路支路34电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 34 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.21 | hwDCEndCabinetRoute2Branch34Power | Route 2 branch 34 power | 2路支路34功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 34 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.22 | hwDCEndCabinetRoute2Branch34SwitchStatus | Route 2 branch 34 switch status | 2路支路34开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 34 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.23 | hwDCEndCabinetRoute2Branch34LoadPercentage | Route 2 branch 34 load percentage | 2路支路34负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 34 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.24 | hwDCEndCabinetRoute2Branch34Electricity | Route 2 branch 34 electricity | 2路支路34电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 34 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.25 | hwDCEndCabinetRoute2Branch34PositiveInsulationResistance | Route 2 branch 34 positive insulation resistance | 2路支路34正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 34 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.26 | hwDCEndCabinetRoute2Branch34NegativeInsulationResistance | Route 2 branch 34 negative insulation resistance | 2路支路34负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 34 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.27 | hwDCEndCabinetRoute2Branch35Voltage | Route 2 branch 35 voltage | 2路支路35电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 35 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.28 | hwDCEndCabinetRoute2Branch35Current | Route 2 branch 35 current | 2路支路35电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 35 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.29 | hwDCEndCabinetRoute2Branch35Power | Route 2 branch 35 power | 2路支路35功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 35 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.30 | hwDCEndCabinetRoute2Branch35SwitchStatus | Route 2 branch 35 switch status | 2路支路35开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 35 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.31 | hwDCEndCabinetRoute2Branch35LoadPercentage | Route 2 branch 35 load percentage | 2路支路35负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 35 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.32 | hwDCEndCabinetRoute2Branch35Electricity | Route 2 branch 35 electricity | 2路支路35电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 35 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.33 | hwDCEndCabinetRoute2Branch35PositiveInsulationResistance | Route 2 branch 35 positive insulation resistance | 2路支路35正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 35 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.34 | hwDCEndCabinetRoute2Branch35NegativeInsulationResistance | Route 2 branch 35 negative insulation resistance | 2路支路35负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 35 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.35 | hwDCEndCabinetRoute2Branch36Voltage | Route 2 branch 36 voltage | 2路支路36电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 36 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.36 | hwDCEndCabinetRoute2Branch36Current | Route 2 branch 36 current | 2路支路36电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 36 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.37 | hwDCEndCabinetRoute2Branch36Power | Route 2 branch 36 power | 2路支路36功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 36 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.38 | hwDCEndCabinetRoute2Branch36SwitchStatus | Route 2 branch 36 switch status | 2路支路36开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 36 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.39 | hwDCEndCabinetRoute2Branch36LoadPercentage | Route 2 branch 36 load percentage | 2路支路36负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 36 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.40 | hwDCEndCabinetRoute2Branch36Electricity | Route 2 branch 36 electricity | 2路支路36电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 36 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.41 | hwDCEndCabinetRoute2Branch36PositiveInsulationResistance | Route 2 branch 36 positive insulation resistance | 2路支路36正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 36 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.42 | hwDCEndCabinetRoute2Branch36NegativeInsulationResistance | Route 2 branch 36 negative insulation resistance | 2路支路36负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 36 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.43 | hwDCEndCabinetRoute2Branch37Voltage | Route 2 branch 37 voltage | 2路支路37电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 37 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.44 | hwDCEndCabinetRoute2Branch37Current | Route 2 branch 37 current | 2路支路37电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 37 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.45 | hwDCEndCabinetRoute2Branch37Power | Route 2 branch 37 power | 2路支路37功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 37 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.46 | hwDCEndCabinetRoute2Branch37SwitchStatus | Route 2 branch 37 switch status | 2路支路37开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 37 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.47 | hwDCEndCabinetRoute2Branch37LoadPercentage | Route 2 branch 37 load percentage | 2路支路37负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 37 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.48 | hwDCEndCabinetRoute2Branch37Electricity | Route 2 branch 37 electricity | 2路支路37电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 37 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.49 | hwDCEndCabinetRoute2Branch37PositiveInsulationResistance | Route 2 branch 37 positive insulation resistance | 2路支路37正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 37 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.50 | hwDCEndCabinetRoute2Branch37NegativeInsulationResistance | Route 2 branch 37 negative insulation resistance | 2路支路37负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 37 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.51 | hwDCEndCabinetRoute2Branch38Voltage | Route 2 branch 38 voltage | 2路支路38电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 38 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.52 | hwDCEndCabinetRoute2Branch38Current | Route 2 branch 38 current | 2路支路38电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 38 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.53 | hwDCEndCabinetRoute2Branch38Power | Route 2 branch 38 power | 2路支路38功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 38 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.54 | hwDCEndCabinetRoute2Branch38SwitchStatus | Route 2 branch 38 switch status | 2路支路38开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 38 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.55 | hwDCEndCabinetRoute2Branch38LoadPercentage | Route 2 branch 38 load percentage | 2路支路38负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 38 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.56 | hwDCEndCabinetRoute2Branch38Electricity | Route 2 branch 38 electricity | 2路支路38电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 38 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.57 | hwDCEndCabinetRoute2Branch38PositiveInsulationResistance | Route 2 branch 38 positive insulation resistance | 2路支路38正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 38 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.58 | hwDCEndCabinetRoute2Branch38NegativeInsulationResistance | Route 2 branch 38 negative insulation resistance | 2路支路38负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 38 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.59 | hwDCEndCabinetRoute2Branch39Voltage | Route 2 branch 39 voltage | 2路支路39电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 39 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.60 | hwDCEndCabinetRoute2Branch39Current | Route 2 branch 39 current | 2路支路39电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 39 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.61 | hwDCEndCabinetRoute2Branch39Power | Route 2 branch 39 power | 2路支路39功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 39 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.62 | hwDCEndCabinetRoute2Branch39SwitchStatus | Route 2 branch 39 switch status | 2路支路39开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 39 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.63 | hwDCEndCabinetRoute2Branch39LoadPercentage | Route 2 branch 39 load percentage | 2路支路39负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 39 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.64 | hwDCEndCabinetRoute2Branch39Electricity | Route 2 branch 39 electricity | 2路支路39电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 39 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.65 | hwDCEndCabinetRoute2Branch39PositiveInsulationResistance | Route 2 branch 39 positive insulation resistance | 2路支路39正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 39 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.66 | hwDCEndCabinetRoute2Branch39NegativeInsulationResistance | Route 2 branch 39 negative insulation resistance | 2路支路39负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 39 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.67 | hwDCEndCabinetRoute2Branch40Voltage | Route 2 branch 40 voltage | 2路支路40电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 40 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.68 | hwDCEndCabinetRoute2Branch40Current | Route 2 branch 40 current | 2路支路40电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 40 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.69 | hwDCEndCabinetRoute2Branch40Power | Route 2 branch 40 power | 2路支路40功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 40 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.70 | hwDCEndCabinetRoute2Branch40SwitchStatus | Route 2 branch 40 switch status | 2路支路40开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 40 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.71 | hwDCEndCabinetRoute2Branch40LoadPercentage | Route 2 branch 40 load percentage | 2路支路40负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 40 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.72 | hwDCEndCabinetRoute2Branch40Electricity | Route 2 branch 40 electricity | 2路支路40电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 40 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.73 | hwDCEndCabinetRoute2Branch40PositiveInsulationResistance | Route 2 branch 40 positive insulation resistance | 2路支路40正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 40 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.74 | hwDCEndCabinetRoute2Branch40NegativeInsulationResistance | Route 2 branch 40 negative insulation resistance | 2路支路40负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 40 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.75 | hwDCEndCabinetRoute2Branch41Voltage | Route 2 branch 41 voltage | 2路支路41电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 41 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.76 | hwDCEndCabinetRoute2Branch41Current | Route 2 branch 41 current | 2路支路41电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 41 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.77 | hwDCEndCabinetRoute2Branch41Power | Route 2 branch 41 power | 2路支路41功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 41 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.78 | hwDCEndCabinetRoute2Branch41SwitchStatus | Route 2 branch 41 switch status | 2路支路41开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 41 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.79 | hwDCEndCabinetRoute2Branch41LoadPercentage | Route 2 branch 41 load percentage | 2路支路41负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 41 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.80 | hwDCEndCabinetRoute2Branch41Electricity | Route 2 branch 41 electricity | 2路支路41电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 41 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.81 | hwDCEndCabinetRoute2Branch41PositiveInsulationResistance | Route 2 branch 41 positive insulation resistance | 2路支路41正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 41 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.82 | hwDCEndCabinetRoute2Branch41NegativeInsulationResistance | Route 2 branch 41 negative insulation resistance | 2路支路41负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 41 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.83 | hwDCEndCabinetRoute2Branch42Voltage | Route 2 branch 42 voltage | 2路支路42电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 42 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.84 | hwDCEndCabinetRoute2Branch42Current | Route 2 branch 42 current | 2路支路42电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 42 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.85 | hwDCEndCabinetRoute2Branch42Power | Route 2 branch 42 power | 2路支路42功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 42 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.86 | hwDCEndCabinetRoute2Branch42SwitchStatus | Route 2 branch 42 switch status | 2路支路42开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 42 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.87 | hwDCEndCabinetRoute2Branch42LoadPercentage | Route 2 branch 42 load percentage | 2路支路42负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 42 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.88 | hwDCEndCabinetRoute2Branch42Electricity | Route 2 branch 42 electricity | 2路支路42电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 42 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.89 | hwDCEndCabinetRoute2Branch42PositiveInsulationResistance | Route 2 branch 42 positive insulation resistance | 2路支路42正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 42 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.90 | hwDCEndCabinetRoute2Branch42NegativeInsulationResistance | Route 2 branch 42 negative insulation resistance | 2路支路42负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 42 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.91 | hwDCEndCabinetRoute2Branch43Voltage | Route 2 branch 43 voltage | 2路支路43电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 43 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.92 | hwDCEndCabinetRoute2Branch43Current | Route 2 branch 43 current | 2路支路43电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 43 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.93 | hwDCEndCabinetRoute2Branch43Power | Route 2 branch 43 power | 2路支路43功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 43 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.94 | hwDCEndCabinetRoute2Branch43SwitchStatus | Route 2 branch 43 switch status | 2路支路43开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 43 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.95 | hwDCEndCabinetRoute2Branch43LoadPercentage | Route 2 branch 43 load percentage | 2路支路43负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 43 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.96 | hwDCEndCabinetRoute2Branch43Electricity | Route 2 branch 43 electricity | 2路支路43电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 43 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.97 | hwDCEndCabinetRoute2Branch43PositiveInsulationResistance | Route 2 branch 43 positive insulation resistance | 2路支路43正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 43 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.98 | hwDCEndCabinetRoute2Branch43NegativeInsulationResistance | Route 2 branch 43 negative insulation resistance | 2路支路43负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 43 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.99 | hwDCEndCabinetRoute2Branch44Voltage | Route 2 branch 44 voltage | 2路支路44电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 44 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.100 | hwDCEndCabinetRoute2Branch44Current | Route 2 branch 44 current | 2路支路44电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 44 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.101 | hwDCEndCabinetRoute2Branch44Power | Route 2 branch 44 power | 2路支路44功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 44 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.102 | hwDCEndCabinetRoute2Branch44SwitchStatus | Route 2 branch 44 switch status | 2路支路44开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 44 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.103 | hwDCEndCabinetRoute2Branch44LoadPercentage | Route 2 branch 44 load percentage | 2路支路44负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 44 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.104 | hwDCEndCabinetRoute2Branch44Electricity | Route 2 branch 44 electricity | 2路支路44电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 44 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.105 | hwDCEndCabinetRoute2Branch44PositiveInsulationResistance | Route 2 branch 44 positive insulation resistance | 2路支路44正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 44 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.106 | hwDCEndCabinetRoute2Branch44NegativeInsulationResistance | Route 2 branch 44 negative insulation resistance | 2路支路44负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 44 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.107 | hwDCEndCabinetRoute2Branch45Voltage | Route 2 branch 45 voltage | 2路支路45电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 45 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.108 | hwDCEndCabinetRoute2Branch45Current | Route 2 branch 45 current | 2路支路45电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 45 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.109 | hwDCEndCabinetRoute2Branch45Power | Route 2 branch 45 power | 2路支路45功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 45 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.110 | hwDCEndCabinetRoute2Branch45SwitchStatus | Route 2 branch 45 switch status | 2路支路45开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 45 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.111 | hwDCEndCabinetRoute2Branch45LoadPercentage | Route 2 branch 45 load percentage | 2路支路45负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 45 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.112 | hwDCEndCabinetRoute2Branch45Electricity | Route 2 branch 45 electricity | 2路支路45电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 45 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.113 | hwDCEndCabinetRoute2Branch45PositiveInsulationResistance | Route 2 branch 45 positive insulation resistance | 2路支路45正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 45 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.114 | hwDCEndCabinetRoute2Branch45NegativeInsulationResistance | Route 2 branch 45 negative insulation resistance | 2路支路45负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 45 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.115 | hwDCEndCabinetRoute2Branch46Voltage | Route 2 branch 46 voltage | 2路支路46电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 46 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.116 | hwDCEndCabinetRoute2Branch46Current | Route 2 branch 46 current | 2路支路46电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 46 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.117 | hwDCEndCabinetRoute2Branch46Power | Route 2 branch 46 power | 2路支路46功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 46 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.118 | hwDCEndCabinetRoute2Branch46SwitchStatus | Route 2 branch 46 switch status | 2路支路46开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 46 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.119 | hwDCEndCabinetRoute2Branch46LoadPercentage | Route 2 branch 46 load percentage | 2路支路46负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 46 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.120 | hwDCEndCabinetRoute2Branch46Electricity | Route 2 branch 46 electricity | 2路支路46电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 46 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.121 | hwDCEndCabinetRoute2Branch46PositiveInsulationResistance | Route 2 branch 46 positive insulation resistance | 2路支路46正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 46 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.122 | hwDCEndCabinetRoute2Branch46NegativeInsulationResistance | Route 2 branch 46 negative insulation resistance | 2路支路46负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 46 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.123 | hwDCEndCabinetRoute2Branch47Voltage | Route 2 branch 47 voltage | 2路支路47电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 47 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.124 | hwDCEndCabinetRoute2Branch47Current | Route 2 branch 47 current | 2路支路47电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 47 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.125 | hwDCEndCabinetRoute2Branch47Power | Route 2 branch 47 power | 2路支路47功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 47 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.126 | hwDCEndCabinetRoute2Branch47SwitchStatus | Route 2 branch 47 switch status | 2路支路47开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 47 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.127 | hwDCEndCabinetRoute2Branch47LoadPercentage | Route 2 branch 47 load percentage | 2路支路47负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 47 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.128 | hwDCEndCabinetRoute2Branch47Electricity | Route 2 branch 47 electricity | 2路支路47电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 47 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.129 | hwDCEndCabinetRoute2Branch47PositiveInsulationResistance | Route 2 branch 47 positive insulation resistance | 2路支路47正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 47 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.130 | hwDCEndCabinetRoute2Branch47NegativeInsulationResistance | Route 2 branch 47 negative insulation resistance | 2路支路47负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 47 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.131 | hwDCEndCabinetRoute2Branch48Voltage | Route 2 branch 48 voltage | 2路支路48电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 48 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.132 | hwDCEndCabinetRoute2Branch48Current | Route 2 branch 48 current | 2路支路48电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 48 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.133 | hwDCEndCabinetRoute2Branch48Power | Route 2 branch 48 power | 2路支路48功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 48 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.134 | hwDCEndCabinetRoute2Branch48SwitchStatus | Route 2 branch 48 switch status | 2路支路48开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 48 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.135 | hwDCEndCabinetRoute2Branch48LoadPercentage | Route 2 branch 48 load percentage | 2路支路48负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 48 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.136 | hwDCEndCabinetRoute2Branch48Electricity | Route 2 branch 48 electricity | 2路支路48电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 48 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.137 | hwDCEndCabinetRoute2Branch48PositiveInsulationResistance | Route 2 branch 48 positive insulation resistance | 2路支路48正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 48 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.138 | hwDCEndCabinetRoute2Branch48NegativeInsulationResistance | Route 2 branch 48 negative insulation resistance | 2路支路48负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 48 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.139 | hwDCEndCabinetRoute2Branch49Voltage | Route 2 branch 49 voltage | 2路支路49电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 49 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.140 | hwDCEndCabinetRoute2Branch49Current | Route 2 branch 49 current | 2路支路49电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 49 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.141 | hwDCEndCabinetRoute2Branch49Power | Route 2 branch 49 power | 2路支路49功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 49 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.142 | hwDCEndCabinetRoute2Branch49SwitchStatus | Route 2 branch 49 switch status | 2路支路49开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 49 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.143 | hwDCEndCabinetRoute2Branch49LoadPercentage | Route 2 branch 49 load percentage | 2路支路49负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 49 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.144 | hwDCEndCabinetRoute2Branch49Electricity | Route 2 branch 49 electricity | 2路支路49电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 49 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.145 | hwDCEndCabinetRoute2Branch49PositiveInsulationResistance | Route 2 branch 49 positive insulation resistance | 2路支路49正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 49 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.146 | hwDCEndCabinetRoute2Branch49NegativeInsulationResistance | Route 2 branch 49 negative insulation resistance | 2路支路49负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 49 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.147 | hwDCEndCabinetRoute2Branch50Voltage | Route 2 branch 50 voltage | 2路支路50电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 50 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.148 | hwDCEndCabinetRoute2Branch50Current | Route 2 branch 50 current | 2路支路50电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 50 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.149 | hwDCEndCabinetRoute2Branch50Power | Route 2 branch 50 power | 2路支路50功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 50 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.150 | hwDCEndCabinetRoute2Branch50SwitchStatus | Route 2 branch 50 switch status | 2路支路50开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 50 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.151 | hwDCEndCabinetRoute2Branch50LoadPercentage | Route 2 branch 50 load percentage | 2路支路50负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 50 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.152 | hwDCEndCabinetRoute2Branch50Electricity | Route 2 branch 50 electricity | 2路支路50电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 50 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.153 | hwDCEndCabinetRoute2Branch50PositiveInsulationResistance | Route 2 branch 50 positive insulation resistance | 2路支路50正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 50 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.154 | hwDCEndCabinetRoute2Branch50NegativeInsulationResistance | Route 2 branch 50 negative insulation resistance | 2路支路50负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 50 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.155 | hwDCEndCabinetRoute2Branch51Voltage | Route 2 branch 51 voltage | 2路支路51电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 51 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.156 | hwDCEndCabinetRoute2Branch51Current | Route 2 branch 51 current | 2路支路51电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 51 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.157 | hwDCEndCabinetRoute2Branch51Power | Route 2 branch 51 power | 2路支路51功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 51 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.158 | hwDCEndCabinetRoute2Branch51SwitchStatus | Route 2 branch 51 switch status | 2路支路51开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 51 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.159 | hwDCEndCabinetRoute2Branch51LoadPercentage | Route 2 branch 51 load percentage | 2路支路51负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 51 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.160 | hwDCEndCabinetRoute2Branch51Electricity | Route 2 branch 51 electricity | 2路支路51电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 51 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.161 | hwDCEndCabinetRoute2Branch51PositiveInsulationResistance | Route 2 branch 51 positive insulation resistance | 2路支路51正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 51 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.162 | hwDCEndCabinetRoute2Branch51NegativeInsulationResistance | Route 2 branch 51 negative insulation resistance | 2路支路51负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 51 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.163 | hwDCEndCabinetRoute2Branch52Voltage | Route 2 branch 52 voltage | 2路支路52电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 52 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.164 | hwDCEndCabinetRoute2Branch52Current | Route 2 branch 52 current | 2路支路52电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 52 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.165 | hwDCEndCabinetRoute2Branch52Power | Route 2 branch 52 power | 2路支路52功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 52 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.166 | hwDCEndCabinetRoute2Branch52SwitchStatus | Route 2 branch 52 switch status | 2路支路52开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 52 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.167 | hwDCEndCabinetRoute2Branch52LoadPercentage | Route 2 branch 52 load percentage | 2路支路52负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 52 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.168 | hwDCEndCabinetRoute2Branch52Electricity | Route 2 branch 52 electricity | 2路支路52电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 52 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.169 | hwDCEndCabinetRoute2Branch52PositiveInsulationResistance | Route 2 branch 52 positive insulation resistance | 2路支路52正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 52 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.170 | hwDCEndCabinetRoute2Branch52NegativeInsulationResistance | Route 2 branch 52 negative insulation resistance | 2路支路52负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 52 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.171 | hwDCEndCabinetRoute2Branch53Voltage | Route 2 branch 53 voltage | 2路支路53电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 53 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.172 | hwDCEndCabinetRoute2Branch53Current | Route 2 branch 53 current | 2路支路53电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 53 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.173 | hwDCEndCabinetRoute2Branch53Power | Route 2 branch 53 power | 2路支路53功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 53 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.174 | hwDCEndCabinetRoute2Branch53SwitchStatus | Route 2 branch 53 switch status | 2路支路53开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 53 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.175 | hwDCEndCabinetRoute2Branch53LoadPercentage | Route 2 branch 53 load percentage | 2路支路53负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 53 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.176 | hwDCEndCabinetRoute2Branch53Electricity | Route 2 branch 53 electricity | 2路支路53电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 53 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.177 | hwDCEndCabinetRoute2Branch53PositiveInsulationResistance | Route 2 branch 53 positive insulation resistance | 2路支路53正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 53 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.178 | hwDCEndCabinetRoute2Branch53NegativeInsulationResistance | Route 2 branch 53 negative insulation resistance | 2路支路53负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 53 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.179 | hwDCEndCabinetRoute2Branch54Voltage | Route 2 branch 54 voltage | 2路支路54电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 54 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.180 | hwDCEndCabinetRoute2Branch54Current | Route 2 branch 54 current | 2路支路54电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 54 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.181 | hwDCEndCabinetRoute2Branch54Power | Route 2 branch 54 power | 2路支路54功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 54 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.182 | hwDCEndCabinetRoute2Branch54SwitchStatus | Route 2 branch 54 switch status | 2路支路54开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 54 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.183 | hwDCEndCabinetRoute2Branch54LoadPercentage | Route 2 branch 54 load percentage | 2路支路54负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 54 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.184 | hwDCEndCabinetRoute2Branch54Electricity | Route 2 branch 54 electricity | 2路支路54电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 54 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.185 | hwDCEndCabinetRoute2Branch54PositiveInsulationResistance | Route 2 branch 54 positive insulation resistance | 2路支路54正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 54 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.186 | hwDCEndCabinetRoute2Branch54NegativeInsulationResistance | Route 2 branch 54 negative insulation resistance | 2路支路54负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 54 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.187 | hwDCEndCabinetRoute2Branch55Voltage | Route 2 branch 55 voltage | 2路支路55电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 55 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.188 | hwDCEndCabinetRoute2Branch55Current | Route 2 branch 55 current | 2路支路55电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 55 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.189 | hwDCEndCabinetRoute2Branch55Power | Route 2 branch 55 power | 2路支路55功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 55 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.190 | hwDCEndCabinetRoute2Branch55SwitchStatus | Route 2 branch 55 switch status | 2路支路55开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 55 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.191 | hwDCEndCabinetRoute2Branch55LoadPercentage | Route 2 branch 55 load percentage | 2路支路55负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 55 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.192 | hwDCEndCabinetRoute2Branch55Electricity | Route 2 branch 55 electricity | 2路支路55电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 55 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.193 | hwDCEndCabinetRoute2Branch55PositiveInsulationResistance | Route 2 branch 55 positive insulation resistance | 2路支路55正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 55 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.194 | hwDCEndCabinetRoute2Branch55NegativeInsulationResistance | Route 2 branch 55 negative insulation resistance | 2路支路55负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 55 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.195 | hwDCEndCabinetRoute2Branch56Voltage | Route 2 branch 56 voltage | 2路支路56电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 56 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.196 | hwDCEndCabinetRoute2Branch56Current | Route 2 branch 56 current | 2路支路56电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 56 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.197 | hwDCEndCabinetRoute2Branch56Power | Route 2 branch 56 power | 2路支路56功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 56 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.198 | hwDCEndCabinetRoute2Branch56SwitchStatus | Route 2 branch 56 switch status | 2路支路56开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 56 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.199 | hwDCEndCabinetRoute2Branch56LoadPercentage | Route 2 branch 56 load percentage | 2路支路56负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 56 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.200 | hwDCEndCabinetRoute2Branch56Electricity | Route 2 branch 56 electricity | 2路支路56电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 56 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.6.1.201 | hwDCEndCabinetRunning6RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7 | hwDCEndCabinetRunning7Table | / | / |  |  | / | / | The running table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.1 | hwDCEndCabinetRunning7Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.2 | hwDCEndCabinetRoute2Branch56PositiveInsulationResistance | Route 2 branch 56 positive insulation resistance | 2路支路56正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 56 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.3 | hwDCEndCabinetRoute2Branch56NegativeInsulationResistance | Route 2 branch 56 negative insulation resistance | 2路支路56负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 56 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.4 | hwDCEndCabinetRoute2Branch57Voltage | Route 2 branch 57 voltage | 2路支路57电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 57 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.5 | hwDCEndCabinetRoute2Branch57Current | Route 2 branch 57 current | 2路支路57电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 57 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.6 | hwDCEndCabinetRoute2Branch57Power | Route 2 branch 57 power | 2路支路57功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 57 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.7 | hwDCEndCabinetRoute2Branch57SwitchStatus | Route 2 branch 57 switch status | 2路支路57开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 57 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.8 | hwDCEndCabinetRoute2Branch57LoadPercentage | Route 2 branch 57 load percentage | 2路支路57负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 57 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.9 | hwDCEndCabinetRoute2Branch57Electricity | Route 2 branch 57 electricity | 2路支路57电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 57 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.10 | hwDCEndCabinetRoute2Branch57PositiveInsulationResistance | Route 2 branch 57 positive insulation resistance | 2路支路57正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 57 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.11 | hwDCEndCabinetRoute2Branch57NegativeInsulationResistance | Route 2 branch 57 negative insulation resistance | 2路支路57负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 57 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.12 | hwDCEndCabinetRoute2Branch58Voltage | Route 2 branch 58 voltage | 2路支路58电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 58 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.13 | hwDCEndCabinetRoute2Branch58Current | Route 2 branch 58 current | 2路支路58电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 58 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.14 | hwDCEndCabinetRoute2Branch58Power | Route 2 branch 58 power | 2路支路58功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 58 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.15 | hwDCEndCabinetRoute2Branch58SwitchStatus | Route 2 branch 58 switch status | 2路支路58开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 58 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.16 | hwDCEndCabinetRoute2Branch58LoadPercentage | Route 2 branch 58 load percentage | 2路支路58负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 58 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.17 | hwDCEndCabinetRoute2Branch58Electricity | Route 2 branch 58 electricity | 2路支路58电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 58 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.18 | hwDCEndCabinetRoute2Branch58PositiveInsulationResistance | Route 2 branch 58 positive insulation resistance | 2路支路58正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 58 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.19 | hwDCEndCabinetRoute2Branch58NegativeInsulationResistance | Route 2 branch 58 negative insulation resistance | 2路支路58负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 58 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.20 | hwDCEndCabinetRoute2Branch59Voltage | Route 2 branch 59 voltage | 2路支路59电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 59 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.21 | hwDCEndCabinetRoute2Branch59Current | Route 2 branch 59 current | 2路支路59电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 59 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.22 | hwDCEndCabinetRoute2Branch59Power | Route 2 branch 59 power | 2路支路59功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 59 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.23 | hwDCEndCabinetRoute2Branch59SwitchStatus | Route 2 branch 59 switch status | 2路支路59开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 59 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.24 | hwDCEndCabinetRoute2Branch59LoadPercentage | Route 2 branch 59 load percentage | 2路支路59负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 59 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.25 | hwDCEndCabinetRoute2Branch59Electricity | Route 2 branch 59 electricity | 2路支路59电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 59 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.26 | hwDCEndCabinetRoute2Branch59PositiveInsulationResistance | Route 2 branch 59 positive insulation resistance | 2路支路59正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 59 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.27 | hwDCEndCabinetRoute2Branch59NegativeInsulationResistance | Route 2 branch 59 negative insulation resistance | 2路支路59负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 59 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.28 | hwDCEndCabinetRoute2Branch60Voltage | Route 2 branch 60 voltage | 2路支路60电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 60 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.29 | hwDCEndCabinetRoute2Branch60Current | Route 2 branch 60 current | 2路支路60电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 60 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.30 | hwDCEndCabinetRoute2Branch60Power | Route 2 branch 60 power | 2路支路60功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 60 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.31 | hwDCEndCabinetRoute2Branch60SwitchStatus | Route 2 branch 60 switch status | 2路支路60开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 60 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.32 | hwDCEndCabinetRoute2Branch60LoadPercentage | Route 2 branch 60 load percentage | 2路支路60负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 60 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.33 | hwDCEndCabinetRoute2Branch60Electricity | Route 2 branch 60 electricity | 2路支路60电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 60 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.34 | hwDCEndCabinetRoute2Branch60PositiveInsulationResistance | Route 2 branch 60 positive insulation resistance | 2路支路60正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 60 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.35 | hwDCEndCabinetRoute2Branch60NegativeInsulationResistance | Route 2 branch 60 negative insulation resistance | 2路支路60负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 60 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.36 | hwDCEndCabinetRoute2Branch61Voltage | Route 2 branch 61 voltage | 2路支路61电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 61 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.37 | hwDCEndCabinetRoute2Branch61Current | Route 2 branch 61 current | 2路支路61电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 61 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.38 | hwDCEndCabinetRoute2Branch61Power | Route 2 branch 61 power | 2路支路61功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 61 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.39 | hwDCEndCabinetRoute2Branch61SwitchStatus | Route 2 branch 61 switch status | 2路支路61开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 61 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.40 | hwDCEndCabinetRoute2Branch61LoadPercentage | Route 2 branch 61 load percentage | 2路支路61负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 61 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.41 | hwDCEndCabinetRoute2Branch61Electricity | Route 2 branch 61 electricity | 2路支路61电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 61 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.42 | hwDCEndCabinetRoute2Branch61PositiveInsulationResistance | Route 2 branch 61 positive insulation resistance | 2路支路61正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 61 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.43 | hwDCEndCabinetRoute2Branch61NegativeInsulationResistance | Route 2 branch 61 negative insulation resistance | 2路支路61负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 61 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.44 | hwDCEndCabinetRoute2Branch62Voltage | Route 2 branch 62 voltage | 2路支路62电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 62 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.45 | hwDCEndCabinetRoute2Branch62Current | Route 2 branch 62 current | 2路支路62电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 62 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.46 | hwDCEndCabinetRoute2Branch62Power | Route 2 branch 62 power | 2路支路62功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 62 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.47 | hwDCEndCabinetRoute2Branch62SwitchStatus | Route 2 branch 62 switch status | 2路支路62开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 62 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.48 | hwDCEndCabinetRoute2Branch62LoadPercentage | Route 2 branch 62 load percentage | 2路支路62负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 62 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.49 | hwDCEndCabinetRoute2Branch62Electricity | Route 2 branch 62 electricity | 2路支路62电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 62 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.50 | hwDCEndCabinetRoute2Branch62PositiveInsulationResistance | Route 2 branch 62 positive insulation resistance | 2路支路62正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 62 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.51 | hwDCEndCabinetRoute2Branch62NegativeInsulationResistance | Route 2 branch 62 negative insulation resistance | 2路支路62负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 62 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.52 | hwDCEndCabinetRoute2Branch63Voltage | Route 2 branch 63 voltage | 2路支路63电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 63 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.53 | hwDCEndCabinetRoute2Branch63Current | Route 2 branch 63 current | 2路支路63电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 63 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.54 | hwDCEndCabinetRoute2Branch63Power | Route 2 branch 63 power | 2路支路63功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 63 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.55 | hwDCEndCabinetRoute2Branch63SwitchStatus | Route 2 branch 63 switch status | 2路支路63开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 63 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.56 | hwDCEndCabinetRoute2Branch63LoadPercentage | Route 2 branch 63 load percentage | 2路支路63负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 63 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.57 | hwDCEndCabinetRoute2Branch63Electricity | Route 2 branch 63 electricity | 2路支路63电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 63 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.58 | hwDCEndCabinetRoute2Branch63PositiveInsulationResistance | Route 2 branch 63 positive insulation resistance | 2路支路63正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 63 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.59 | hwDCEndCabinetRoute2Branch63NegativeInsulationResistance | Route 2 branch 63 negative insulation resistance | 2路支路63负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 63 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.60 | hwDCEndCabinetRoute2Branch64Voltage | Route 2 branch 64 voltage | 2路支路64电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 64 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.61 | hwDCEndCabinetRoute2Branch64Current | Route 2 branch 64 current | 2路支路64电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 64 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.62 | hwDCEndCabinetRoute2Branch64Power | Route 2 branch 64 power | 2路支路64功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 64 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.63 | hwDCEndCabinetRoute2Branch64SwitchStatus | Route 2 branch 64 switch status | 2路支路64开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 64 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.64 | hwDCEndCabinetRoute2Branch64LoadPercentage | Route 2 branch 64 load percentage | 2路支路64负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 64 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.65 | hwDCEndCabinetRoute2Branch64Electricity | Route 2 branch 64 electricity | 2路支路64电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 64 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.66 | hwDCEndCabinetRoute2Branch64PositiveInsulationResistance | Route 2 branch 64 positive insulation resistance | 2路支路64正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 64 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.67 | hwDCEndCabinetRoute2Branch64NegativeInsulationResistance | Route 2 branch 64 negative insulation resistance | 2路支路64负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 64 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.68 | hwDCEndCabinetRoute2Branch65Voltage | Route 2 branch 65 voltage | 2路支路65电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 65 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.69 | hwDCEndCabinetRoute2Branch65Current | Route 2 branch 65 current | 2路支路65电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 65 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.70 | hwDCEndCabinetRoute2Branch65Power | Route 2 branch 65 power | 2路支路65功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 65 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.71 | hwDCEndCabinetRoute2Branch65SwitchStatus | Route 2 branch 65 switch status | 2路支路65开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 65 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.72 | hwDCEndCabinetRoute2Branch65LoadPercentage | Route 2 branch 65 load percentage | 2路支路65负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 65 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.73 | hwDCEndCabinetRoute2Branch65Electricity | Route 2 branch 65 electricity | 2路支路65电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 65 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.74 | hwDCEndCabinetRoute2Branch65PositiveInsulationResistance | Route 2 branch 65 positive insulation resistance | 2路支路65正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 65 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.75 | hwDCEndCabinetRoute2Branch65NegativeInsulationResistance | Route 2 branch 65 negative insulation resistance | 2路支路65负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 65 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.76 | hwDCEndCabinetRoute2Branch66Voltage | Route 2 branch 66 voltage | 2路支路66电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 66 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.77 | hwDCEndCabinetRoute2Branch66Current | Route 2 branch 66 current | 2路支路66电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 66 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.78 | hwDCEndCabinetRoute2Branch66Power | Route 2 branch 66 power | 2路支路66功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 66 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.79 | hwDCEndCabinetRoute2Branch66SwitchStatus | Route 2 branch 66 switch status | 2路支路66开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 66 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.80 | hwDCEndCabinetRoute2Branch66LoadPercentage | Route 2 branch 66 load percentage | 2路支路66负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 66 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.81 | hwDCEndCabinetRoute2Branch66Electricity | Route 2 branch 66 electricity | 2路支路66电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 66 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.82 | hwDCEndCabinetRoute2Branch66PositiveInsulationResistance | Route 2 branch 66 positive insulation resistance | 2路支路66正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 66 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.83 | hwDCEndCabinetRoute2Branch66NegativeInsulationResistance | Route 2 branch 66 negative insulation resistance | 2路支路66负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 66 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.84 | hwDCEndCabinetRoute2Branch67Voltage | Route 2 branch 67 voltage | 2路支路67电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 67 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.85 | hwDCEndCabinetRoute2Branch67Current | Route 2 branch 67 current | 2路支路67电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 67 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.86 | hwDCEndCabinetRoute2Branch67Power | Route 2 branch 67 power | 2路支路67功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 67 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.87 | hwDCEndCabinetRoute2Branch67SwitchStatus | Route 2 branch 67 switch status | 2路支路67开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 67 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.88 | hwDCEndCabinetRoute2Branch67LoadPercentage | Route 2 branch 67 load percentage | 2路支路67负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 67 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.89 | hwDCEndCabinetRoute2Branch67Electricity | Route 2 branch 67 electricity | 2路支路67电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 67 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.90 | hwDCEndCabinetRoute2Branch67PositiveInsulationResistance | Route 2 branch 67 positive insulation resistance | 2路支路67正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 67 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.91 | hwDCEndCabinetRoute2Branch67NegativeInsulationResistance | Route 2 branch 67 negative insulation resistance | 2路支路67负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 67 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.92 | hwDCEndCabinetRoute2Branch68Voltage | Route 2 branch 68 voltage | 2路支路68电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 68 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.93 | hwDCEndCabinetRoute2Branch68Current | Route 2 branch 68 current | 2路支路68电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 68 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.94 | hwDCEndCabinetRoute2Branch68Power | Route 2 branch 68 power | 2路支路68功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 68 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.95 | hwDCEndCabinetRoute2Branch68SwitchStatus | Route 2 branch 68 switch status | 2路支路68开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 68 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.96 | hwDCEndCabinetRoute2Branch68LoadPercentage | Route 2 branch 68 load percentage | 2路支路68负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 68 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.97 | hwDCEndCabinetRoute2Branch68Electricity | Route 2 branch 68 electricity | 2路支路68电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 68 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.98 | hwDCEndCabinetRoute2Branch68PositiveInsulationResistance | Route 2 branch 68 positive insulation resistance | 2路支路68正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 68 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.99 | hwDCEndCabinetRoute2Branch68NegativeInsulationResistance | Route 2 branch 68 negative insulation resistance | 2路支路68负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 68 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.100 | hwDCEndCabinetRoute2Branch69Voltage | Route 2 branch 69 voltage | 2路支路69电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 69 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.101 | hwDCEndCabinetRoute2Branch69Current | Route 2 branch 69 current | 2路支路69电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 69 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.102 | hwDCEndCabinetRoute2Branch69Power | Route 2 branch 69 power | 2路支路69功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 69 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.103 | hwDCEndCabinetRoute2Branch69SwitchStatus | Route 2 branch 69 switch status | 2路支路69开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 69 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.104 | hwDCEndCabinetRoute2Branch69LoadPercentage | Route 2 branch 69 load percentage | 2路支路69负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 69 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.105 | hwDCEndCabinetRoute2Branch69Electricity | Route 2 branch 69 electricity | 2路支路69电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 69 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.106 | hwDCEndCabinetRoute2Branch69PositiveInsulationResistance | Route 2 branch 69 positive insulation resistance | 2路支路69正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 69 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.107 | hwDCEndCabinetRoute2Branch69NegativeInsulationResistance | Route 2 branch 69 negative insulation resistance | 2路支路69负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 69 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.108 | hwDCEndCabinetRoute2Branch70Voltage | Route 2 branch 70 voltage | 2路支路70电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 70 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.109 | hwDCEndCabinetRoute2Branch70Current | Route 2 branch 70 current | 2路支路70电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 70 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.110 | hwDCEndCabinetRoute2Branch70Power | Route 2 branch 70 power | 2路支路70功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 70 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.111 | hwDCEndCabinetRoute2Branch70SwitchStatus | Route 2 branch 70 switch status | 2路支路70开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 70 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.112 | hwDCEndCabinetRoute2Branch70LoadPercentage | Route 2 branch 70 load percentage | 2路支路70负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 70 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.113 | hwDCEndCabinetRoute2Branch70Electricity | Route 2 branch 70 electricity | 2路支路70电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 70 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.114 | hwDCEndCabinetRoute2Branch70PositiveInsulationResistance | Route 2 branch 70 positive insulation resistance | 2路支路70正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 70 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.115 | hwDCEndCabinetRoute2Branch70NegativeInsulationResistance | Route 2 branch 70 negative insulation resistance | 2路支路70负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 70 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.116 | hwDCEndCabinetRoute2Branch71Voltage | Route 2 branch 71 voltage | 2路支路71电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 71 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.117 | hwDCEndCabinetRoute2Branch71Current | Route 2 branch 71 current | 2路支路71电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 71 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.118 | hwDCEndCabinetRoute2Branch71Power | Route 2 branch 71 power | 2路支路71功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 71 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.119 | hwDCEndCabinetRoute2Branch71SwitchStatus | Route 2 branch 71 switch status | 2路支路71开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 71 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.120 | hwDCEndCabinetRoute2Branch71LoadPercentage | Route 2 branch 71 load percentage | 2路支路71负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 71 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.121 | hwDCEndCabinetRoute2Branch71Electricity | Route 2 branch 71 electricity | 2路支路71电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 71 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.122 | hwDCEndCabinetRoute2Branch71PositiveInsulationResistance | Route 2 branch 71 positive insulation resistance | 2路支路71正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 71 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.123 | hwDCEndCabinetRoute2Branch71NegativeInsulationResistance | Route 2 branch 71 negative insulation resistance | 2路支路71负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 71 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.124 | hwDCEndCabinetRoute2Branch72Voltage | Route 2 branch 72 voltage | 2路支路72电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 72 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.125 | hwDCEndCabinetRoute2Branch72Current | Route 2 branch 72 current | 2路支路72电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 72 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.126 | hwDCEndCabinetRoute2Branch72Power | Route 2 branch 72 power | 2路支路72功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 72 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.127 | hwDCEndCabinetRoute2Branch72SwitchStatus | Route 2 branch 72 switch status | 2路支路72开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 72 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.128 | hwDCEndCabinetRoute2Branch72LoadPercentage | Route 2 branch 72 load percentage | 2路支路72负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 72 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.129 | hwDCEndCabinetRoute2Branch72Electricity | Route 2 branch 72 electricity | 2路支路72电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 72 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.130 | hwDCEndCabinetRoute2Branch72PositiveInsulationResistance | Route 2 branch 72 positive insulation resistance | 2路支路72正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 72 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.131 | hwDCEndCabinetRoute2Branch72NegativeInsulationResistance | Route 2 branch 72 negative insulation resistance | 2路支路72负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 72 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.132 | hwDCEndCabinetRoute2Branch73Voltage | Route 2 branch 73 voltage | 2路支路73电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 73 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.133 | hwDCEndCabinetRoute2Branch73Current | Route 2 branch 73 current | 2路支路73电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 73 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.134 | hwDCEndCabinetRoute2Branch73Power | Route 2 branch 73 power | 2路支路73功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 73 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.135 | hwDCEndCabinetRoute2Branch73SwitchStatus | Route 2 branch 73 switch status | 2路支路73开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 73 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.136 | hwDCEndCabinetRoute2Branch73LoadPercentage | Route 2 branch 73 load percentage | 2路支路73负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 73 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.137 | hwDCEndCabinetRoute2Branch73Electricity | Route 2 branch 73 electricity | 2路支路73电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 73 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.138 | hwDCEndCabinetRoute2Branch73PositiveInsulationResistance | Route 2 branch 73 positive insulation resistance | 2路支路73正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 73 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.139 | hwDCEndCabinetRoute2Branch73NegativeInsulationResistance | Route 2 branch 73 negative insulation resistance | 2路支路73负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 73 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.140 | hwDCEndCabinetRoute2Branch74Voltage | Route 2 branch 74 voltage | 2路支路74电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 74 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.141 | hwDCEndCabinetRoute2Branch74Current | Route 2 branch 74 current | 2路支路74电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 74 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.142 | hwDCEndCabinetRoute2Branch74Power | Route 2 branch 74 power | 2路支路74功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 74 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.143 | hwDCEndCabinetRoute2Branch74SwitchStatus | Route 2 branch 74 switch status | 2路支路74开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 74 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.144 | hwDCEndCabinetRoute2Branch74LoadPercentage | Route 2 branch 74 load percentage | 2路支路74负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 74 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.145 | hwDCEndCabinetRoute2Branch74Electricity | Route 2 branch 74 electricity | 2路支路74电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 74 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.146 | hwDCEndCabinetRoute2Branch74PositiveInsulationResistance | Route 2 branch 74 positive insulation resistance | 2路支路74正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 74 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.147 | hwDCEndCabinetRoute2Branch74NegativeInsulationResistance | Route 2 branch 74 negative insulation resistance | 2路支路74负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 74 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.148 | hwDCEndCabinetRoute2Branch75Voltage | Route 2 branch 75 voltage | 2路支路75电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 75 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.149 | hwDCEndCabinetRoute2Branch75Current | Route 2 branch 75 current | 2路支路75电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 75 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.150 | hwDCEndCabinetRoute2Branch75Power | Route 2 branch 75 power | 2路支路75功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 75 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.151 | hwDCEndCabinetRoute2Branch75SwitchStatus | Route 2 branch 75 switch status | 2路支路75开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 75 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.152 | hwDCEndCabinetRoute2Branch75LoadPercentage | Route 2 branch 75 load percentage | 2路支路75负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 75 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.153 | hwDCEndCabinetRoute2Branch75Electricity | Route 2 branch 75 electricity | 2路支路75电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 75 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.154 | hwDCEndCabinetRoute2Branch75PositiveInsulationResistance | Route 2 branch 75 positive insulation resistance | 2路支路75正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 75 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.155 | hwDCEndCabinetRoute2Branch75NegativeInsulationResistance | Route 2 branch 75 negative insulation resistance | 2路支路75负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 75 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.156 | hwDCEndCabinetRoute2Branch76Voltage | Route 2 branch 76 voltage | 2路支路76电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 76 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.157 | hwDCEndCabinetRoute2Branch76Current | Route 2 branch 76 current | 2路支路76电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 76 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.158 | hwDCEndCabinetRoute2Branch76Power | Route 2 branch 76 power | 2路支路76功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 76 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.159 | hwDCEndCabinetRoute2Branch76SwitchStatus | Route 2 branch 76 switch status | 2路支路76开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 76 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.160 | hwDCEndCabinetRoute2Branch76LoadPercentage | Route 2 branch 76 load percentage | 2路支路76负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 76 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.161 | hwDCEndCabinetRoute2Branch76Electricity | Route 2 branch 76 electricity | 2路支路76电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 76 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.162 | hwDCEndCabinetRoute2Branch76PositiveInsulationResistance | Route 2 branch 76 positive insulation resistance | 2路支路76正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 76 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.163 | hwDCEndCabinetRoute2Branch76NegativeInsulationResistance | Route 2 branch 76 negative insulation resistance | 2路支路76负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 76 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.164 | hwDCEndCabinetRoute2Branch77Voltage | Route 2 branch 77 voltage | 2路支路77电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 77 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.165 | hwDCEndCabinetRoute2Branch77Current | Route 2 branch 77 current | 2路支路77电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 77 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.166 | hwDCEndCabinetRoute2Branch77Power | Route 2 branch 77 power | 2路支路77功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 77 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.167 | hwDCEndCabinetRoute2Branch77SwitchStatus | Route 2 branch 77 switch status | 2路支路77开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 77 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.168 | hwDCEndCabinetRoute2Branch77LoadPercentage | Route 2 branch 77 load percentage | 2路支路77负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 77 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.169 | hwDCEndCabinetRoute2Branch77Electricity | Route 2 branch 77 electricity | 2路支路77电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 77 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.170 | hwDCEndCabinetRoute2Branch77PositiveInsulationResistance | Route 2 branch 77 positive insulation resistance | 2路支路77正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 77 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.171 | hwDCEndCabinetRoute2Branch77NegativeInsulationResistance | Route 2 branch 77 negative insulation resistance | 2路支路77负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 77 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.172 | hwDCEndCabinetRoute2Branch78Voltage | Route 2 branch 78 voltage | 2路支路78电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 78 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.173 | hwDCEndCabinetRoute2Branch78Current | Route 2 branch 78 current | 2路支路78电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 78 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.174 | hwDCEndCabinetRoute2Branch78Power | Route 2 branch 78 power | 2路支路78功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 78 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.175 | hwDCEndCabinetRoute2Branch78SwitchStatus | Route 2 branch 78 switch status | 2路支路78开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 78 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.176 | hwDCEndCabinetRoute2Branch78LoadPercentage | Route 2 branch 78 load percentage | 2路支路78负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 78 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.177 | hwDCEndCabinetRoute2Branch78Electricity | Route 2 branch 78 electricity | 2路支路78电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 78 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.178 | hwDCEndCabinetRoute2Branch78PositiveInsulationResistance | Route 2 branch 78 positive insulation resistance | 2路支路78正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 78 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.179 | hwDCEndCabinetRoute2Branch78NegativeInsulationResistance | Route 2 branch 78 negative insulation resistance | 2路支路78负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 78 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.180 | hwDCEndCabinetRoute2Branch79Voltage | Route 2 branch 79 voltage | 2路支路79电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 79 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.181 | hwDCEndCabinetRoute2Branch79Current | Route 2 branch 79 current | 2路支路79电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 79 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.182 | hwDCEndCabinetRoute2Branch79Power | Route 2 branch 79 power | 2路支路79功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 79 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.183 | hwDCEndCabinetRoute2Branch79SwitchStatus | Route 2 branch 79 switch status | 2路支路79开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 79 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.184 | hwDCEndCabinetRoute2Branch79LoadPercentage | Route 2 branch 79 load percentage | 2路支路79负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 79 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.185 | hwDCEndCabinetRoute2Branch79Electricity | Route 2 branch 79 electricity | 2路支路79电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 79 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.186 | hwDCEndCabinetRoute2Branch79PositiveInsulationResistance | Route 2 branch 79 positive insulation resistance | 2路支路79正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 79 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.187 | hwDCEndCabinetRoute2Branch79NegativeInsulationResistance | Route 2 branch 79 negative insulation resistance | 2路支路79负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 79 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.188 | hwDCEndCabinetRoute2Branch80Voltage | Route 2 branch 80 voltage | 2路支路80电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 80 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.189 | hwDCEndCabinetRoute2Branch80Current | Route 2 branch 80 current | 2路支路80电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 80 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.190 | hwDCEndCabinetRoute2Branch80Power | Route 2 branch 80 power | 2路支路80功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 80 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.191 | hwDCEndCabinetRoute2Branch80SwitchStatus | Route 2 branch 80 switch status | 2路支路80开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 80 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.192 | hwDCEndCabinetRoute2Branch80LoadPercentage | Route 2 branch 80 load percentage | 2路支路80负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 80 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.193 | hwDCEndCabinetRoute2Branch80Electricity | Route 2 branch 80 electricity | 2路支路80电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 80 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.194 | hwDCEndCabinetRoute2Branch80PositiveInsulationResistance | Route 2 branch 80 positive insulation resistance | 2路支路80正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 80 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.195 | hwDCEndCabinetRoute2Branch80NegativeInsulationResistance | Route 2 branch 80 negative insulation resistance | 2路支路80负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 80 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.196 | hwDCEndCabinetRoute2Branch81Voltage | Route 2 branch 81 voltage | 2路支路81电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 81 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.197 | hwDCEndCabinetRoute2Branch81Current | Route 2 branch 81 current | 2路支路81电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 81 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.198 | hwDCEndCabinetRoute2Branch81Power | Route 2 branch 81 power | 2路支路81功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 81 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.199 | hwDCEndCabinetRoute2Branch81SwitchStatus | Route 2 branch 81 switch status | 2路支路81开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 81 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.200 | hwDCEndCabinetRoute2Branch81LoadPercentage | Route 2 branch 81 load percentage | 2路支路81负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 81 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.7.1.201 | hwDCEndCabinetRunning7RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8 | hwDCEndCabinetRunning8Table | / | / |  |  | / | / | The running table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.1 | hwDCEndCabinetRunning8Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.2 | hwDCEndCabinetRoute2Branch81Electricity | Route 2 branch 81 electricity | 2路支路81电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 81 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.3 | hwDCEndCabinetRoute2Branch81PositiveInsulationResistance | Route 2 branch 81 positive insulation resistance | 2路支路81正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 81 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.4 | hwDCEndCabinetRoute2Branch81NegativeInsulationResistance | Route 2 branch 81 negative insulation resistance | 2路支路81负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 81 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.5 | hwDCEndCabinetRoute2Branch82Voltage | Route 2 branch 82 voltage | 2路支路82电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 82 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.6 | hwDCEndCabinetRoute2Branch82Current | Route 2 branch 82 current | 2路支路82电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 82 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.7 | hwDCEndCabinetRoute2Branch82Power | Route 2 branch 82 power | 2路支路82功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 82 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.8 | hwDCEndCabinetRoute2Branch82SwitchStatus | Route 2 branch 82 switch status | 2路支路82开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 82 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.9 | hwDCEndCabinetRoute2Branch82LoadPercentage | Route 2 branch 82 load percentage | 2路支路82负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 82 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.10 | hwDCEndCabinetRoute2Branch82Electricity | Route 2 branch 82 electricity | 2路支路82电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 82 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.11 | hwDCEndCabinetRoute2Branch82PositiveInsulationResistance | Route 2 branch 82 positive insulation resistance | 2路支路82正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 82 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.12 | hwDCEndCabinetRoute2Branch82NegativeInsulationResistance | Route 2 branch 82 negative insulation resistance | 2路支路82负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 82 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.13 | hwDCEndCabinetRoute2Branch83Voltage | Route 2 branch 83 voltage | 2路支路83电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 83 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.14 | hwDCEndCabinetRoute2Branch83Current | Route 2 branch 83 current | 2路支路83电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 83 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.15 | hwDCEndCabinetRoute2Branch83Power | Route 2 branch 83 power | 2路支路83功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 83 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.16 | hwDCEndCabinetRoute2Branch83SwitchStatus | Route 2 branch 83 switch status | 2路支路83开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 83 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.17 | hwDCEndCabinetRoute2Branch83LoadPercentage | Route 2 branch 83 load percentage | 2路支路83负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 83 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.18 | hwDCEndCabinetRoute2Branch83Electricity | Route 2 branch 83 electricity | 2路支路83电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 83 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.19 | hwDCEndCabinetRoute2Branch83PositiveInsulationResistance | Route 2 branch 83 positive insulation resistance | 2路支路83正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 83 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.20 | hwDCEndCabinetRoute2Branch83NegativeInsulationResistance | Route 2 branch 83 negative insulation resistance | 2路支路83负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 83 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.21 | hwDCEndCabinetRoute2Branch84Voltage | Route 2 branch 84 voltage | 2路支路84电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 84 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.22 | hwDCEndCabinetRoute2Branch84Current | Route 2 branch 84 current | 2路支路84电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 84 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.23 | hwDCEndCabinetRoute2Branch84Power | Route 2 branch 84 power | 2路支路84功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 84 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.24 | hwDCEndCabinetRoute2Branch84SwitchStatus | Route 2 branch 84 switch status | 2路支路84开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 84 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.25 | hwDCEndCabinetRoute2Branch84LoadPercentage | Route 2 branch 84 load percentage | 2路支路84负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 84 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.26 | hwDCEndCabinetRoute2Branch84Electricity | Route 2 branch 84 electricity | 2路支路84电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 84 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.27 | hwDCEndCabinetRoute2Branch84PositiveInsulationResistance | Route 2 branch 84 positive insulation resistance | 2路支路84正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 84 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.28 | hwDCEndCabinetRoute2Branch84NegativeInsulationResistance | Route 2 branch 84 negative insulation resistance | 2路支路84负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 84 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.29 | hwDCEndCabinetRoute2Branch85Voltage | Route 2 branch 85 voltage | 2路支路85电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 85 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.30 | hwDCEndCabinetRoute2Branch85Current | Route 2 branch 85 current | 2路支路85电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 85 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.31 | hwDCEndCabinetRoute2Branch85Power | Route 2 branch 85 power | 2路支路85功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 85 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.32 | hwDCEndCabinetRoute2Branch85SwitchStatus | Route 2 branch 85 switch status | 2路支路85开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 85 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.33 | hwDCEndCabinetRoute2Branch85LoadPercentage | Route 2 branch 85 load percentage | 2路支路85负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 85 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.34 | hwDCEndCabinetRoute2Branch85Electricity | Route 2 branch 85 electricity | 2路支路85电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 85 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.35 | hwDCEndCabinetRoute2Branch85PositiveInsulationResistance | Route 2 branch 85 positive insulation resistance | 2路支路85正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 85 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.36 | hwDCEndCabinetRoute2Branch85NegativeInsulationResistance | Route 2 branch 85 negative insulation resistance | 2路支路85负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 85 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.37 | hwDCEndCabinetRoute2Branch86Voltage | Route 2 branch 86 voltage | 2路支路86电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 86 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.38 | hwDCEndCabinetRoute2Branch86Current | Route 2 branch 86 current | 2路支路86电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 86 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.39 | hwDCEndCabinetRoute2Branch86Power | Route 2 branch 86 power | 2路支路86功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 86 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.40 | hwDCEndCabinetRoute2Branch86SwitchStatus | Route 2 branch 86 switch status | 2路支路86开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 86 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.41 | hwDCEndCabinetRoute2Branch86LoadPercentage | Route 2 branch 86 load percentage | 2路支路86负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 86 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.42 | hwDCEndCabinetRoute2Branch86Electricity | Route 2 branch 86 electricity | 2路支路86电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 86 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.43 | hwDCEndCabinetRoute2Branch86PositiveInsulationResistance | Route 2 branch 86 positive insulation resistance | 2路支路86正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 86 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.44 | hwDCEndCabinetRoute2Branch86NegativeInsulationResistance | Route 2 branch 86 negative insulation resistance | 2路支路86负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 86 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.45 | hwDCEndCabinetRoute2Branch87Voltage | Route 2 branch 87 voltage | 2路支路87电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 87 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.46 | hwDCEndCabinetRoute2Branch87Current | Route 2 branch 87 current | 2路支路87电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 87 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.47 | hwDCEndCabinetRoute2Branch87Power | Route 2 branch 87 power | 2路支路87功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 87 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.48 | hwDCEndCabinetRoute2Branch87SwitchStatus | Route 2 branch 87 switch status | 2路支路87开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 87 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.49 | hwDCEndCabinetRoute2Branch87LoadPercentage | Route 2 branch 87 load percentage | 2路支路87负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 87 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.50 | hwDCEndCabinetRoute2Branch87Electricity | Route 2 branch 87 electricity | 2路支路87电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 87 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.51 | hwDCEndCabinetRoute2Branch87PositiveInsulationResistance | Route 2 branch 87 positive insulation resistance | 2路支路87正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 87 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.52 | hwDCEndCabinetRoute2Branch87NegativeInsulationResistance | Route 2 branch 87 negative insulation resistance | 2路支路87负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 87 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.53 | hwDCEndCabinetRoute2Branch88Voltage | Route 2 branch 88 voltage | 2路支路88电压 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Route 2 branch 88 voltage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.54 | hwDCEndCabinetRoute2Branch88Current | Route 2 branch 88 current | 2路支路88电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Route 2 branch 88 current of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.55 | hwDCEndCabinetRoute2Branch88Power | Route 2 branch 88 power | 2路支路88功率 | 0-Read_Only | 只读 | 0..6550 | 0..6550 | Route 2 branch 88 power of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.56 | hwDCEndCabinetRoute2Branch88SwitchStatus | Route 2 branch 88 switch status | 2路支路88开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Route 2 branch 88 switch status of the device config table for the DC End Cabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.57 | hwDCEndCabinetRoute2Branch88LoadPercentage | Route 2 branch 88 load percentage | 2路支路88负载率 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 88 load percentage of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.58 | hwDCEndCabinetRoute2Branch88Electricity | Route 2 branch 88 electricity | 2路支路88电能 | 0-Read_Only | 只读 | 0..4294967294 | 0..4294967294 | Route 2 branch 88 electricity of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.59 | hwDCEndCabinetRoute2Branch88PositiveInsulationResistance | Route 2 branch 88 positive insulation resistance | 2路支路88正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 88 positive insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.60 | hwDCEndCabinetRoute2Branch88NegativeInsulationResistance | Route 2 branch 88 negative insulation resistance | 2路支路88负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Route 2 branch 88 negative insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.61 | hwDCEndCabinetAMainStatus | A main status | A主路状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | A main status of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.62 | hwDCEndCabinetBMainStatus | B main status | B主路状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | B main status of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.63 | hwDCEndCabinetABranchStatus1 | A branch status 1 | A支路状态1 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | A branch status 1 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.64 | hwDCEndCabinetABranchStatus2 | A branch status 2 | A支路状态2 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | A branch status 2 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.65 | hwDCEndCabinetABranchStatus3 | A branch status 3 | A支路状态3 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | A branch status 3 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.66 | hwDCEndCabinetABranchStatus4 | A branch status 4 | A支路状态4 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | A branch status 4 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.67 | hwDCEndCabinetABranchStatus5 | A branch status 5 | A支路状态5 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | A branch status 5 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.68 | hwDCEndCabinetABranchStatus6 | A branch status 6 | A支路状态6 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | A branch status 6 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.69 | hwDCEndCabinetBBranchStatus1 | B branch status 1 | B支路状态1 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | B branch status 1 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.70 | hwDCEndCabinetBBranchStatus2 | B branch status 2 | B支路状态2 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | B branch status 2 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.71 | hwDCEndCabinetBBranchStatus3 | B branch status 3 | B支路状态3 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | B branch status 3 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.72 | hwDCEndCabinetBBranchStatus4 | B branch status 4 | B支路状态4 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | B branch status 4 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.73 | hwDCEndCabinetBBranchStatus5 | B branch status 5 | B支路状态5 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | B branch status 5 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.74 | hwDCEndCabinetBBranchStatus6 | B branch status 6 | B支路状态6 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | B branch status 6 of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.8.1.101 | hwDCEndCabinetRunning8RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9 | hwDCEndCabinetConfig9Table | / | / |  |  | / | / | The config table of DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.1 | hwDCEndCabinetConfig9Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.2 | hwDCEndCabinetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.3 | hwDCEndCabinet220VDcOvervoltageAlarmThreshold | DC overvoltage alarm threshold | 直流过压告警点 | 1-Read_Write | 读写 | 2700..3025 | 2700..3025 | DC overvoltage alarm threshold of the device config table for the DC End Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.4 | hwDCEndCabinet220VDcUndervoltageAlarmThreshold | DC undervoltage alarm threshold | 直流欠压告警点 | 1-Read_Write | 读写 | 1900..2690 | 1900..2690 | DC undervoltage alarm threshold of the device config table for the DC End Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.5 | hwDCEndCabinet336VDcOvervoltageAlarmThreshold | DC overvoltage alarm threshold | 直流过压告警点 | 1-Read_Write | 读写 | 3780..4100 | 3780..4100 | DC overvoltage alarm threshold of the device config table for the DC End Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.6 | hwDCEndCabinet336VDcUndervoltageAlarmThreshold | DC undervoltage alarm threshold | 直流欠压告警点 | 1-Read_Write | 读写 | 2800..3770 | 2800..3770 | DC undervoltage alarm threshold of the device config table for the DC End Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.7 | hwDCEndCabinetDcTotalLoadOvercurrentAlarmThreshold | DC total load overcurrent alarm threshold | 直流总负载过流告警点 | 1-Read_Write | 读写 | 50..100 | 50..100 | DC total load overcurrent alarm threshold of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.8 | hwDCEndCabinetDcOutputQflBranchOvercurrentAlarmThreshold | DC output QFL branch overcurrent alarm threshold | 直流输出QFL支路过流告警点 | 1-Read_Write | 读写 | 50..100 | 50..100 | DC output QFL branch overcurrent alarm threshold of the device config table for the DC End Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.9 | hwDCEndCabinetInsulationResistance | Insulation resistance | 绝缘电阻 | 1-Read_Write | 读写 | 50..700 | 50..700 | Insulation resistance of the device config table for the DC End Cabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.9.14.9.1.101 | hwDCEndCabinetConfig9RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC End Cabinet.

## PDU-Sinexcel-svg100
配电柜-盛弘-svg100
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.16 | PDUSinexcelsvg100 | PDU-Sinexcel-svg100 | 配电柜-盛弘-svg100 | / | / | / | / | PDU-Sinexcel-svg100 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1 | hwPDUSinexcelsvg100RunningandConfig1Table | / | / |  |  | / | / | The running table of PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.1 | hwPDUSinexcelsvg100RunningandConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.2 | hwPDUSinexcelsvg100L1LoadCurrent | L1 load current | 负载A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 load current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.3 | hwPDUSinexcelsvg100L2LoadCurrent | L2 load current | 负载B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 load current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.4 | hwPDUSinexcelsvg100L3LoadCurrent | L3 load current | 负载C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 load current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.5 | hwPDUSinexcelsvg100L1LoadThdi | L1 load THDI | 负载A相THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 load THDI of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.6 | hwPDUSinexcelsvg100L2LoadThdi | L2 load THDI | 负载B相THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 load THDI of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.7 | hwPDUSinexcelsvg100L3LoadThdi | L3 load THDI | 负载C相THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 load THDI of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.8 | hwPDUSinexcelsvg100L1InductorCurrent | L1 inductor current | A相电感电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 inductor current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.9 | hwPDUSinexcelsvg100L2InductorCurrent | L2 inductor current | B相电感电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 inductor current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.10 | hwPDUSinexcelsvg100L3InductorCurrent | L3 inductor current | C相电感电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 inductor current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.11 | hwPDUSinexcelsvg100L1GridApparentPower | L1 grid apparent power | 源侧A相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 grid apparent power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.12 | hwPDUSinexcelsvg100L2GridApparentPower | L2 grid apparent power | 源侧B相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 grid apparent power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.13 | hwPDUSinexcelsvg100L3GridApparentPower | L3 grid apparent power | 源侧C相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 grid apparent power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.14 | hwPDUSinexcelsvg100L1ActivePower | L1 active power | 源侧A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 active power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.15 | hwPDUSinexcelsvg100L2ActivePower | L2 active power | 源侧B相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 active power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.16 | hwPDUSinexcelsvg100L3ActivePower | L3 active power | 源侧C相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 active power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.17 | hwPDUSinexcelsvg100NLineGridCurrent | N line grid current | 源侧N线电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | N line grid current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.18 | hwPDUSinexcelsvg100NLineLoadCurrent | N line load current | 负载N线电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | N line load current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.19 | hwPDUSinexcelsvg100L1GridCurrent | L1 grid current | 源侧A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 grid current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.20 | hwPDUSinexcelsvg100L2GridCurrent | L2 grid current | 源侧B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 grid current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.21 | hwPDUSinexcelsvg100L3GridCurrent | L3 grid current | 源侧C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 grid current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.22 | hwPDUSinexcelsvg100L1GridThdi | L1 grid THDI | 源侧A相THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 grid THDI of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.23 | hwPDUSinexcelsvg100L2GridThdi | L2 grid THDI | 源侧B相THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 grid THDI of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.24 | hwPDUSinexcelsvg100L3GridThdi | L3 grid THDI | 源侧C相THDI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 grid THDI of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.25 | hwPDUSinexcelsvg100Temperature1 | Temperature1 | 温度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature1 of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.26 | hwPDUSinexcelsvg100Temperature2 | Temperature2 | 温度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature2 of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.27 | hwPDUSinexcelsvg100Temperature3 | Temperature3 | 温度3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature3 of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.28 | hwPDUSinexcelsvg100L1GridReactivePower | L1 grid reactive power | 源侧A相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 grid reactive power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.29 | hwPDUSinexcelsvg100L2GridReactivePower | L2 grid reactive power | 源侧B相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 grid reactive power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.30 | hwPDUSinexcelsvg100L3GridReactivePower | L3 grid reactive power | 源侧C相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 grid reactive power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.31 | hwPDUSinexcelsvg100L1GridCosphi | L1 grid COSPHI | 源侧A相COSPHI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 grid COSPHI of the device config table for the PDU-Sinexcel-svg100.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.32 | hwPDUSinexcelsvg100L2GridCosphi | L2 grid COSPHI | 源侧B相COSPHI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 grid COSPHI of the device config table for the PDU-Sinexcel-svg100.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.33 | hwPDUSinexcelsvg100L3GridCosphi | L3 grid COSPHI | 源侧C相COSPHI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 grid COSPHI of the device config table for the PDU-Sinexcel-svg100.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.34 | hwPDUSinexcelsvg100L1LoadReactivePower | L1 load reactive power | 负载A相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 load reactive power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.35 | hwPDUSinexcelsvg100L2LoadReactivePower | L2 load reactive power | 负载B相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 load reactive power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.36 | hwPDUSinexcelsvg100L3LoadReactivePower | L3 load reactive power | 负载C相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 load reactive power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.37 | hwPDUSinexcelsvg100L1CompensationCurrent | L1 compensation current | A相补偿电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 compensation current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.38 | hwPDUSinexcelsvg100L2CompensationCurrent | L2 compensation current | B相补偿电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 compensation current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.39 | hwPDUSinexcelsvg100L3CompensationCurrent | L3 compensation current | C相补偿电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 compensation current of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.40 | hwPDUSinexcelsvg100L1CompensationCurrentLoadRate | L1 compensation current load rate | A相补偿电流负载率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 compensation current load rate of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.41 | hwPDUSinexcelsvg100L2CompensationCurrentLoadRate | L2 compensation current load rate | B相补偿电流负载率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 compensation current load rate of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.42 | hwPDUSinexcelsvg100L3CompensationCurrentLoadRate | L3 compensation current load rate | C相补偿电流负载率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 compensation current load rate of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.43 | hwPDUSinexcelsvg100Temperature4 | Temperature4 | 温度4 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature4 of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.44 | hwPDUSinexcelsvg100Temperature5 | Temperature5 | 温度5 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature5 of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.45 | hwPDUSinexcelsvg100Temperature6 | Temperature6 | 温度6 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature6 of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.46 | hwPDUSinexcelsvg100L1LoadApparentPower | L1 load apparent power | 负载A相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 load apparent power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.47 | hwPDUSinexcelsvg100L2LoadApparentPower | L2 load apparent power | 负载B相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 load apparent power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.48 | hwPDUSinexcelsvg100L3LoadApparentPower | L3 load apparent power | 负载C相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 load apparent power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.49 | hwPDUSinexcelsvg100L1LoadActivePower | L1 load active power | 负载A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 load active power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.50 | hwPDUSinexcelsvg100L2LoadActivePower | L2 load active power | 负载B相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 load active power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.51 | hwPDUSinexcelsvg100L3LoadActivePower | L3 load active power | 负载C相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 load active power of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.52 | hwPDUSinexcelsvg100L1LoadCosphi | L1 load COSPHI | 负载A相COSPHI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 load COSPHI of the device config table for the PDU-Sinexcel-svg100.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.53 | hwPDUSinexcelsvg100L2LoadCosphi | L2 load COSPHI | 负载B相COSPHI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 load COSPHI of the device config table for the PDU-Sinexcel-svg100.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.54 | hwPDUSinexcelsvg100L3LoadCosphi | L3 load COSPHI | 负载C相COSPHI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 load COSPHI of the device config table for the PDU-Sinexcel-svg100.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.55 | hwPDUSinexcelsvg100L1GridVoltage | L1 grid voltage | 源侧A相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 grid voltage of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.56 | hwPDUSinexcelsvg100L2GridVoltage | L2 grid voltage | 源侧B相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 grid voltage of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.57 | hwPDUSinexcelsvg100L3GridVoltage | L3 grid voltage | 源侧C相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 grid voltage of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.58 | hwPDUSinexcelsvg100L1GridFrequency | L1 grid frequency | 源侧A相频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 grid frequency of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.59 | hwPDUSinexcelsvg100L2GridFrequency | L2 grid frequency | 源侧B相频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 grid frequency of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.60 | hwPDUSinexcelsvg100L3GridFrequency | L3 grid frequency | 源侧C相频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 grid frequency of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.61 | hwPDUSinexcelsvg100L1GridThdu | L1 grid THDU | 源侧A相THDU | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L1 grid THDU of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.62 | hwPDUSinexcelsvg100L2GridThdu | L2 grid THDU | 源侧B相THDU | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L2 grid THDU of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.63 | hwPDUSinexcelsvg100L3GridThdu | L3 grid THDU | 源侧C相THDU | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | L3 grid THDU of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.64 | hwPDUSinexcelsvg100OperationTime | Operation time | 整机运行时间 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Operation time of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.65 | hwPDUSinexcelsvg100Over50LoadOperationTime | Over 50% load operation time | 大于50%载运行时间 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Over 50% load operation time of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.66 | hwPDUSinexcelsvg100Below50LoadOperationTime | Below 50% load operation time | 小于50%载运行时间 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Below 50% load operation time of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.67 | hwPDUSinexcelsvg100PositiveDcBusVoltage | Positive DC bus voltage | 正直流母线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive DC bus voltage of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.68 | hwPDUSinexcelsvg100NegativeDcBusVoltage | Negative DC bus voltage | 负直流母线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative DC bus voltage of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.69 | hwPDUSinexcelsvg100InductorTemperature | Inductor temperature | 电感温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inductor temperature of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.70 | hwPDUSinexcelsvg100CapacitanceCurrent | Capacitance current | 电容电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Capacitance current of the device config table for the PDU-Sinexcel-svg100.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.71 | hwPDUSinexcelsvg100InitializeFlag | Initialize flag | 初始化标志 | 0-Read_Only | 只读 | noInitializationIsRequired(1), initializationRequired(2), unknown(255) | [不需要初始化=1]/[需要初始化=2] | Initialize flag of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate no initialization is required Value 2 indicate initialization required
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.72 | hwPDUSinexcelsvg100RunningStatus | Running status | 运行状态 | 0-Read_Only | 只读 | standby(1), run(2), unknown(255) | [待机=1]/[运行=2] | Running status of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate standby Value 2 indicate run
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.73 | hwPDUSinexcelsvg100ProtocolVersionNumber | Protocol version number | 协议版本号 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Protocol version number of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.74 | hwPDUSinexcelsvg100SoftwareVersionNumber | Software version number | 软件版本号 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Software version number of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.75 | hwPDUSinexcelsvg100PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.76 | hwPDUSinexcelsvg100ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.77 | hwPDUSinexcelsvg100CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.78 | hwPDUSinexcelsvg100DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.79 | hwPDUSinexcelsvg100NumberOfSlave | Number of slave | 从机数量 | 1-Read_Write | 读写 | 1..10 | 1..10 | Number of slave of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.80 | hwPDUSinexcelsvg100CtRatio | CT ratio | 设定CT变比 | 1-Read_Write | 读写 | 0..30000 | 0..30000 | CT ratio of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.81 | hwPDUSinexcelsvg100ExternalTransformerRatio | External transformer ratio | 外置变压器比例 | 1-Read_Write | 读写 | 1..750 | 1..750 | External transformer ratio of the device config table for the PDU-Sinexcel-svg100.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.82 | hwPDUSinexcelsvg100ParallelMachineCapacity | Parallel machine capacity | 并机容量 | 1-Read_Write | 读写 | 10..30000 | 10..30000 | Parallel machine capacity of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.83 | hwPDUSinexcelsvg100HarmonicCompensationRate | Harmonic compensation rate | 谐波补偿率设置 | 1-Read_Write | 读写 | 1..100 | 1..100 | Harmonic compensation rate of the device config table for the PDU-Sinexcel-svg100.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.84 | hwPDUSinexcelsvg100TargetPowerFactor | Target power factor | 设定目标功率因数 | 1-Read_Write | 读写 | -100..100 | -100..100 | Target power factor of the device config table for the PDU-Sinexcel-svg100.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.85 | hwPDUSinexcelsvg100PowerOnMode | Power on mode | 启动方式 | 1-Read_Write | 读写 | autoPowerOnMode(1), manualStartupMode(2), unknown(255) | [自动开机模式=1]/[手动开机模式=2] | Power on mode of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate auto power on mode Value 2 indicate manual startup mode
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.86 | hwPDUSinexcelsvg100CompensationMode | Compensation mode | 谐波补偿模式 | 1-Read_Write | 读写 | intelligentCompensation(1), successiveCompensationMode(2), fullCompensationMode(3), unknown(255) | [智能补偿=1]/[逐次补偿模式=2]/[全补偿模式=3] | Compensation mode of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate intelligent compensation Value 2 indicate successive compensation mode Value 3 indicate full compensation mode
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.87 | hwPDUSinexcelsvg100CtLocation | CT location | 设定CT位置 | 1-Read_Write | 读写 | powerSupplySide(1), loadSide(2), unknown(255) | [电源侧=1]/[负载侧=2] | CT location of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate power supply side Value 2 indicate load side
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.88 | hwPDUSinexcelsvg100NetworkWiringConfiguration | Network wiring configuration | 三相三线/三相四线制 | 1-Read_Write | 读写 | threePhaseFourWireSystem(1), threePhaseThreeWireSystem(2), unknown(255) | [三相四线制=1]/[三相三线制=2] | Network wiring configuration of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate three-phase four-wire system Value 2 indicate three-phase three-wire system
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.89 | hwPDUSinexcelsvg100CtSecondaryWiring | CT secondary wiring | CT副边接线方式 | 1-Read_Write | 读写 | tandem(1), parallel(2), unknown(255) | [串联=1]/[并联=2] | CT secondary wiring of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate tandem Value 2 indicate parallel
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.90 | hwPDUSinexcelsvg100InductanceCurrentCalibrationProcess | Inductance current calibration process | 电感电流校准进程 | 1-Read_Write | 读写 | capacitiveCurrentCalibration(1), inductiveCurrentCalibration(2), unknown(255) | [容性电流校准=1]/[感性电流校准=2] | Inductance current calibration process of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate capacitive current calibration Value 2 indicate inductive current calibration
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.91 | hwPDUSinexcelsvg100InputFrequencyLevel | Input frequency level | 输入频率等级 | 1-Read_Write | 读写 | fiftyHz(1), sixtyHz(2), unknown(255) | [50Hz=1]/[60Hz=2] | Input frequency level of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate 50hz Value 2 indicate 60hz
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.92 | hwPDUSinexcelsvg100PplEnable | PPL enable | 锁相环使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [不使能=1]/[使能=2] | PPL enable of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.93 | hwPDUSinexcelsvg100InputCurrentAbnormalEnable | Input current abnormal enable | 输入电流异常使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [不使能=1]/[使能=2] | Input current abnormal enable of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.94 | hwPDUSinexcelsvg100TemperatureDeratingEnable | Temperature derating enable | 温度降额 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Temperature derating enable of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.95 | hwPDUSinexcelsvg100CapacitiveReactivePowerCompensationEnable | Capacitive reactive power compensation enable | 补偿容性无功 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Capacitive reactive power compensation enable of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.96 | hwPDUSinexcelsvg100GridVoltageAdjustmentEnable | Grid voltage adjustment enable | 电网电压调节使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Grid voltage adjustment enable of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.97 | hwPDUSinexcelsvg100TargetVoltage | Target voltage | 电压目标值 | 1-Read_Write | 读写 | 1000..7000 | 1000..7000 | Target voltage of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.98 | hwPDUSinexcelsvg100ConstantReactive | Constant reactive | 无功设置值 | 1-Read_Write | 读写 | -30000..30000 | -30000..30000 | Constant reactive of the device config table for the PDU-Sinexcel-svg100.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.99 | hwPDUSinexcelsvg100VoltageUpperLimit | Voltage upper limit | 调压上限 | 1-Read_Write | 读写 | -20..20 | -20..20 | Voltage upper limit of the device config table for the PDU-Sinexcel-svg100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.100 | hwPDUSinexcelsvg100VoltageLowerLimit | Voltage lower limit | 调压下限 | 1-Read_Write | 读写 | -20..20 | -20..20 | Voltage lower limit of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.101 | hwPDUSinexcelsvg100ThduLimit | THDu limit | THDU限值 | 1-Read_Write | 读写 | 0..50 | 0..50 | THDu limit of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.102 | hwPDUSinexcelsvg100UnbalanceLimit | Unbalance limit | 不平衡度限值 | 1-Read_Write | 读写 | 0..1 | 0..1 | Unbalance limit of the device config table for the PDU-Sinexcel-svg100.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.103 | hwPDUSinexcelsvg100ReactivePowerTrackingControlValue | Reactive power tracking control value | 无功跟踪控制值 | 1-Read_Write | 读写 | -30000..30000 | -30000..30000 | Reactive power tracking control value of the device config table for the PDU-Sinexcel-svg100.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.104 | hwPDUSinexcelsvg100LowLoadEnergySavingShutdownMode | Low load energy-saving shutdown mode | 低载节能关机模式设定值 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | Low load energy-saving shutdown mode of the device config table for the PDU-Sinexcel-svg100.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.105 | hwPDUSinexcelsvg100ClearFault | Clear fault | 清除故障 | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear fault of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.106 | hwPDUSinexcelsvg100PowerOn | Power on | 开机 | 1-Read_Write | 读写 | yes(1) | [是=1] | Power on of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.107 | hwPDUSinexcelsvg100PowerOff | Power off | 关机 | 1-Read_Write | 读写 | yes(1) | [是=1] | Power off of the device config table for the PDU-Sinexcel-svg100. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.16.1.1.300 | hwPDUSinexcelsvg100RunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PDU-Sinexcel-svg100.

## Feeder Cabinet
馈线柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.10 | FeederCabinet | Feeder Cabinet | 馈线柜 | / | / | / | / | Feeder Cabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1 | hwFeederCabinetRunning1Table | / | / |  |  | / | / | The running table of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.1 | hwFeederCabinetRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.2 | hwFeederCabinetL1PhaseVoltage | L1 phase voltage | L1相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 phase voltage of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.3 | hwFeederCabinetCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Feeder Cabinet. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.4 | hwFeederCabinetELabel | / | / | 0-Read_Only | 只读 | 0..2048 | / | E-label of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.5 | hwFeederCabinetSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.6 | hwFeederCabinetHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.7 | hwFeederCabinetL2PhaseVoltage | L2 phase voltage | L2相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 phase voltage of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.8 | hwFeederCabinetL3PhaseVoltage | L3 phase voltage | L3相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 phase voltage of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.9 | hwFeederCabinetL1L2LineVoltage | L1-L2 line voltage | L1-L2线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1-L2 line voltage of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.10 | hwFeederCabinetL2L3LineVoltage | L2-L3 line voltage | L2-L3线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2-L3 line voltage of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.11 | hwFeederCabinetL3L1LineVoltage | L3-L1 line voltage | L3-L1线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3-L1 line voltage of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.12 | hwFeederCabinetNPeVoltage | N-PE voltage | N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | N-PE voltage of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.13 | hwFeederCabinetL1Current | L1 current | L1电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L1 current of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.14 | hwFeederCabinetL2Current | L2 current | L2电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L2 current of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.15 | hwFeederCabinetL3Current | L3 current | L3电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L3 current of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.16 | hwFeederCabinetFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Frequency of the device config table for the Feeder Cabinet.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.17 | hwFeederCabinetL1ActivePower | L1 active power | L1有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 active power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.18 | hwFeederCabinetL2ActivePower | L2 active power | L2有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 active power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.19 | hwFeederCabinetL3ActivePower | L3 active power | L3有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 active power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.20 | hwFeederCabinetL1ApparentPower | L1 apparent power | L1视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 apparent power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.21 | hwFeederCabinetL2ApparentPower | L2 apparent power | L2视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 apparent power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.22 | hwFeederCabinetL3ApparentPower | L3 apparent power | L3视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 apparent power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.23 | hwFeederCabinetL1ReactivePower | L1 reactive power | L1无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 reactive power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.24 | hwFeederCabinetL2ReactivePower | L2 reactive power | L2无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 reactive power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.25 | hwFeederCabinetL3ReactivePower | L3 reactive power | L3无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 reactive power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.26 | hwFeederCabinetL1LoadRatio | L1 load ratio | L1负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L1 load ratio of the device config table for the Feeder Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.27 | hwFeederCabinetL2LoadRatio | L2 load ratio | L2负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L2 load ratio of the device config table for the Feeder Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.28 | hwFeederCabinetL3LoadRatio | L3 load ratio | L3负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L3 load ratio of the device config table for the Feeder Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.29 | hwFeederCabinetL1ThdU | L1 THD-u | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-u of the device config table for the Feeder Cabinet.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.30 | hwFeederCabinetL2ThdU | L2 THD-u | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-u of the device config table for the Feeder Cabinet.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.31 | hwFeederCabinetL3ThdU | L3 THD-u | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-u of the device config table for the Feeder Cabinet.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.32 | hwFeederCabinetL1ThdI | L1 THD-i | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-i of the device config table for the Feeder Cabinet.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.33 | hwFeederCabinetL2ThdI | L2 THD-i | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-i of the device config table for the Feeder Cabinet.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.34 | hwFeederCabinetL3ThdI | L3 THD-i | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-i of the device config table for the Feeder Cabinet.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.35 | hwFeederCabinetTotalActivePower | Total active power | 总有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total active power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.36 | hwFeederCabinetTotalApparentPower | Total apparent power | 总视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total apparent power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.37 | hwFeederCabinetTotalReactivePower | Total reactive power | 总无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total reactive power of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.38 | hwFeederCabinetTotalActiveEnergy | Total active energy | 总有功电能 | 0-Read_Only | 只读 | 0..4290000000 | 0..4290000000 | Total active energy of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.39 | hwFeederCabinetTotalLoadRatio | Total load ratio | 总负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | Total load ratio of the device config table for the Feeder Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.40 | hwFeederCabinetSwitchNumber | Switch number | 开关数目 | 0-Read_Only | 只读 | 1..18 | 1..18 | Switch number of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.41 | hwFeederCabinetL1Input1CopperBarTemperature | Input 1 L1 copper bar temperature | 输入1 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 1 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.42 | hwFeederCabinetL2Input1CopperBarTemperature | Input 1 L2 copper bar temperature | 输入1 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 1 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.43 | hwFeederCabinetL3Input1CopperBarTemperature | Input 1 L3 copper bar temperature | 输入1 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 1 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.44 | hwFeederCabinetCopperBarEnvironmentTemperature | Copper bar environment temperature | 铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Copper bar environment temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.45 | hwFeederCabinetL1Input1PredictedCopperBarTemperature | Input 1 L1 predicted copper bar temperature | 输入1 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 1 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.46 | hwFeederCabinetL2Input1PredictedCopperBarTemperature | Input 1 L2 predicted copper bar temperature | 输入1 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 1 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.47 | hwFeederCabinetL3Input1PredictedCopperBarTemperature | Input 1 L3 predicted copper bar temperature | 输入1 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 1 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.48 | hwFeederCabinetNInput1CopperBarTemperature | Input 1 N copper bar temperature | 输入1 N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | N input 1 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.49 | hwFeederCabinetRunningIndicatorStatus | Running indicator status | 运行灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Running indicator status of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.50 | hwFeederCabinetAlarmIndicatorStatus | Alarm indicator status | 告警灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Alarm indicator status of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.51 | hwFeederCabinetMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.52 | hwFeederCabinetIp | IP | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IP of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.53 | hwFeederCabinetEsn | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.54 | hwFeederCabinetLightningProtectionStatus | Lightning protection status | 防雷器状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [正常=1]/[异常=2] | Lightning protection status of the device config table for the Feeder Cabinet. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.55 | hwFeederCabinetDetailModel | Detail model | 详细机型 | 0-Read_Only | 只读 | feederCabinet(1), lowVoltageCabinet(2), unknown(255) | [馈线柜=1]/[低压柜=2] | Detail model of the device config table for the Feeder Cabinet. Value 1 indicate feeder cabinet Value 2 indicate low voltage cabinet
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.56 | hwFeederCabinetM3SoftwareVersion | Main control board M3 software version | 主控板M3软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Main control board M3 software version of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.57 | hwFeederCabinetTotalReactiveEnery | Total reactive energy | 总无功电能 | 0-Read_Only | 只读 | 0..4290000000 | 0..4290000000 | Total reactive energy of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.9.10.1.1.101 | hwFeederCabinetRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2 | hwFeederCabinetConfig1Table | / | / |  |  | / | / | The config table of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.1 | hwFeederCabinetConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.2 | hwFeederCabinetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.3 | hwFeederCabinetOpenPhaseThreshold | Open phase threshold | 缺相告警阈值 | 1-Read_Write | 读写 | 0..60 | 0..60 | Open phase threshold of the device config table for the Feeder Cabinet.SigUnitInfo:V.
| [Nouse]hwFeederCabinetHarmonicAlarm | Harmonic alarm | 谐波告警 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Harmonic alarm of the device config table for the Feeder Cabinet. Value 1 indicate forbid Value 2 indicate enabled
| [Nouse]hwFeederCabinetVoltageHarmonicAlarmThreshold | Voltage harmonic alarm threshold | 电压谐波告警阈值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Voltage harmonic alarm threshold of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:%.
| [Nouse]hwFeederCabinetCurrentHarmonicAlarmThreshold | Current harmonic alarm threshold | 电流谐波告警阈值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Current harmonic alarm threshold of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.7 | hwFeederCabinetOvervoltageThreshold | Overvoltage threshold | 过压告警阈值 | 1-Read_Write | 读写 | 1050..1300 | 1050..1300 | Overvoltage threshold of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.8 | hwFeederCabinetOvervoltageAcknowledgeTime | Overvoltage acknowledge time | 过压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overvoltage acknowledge time of the device config table for the Feeder Cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.9 | hwFeederCabinetUndervoltageThreshold | Undervoltage threshold | 欠压告警阈值 | 1-Read_Write | 读写 | 750..950 | 750..950 | Undervoltage threshold of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.10 | hwFeederCabinetUndervoltageAcknowledgeTime | Undervoltage acknowledge time | 欠压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Undervoltage acknowledge time of the device config table for the Feeder Cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.11 | hwFeederCabinetOverloadThreshold | Overload threshold | 负载过载阈值 | 1-Read_Write | 读写 | 100..120 | 100..120 | Overload threshold of the device config table for the Feeder Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.12 | hwFeederCabinetOverloadAcknowledgeTime | Overload acknowledge time | 负载过载确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overload acknowledge time of the device config table for the Feeder Cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.13 | hwFeederCabinetOverfrequencyThreshold | Overfrequency threshold | 频率越限阈值 | 1-Read_Write | 读写 | 10..100 | 10..100 | Overfrequency threshold of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.14 | hwFeederCabinetOverfrequencyAcknowledgeTime | Overfrequency acknowledge time | 频率越限确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overfrequency acknowledge time of the device config table for the Feeder Cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.15 | hwFeederCabinetThreePhaseLoadImbalance | Three-phase load imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..50 | 0..50 | Three-phase load imbalance of the device config table for the Feeder Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.16 | hwFeederCabinetOvercurrentThreshold | Overcurrent threshold | 电流高阈值 | 1-Read_Write | 读写 | 40..100 | 40..100 | Overcurrent threshold of the device config table for the Feeder Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.17 | hwFeederCabinetUndercurrentThreshold | Undercurrent threshold | 电流低阈值 | 1-Read_Write | 读写 | 30..80 | 30..80 | Undercurrent threshold of the device config table for the Feeder Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.19 | hwFeederCabinetBranchMonitoringBoardDoAssociatedAlarm | Branch monitoring board DO associated alarm | 支路监控板DO关联告警 | 1-Read_Write | 读写 | none(1), switchOpen(2), overTemperature(3), overCurrent(4), switchTrip(5), unknown(255) | [无=1]/[开关断开=2]/[过温=3]/[过流=4]/[开关脱扣=5] | Branch monitoring board DO associated alarm of the device config table for the Feeder Cabinet. Value 1 indicate none Value 2 indicate switch open Value 3 indicate overtemperature Value 4 indicate overcurrent Value 5 indicate switch trip
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.20 | hwFeederCabinetLightningProtection | Lightning protection | 防雷器 | 1-Read_Write | 读写 | none(1), have(2), unknown(255) | [无=1]/[有=2] | Lightning protection of the device config table for the Feeder Cabinet. Value 1 indicate none Value 2 indicate have
1.3.6.1.4.1.2011.6.178.1.1.9.10.2.1.101 | hwFeederCabinetConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3 | hwFeederCabinetRunning2Table | / | / |  |  | / | / | The running table of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.1 | hwFeederCabinetRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Feeder Cabinet.
| [Nouse]hwFeederCabinetMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 1..28 | 1..28 | MACAddress of the device running table for the Feeder Cabinet
| [Nouse]hwFeederCabinetIP | IP | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IPAddress of the device running table for the Feeder Cabinet
| [Nouse]hwFeederCabinetESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.5 | hwFeederCabinetL1Input2CopperBarTemperature | Input 2 L1 copper bar temperature | 输入2 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 2 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.6 | hwFeederCabinetL2Input2CopperBarTemperature | Input 2 L2 copper bar temperature | 输入2 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 2 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.7 | hwFeederCabinetL3Input2CopperBarTemperature | Input 2 L3 copper bar temperature | 输入2 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 2 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.8 | hwFeederCabinetL1Output1CopperBarTemperature | Output 1 L1 copper bar temperature | 输出1 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 1 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.9 | hwFeederCabinetL2Output1CopperBarTemperature | Output 1 L2 copper bar temperature | 输出1 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 1 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.10 | hwFeederCabinetL3Output1CopperBarTemperature | Output 1 L3 copper bar temperature | 输出1 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 1 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.11 | hwFeederCabinetNOutput1CopperBarTemperature | Output 1 N copper bar temperature | 输出1 N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | N output 1 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.12 | hwFeederCabinetL1Output2CopperBarTemperature | Output 2 L1 copper bar temperature | 输出2 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 2 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.13 | hwFeederCabinetL2Output2CopperBarTemperature | Output 2 L2 copper bar temperature | 输出2 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 2 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.14 | hwFeederCabinetL3Output2CopperBarTemperature | Output 2 L3 copper bar temperature | 输出2 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 2 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.15 | hwFeederCabinetNOutput2CopperBarTemperature | Output 2 N copper bar temperature | 输出2 N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | N output 2 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.16 | hwFeederCabinetL1Input2PredictedCopperBarTemperature | Input 2 L1 predicted copper bar temperature | 输入2 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 2 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.17 | hwFeederCabinetL2Input2PredictedCopperBarTemperature | Input 2 L2 predicted copper bar temperature | 输入2 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 2 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.18 | hwFeederCabinetL3Input2PredictedCopperBarTemperature | Input 2 L3 predicted copper bar temperature | 输入2 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 2 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.19 | hwFeederCabinetL1Output1PredictedCopperBarTemperature | Output 1 L1 predicted copper bar temperature | 输出1 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 1 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.20 | hwFeederCabinetL2Output1PredictedCopperBarTemperature | Output 1 L2 predicted copper bar temperature | 输出1 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 1 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.21 | hwFeederCabinetL3Output1PredictedCopperBarTemperature | Output 1 L3 predicted copper bar temperature | 输出1 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 1 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.22 | hwFeederCabinetL1Output2PredictedCopperBarTemperature | Output 2 L1 predicted copper bar temperature | 输出2 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 2 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.23 | hwFeederCabinetL2Output2PredictedCopperBarTemperature | Output 2 L2 predicted copper bar temperature | 输出2 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 2 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.24 | hwFeederCabinetL3Output2PredictedCopperBarTemperature | Output 2 L3 predicted copper bar temperature | 输出2 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 2 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.25 | hwFeederCabinetNInput2CopperBarTemperature | Output 2 N copper bar temperature | 输入2 N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | N input 2 copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.26 | hwFeederCabinetL1Input3CopperBarTemperature | Input 3 L1 copper bar temperature | 输入3 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 3 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.27 | hwFeederCabinetL2Input3CopperBarTemperature | Input 3 L2 copper bar temperature | 输入3 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 3 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.28 | hwFeederCabinetL3Input3CopperBarTemperature | Input 3 L3 copper bar temperature | 输入3 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 3 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.29 | hwFeederCabinetL1Output3CopperBarTemperature | Output 3 L1 copper bar temperature | 输出3 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 3 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.30 | hwFeederCabinetL2Output3CopperBarTemperature | Output 3 L2 copper bar temperature | 输出3 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 3 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.31 | hwFeederCabinetL3Output3CopperBarTemperature | Output 3 L3 copper bar temperature | 输出3 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 3 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.32 | hwFeederCabinetL1Input4CopperBarTemperature | Input 4 L1 copper bar temperature | 输入4 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 4 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.33 | hwFeederCabinetL2Input4CopperBarTemperature | Input 4 L2 copper bar temperature | 输入4 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 4 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.34 | hwFeederCabinetL3Input4CopperBarTemperature | Input 4 L3 copper bar temperature | 输入4 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 4 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.35 | hwFeederCabinetL1Output4CopperBarTemperature | Output 4 L1 copper bar temperature | 输出4 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 4 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.36 | hwFeederCabinetL2Output4CopperBarTemperature | Output 4 L2 copper bar temperature | 输出4 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 4 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.37 | hwFeederCabinetL3Output4CopperBarTemperature | Output 4 L3 copper bar temperature | 输出4 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 4 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.38 | hwFeederCabinetL1Input5CopperBarTemperature | Input 5 L1 copper bar temperature | 输入5 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 5 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.39 | hwFeederCabinetL2Input5CopperBarTemperature | Input 5 L2 copper bar temperature | 输入5 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 5 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.40 | hwFeederCabinetL3Input5CopperBarTemperature | Input 5 L3 copper bar temperature | 输入5 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 5 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.41 | hwFeederCabinetL1Output5CopperBarTemperature | Output 5 L1 copper bar temperature | 输出5 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 5 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.42 | hwFeederCabinetL2Output5CopperBarTemperature | Output 5 L2 copper bar temperature | 输出5 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 5 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.43 | hwFeederCabinetL3Output5CopperBarTemperature | Output 5 L3 copper bar temperature | 输出5 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 5 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.44 | hwFeederCabinetL1Input6CopperBarTemperature | Input 6 L1 copper bar temperature | 输入6 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 6 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.45 | hwFeederCabinetL2Input6CopperBarTemperature | Input 6 L2 copper bar temperature | 输入6 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 6 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.46 | hwFeederCabinetL3Input6CopperBarTemperature | Input 6 L3 copper bar temperature | 输入6 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 6 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.47 | hwFeederCabinetL1Output6CopperBarTemperature | Output 6 L1 copper bar temperature | 输出6 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 6 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.48 | hwFeederCabinetL2Output6CopperBarTemperature | Output 6 L2 copper bar temperature | 输出6 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 6 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.49 | hwFeederCabinetL3Output6CopperBarTemperature | Output 6 L3 copper bar temperature | 输出6 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 6 predicted copper bar temperature of the device config table for the Feeder Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.10.3.1.101 | hwFeederCabinetRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.4 | hwFeederCabinetConfig2Table | / | / |  |  | / | / | The config table of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.4.1.1 | hwFeederCabinetConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.4.1.2 | hwFeederCabinetSetBranchMonitoringBoardDoAssociatedAlarm | Branch monitoring board DO associated alarm | 支路监控板DO关联告警 | 1-Read_Write | 读写 | none(1), switchOpen(2), overTemperature(3), overCurrent(4), switchTrip(5), unknown(255) | [无=1]/[开关断开=2]/[过温=3]/[过流=4]/[开关脱扣=5] | Branch monitoring board DO associated alarm of the device config table for the Feeder Cabinet. Value 1 indicate none Value 2 indicate switch open Value 3 indicate overtemperature Value 4 indicate overcurrent Value 5 indicate switch trip
1.3.6.1.4.1.2011.6.178.1.1.9.10.4.1.101 | hwFeederCabinetConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.5 | hwFeederCabinetConfig3Table | / | / |  |  | / | / | The config table of Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.5.1.1 | hwFeederCabinetConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Feeder Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.10.5.1.2 | hwFeederCabinetSetClearFaults | Clear faults | 故障清除 | 1-Read_Write | 读写 | effective(1), unknown(255) | [有效=1] | Clear faults of the device config table for the Feeder Cabinet. Value 1 indicate effective
1.3.6.1.4.1.2011.6.178.1.1.9.10.5.1.101 | hwFeederCabinetConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Feeder Cabinet.

## Feeder cabinet switch
馈线柜开关
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.11 | Feedercabinetswitch | Feeder cabinet switch | 馈线柜开关 | / | / | / | / | Feeder cabinet switch Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1 | hwFeedercabinetswitchRunning1Table | / | / |  |  | / | / | The running table of Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.1 | hwFeedercabinetswitchRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.2 | hwFeedercabinetswitchL1Current | L1 current | L1电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L1 current of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.3 | hwFeedercabinetswitchL2Current | L2 current | L2电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L2 current of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.4 | hwFeedercabinetswitchL3Current | L3 current | L3电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L3 current of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.5 | hwFeedercabinetswitchNCurrent | N current | N线电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | N current of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.6 | hwFeedercabinetswitchL1ActivePower | L1 active power | L1有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 active power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.7 | hwFeedercabinetswitchL2ActivePower | L2 active power | L2有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 active power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.8 | hwFeedercabinetswitchL3ActivePower | L3 active power | L3有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 active power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.9 | hwFeedercabinetswitchL1ApparentPower | L1 apparent power | L1视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 apparent power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.10 | hwFeedercabinetswitchL2ApparentPower | L2 apparent power | L2视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 apparent power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.11 | hwFeedercabinetswitchL3ApparentPower | L3 apparent power | L3视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 apparent power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.12 | hwFeedercabinetswitchL1ReactivePower | L1 reactive power | L1无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 reactive power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.13 | hwFeedercabinetswitchL2ReactivePower | L2 reactive power | L2无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 reactive power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.14 | hwFeedercabinetswitchL3ReactivePower | L3 reactive power | L3无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 reactive power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.15 | hwFeedercabinetswitchL1PowerFactor | L1 power factor | L1功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L1 power factor of the device config table for the Feeder cabinet switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.16 | hwFeedercabinetswitchL2PowerFactor | L2 power factor | L2功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L2 power factor of the device config table for the Feeder cabinet switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.17 | hwFeedercabinetswitchL3PowerFactor | L3 power factor | L3功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L3 power factor of the device config table for the Feeder cabinet switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.18 | hwFeedercabinetswitchActiveEnergy | Active energy | 有功电能 | 0-Read_Only | 只读 | 0..4290000000 | 0..4290000000 | Active energy of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.19 | hwFeedercabinetswitchL1LoadRatio | L1 load ratio | L1负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L1 load ratio of the device config table for the Feeder cabinet switch.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.20 | hwFeedercabinetswitchL2LoadRatio | L2 load ratio | L2负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L2 load ratio of the device config table for the Feeder cabinet switch.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.21 | hwFeedercabinetswitchL3LoadRatio | L3 load ratio | L3负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L3 load ratio of the device config table for the Feeder cabinet switch.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.34 | hwFeedercabinetswitchL1ThdI | L1 THD-i | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-u of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.35 | hwFeedercabinetswitchL2ThdI | L2 THD-i | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-u of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.36 | hwFeedercabinetswitchL3ThdI | L3 THD-i | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-u of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.37 | hwFeedercabinetswitchL1fifthThdI | L1 5th THD-i | L1 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.38 | hwFeedercabinetswitchL2fifthThdI | L2 5th THD-i | L2 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.39 | hwFeedercabinetswitchL3fifthThdI | L3 5th THD-i | L3 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.40 | hwFeedercabinetswitchL1seventhThdI | L1 7th THD-i | L1 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.41 | hwFeedercabinetswitchL2seventhThdI | L2 7th THD-i | L2 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.42 | hwFeedercabinetswitchL3seventhThdI | L3 7th THD-i | L3 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.43 | hwFeedercabinetswitchL1eleventhThdI | L1 11th THD-i | L1 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.44 | hwFeedercabinetswitchL2eleventhThdI | L2 11th THD-i | L2 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.45 | hwFeedercabinetswitchL3eleventhThdI | L3 11th THD-i | L3 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-i of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.46 | hwFeedercabinetswitchTotalOutputActivePower | Total output active power | 总输出有功功率 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Total output active power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.47 | hwFeedercabinetswitchTotalOutputApparentPower | Total output apparent power | 总输出视在功率 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Total output apparent power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.48 | hwFeedercabinetswitchTotalOutputReactivePower | Total output reactive power | 总输出无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output reactive power of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.49 | hwFeedercabinetswitchL1InputCopperBarTemperature | Input L1 copper bar temperature | 输入 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.50 | hwFeedercabinetswitchL2InputCopperBarTemperature | Input L2 copper bar temperature | 输入 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.51 | hwFeedercabinetswitchL3InputCopperBarTemperature | Input L3 copper bar temperature | 输入 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.52 | hwFeedercabinetswitchL1OutputCopperBarTemperature | Output L1 copper bar temperature | 输出 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.53 | hwFeedercabinetswitchL2OutputCopperBarTemperature | Output L2 copper bar temperature | 输出 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.54 | hwFeedercabinetswitchL3OutputCopperBarTemperature | Output L3 copper bar temperature | 输出 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.55 | hwFeedercabinetswitchCopperBarEnvironmentTemperature | Copper bar environment temperature | 铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Copper bar environment temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.56 | hwFeedercabinetswitchL1OutputPredictedCopperBarTemperature | Output L1 predicted copper bar temperature | 输出 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output predicted copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.57 | hwFeedercabinetswitchL2OutputPredictedCopperBarTemperature | Output L2 predicted copper bar temperature | 输出 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output predicted copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.58 | hwFeedercabinetswitchL3OutputPredictedCopperBarTemperature | Output L3 predicted copper bar temperature | 输出 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output predicted copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.59 | hwFeedercabinetswitchSwitchStatus | Switch status | 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Switch status of the device config table for the Feeder cabinet switch. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.60 | hwFeedercabinetswitchTrippingStatus | Tripping status | 脱扣状态 | 0-Read_Only | 只读 | normal(1), tripping(2), unknown(255) | [正常=1]/[脱扣=2] | Tripping status of the device config table for the Feeder cabinet switch. Value 1 indicate normal Value 2 indicate tripping
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.61 | hwFeedercabinetswitchCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Feeder cabinet switch. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.62 | hwFeedercabinetswitchSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.63 | hwFeedercabinetswitchHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.64 | hwFeedercabinetswitchRunningIndicatorStatus | Running indicator status | 运行灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Running indicator status of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.65 | hwFeedercabinetswitchAlarmIndicatorStatus | Alarm indicator status | 告警灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Alarm indicator status of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.66 | hwFeedercabinetswitchACInputSwitchIndicator | AC input switch indicator | AC输入开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC input switch indicator of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.67 | hwFeedercabinetswitchACOutputSwitchIndicator | AC output switch indicator | AC输出开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC output switch indicator of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.68 | hwFeedercabinetswitchM3SoftwareVersion | Tributary board M3 software version | 支路板M3软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Tributary board M3 software version of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.69 | hwFeedercabinetswitchTotalReactiveEnery | Total reactive energy | 总无功电能 | 0-Read_Only | 只读 | 0..4290000000 | 0..4290000000 | Total reactive energy of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.70 | hwFeedercabinetswitchEsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the Feeder Cabinet Switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.71 | hwFeedercabinetMccbOutputL1JointSwitchBarTemp | Output L1 joint switch copper bar temperature | 输出L1开关连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output L1 joint switch copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.72 | hwFeedercabinetMccbOutputL2JointSwitchBarTemp | Output L2 joint switch copper bar temperature | 输出L2开关连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output L2 joint switch copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.73 | hwFeedercabinetMccbOutputL3JointSwitchBarTemp | Output L3 joint switch copper bar temperature | 输出L3开关连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output L3 joint switch copper bar temperature of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.74 | hwFeedercabinetMccbAmbientTempInside | Ambient temperature inside | 开关内环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Ambient temperature inside of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.75 | hwFeedercabinetMccbHealthDegree | Health degree | 健康度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Health degree of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.76 | hwFeedercabinetMccbSerialnumber | Serial number | 断路器序列号 | 0-Read_Only | 只读 | 0..16 | 0..16 | Serial number of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.77 | hwFeedercabinetEarthCurrent | Earth current | 地线电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | Earth current of the device config table for the Feeder cabinet switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.11.1.1.101 | hwFeedercabinetswitchRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2 | hwFeedercabinetswitchConfig1Table | / | / |  |  | / | / | The config table of Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.1 | hwFeedercabinetswitchConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.2 | hwFeedercabinetswitchDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Feeder cabinet switch.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.3 | hwFeedercabinetswitchRateCurrent | Rate current | 额定电流设置 | 1-Read_Write | 读写 | 63..6300 | 63..6300 | Rate current of the device config table for the Feeder cabinet switch.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.4 | hwFeedercabinetswitchTripUnitType | Trip unit type | 脱扣器类型 | 1-Read_Write | 读写 | e(1), tm(2), unknown(255) | [E=1]/[TM=2] | Trip unit type of the device config table for the Feeder cabinet switch. Value 1 indicate e Value 2 indicate tm
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.5 | hwFeedercabinetswitchTripUnitModel | Trip unit model | 脱扣器型号 | 1-Read_Write | 读写 | ekipDipLsOrI(1), ekipDipLsi(2), ekipTouchLsi(3), ekipHiAndTouchLsi(4), tma(5), tmd(6), unknown(255) | [Ekip dip ls/I=1]/[Ekip dip lsi=2]/[Ekip touch lsi=3]/[Ekip hi-touch lsi=4]/[TMA=5]/[TMD=6] | Trip unit model of the device config table for the Feeder cabinet switch. Value 1 indicate ekip dip ls/i Value 2 indicate ekip dip lsi Value 3 indicate ekip touch lsi Value 4 indicate ekip hi-touch lsi Value 5 indicate tma Value 6 indicate tmd
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.6 | hwFeedercabinetswitchProtectionMode | Protection mode | 保护模式 | 1-Read_Write | 读写 | lsi(1), ls(2), li(3), unknown(255) | [LSI=1]/[LS=2]/[LI=3] | Protection mode of the device config table for the Feeder cabinet switch. Value 1 indicate lsi Value 2 indicate ls Value 3 indicate li
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.12 | hwFeedercabinetswitchDiscriminativeProtection | Discriminative protection | 是否实现选择性保护 | 1-Read_Write | 读写 | yes(1), no(2), unknown(255) | [是=1]/[否=2] | Discriminative protection of the device config table for the Feeder cabinet switch. Value 1 indicate yes Value 2 indicate no
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.13 | hwFeedercabinetswitchBreakerModel | Breaker model | 断路器型号 | 1-Read_Write | 读写 | tmaxt1(1), tmaxt2(2), tmaxt3(3), tmaxt4(4), tmaxt5(5), tmaxt6(6), tmaxxt1(7), tmaxxt2(8), tmaxxt3(9), tmaxxt4(10), tmaxxt5(11), tmaxxt6(12), tmaxxt7(13), tmaxxt7m(14), emax2e1point2(15), emax2e2point2(16), emax2e4point2(17), emax2e6point2(18), unknown(255) | [Tmax T1=1]/[Tmax T2=2]/[Tmax T3=3]/[Tmax T4=4]/[Tmax T5=5]/[Tmax T6=6]/[Tmax XT1=7]/[Tmax XT2=8]/[Tmax XT3=9]/[Tmax XT4=10]/[Tmax XT5=11]/[Tmax XT6=12]/[Tmax XT7=13]/[Tmax XT7m=14]/[Emax2 E1.2=15]/[Emax2 E2.2=16]/[Emax2 E4.2=17]/[Emax2 E6.2=18] | Breaker model of the device config table for the Feeder cabinet switch. Value 1 indicate tmaxt1 Value 2 indicate tmaxt2 Value 3 indicate tmaxt3 Value 4 indicate tmaxt4 Value 5 indicate tmaxt5 Value 6 indicate tmaxt6 Value 7 indicate tmaxxt1 Value 8 indicate tmaxxt2 Value 9 indicate tmaxxt3 Value 10 indicate tmaxxt4 Value 11 indicate tmaxxt5 Value 12 indicate tmaxxt6 Value 13 indicate tmaxxt7 Value 14 indicate tmaxxt7m Value 15 indicate emax2e1.2 Value 16 indicate emax2e2.2 Value 17 indicate emax2e4.2 Value 18 indicate emax2e6.2
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.14 | hwFeedercabinetswitchSwitchType | Switch type | 开关类型 | 1-Read_Write | 读写 | nocommunicationmodule(1), supportekipcom(2), unknown(255) | [无通讯模块=1]/[支持Ekip Com=2] | Switch type of the device config table for the Feeder cabinet switch. Value 1 indicate no communication module Value 2 indicate support ekip com
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.16 | hwFeedercabinetMccbProtectionMode | Protection mode | 保护模式 | 1-Read_Write | 读写 | sIsEnabledAndIIsDisabled(1), sIsDisabledAndIIsEnabled(2), bothSAndIAreEnabled(3), unknown(255) | [S使能和I不使能=1]/[S不使能和I使能=2]/[S和I都使能=3] | Protection mode of the device config table for the Feeder cabinet switch. Value 1 indicate S is enabled and I is disabled Value 2 indicate S is disabled and I is enabled Value 3 indicate Both S and I are enabled
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.17 | hwFeedercabinetMccbLongTimeDelayProtectionCurrentCoefficient | Long time delay protection current coefficient | 长延时保护电流系数 | 1-Read_Write | 读写 | 400..1000 | 400..1000 | Long time delay protection current coefficient of the device config table for the Feeder cabinet switch.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.18 | hwFeedercabinetMccbLongTimeDelayProtectionTime | Long time delay protection time | 长延时保护时间 | 1-Read_Write | 读写 | 300..4800 | 300..4800 | Long time delay protection time of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.19 | hwFeedercabinetMccbShortTimeDelayProtectionCurrentCoefficient | Short time delay protection current coefficient | 短延时保护电流系数 | 1-Read_Write | 读写 | 60..1000 | 60..1000 | Short time delay protection current coefficient of the device config table for the Feeder cabinet switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.20 | hwFeedercabinetMccbShortTimeDelayProtectionTime | Short time delay protection time | 短延时保护时间 | 1-Read_Write | 读写 | 5..50 | 5..50 | Short time delay protection time of the device config table for the Feeder cabinet switch.Multiple:100.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.21 | hwFeedercabinetMccbInstantaneousProtectionCurrent | Instantaneous protection current | 瞬时保护电流系数 | 1-Read_Write | 读写 | 150..1000 | 150..1000 | Instantaneous protection current of the device config table for the Feeder cabinet switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.11.2.1.101 | hwFeedercabinetswitchConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of LV switchgear switch.

## Low Voltage Cabinet
低压柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.12 | Lowvoltagecabinet | Low Voltage Cabinet | 低压柜 | / | / | / | / | Low voltage cabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1 | hwLowvoltagecabinetRunning1Table | / | / |  |  | / | / | The running table of Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.1 | hwLowvoltagecabinetRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.2 | hwLowvoltagecabinetL1Input1CopperBarTemperature | Input 1 L1 copper bar temperature | 输入1 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 1 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.3 | hwLowvoltagecabinetCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Low voltage cabinet. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.4 | hwLowvoltagecabinetELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.5 | hwLowvoltagecabinetSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.6 | hwLowvoltagecabinetHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.7 | hwLowvoltagecabinetL2Input1CopperBarTemperature | Input 1 L2 copper bar temperature | 输入1 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 1 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.8 | hwLowvoltagecabinetL3Input1CopperBarTemperature | Input 1 L3 copper bar temperature | 输入1 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 1 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.9 | hwLowvoltagecabinetL1Input2CopperBarTemperature | Input 2 L1 copper bar temperature | 输入2 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 2 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.10 | hwLowvoltagecabinetL2Input2CopperBarTemperature | Input 2 L2 copper bar temperature | 输入2 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 2 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.11 | hwLowvoltagecabinetL3Input2CopperBarTemperature | Input 2 L3 copper bar temperature | 输入2 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 2 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.12 | hwLowvoltagecabinetL1Output1CopperBarTemperature | Output 1 L1 copper bar temperature | 输出1 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 1 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.13 | hwLowvoltagecabinetL2Output1CopperBarTemperature | Output 1 L2 copper bar temperature | 输出1 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 1 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.14 | hwLowvoltagecabinetL3Output1CopperBarTemperature | Output 1 L3 copper bar temperature | 输出1 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 1 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.15 | hwLowvoltagecabinetNOutput1CopperBarTemperature | Output 1 N copper bar temperature | 输出1 N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | N output 1 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.16 | hwLowvoltagecabinetL1Output2CopperBarTemperature | Output 2 L1 copper bar temperature | 输出2 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 2 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.17 | hwLowvoltagecabinetL2Output2CopperBarTemperature | Output 2 L2 copper bar temperature | 输出2 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 2 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.18 | hwLowvoltagecabinetL3Output2CopperBarTemperature | Output 2 L3 copper bar temperature | 输出2 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 2 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.19 | hwLowvoltagecabinetCopperBarEnvironmentTemperature | Copper bar environment temperature | 铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Copper bar environment temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.20 | hwLowvoltagecabinetL1Input1PredictedCopperBarTemperature | Input 1 L1 predicted copper bar temperature | 输入1 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 1 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.21 | hwLowvoltagecabinetL2Input1PredictedCopperBarTemperature | Input 1 L2 predicted copper bar temperature | 输入1 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 1 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.22 | hwLowvoltagecabinetL3Input1PredictedCopperBarTemperature | Input 1 L3 predicted copper bar temperature | 输入1 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 1 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.23 | hwLowvoltagecabinetL1Input2PredictedCopperBarTemperature | Input 2 L1 predicted copper bar temperature | 输入2 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 2 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.24 | hwLowvoltagecabinetL2Input2PredictedCopperBarTemperature | Input 2 L2 predicted copper bar temperature | 输入2 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 2 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.25 | hwLowvoltagecabinetL3Input2PredictedCopperBarTemperature | Input 2 L3 predicted copper bar temperature | 输入2 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 2 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.26 | hwLowvoltagecabinetL1Output1PredictedCopperBarTemperature | Output 1 L1 predicted copper bar temperature | 输出1 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 1 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.27 | hwLowvoltagecabinetL2Output1PredictedCopperBarTemperature | Output 1 L2 predicted copper bar temperature | 输出1 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 1 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.28 | hwLowvoltagecabinetL3Output1PredictedCopperBarTemperature | Output 1 L3 predicted copper bar temperature | 输出1 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 1 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.29 | hwLowvoltagecabinetL1Output2PredictedCopperBarTemperature | Output 2 L1 predicted copper bar temperature | 输出2 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 2 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.30 | hwLowvoltagecabinetL2Output2PredictedCopperBarTemperature | Output 2 L2 predicted copper bar temperature | 输出2 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 2 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.31 | hwLowvoltagecabinetL3Output2PredictedCopperBarTemperature | Output 2 L3 predicted copper bar temperature | 输出2 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 2 predicted copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.32 | hwLowvoltagecabinetNInput1CopperBarTemperature | Input 1 N copper bar temperature | 输入1 N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | N input 1 copper bar temperature of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.33 | hwLowvoltagecabinetMAC | MAC | MAC地址 | 0-Read_Only | 只读 | 1..28 | 1..28 | MACAddress of the device running table for the low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.34 | hwLowvoltagecabinetIP | IP | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IPAddress of the device running table for the low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.35 | hwLowvoltagecabinetESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | the ESN. of Device.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.36 | hwLowvoltagecabinetDetailModel | Detail model | 详细机型 | 0-Read_Only | 只读 | incomingAndCouplerCabinet(1), mbsCabinet(2), upsInputAndBypassCabinet(3), upsOutputCabinet(4), feederCabinet(5), incomingCabinet(6), couplerCabinet(7), upsInputCabinet(8), upsOutputAndMbsCabinet(9), lvSwitchgear(10), lvSwitchgearMultiPhaseInputAndSinglePhaseOutput(11), lvFeederCabinet(12), upsInputCabinetAndTwoSwitches(13), upsOutputCabinetAndSingleSwitch(14), upsInputAndMBSCabinet(15), incomingCabinetAndTwoSwitches(16), mbsCabinetAndTwoSwitches(17), unknown(255) | [进线&母联柜=1]/[维修旁路柜=2]/[UPS输入&旁路柜=3]/[UPS输出柜=4]/[馈线柜=5]/[进线柜=6]/[母联柜=7]/[UPS输入柜=8]/[UPS输出&维修旁路柜=9]/[低压配电柜=10]/[低压配电柜-多进单出=11]/[低压馈线柜=12]/[UPS输入柜=13]/[UPS输出柜=14]/[UPS输入&维修旁路柜=15]/[进线柜=16]/[维修旁路柜=17] | Detail model of the device config table for the Low voltage cabinet. Value 1 indicate Incoming&Coupler cabinet Value 2 indicate MBS cabinet Value 3 indicate UPS input&Bypass cabinet Value 4 indicate UPS output cabinet Value 5 indicate Feeder cabinet Value 6 indicate Incoming cabinet Value 7 indicate Coupler cabinet Value 8 indicate UPS input cabinet Value 9 indicate UPS output&MBS cabinet Value 10 indicate LV switchgear Value 11 indicate LV switchgear multi phase input and single phase output Value 12 indicate LV feeder cabinet Value 13 indicate UPS input cabinet (two switches) Value 14 indicate UPS output cabinet (single switch) Value 15 indicate UPS input&MBS cabinet Value 16 indicate Incoming cabinet (two switches) Value 17 indicate MBS cabinet (two switches)
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.37 | hwLowvoltagecabinetRunningIndicatorStatus | Running indicator status | 运行灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Running indicator status of the device config table for the low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.38 | hwLowvoltagecabinetAlarmIndicatorStatus | Alarm indicator status | 告警灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Alarm indicator status of the device config table for the low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.39 | hwLowVoltageCabinetLightningProtectionStatus | Lightning protection status | 防雷器状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [正常=1]/[异常=2] | Lightning protection status of the device config table for the Low Voltage Cabinet. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.40 | hwLowvoltagecabinetM3SoftwareVersion | Main control board M3 software version | 主控板M3软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Main control board M3 software version of the device config table for the Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.41 | hwLowVoltageCabinetNOutput2CopperBarTemperature | Output 2 N copper bar temperature | 输出2 N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 2 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.42 | hwLowVoltageCabinetNInput2CopperBarTemperature | Input 2 N copper bar temperature | 输入2 N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | N input 2 copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.43 | hwLowVoltageCabinetL1Input3CopperBarTemperature | Input 3 L1 copper bar temperature | 输入3 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 3 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.44 | hwLowVoltageCabinetL2Input3CopperBarTemperature | Input 3 L2 copper bar temperature | 输入3 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 3 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.45 | hwLowVoltageCabinetL3Input3CopperBarTemperature | Input 3 L3 copper bar temperature | 输入3 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 3 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.46 | hwLowVoltageCabinetL1Output3CopperBarTemperature | Output 3 L1 copper bar temperature | 输出3 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 3 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.47 | hwLowVoltageCabinetL2Output3CopperBarTemperature | Output 3 L2 copper bar temperature | 输出3 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 3 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.48 | hwLowVoltageCabinetL3Output3CopperBarTemperature | Output 3 L3 copper bar temperature | 输出3 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 3 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.49 | hwLowVoltageCabinetL1Input4CopperBarTemperature | Input 4 L1 copper bar temperature | 输入4 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 4 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.50 | hwLowVoltageCabinetL2Input4CopperBarTemperature | Input 4 L2 copper bar temperature | 输入4 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 4 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.51 | hwLowVoltageCabinetL3Input4CopperBarTemperature | Input 4 L3 copper bar temperature | 输入4 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 4 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.52 | hwLowVoltageCabinetL1Output4CopperBarTemperature | Output 4 L1 copper bar temperature | 输出4 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 4 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.53 | hwLowVoltageCabinetL2Output4CopperBarTemperature | Output 4 L2 copper bar temperature | 输出4 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 4 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.54 | hwLowVoltageCabinetL3Output4CopperBarTemperature | Output 4 L3 copper bar temperature | 输出4 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 4 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.55 | hwLowVoltageCabinetL1Input5CopperBarTemperature | Input 5 L1 copper bar temperature | 输入5 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 5 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.56 | hwLowVoltageCabinetL2Input5CopperBarTemperature | Input 5 L2 copper bar temperature | 输入5 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 5 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.57 | hwLowVoltageCabinetL3Input5CopperBarTemperature | Input 5 L3 copper bar temperature | 输入5 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 5 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.58 | hwLowVoltageCabinetL1Output5CopperBarTemperature | Output 5 L1 copper bar temperature | 输出5 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 5 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.59 | hwLowVoltageCabinetL2Output5CopperBarTemperature | Output 5 L2 copper bar temperature | 输出5 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 5 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.60 | hwLowVoltageCabinetL3Output5CopperBarTemperature | Output 5 L3 copper bar temperature | 输出5 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 5 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.61 | hwLowVoltageCabinetL1Input6CopperBarTemperature | Input 6 L1 copper bar temperature | 输入6 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input 6 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.62 | hwLowVoltageCabinetL2Input6CopperBarTemperature | Input 6 L2 copper bar temperature | 输入6 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input 6 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.63 | hwLowVoltageCabinetL3Input6CopperBarTemperature | Input 6 L3 copper bar temperature | 输入6 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input 6 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.64 | hwLowVoltageCabinetL1Output6CopperBarTemperature | Output 6 L1 copper bar temperature | 输出6 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output 6 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.65 | hwLowVoltageCabinetL2Output6CopperBarTemperature | Output 6 L2 copper bar temperature | 输出6 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output 6 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.66 | hwLowVoltageCabinetL3Output6CopperBarTemperature | Output 6 L3 copper bar temperature | 输出6 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output 6 predicted copper bar temperature of the device config table for the Low Voltage Cabinet.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.12.1.1.101 | hwLowvoltagecabinetRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2 | hwLowvoltagecabinetConfig1Table | / | / |  |  | / | / | The config table of Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.1 | hwLowvoltagecabinetConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.2 | hwLowvoltagecabinetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Low voltage cabinet.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.3 | hwLowvoltagecabinetOpenPhaseThreshold | Open phase threshold | 缺相告警阈值 | 1-Read_Write | 读写 | 0..60 | 0..60 | Open phase threshold of the device config table for the Low voltage cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.7 | hwLowvoltagecabinetOvervoltageThreshold | Overvoltage threshold | 过压告警阈值 | 1-Read_Write | 读写 | 1050..1300 | 1050..1300 | Overvoltage threshold of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.8 | hwLowvoltagecabinetOvervoltageAcknowledgeTime | Overvoltage acknowledge time | 过压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overvoltage acknowledge time of the device config table for the Low voltage cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.9 | hwLowvoltagecabinetUndervoltageThreshold | Undervoltage threshold | 欠压告警阈值 | 1-Read_Write | 读写 | 750..950 | 750..950 | Undervoltage threshold of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.10 | hwLowvoltagecabinetUndervoltageAcknowledgeTime | Undervoltage acknowledge time | 欠压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Undervoltage acknowledge time of the device config table for the Low voltage cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.11 | hwLowvoltagecabinetOverloadThreshold | Overload threshold | 负载过载阈值 | 1-Read_Write | 读写 | 100..120 | 100..120 | Overload threshold of the device config table for the Low voltage cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.12 | hwLowvoltagecabinetOverloadAcknowledgeTime | Overload acknowledge time | 负载过载确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overload acknowledge time of the device config table for the Low voltage cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.13 | hwLowvoltagecabinetOverfrequencyThreshold | Overfrequency threshold | 频率越限阈值 | 1-Read_Write | 读写 | 10..100 | 10..100 | Overfrequency threshold of the device config table for the Low voltage cabinet.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.14 | hwLowvoltagecabinetOverfrequencyAcknowledgeTime | Overfrequency acknowledge time | 频率越限确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overfrequency acknowledge time of the device config table for the Low voltage cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.15 | hwLowvoltagecabinetThreePhaseLoadImbalance | Three-phase load imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..50 | 0..50 | Three-phase load imbalance of the device config table for the Low voltage cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.16 | hwLowvoltagecabinetOvercurrentThreshold | Overcurrent threshold | 电流高阈值 | 1-Read_Write | 读写 | 40..100 | 40..100 | Overcurrent threshold of the device config table for the Low voltage cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.17 | hwLowvoltagecabinetUndercurrentThreshold | Undercurrent threshold | 电流低阈值 | 1-Read_Write | 读写 | 30..80 | 30..80 | Undercurrent threshold of the device config table for the Low voltage cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.19 | hwLowVoltageCabinetBranchMonitoringBoardDoAssociatedAlarm | Branch monitoring board DO associated alarm | 支路监控板DO关联告警 | 1-Read_Write | 读写 | none(1), switchOpen(2), overTemperature(3), overCurrent(4), switchTrip(5), unknown(255) | [无=1]/[开关断开=2]/[过温=3]/[过流=4]/[开关脱扣=5] | Branch monitoring board DO associated alarm of the device config table for the Low Voltage Cabinet. Value 1 indicate none Value 2 indicate switch open Value 3 indicate overtemperature Value 4 indicate overcurrent Value 5 indicate switch trip
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.20 | hwLowVoltageCabinetLightningProtection | Lightning protection | 防雷器 | 1-Read_Write | 读写 | none(1), have(2), unknown(255) | [无=1]/[有=2] | Lightning protection of the device config table for the Low Voltage Cabinet. Value 1 indicate none Value 2 indicate have
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.21 | hwLowVoltageCabinetSetClearFaults | Clear faults | 故障清除 | 1-Read_Write | 读写 | effective(1), unknown(255) | [有效=1] | Clear faults of the device config table for the low Voltage Cabinet. Value 1 indicate effective
1.3.6.1.4.1.2011.6.178.1.1.9.12.2.1.101 | hwLowvoltagecabinetConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Low voltage cabinet.

## LV switchgear switch
低压柜开关
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.13 | LVswitchgearswitch | LV switchgear switch | 低压柜开关 | / | / | / | / | LV switchgear switch Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1 | hwLVswitchgearswitchRunning1Table | / | / |  |  | / | / | The running table of LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.1 | hwLVswitchgearswitchRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.2 | hwLVswitchgearswitchL1Current | L1 current | L1电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L1 current of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.3 | hwLVswitchgearswitchL2Current | L2 current | L2电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L2 current of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.4 | hwLVswitchgearswitchL3Current | L3 current | L3电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L3 current of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.5 | hwLVswitchgearswitchNCurrent | N current | N线电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | N current of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.6 | hwLVswitchgearswitchL1ActivePower | L1 active power | L1有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 active power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.7 | hwLVswitchgearswitchL2ActivePower | L2 active power | L2有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 active power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.8 | hwLVswitchgearswitchL3ActivePower | L3 active power | L3有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 active power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.9 | hwLVswitchgearswitchL1ApparentPower | L1 apparent power | L1视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 apparent power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.10 | hwLVswitchgearswitchL2ApparentPower | L2 apparent power | L2视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 apparent power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.11 | hwLVswitchgearswitchL3ApparentPower | L3 apparent power | L3视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 apparent power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.12 | hwLVswitchgearswitchL1ReactivePower | L1 reactive power | L1无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 reactive power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.13 | hwLVswitchgearswitchL2ReactivePower | L2 reactive power | L2无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 reactive power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.14 | hwLVswitchgearswitchL3ReactivePower | L3 reactive power | L3无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 reactive power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.15 | hwLVswitchgearswitchL1PowerFactor | L1 power factor | L1功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L1 power factor of the device config table for the LV switchgear switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.16 | hwLVswitchgearswitchL2PowerFactor | L2 power factor | L2功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L2 power factor of the device config table for the LV switchgear switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.17 | hwLVswitchgearswitchL3PowerFactor | L3 power factor | L3功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L3 power factor of the device config table for the LV switchgear switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.18 | hwLVswitchgearswitchActiveEnergy | Active energy | 有功电能 | 0-Read_Only | 只读 | 0..4290000000 | 0..4290000000 | Active energy of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.19 | hwLVswitchgearswitchL1LoadRatio | L1 load ratio | L1负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L1 load ratio of the device config table for the LV switchgear switch.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.20 | hwLVswitchgearswitchL2LoadRatio | L2 load ratio | L2负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L2 load ratio of the device config table for the LV switchgear switch.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.21 | hwLVswitchgearswitchL3LoadRatio | L3 load ratio | L3负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L3 load ratio of the device config table for the LV switchgear switch.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.22 | hwLVswitchgearswitchL1ThdU | L1 THD-u | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.23 | hwLVswitchgearswitchL2ThdU | L2 THD-u | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.24 | hwLVswitchgearswitchL3ThdU | L3 THD-u | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.25 | hwLVswitchgearswitchL1fifthThdU | L1 5th THD-u | L1 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.26 | hwLVswitchgearswitchL2fifthThdU | L2 5th THD-u | L2 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.27 | hwLVswitchgearswitchL3fifthThdU | L3 5th THD-u | L3 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.28 | hwLVswitchgearswitchL1seventhThdU | L1 7th THD-u | L1 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.29 | hwLVswitchgearswitchL2seventhThdU | L2 7th THD-u | L2 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.30 | hwLVswitchgearswitchL3seventhThdU | L3 7th THD-u | L3 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.31 | hwLVswitchgearswitchL1eleventhThdU | L1 11th THD-u | L1 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.32 | hwLVswitchgearswitchL2eleventhThdU | L2 11th THD-u | L2 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.33 | hwLVswitchgearswitchL3eleventhThdU | L3 11th THD-u | L3 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.34 | hwLVswitchgearswitchL1ThdI | L1 THD-i | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.35 | hwLVswitchgearswitchL2ThdI | L2 THD-i | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.36 | hwLVswitchgearswitchL3ThdI | L3 THD-i | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-u of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.37 | hwLVswitchgearswitchL1fifthThdI | L1 5th THD-i | L1 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.38 | hwLVswitchgearswitchL2fifthThdI | L2 5th THD-i | L2 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.39 | hwLVswitchgearswitchL3fifthThdI | L3 5th THD-i | L3 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.40 | hwLVswitchgearswitchL1seventhThdI | L1 7th THD-i | L1 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.41 | hwLVswitchgearswitchL2seventhThdI | L2 7th THD-i | L2 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.42 | hwLVswitchgearswitchL3seventhThdI | L3 7th THD-i | L3 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.43 | hwLVswitchgearswitchL1eleventhThdI | L1 11th THD-i | L1 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.44 | hwLVswitchgearswitchL2eleventhThdI | L2 11th THD-i | L2 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.45 | hwLVswitchgearswitchL3eleventhThdI | L3 11th THD-i | L3 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-i of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.46 | hwLVswitchgearswitchTotalOutputActivePower | Total output active power | 总输出有功功率 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Total output active power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.47 | hwLVswitchgearswitchTotalOutputApparentPower | Total output apparent power | 总输出视在功率 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Total output apparent power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.48 | hwLVswitchgearswitchTotalOutputReactivePower | Total output reactive power | 总输出无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output reactive power of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.49 | hwLVswitchgearswitchSwitchStatus | Switch status | 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Switch status of the device config table for the LV switchgear switch. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.50 | hwLVswitchgearswitchTrippingStatus | Tripping status | 脱扣状态 | 0-Read_Only | 只读 | normal(1), tripping(2), unknown(255) | [正常=1]/[脱扣=2] | Tripping status of the device config table for the LV switchgear switch. Value 1 indicate normal Value 2 indicate tripping
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.52 | hwLVswitchgearswitchSwitchOnStatus | Closing status | 合闸状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [分=1]/[合=2] | Closing status of the device config table for the LV switchgear switch. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.53 | hwLVswitchgearswitchEnergyStorageStatus | Energy storage status | 储能状态 | 0-Read_Only | 只读 | energyisnotfull(1), fullenergystorage(2), unknown(255) | [储能未满=1]/[储能满=2] | Energy storage status of the device config table for the LV switchgear switch. Value 1 indicate energy is not full Value 2 indicate full energy storage
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.54 | hwLVswitchgearswitchPositionStatus | Position status | 抽出状态 | 0-Read_Only | 只读 | connectOrTest(1), disconnect(2), unknown(255) | [未抽出=1]/[抽出=2] | Position status of the device config table for the LV switchgear switch. Value 1 indicate connect or test Value 2 indicate disconnect
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.55 | hwLVswitchgearswitchCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the LV switchgear switch. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.56 | hwLVswitchgearswitchRunningIndicatorStatus | Running indicator status | 运行灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Running indicator status of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.57 | hwLVswitchgearswitchAlarmIndicatorStatus | Alarm indicator status | 告警灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Alarm indicator status of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.58 | hwLVswitchgearswitchACInputSwitchIndicator | AC input switch indicator | AC输入开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC input switch indicator of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.59 | hwLVswitchgearswitchACOutputSwitchIndicator | AC output switch indicator | AC输出开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC output switch indicator of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.60 | hwLVswitchgearswitchM3SoftwareVersion | Tributary board M3 software version | 支路板M3软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Tributary board M3 software version of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.61 | hwLVswitchgearswitchTotalReactiveEnery | Total reactive energy | 总无功电能 | 0-Read_Only | 只读 | 0..4290000000 | 0..4290000000 | Total reactive energy of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kvarh
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.62 | hwLVswitchgearswitchEsn | ESN | ESN | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.63 | hwLVswitchgearMccbOutputL1JointSwitchBarTemp | Output L1 joint switch copper bar temperature | 输出L1开关连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output L1 joint switch copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.64 | hwLVswitchgearMccbOutputL2JointSwitchBarTemp | Output L2 joint switch copper bar temperature | 输出L2开关连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output L2 joint switch copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.65 | hwLVswitchgearMccbOutputL3JointSwitchBarTemp | Output L3 joint switch copper bar temperature | 输出L3开关连接处铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output L3 joint switch copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.66 | hwLVswitchgearMccbAmbientTempInside | Ambient temperature inside | 开关内环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Ambient temperature inside of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.67 | hwLVswitchgearMccbHealthDegree | Health degree | 健康度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Health degree of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.68 | hwLVswitchgearMccbSerialnumber | Serial number | 断路器序列号 | 0-Read_Only | 只读 | 0..16 | 0..16 | Serial number of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.69 | hwLVswitchgearswitchFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Frequency of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.70 | hwLVswitchgearAcbProductModel | Product model | 产品型号 | 0-Read_Only | 只读 | 0..16 | 0..16 | Product model of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.71 | hwLVswitchgearAcbRatedCurrent | Rated current | 额定电流 | 0-Read_Only | 只读 | 0..6300 | 0..6300 | Rated current of the device config table for the LV switchgear switch.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.72 | hwLVswitchgearAcbContactWearPercentage | Contact wear percentage | 触头磨损百分比 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Contact wear percentage of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.73 | hwLVswitchgearAcbTotalNumberOfOperations | Total number of operations | 总操作次数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Total number of operations of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.74 | hwLVswitchgearAcbHealthDegree | Health degree | 健康度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Health degree of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.1.1.300 | hwLVswitchgearswitchRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.2 | hwLVswitchgearswitchConfig1Table | / | / |  |  | / | / | The config table of LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.2.1.1 | hwLVswitchgearswitchConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.2.1.2 | hwLVswitchgearswitchDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.2.1.101 | hwLVswitchgearswitchConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3 | hwLVswitchgearswitchRunning2Table | / | / |  |  | / | / | The running table of LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.1 | hwLVswitchgearswitchRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.2 | hwLVswitchgearswitchNominalCurrent | Nominal current | 标称电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Nominal current of the device config table for the LV switchgear switch.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.3 | hwLVswitchgearswitchOperationsPerYear | Operations per year | 年操作次数 | 0-Read_Only | 只读 | 100..6300 | 100..6300 | Operations per year of the device config table for the LV switchgear switch.SigUnitInfo:U.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.4 | hwLVswitchgearswitchAlarmStatus | Alarm status | 告警状态 | 0-Read_Only | 只读 | 0..1 | 0..1 | Alarm status of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.5 | hwLVswitchgearswitchSampProtectionMode | Protection mode | 保护模式 | 0-Read_Only | 只读 | lsi(1), ls(2), li(3), unknown(255) | [LSI=1]/[LS=2]/[LI=3] | Protection mode of the device config table for the LV switchgear switch. Value 1 indicate lsi Value 2 indicate ls Value 3 indicate li
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.6 | hwLVswitchgearswitchL1InputCopperBarTemperature | Input L1 copper bar temperature | 输入 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.7 | hwLVswitchgearswitchL2InputCopperBarTemperature | Input L2 copper bar temperature | 输入 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.8 | hwLVswitchgearswitchL3InputCopperBarTemperature | Input L3 copper bar temperature | 输入 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.9 | hwLVswitchgearswitchL1OutputCopperBarTemperature | Output L1 copper bar temperature | 输出 L1铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.10 | hwLVswitchgearswitchL2OutputCopperBarTemperature | Output L2 copper bar temperature | 输出 L2铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.11 | hwLVswitchgearswitchL3OutputCopperBarTemperature | Output L3 copper bar temperature | 输出 L3铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.12 | hwLVswitchgearswitchCopperBarEnvironmentTemperature | Copper bar environment temperature | 铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Copper bar environment temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.13 | hwLVswitchgearswitchL1OutputPredictedCopperBarTemperature | Output L1 predicted copper bar temperature | 输出 L1铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output predicted copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.14 | hwLVswitchgearswitchL2OutputPredictedCopperBarTemperature | Output L2 predicted copper bar temperature | 输出 L2铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output predicted copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.15 | hwLVswitchgearswitchL3OutputPredictedCopperBarTemperature | Output L3 predicted copper bar temperature | 输出 L3铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output predicted copper bar temperature of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.16 | hwLVswitchgearswitchL1phasevoltage | L1 phase voltage | L1相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 phase voltage of the device running table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.17 | hwLVswitchgearswitchL2phasevoltage | L2 phase voltage | L2相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 phase voltage of the device running table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.18 | hwLVswitchgearswitchL3phasevoltage | L3 phase voltage | L3相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 phase voltage of the device running table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.19 | hwLVswitchgearswitchL1L2linevoltage | L1-L2 line voltage | L1-L2线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1-L2 line voltage of the device running table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.20 | hwLVswitchgearswitchL2L3linevoltage | L2-L3 line voltage | L2-L3线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2-L3 line voltage of the device running table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.21 | hwLVswitchgearswitchL3L1linevoltage | L3-L1 line voltage | L3-L1线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3-L1 line voltage of the device running table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.22 | hwLVswitchgearswitchAbbAbrasion | Abrasion | 磨损程度 | 0-Read_Only | 只读 | 0..100 | 0..100 | ABB abrasion of the device config table for the LV switchgear switch.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.23 | hwLVswitchgearswitchAbbVoltageLevel | Voltage level | 电压等级 | 0-Read_Only | 只读 | onehundred(1), onehundredandfifteen(2), onehundredandtwenty(3), onehundredandninety(4), twohundredandeight(5), twohundredandtwenty(6), twohundredandthirty(7), twohundredandforty(8), twohundredandseventyseven(9), threehundredandfortyseven(10), threehundredandeighty(11), fourhundred(12), fourhundredandfifteen(13), fourhundredandforty(14), fourhundredandeighty(15), fivehundred(16), fivehundredandfifty(17), sixhundred(18), sixhundredandsixty(19), sixhundredandninety(20), ninehundredandten(21), ninehundredandfifty(22), onethousand(23), onethousandonehundredandfifty(24), unknown(255) | [100=1]/[115=2]/[120=3]/[190=4]/[208=5]/[220=6]/[230=7]/[240=8]/[277=9]/[347=10]/[380=11]/[400=12]/[415=13]/[440=14]/[480=15]/[500=16]/[550=17]/[600=18]/[660=19]/[690=20]/[910=21]/[950=22]/[1000=23]/[1150=24] | ABB voltage level of the device config table for the LV switchgear switch. Value 1 indicate 100v Value 2 indicate 115v Value 3 indicate 120v Value 4 indicate 190v Value 5 indicate 208v Value 6 indicate 220v Value 7 indicate 230v Value 8 indicate 240v Value 9 indicate 277v Value 10 indicate 347v Value 11 indicate 380v Value 12 indicate 400v Value 13 indicate 415v Value 14 indicate 440v Value 15 indicate 480v Value 16 indicate 500v Value 17 indicate 550v Value 18 indicate 600v Value 19 indicate 660v Value 20 indicate 690v Value 21 indicate 910v Value 22 indicate 950v Value 23 indicate 1000v Value 24 indicate 1150vSigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.24 | hwLVswitchgearswitchAbbCircuitBreakerNumber | Circuit breaker number | 断路器序列号 | 0-Read_Only | 只读 | 0..32 | 0..32 | ABB circuit breaker number of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.25 | hwLVswitchgearswitchAbbCircuitBreakerName | Circuit breaker name | 断路器名称 | 0-Read_Only | 只读 | 0..32 | 0..32 | ABB circuit breaker name of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.26 | hwLVswitchgearswitchLocationStatus | Location status | 位置状态 | 0-Read_Only | 只读 | rackedIn(1), test(2), rackedOut(3), abnormal(4), unknown(255) | [摇入=1]/[测试=2]/[摇出=3]/[异常=4] | Location status of the device config table for the LV switchgear switch. Value 1 indicate racked in Value 2 indicate test Value 3 indicate racked out Value 4 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.27 | hwLVswitchL1phaseVoltageAts | L1 phase voltage-ATS | L1相电压-ATS | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 phase voltage ATS of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.28 | hwLVswitchL2phaseVoltageAts | L2 phase voltage-ATS | L2相电压-ATS | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 phase voltage ATS of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.29 | hwLVswitchL3phaseVoltageAts | L3 phase voltage-ATS | L3相电压-ATS | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 phase voltage ATS of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.30 | hwLVswitchL1L2LineVoltageAts | L1-L2 line voltage-ATS | L1-L2线电压-ATS | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1L2 line voltage ATS of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.31 | hwLVswitchL2L3LineVoltageAts | L2-L3 line voltage-ATS | L2-L3线电压-ATS | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2L3 line voltage ATS of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.32 | hwLVswitchL3L1LineVoltageAts | L3-L1 line voltage-ATS | L3-L1线电压-ATS | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3L1 line voltage ATS of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.33 | hwLVswitchEarthCurrent | Earth current | 地线电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | Earth current of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.34 | hwLVswitchApparentEnergy | Apparent energy | 视在电能 | 0-Read_Only | 只读 | 0..2147483680 | 0..2147483680 | Apparent energy of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.35 | hwLVswitchAverageCurrent | Average current | 电流平均值 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | Average current of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.36 | hwLVswitchAverageLineVoltage | Average line voltage | 线电压平均值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Average line voltage of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.37 | hwLVswitchAveragePhaseVoltage | inameAveragePhaseVoltage | 相电压平均值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Average phase voltage of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.38 | hwLVswitchTotalPowerFactor | Total power factor | 总功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Total power factor of the device config table for the LV switchgear switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.13.3.1.101 | hwLVswitchgearswitchRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4 | hwLVswitchgearswitchConfig2Table | / | / |  |  | / | / | The config table of LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.1 | hwLVswitchgearswitchConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.2 | hwLVswitchgearswitchSwitchType | Switch type | 开关类型 | 1-Read_Write | 读写 | nocommunicationmodule(1), supportekipcom(2), unknown(255) | [无通讯模块=1]/[支持Ekip Com=2]/[支持自研通信模块=3] | Switch type of the device config table for the LV switchgear switch. Value 1 indicate no communication module Value 2 indicate support ekip com
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.3 | hwLVswitchgearswitchTripUnitType | Trip unit type | 脱扣器类型 | 1-Read_Write | 读写 | e(1), tm(2), unknown(255) | [E=1]/[TM=2] | Trip unit type of the device config table for the LV switchgear switch. Value 1 indicate e Value 2 indicate tm
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.4 | hwLVswitchgearswitchTripUnitModel | Trip unit model | 脱扣器型号 | 1-Read_Write | 读写 | ekipDipLsOrI(1), ekipDipLsi(2), ekipTouchLsi(3), ekipHiAndTouchLsi(4), tma(5), tmd(6), unknown(255) | [Ekip dip ls/I=1]/[Ekip dip lsi=2]/[Ekip touch lsi=3]/[Ekip hi-touch lsi=4]/[TMA=5]/[TMD=6] | Trip unit model of the device config table for the LV switchgear switch. Value 1 indicate ekip dip ls/i Value 2 indicate ekip dip lsi Value 3 indicate ekip touch lsi Value 4 indicate ekip hi-touch lsi Value 5 indicate tma Value 6 indicate tmd
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.6 | hwLVswitchgearswitchLongTimeDelayProtectionCurrentCoefficient | Long time delay protection current coefficient | 长延时保护电流系数 | 1-Read_Write | 读写 | 400..1000 | 400..1000 | Long time delay protection current coefficient of the device config table for the LV switchgear switch.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.7 | hwLVswitchgearswitchLongTimeDelayProtectionTime | Long time delay protection time | 长延时保护时间 | 1-Read_Write | 读写 | 300..14400 | 300..14400 | Long time delay protection time of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.8 | hwLVswitchgearswitchShortTimeDelayProtectionCurrentCoefficient | Short time delay protection current coefficient | 短延时保护电流系数 | 1-Read_Write | 读写 | 60..1000 | 60..1000 | Short time delay protection current coefficient of the device config table for the LV switchgear switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.9 | hwLVswitchgearswitchShortTimeDelayProtectionTime | Short time delay protection time | 短延时保护时间 | 1-Read_Write | 读写 | 5..80 | 5..80 | Short time delay protection time of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.10 | hwLVswitchgearswitchInstantaneousProtectionCurrent | Instantaneous protection current | 瞬时保护电流系数 | 1-Read_Write | 读写 | 150..1500 | 150..1500 | Instantaneous protection current of the device config table for the LV switchgear switch.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.12 | hwLVswitchgearswitchBreakerModel | Breaker model | 断路器型号 | 1-Read_Write | 读写 | tmaxt1(1), tmaxt2(2), tmaxt3(3), tmaxt4(4), tmaxt5(5), tmaxt6(6), tmaxxt1(7), tmaxxt2(8), tmaxxt3(9), tmaxxt4(10), tmaxxt5(11), tmaxxt6(12), tmaxxt7(13), tmaxxt7m(14), emax2e1point2(15), emax2e2point2(16), emax2e4point2(17), emax2e6point2(18), w800(19), w1000(20), w1250(21), w1600(22), w2000(23), w2500(24), w3200(25), w4000(26), w5000(27), w6300(28), unknown(255) | [Tmax T1=1]/[Tmax T2=2]/[Tmax T3=3]/[Tmax T4=4]/[Tmax T5=5]/[Tmax T6=6]/[Tmax XT1=7]/[Tmax XT2=8]/[Tmax XT3=9]/[Tmax XT4=10]/[Tmax XT5=11]/[Tmax XT6=12]/[Tmax XT7=13]/[Tmax XT7m=14]/[Emax2 E1.2=15]/[Emax2 E2.2=16]/[Emax2 E4.2=17]/[Emax2 E6.2=18]/[W800=19]/[W1000=20]/[W1250=21]/[W1600=22]/[W2000=23]/[W2500=24]/[W3200=25]/[W4000=26]/[W5000=27]/[W6300=28] | Breaker model of the device config table for the LV switchgear switch. Value 1 indicate tmaxt1 Value 2 indicate tmaxt2 Value 3 indicate tmaxt3 Value 4 indicate tmaxt4 Value 5 indicate tmaxt5 Value 6 indicate tmaxt6 Value 7 indicate tmaxxt1 Value 8 indicate tmaxxt2 Value 9 indicate tmaxxt3 Value 10 indicate tmaxxt4 Value 11 indicate tmaxxt5 Value 12 indicate tmaxxt6 Value 13 indicate tmaxxt7 Value 14 indicate tmaxxt7m Value 15 indicate emax2e1.2 Value 16 indicate emax2e2.2 Value 17 indicate emax2e4.2 Value 18 indicate emax2e6.2 Value 19 indicate w800 Value 20 indicate w1000 Value 21 indicate w1250 Value 22 indicate w1600 Value 23 indicate w2000 Value 24 indicate w2500 Value 25 indicate w3200 Value 26 indicate w4000 Value 27 indicate w5000 Value 28 indicate w6300
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.13 | hwLVswitchgearswitchRateCurrent | Rate current | 额定电流设置 | 1-Read_Write | 读写 | 63..6300 | 63..6300 | Rate current of the device config table for the LV switchgear switch.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.14 | hwLVswitchgearswitchSetProtectionMode | Protection mode | 保护模式 | 1-Read_Write | 读写 | lsi(1), ls(2), li(3), unknown(255) | [LSI=1]/[LS=2]/[LI=3] | Protection mode of the device config table for the LV switchgear switch. Value 1 indicate lsi Value 2 indicate ls Value 3 indicate li
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.15 | hwLVswitchgearswitchDiscriminativeProtection | Discriminative protection | 是否实现选择性保护 | 1-Read_Write | 读写 | yes(1), no(2), unknown(255) | [是=1]/[否=2] | Discriminative protection of the device config table for the LV switchgear switch. Value 1 indicate yes Value 2 indicate no
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.16 | hwLVswitchgearMccbSetProtectionMode | Protection mode | 保护模式 | 1-Read_Write | 读写 | sIsEnabledAndIIsDisabled(1), sIsDisabledAndIIsEnabled(2), bothSAndIAreEnabled(3), unknown(255) | [S使能和I不使能=1]/[S不使能和I使能=2]/[S和I都使能=3] | Protection mode of the device config table for the LV switchgear switch. Value 1 indicate S is enabled and I is disabled Value 2 indicate S is disabled and I is enabled Value 3 indicate Both S and I are enabled
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.17 | hwLVswitchgearMccbLongTimeDelayProtectionCurrentCoefficient | Long time delay protection current coefficient | 长延时保护电流系数 | 1-Read_Write | 读写 | 400..1000 | 400..1000 | Long time delay protection current coefficient of the device config table for the LV switchgear switch.Multiple:1000.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.18 | hwLVswitchgearMccbLongTimeDelayProtectionTime | Long time delay protection time | 长延时保护时间 | 1-Read_Write | 读写 | 300..4800 | 300..4800 | Long time delay protection time of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.19 | hwLVswitchgearMccbShortTimeDelayProtectionCurrentCoefficient | Short time delay protection current coefficient | 短延时保护电流系数 | 1-Read_Write | 读写 | 60..1000 | 60..1000 | Short time delay protection current coefficient of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.20 | hwLVswitchgearMccbShortTimeDelayProtectionTime | Short time delay protection time | 短延时保护时间 | 1-Read_Write | 读写 | 5..50 | 5..50 | Short time delay protection time of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.21 | hwLVswitchgearMccbInstantaneousProtectionCurrent | Instantaneous protection current | 瞬时保护电流系数 | 1-Read_Write | 读写 | 150..1000 | 150..1000 | Instantaneous protection current of the device config table for the LV switchgear switch.Multiple:100.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.22 | hwLVswitchgearAcbLongTimeDelayProtectionCurrentCoefficient | Long time delay protection current coefficient | 长延时保护电流系数 | 1-Read_Write | 读写 | 400..1000 | 400..1000 | Long time delay protection current coefficient of the device config table for the LV switchgear switch.Multiple:1000.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.23 | hwLVswitchgearAcbLongTimeDelayProtectionTime | Long time delay protection time | 长延时保护时间 | 1-Read_Write | 读写 | fifteen(1), thirty(2), sixty(3), oneHundredAndTwenty(4), twoHundredAndForty(5), threeHundredAndSixty(6), fourHundredAndEighty(7), sixHundred(8), sevenHundredAndTwenty(9), eightHundredAndForty(10), nineHundredAndSixty(11), unknown(255) | [15s=1]/[30s=2]/[60s=3]/[360s=4]/[720s=5]/[840s=6]/[960s=7]/[120s=8]/[240s=9]/[480s=10]/[600s=11] | Long time delay protection time of the device config table for the LV switchgear switch. Value 1 indicate 15 Value 2 indicate 30 Value 3 indicate 60 Value 4 indicate 120 Value 5 indicate 240 Value 6 indicate 360 Value 7 indicate 480 Value 8 indicate 600 Value 9 indicate 720 Value 10 indicate 840 Value 11 indicate 960SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.24 | hwLVswitchgearAcbShortTimeDelayProtectionCurrentCoefficient | Short time delay protection current coefficient | 短延时保护电流系数 | 1-Read_Write | 读写 | 1500..15000 | 1500..15000 | Short time delay protection current coefficient of the device config table for the LV switchgear switch.Multiple:1000.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.25 | hwLVswitchgearAcbShortTimeDelayProtectionTime | Short time delay protection time | 短延时保护时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Short time delay protection time of the device config table for the LV switchgear switch.Multiple:10.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.26 | hwLVswitchgearAcbInstantaneousProtectionCurrent | Instantaneous protection current | 瞬时保护电流系数 | 1-Read_Write | 读写 | 1000..20000 | 1000..20000 | Instantaneous protection current of the device config table for the LV switchgear switch.Multiple:1000.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.27 | hwLVswitchgearAcbActionValueOfGroundingProtection | Action value of grounding protection | 接地保护动作值 | 1-Read_Write | 读写 | 200..1000 | 200..1000 | Action value of grounding protection of the device config table for the LV switchgear switch.Multiple:1000.SigUnitInfo:In.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.28 | hwLVswitchgearswitchSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.29 | hwLVswitchgearswitchHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.30 | hwLVswitchgearswitchFrameCircuitBreakerSoftwareVersion | Frame circuit breaker software version | 框架断路器软件版本号 | 0-Read_Only | 只读 | 0..5 | 0..5 | Frame circuit breaker software version of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.31 | hwLVswitchgearswitchFrameCircuitBreakerHardwareVersion | Frame circuit breaker hardware version | 框架断路器硬件版本号 | 0-Read_Only | 只读 | 0..3 | 0..3 | Frame circuit breaker hardware version of the device config table for the LV switchgear switch.
1.3.6.1.4.1.2011.6.178.1.1.9.13.4.1.101 | hwLVswitchgearswitchConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of LV switchgear switch.

## Smart PDU
智能PDU
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.9.82 | SmartPDU | Smart PDU | 智能PDU | / | / | / | / | Smart PDU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1 | hwSmartPDURunning1Table | / | / |  |  | / | / | The running table of Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.1 | hwSmartPDURunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.2 | hwSmartPDUPduTotalInputActiveEnergy | PDU total input active energy | PDU输入总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | PDU total input active energy of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.3 | hwSmartPDUItCabinetTotalOutputActiveEnergy | IT cabinet total output active energy | IT机柜输出总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | IT cabinet total output active energy of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.4 | hwSmartPDUAorCTotalOutputActiveEnergy | A/C total output active energy | 空调输出总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | A/C total output active energy of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.5 | hwSmartPDUMainInputInputActivePower | Main input-input active power | 主路-输入有功电能 | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Main input-input active power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.6 | hwSmartPDUMeterFrequency | Meter-frequency | 电表-频率 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | Meter-frequency of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.7 | hwSmartPDUQF7Power | QF7 power(L1) | QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF7 power(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.8 | hwSmartPDUQF8Power | QF8 power(L2) | QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF8 power(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.9 | hwSmartPDUQF9Power | QF9 power(L3) | QF9 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF9 power(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.10 | hwSmartPDUQF10Power | QF10 power(L1) | QF10 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF10 power(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.11 | hwSmartPDUQF11Power | QF11 power(L2) | QF11 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF11 power(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.12 | hwSmartPDUQF12Power | QF12 power(L3) | QF12 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF12 power(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.13 | hwSmartPDUQF13Power | QF13 power(L1) | QF13 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF13 power(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.14 | hwSmartPDUQF14Power | QF14 power(L2) | QF14 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF14 power(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.15 | hwSmartPDUQF15Power | QF15 power(L3) | QF15 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF15 power(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.16 | hwSmartPDUQF16Power | QF16 power(L1) | QF16 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF16 power(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.17 | hwSmartPDUQF17Power | QF17 power(L2) | QF17 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF17 power(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.18 | hwSmartPDUQF18Power | QF18 power(L3) | QF18 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF18 power(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.19 | hwSmartPDUQF19Power | QF19 power(L1) | QF19 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF19 power(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.20 | hwSmartPDUQF20Power | QF20 power(L2) | QF20 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF20 power(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.21 | hwSmartPDUQF21Power | QF21 power(L3) | QF21 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF21 power(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.22 | hwSmartPDUQF22Power | QF22 power(L1) | QF22 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF22 power(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.23 | hwSmartPDUQF23Power | QF23 power(L2) | QF23 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF23 power(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.24 | hwSmartPDUQF24Power | QF24 power(L3) | QF24 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | QF24 power(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.25 | hwSmartPDUQF7ElectricityEnergy | QF7 electricity energy(L1) | QF7 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF7 electricity energy(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.26 | hwSmartPDUQF8ElectricityEnergy | QF8 electricity energy(L2) | QF8 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF8 electricity energy(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.27 | hwSmartPDUQF9ElectricityEnergy | QF9 electricity energy(L3) | QF9 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF9 electricity energy(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.28 | hwSmartPDUQF10ElectricityEnergy | QF10 electricity energy(L1) | QF10 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF10 electricity energy(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.29 | hwSmartPDUQF11ElectricityEnergy | QF11 electricity energy(L2) | QF11 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF11 electricity energy(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.30 | hwSmartPDUQF12ElectricityEnergy | QF12 electricity energy(L3) | QF12 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF12 electricity energy(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.31 | hwSmartPDUQF13ElectricityEnergy | QF13 electricity energy(L1) | QF13 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF13 electricity energy(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.32 | hwSmartPDUQF14ElectricityEnergy | QF14 electricity energy(L2) | QF14 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF14 electricity energy(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.33 | hwSmartPDUQF15ElectricityEnergy | QF15 electricity energy(L3) | QF15 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF15 electricity energy(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.34 | hwSmartPDUQF16ElectricityEnergy | QF16 electricity energy(L1) | QF16 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF16 electricity energy(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.35 | hwSmartPDUQF17ElectricityEnergy | QF17 electricity energy(L2) | QF17 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF17 electricity energy(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.36 | hwSmartPDUQF18ElectricityEnergy | QF18 electricity energy(L3) | QF18 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF18 electricity energy(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.37 | hwSmartPDUQF19ElectricityEnergy | QF19 electricity energy(L1) | QF19 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF19 electricity energy(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.38 | hwSmartPDUQF20ElectricityEnergy | QF20 electricity energy(L2) | QF20 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF20 electricity energy(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.39 | hwSmartPDUQF21ElectricityEnergy | QF21 electricity energy(L3) | QF21 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF21 electricity energy(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.40 | hwSmartPDUQF22ElectricityEnergy | QF22 electricity energy(L1) | QF22 电能(L1) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF22 electricity energy(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.41 | hwSmartPDUQF23ElectricityEnergy | QF23 electricity energy(L2) | QF23 电能(L2) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF23 electricity energy(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.42 | hwSmartPDUQF24ElectricityEnergy | QF24 electricity energy(L3) | QF24 电能(L3) | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF24 electricity energy(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.43 | hwSmartPDUQF7Temperature | QF7 temperature(L1) | QF7 温度(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF7 temperature(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.44 | hwSmartPDUQF8Temperature | QF8 temperature(L2) | QF8 温度(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF8 temperature(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.45 | hwSmartPDUQF9Temperature | QF9 temperature(L3) | QF9 温度(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF9 temperature(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.46 | hwSmartPDUQF10Temperature | QF10 temperature(L1) | QF10 温度(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF10 temperature(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.47 | hwSmartPDUQF11Temperature | QF11 temperature(L2) | QF11 温度(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF11 temperature(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.48 | hwSmartPDUQF12Temperature | QF12 temperature(L3) | QF12 温度(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF12 temperature(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.49 | hwSmartPDUQF13Temperature | QF13 temperature(L1) | QF13 温度(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF13 temperature(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.50 | hwSmartPDUQF14Temperature | QF14 temperature(L2) | QF14 温度(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF14 temperature(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.51 | hwSmartPDUQF15Temperature | QF15 temperature(L3) | QF15 温度(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF15 temperature(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.52 | hwSmartPDUQF16Temperature | QF16 temperature(L1) | QF16 温度(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF16 temperature(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.53 | hwSmartPDUQF17Temperature | QF17 temperature(L2) | QF17 温度(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF17 temperature(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.54 | hwSmartPDUQF18Temperature | QF18 temperature(L3) | QF18 温度(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF18 temperature(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.55 | hwSmartPDUQF19Temperature | QF19 temperature(L1) | QF19 温度(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF19 temperature(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.56 | hwSmartPDUQF20Temperature | QF20 temperature(L2) | QF20 温度(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF20 temperature(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.57 | hwSmartPDUQF21Temperature | QF21 temperature(L3) | QF21 温度(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF21 temperature(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.58 | hwSmartPDUQF22Temperature | QF22 temperature(L1) | QF22 温度(L1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF22 temperature(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.59 | hwSmartPDUQF23Temperature | QF23 temperature(L2) | QF23 温度(L2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF23 temperature(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.60 | hwSmartPDUQF24Temperature | QF24 temperature(L3) | QF24 温度(L3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF24 temperature(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.61 | hwSmartPDUQF7Current | QF7 current(L1) | QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF7 current(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.62 | hwSmartPDUQF8Current | QF8 current(L2) | QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF8 current(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.63 | hwSmartPDUQF9Current | QF9 current(L3) | QF9 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF9 current(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.64 | hwSmartPDUQF10Current | QF10 current(L1) | QF10 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF10 current(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.65 | hwSmartPDUQF11Current | QF11 current(L2) | QF11 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF11 current(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.66 | hwSmartPDUQF12Current | QF12 current(L3) | QF12 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF12 current(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.67 | hwSmartPDUQF13Current | QF13 current(L1) | QF13 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF13 current(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.68 | hwSmartPDUQF14Current | QF14 current(L2) | QF14 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF14 current(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.69 | hwSmartPDUQF15Current | QF15 current(L3) | QF15 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF15 current(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.70 | hwSmartPDUQF16Current | QF16 current(L1) | QF16 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF16 current(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.71 | hwSmartPDUQF17Current | QF17 current(L2) | QF17 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF17 current(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.72 | hwSmartPDUQF18Current | QF18 current(L3) | QF18 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF18 current(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.73 | hwSmartPDUQF19Current | QF19 current(L1) | QF19 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF19 current(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.74 | hwSmartPDUQF20Current | QF20 current(L2) | QF20 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF20 current(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.75 | hwSmartPDUQF21Current | QF21 current(L3) | QF21 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF21 current(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.76 | hwSmartPDUQF22Current | QF22 current(L1) | QF22 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF22 current(L1) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.77 | hwSmartPDUQF23Current | QF23 current(L2) | QF23 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF23 current(L2) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.78 | hwSmartPDUQF24Current | QF24 current(L3) | QF24 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | QF24 current(L3) of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.79 | hwSmartPDUQF7LoadFactor | QF7 load factor(L1) | QF7 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF7 load factor(L1) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.80 | hwSmartPDUQF8LoadFactor | QF8 load factor(L2) | QF8 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF8 load factor(L2) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.81 | hwSmartPDUQF9LoadFactor | QF9 load factor(L3) | QF9 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF9 load factor(L3) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.82 | hwSmartPDUQF10LoadFactor | QF10 load factor(L1) | QF10 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF10 load factor(L1) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.83 | hwSmartPDUQF11LoadFactor | QF11 load factor(L2) | QF11 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF11 load factor(L2) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.84 | hwSmartPDUQF12LoadFactor | QF12 load factor(L3) | QF12 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF12 load factor(L3) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.85 | hwSmartPDUQF13LoadFactor | QF13 load factor(L1) | QF13 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF13 load factor(L1) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.86 | hwSmartPDUQF14LoadFactor | QF14 load factor(L2) | QF14 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF14 load factor(L2) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.87 | hwSmartPDUQF15LoadFactor | QF15 load factor(L3) | QF15 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF15 load factor(L3) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.88 | hwSmartPDUQF16LoadFactor | QF16 load factor(L1) | QF16 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF16 load factor(L1) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.89 | hwSmartPDUQF17LoadFactor | QF17 load factor(L2) | QF17 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF17 load factor(L2) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.90 | hwSmartPDUQF18LoadFactor | QF18 load factor(L3) | QF18 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF18 load factor(L3) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.91 | hwSmartPDUQF19LoadFactor | QF19 load factor(L1) | QF19 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF19 load factor(L1) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.92 | hwSmartPDUQF20LoadFactor | QF20 load factor(L2) | QF20 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF20 load factor(L2) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.93 | hwSmartPDUQF21LoadFactor | QF21 load factor(L3) | QF21 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF21 load factor(L3) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.94 | hwSmartPDUQF22LoadFactor | QF22 load factor(L1) | QF22 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF22 load factor(L1) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.95 | hwSmartPDUQF23LoadFactor | QF23 load factor(L2) | QF23 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF23 load factor(L2) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.96 | hwSmartPDUQF24LoadFactor | QF24 load factor(L3) | QF24 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | QF24 load factor(L3) of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.97 | hwSmartPDUQF7SwitchStatus | QF7 switch status(L1) | QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF7 switch status(L1) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.98 | hwSmartPDUQF8SwitchStatus | QF8 switch status(L2) | QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF8 switch status(L2) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.99 | hwSmartPDUQF9SwitchStatus | QF9 switch status(L3) | QF9 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF9 switch status(L3) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.100 | hwSmartPDUQF10SwitchStatus | QF10 switch status(L1) | QF10 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF10 switch status(L1) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.101 | hwSmartPDUQF11SwitchStatus | QF11 switch status(L2) | QF11 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF11 switch status(L2) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.102 | hwSmartPDUQF12SwitchStatus | QF12 switch status(L3) | QF12 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF12 switch status(L3) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.103 | hwSmartPDUQF13SwitchStatus | QF13 switch status(L1) | QF13 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF13 switch status(L1) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.104 | hwSmartPDUQF14SwitchStatus | QF14 switch status(L2) | QF14 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF14 switch status(L2) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.105 | hwSmartPDUQF15SwitchStatus | QF15 switch status(L3) | QF15 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF15 switch status(L3) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.106 | hwSmartPDUQF16SwitchStatus | QF16 switch status(L1) | QF16 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF16 switch status(L1) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.107 | hwSmartPDUQF17SwitchStatus | QF17 switch status(L2) | QF17 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF17 switch status(L2) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.108 | hwSmartPDUQF18SwitchStatus | QF18 switch status(L3) | QF18 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF18 switch status(L3) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.109 | hwSmartPDUQF19SwitchStatus | QF19 switch status(L1) | QF19 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF19 switch status(L1) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.110 | hwSmartPDUQF20SwitchStatus | QF20 switch status(L2) | QF20 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF20 switch status(L2) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.111 | hwSmartPDUQF21SwitchStatus | QF21 switch status(L3) | QF21 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF21 switch status(L3) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.112 | hwSmartPDUQF22SwitchStatus | QF22 switch status(L1) | QF22 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF22 switch status(L1) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.113 | hwSmartPDUQF23SwitchStatus | QF23 switch status(L2) | QF23 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF23 switch status(L2) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.114 | hwSmartPDUQF24SwitchStatus | QF24 switch status(L3) | QF24 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF24 switch status(L3) of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.115 | hwSmartPDUUps1InputSwitchL1Temperature | UPS1 input switch L1 temperature | UPS1输入开关L1温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS1 input switch L1 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.116 | hwSmartPDUUps1InputSwitchL2Temperature | UPS1 input switch L2 temperature | UPS1输入开关L2温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS1 input switch L2 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.117 | hwSmartPDUUps1InputSwitchL3Temperature | UPS1 input switch L3 temperature | UPS1输入开关L3温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS1 input switch L3 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.118 | hwSmartPDUUps2InputSwitchL1Temperature | UPS2 input switch L1 temperature | UPS2输入开关L1温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS2 input switch L1 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.119 | hwSmartPDUUps2InputSwitchL2Temperature | UPS2 input switch L2 temperature | UPS2输入开关L2温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS2 input switch L2 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.120 | hwSmartPDUUps2InputSwitchL3Temperature | UPS2 input switch L3 temperature | UPS2输入开关L3温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS2 input switch L3 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.121 | hwSmartPDUUps1OutputSwitchL1Temperature | UPS1 output switch L1 temperature | UPS1输出开关L1温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS1 output switch L1 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.122 | hwSmartPDUUps1OutputSwitchL2Temperature | UPS1 output switch L2 temperature | UPS1输出开关L2温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS1 output switch L2 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.123 | hwSmartPDUUps1OutputSwitchL3Temperature | UPS1 output switch L3 temperature | UPS1输出开关L3温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS1 output switch L3 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.124 | hwSmartPDUUps2OutputSwitchL1Temperature | UPS2 output switch L1 temperature | UPS2输出开关L1温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS2 output switch L1 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.125 | hwSmartPDUUps2OutputSwitchL2Temperature | UPS2 output switch L2 temperature | UPS2输出开关L2温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS2 output switch L2 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.126 | hwSmartPDUUps2OutputSwitchL3Temperature | UPS2 output switch L3 temperature | UPS2输出开关L3温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | UPS2 output switch L3 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.127 | hwSmartPDUCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Smart PDU. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.128 | hwSmartPDUMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.129 | hwSmartPDUPduIp | PDU IP | PDU IP地址 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | PDU IP of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.130 | hwSmartPDUEsn | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.131 | hwSmartPDUSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.132 | hwSmartPDUELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.133 | hwSmartPDUMainInputL1InputVoltage | Main input-L1 input voltage | 主路-L1输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input-L1 input voltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.134 | hwSmartPDUMainInputL2InputVoltage | Main input-L2 input voltage | 主路-L2输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input-L2 input voltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.135 | hwSmartPDUMainInputL3InputVoltage | Main input-L3 input voltage | 主路-L3输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input-L3 input voltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.136 | hwSmartPDUMainInputL1InputCurrent | Main input-L1 input current | 主路-L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main input-L1 input current of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.137 | hwSmartPDUMainInputL2InputCurrent | Main input-L2 input current | 主路-L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main input-L2 input current of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.138 | hwSmartPDUMainInputL3InputCurrent | Main input-L3 input current | 主路-L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main input-L3 input current of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.139 | hwSmartPDUMainInputInputFrequency | Main input input frequency | 主路-输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input input frequency of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.140 | hwSmartPDUMainInputL1InputActivePower | Main input-L1 input active power | 主路-L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main input-L1 input active power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.141 | hwSmartPDUMainInputL2InputActivePower | Main input-L2 input active power | 主路-L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main input-L2 input active power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.142 | hwSmartPDUMainInputL3InputActivePower | Main input-L3 input active power | 主路-L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main input-L3 input active power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.143 | hwSmartPDUMainInputL1InputApparentPower | Main input-L1 input apparent power | 主路-L1输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | Main input-L1 input apparent power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.144 | hwSmartPDUMainInputL2InputApparentPower | Main input-L2 input apparent power | 主路-L2输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | Main input-L2 input apparent power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.145 | hwSmartPDUMainInputL3InputApparentPower | Main input-L3 input apparent power | 主路-L3输入视在功率 | 0-Read_Only | 只读 | 0..2500 | 0..2500 | Main input-L3 input apparent power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.146 | hwSmartPDUMainInputL1InputReactivePower | Main input-L1 input reactive power | 主路-L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main input-L1 input reactive power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.147 | hwSmartPDUMainInputL2InputReactivePower | Main input-L2 input reactive power | 主路-L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main input-L2 input reactive power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.148 | hwSmartPDUMainInputL3InputReactivePower | Main input-L3 input reactive power | 主路-L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main input-L3 input reactive power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.149 | hwSmartPDUMainInputL1InputPowerFactor | Main input-L1 input power factor | 主路-L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input-L1 input power factor of the device config table for the Smart PDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.150 | hwSmartPDUMainInputL2InputPowerFactor | Main input-L2 input power factor | 主路-L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input-L2 input power factor of the device config table for the Smart PDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.151 | hwSmartPDUMainInputL3InputPowerFactor | Main input-L3 input power factor | 主路-L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main input-L3 input power factor of the device config table for the Smart PDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.152 | hwSmartPDUMainInputL1InputPowerLoadRate | Main input-L1 input power load rate | 主路-L1输入电源负载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main input-L1 input power load rate of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.153 | hwSmartPDUMainInputL2InputPowerLoadRate | Main input-L2 input power load rate | 主路-L2输入电源负载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main input-L2 input power load rate of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.154 | hwSmartPDUMainInputL3InputPowerLoadRate | Main input-L3 input power load rate | 主路-L3输入电源负载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main input-L3 input power load rate of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.155 | hwSmartPDUMainInputNWireCurrent | Main input-N wire current | 主路-输入N线电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input-N wire current of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.156 | hwSmartPDUMainInputL1Thdu | Main input-L1 THDu | 主路-L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input-L1 THDu of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.157 | hwSmartPDUMainInputL2Thdu | Main input-L2 THDu | 主路-L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input-L2 THDu of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.158 | hwSmartPDUMainInputL3Thdu | Main input-L3 THDu | 主路-L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input-L3 THDu of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.159 | hwSmartPDUMainInputL1Thdi | Main input-L1 THDi | 主路-L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input-L1 THDi of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.160 | hwSmartPDUMainInputL2Thdi | Main input-L2 THDi | 主路-L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input-L2 THDi of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.161 | hwSmartPDUMainInputL3Thdi | Main input-L3 THDi | 主路-L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Main input-L3 THDi of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.162 | hwSmartPDUMainInputTotalInputActivePower | Main input-total input active power | 主路-总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main input-total input active power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.163 | hwSmartPDUMainInputTotalInputApparentPower | Main input-total input apparent power | 主路-总输入视在功率 | 0-Read_Only | 只读 | 0..7500 | 0..7500 | Main input-total input apparent power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.164 | hwSmartPDUMainInputTotalInputReactivePower | Main input-total input reactive power | 主路-总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main input-total input reactive power of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.165 | hwSmartPDUMainInputNPeInputVoltage | Main input-N-PE input voltage | 主路-输入N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input-N-PE input voltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.166 | hwSmartPDUCabinetInputPower | Cabinet input power | 机柜输入功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Cabinet input power of the device config table for the Smart PDU.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.167 | hwSmartPDUCabinetHeatConsumptionPower | Cabinet heat consumption power | 机柜热耗功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Cabinet heat consumption power of the device config table for the Smart PDU.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.168 | hwSmartPDUIt1CabinetNumber | IT1 cabinet number | IT支路1数目 | 0-Read_Only | 只读 | 0..24 | 0..24 | IT1 cabinet number of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.169 | hwSmartPDUPduTotalInputLoadFactor | PDU total input load factor | PDU总输入负载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | PDU total input load factor of the device config table for the Smart PDU.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.170 | hwSmartPDUMeterPhaseL1Voltage | Meter-phase L1 voltage | 电表-L1相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Meter-phase L1 voltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.171 | hwSmartPDUMeterPhaseL2Voltage | Meter-phase L2 voltage | 电表-L2相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Meter-phase L2 voltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.172 | hwSmartPDUMeterPhaseL3Voltage | Meter-phase L3 voltage | 电表-L3相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Meter-phase L3 voltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.173 | hwSmartPDUMeterPhaseL1Angel | Meter-phase L1 angel | 电表-L1相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Meter-phase L1 angel of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.174 | hwSmartPDUMeterPhaseL2Angel | Meter-phase L2 angel | 电表-L2相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Meter-phase L2 angel of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.175 | hwSmartPDUMeterPhaseL3Angel | Meter-phase L3 angel | 电表-L3相相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Meter-phase L3 angel of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:°.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.176 | hwSmartPDUMeterChannel1PhaseL1Current | Meter-channel 1 phase L1 current | 电表-通道1 L1相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Meter-channel 1 phase L1 current of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.177 | hwSmartPDUMeterChannel1PhaseL2Current | Meter-channel 1 phase L2 current | 电表-通道1 L2相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Meter-channel 1 phase L2 current of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.178 | hwSmartPDUMeterChannel1PhaseL3Current | Meter-channel 1 phase L3 current | 电表-通道1 L3相电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Meter-channel 1 phase L3 current of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.179 | hwSmartPDUMeterChannel1ActivePower | Meter-channel1 active power | 电表-通道1 有功功率 | 0-Read_Only | 只读 | -75000..75000 | -75000..75000 | Meter-channel1 active power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.180 | hwSmartPDUMeterChannel1ReactPower | Meter-channel1 react power | 电表-通道1 总无功功率 | 0-Read_Only | 只读 | -75000..75000 | -75000..75000 | Meter-channel1 react power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.181 | hwSmartPDUMeterChannel1ApparentPower | Meter-channel1 apparent power | 电表-通道1 总视在功率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | Meter-channel1 apparent power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.182 | hwSmartPDUMeterChannel1PowerFactor | Meter-channel1 power factor | 电表-通道1 功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Meter-channel1 power factor of the device config table for the Smart PDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.183 | hwSmartPDUMeterChannel1PhaseL1ActivePower | Meter-channel1 phase L1 active power | 电表-通道1 L1相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Meter-channel1 phase L1 active power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.184 | hwSmartPDUMeterChannel1PhaseL2ActivePower | Meter-channel1 phase L2 active power | 电表-通道1 L2相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Meter-channel1 phase L2 active power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.185 | hwSmartPDUMeterChannel1PhaseL3ActivePower | Meter-channel1 phase L3 active power | 电表-通道1 L3相有功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Meter-channel1 phase L3 active power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.186 | hwSmartPDUMeterChannel1PhaseL1ReactPower | Meter-channel1 phase L1 react power | 电表-通道1 L1相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Meter-channel1 phase L1 react power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.187 | hwSmartPDUMeterChannel1PhaseL2ReactPower | Meter-channel1 phase L2 react power | 电表-通道1 L2相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Meter-channel1 phase L2 react power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.188 | hwSmartPDUMeterChannel1PhaseL3ReactPower | Meter-channel1 phase L3 react power | 电表-通道1 L3相无功功率 | 0-Read_Only | 只读 | -25000..25000 | -25000..25000 | Meter-channel1 phase L3 react power of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.189 | hwSmartPDUMeterChannel1PhaseL1PowerFactor | Meter-channel1 phase L1 power factor | 电表-通道1 L1相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Meter-channel1 phase L1 power factor of the device config table for the Smart PDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.190 | hwSmartPDUMeterChannel1PhaseL2PowerFactor | Meter-channel1 phase L2 power factor | 电表-通道1 L2相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Meter-channel1 phase L2 power factor of the device config table for the Smart PDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.191 | hwSmartPDUMeterChannel1PhaseL3PowerFactor | Meter-channel1 phase L3 power factor | 电表-通道1 L3相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Meter-channel1 phase L3 power factor of the device config table for the Smart PDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.192 | hwSmartPDUMeterChannel1PowerConsumption | Meter-channel1 power consumption | 电表-通道1 有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Meter-channel1 power consumption of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.193 | hwSmartPDUMeterChannel1PhaseL1ActiveElectricity | Meter-channel1 phase L1 active electricity | 电表-通道1 L1相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Meter-channel1 phase L1 active electricity of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.194 | hwSmartPDUMeterChannel1PhaseL2ActiveElectricity | Meter-channel1 phase L2 active electricity | 电表-通道1 L2相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Meter-channel1 phase L2 active electricity of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.195 | hwSmartPDUMeterChannel1PhaseL3ActiveElectricity | Meter-channel1 phase L3 active electricity | 电表-通道1 L3相有功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Meter-channel1 phase L3 active electricity of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.196 | hwSmartPDUMeterThdVa | Meter-THD VA | 电表-THD VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-THD VA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.197 | hwSmartPDUMeterBasicWaveVa | Meter-basic wave VA | 电表-基波 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-basic wave VA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.198 | hwSmartPDUMeter3ThThdVa | Meter-3th THD VA | 电表-3次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-3th THD VA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.199 | hwSmartPDUMeter5ThThdVa | Meter-5th THD VA | 电表-5次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-5th THD VA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.200 | hwSmartPDUMeter7ThThdVa | Meter-7th THD VA | 电表-7次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-7th THD VA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.1.1.201 | hwSmartPDURunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2 | hwSmartPDURunning2Table | / | / |  |  | / | / | The running table of Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.1 | hwSmartPDURunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.2 | hwSmartPDUMeter9ThThdVa | Meter-9th THD VA | 电表-9次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-9th THD VA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.3 | hwSmartPDUMeter11ThThdVa | Meter-11th THD VA | 电表-11次谐波含量 VA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-11th THD VA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.4 | hwSmartPDUMeterThdVb | Meter-THD VB | 电表-THD VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-THD VB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.5 | hwSmartPDUMeterBasicWaveVb | Meter-basic wave VB | 电表-基波 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-basic wave VB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.6 | hwSmartPDUMeter3ThThdVb | Meter-3th THD VB | 电表-3次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-3th THD VB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.7 | hwSmartPDUMeter5ThThdVb | Meter-5th THD VB | 电表-5次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-5th THD VB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.8 | hwSmartPDUMeter7ThThdVb | Meter-7th THD VB | 电表-7次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-7th THD VB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.9 | hwSmartPDUMeter9ThThdVb | Meter-9th THD VB | 电表-9次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-9th THD VB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.10 | hwSmartPDUMeter11ThThdVb | Meter-11th THD VB | 电表-11次谐波含量 VB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-11th THD VB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.11 | hwSmartPDUMeterThdVc | Meter-THD VC | 电表-THD VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-THD VC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.12 | hwSmartPDUMeterBasicWaveVc | Meter-basic wave VC | 电表-基波 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-basic wave VC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.13 | hwSmartPDUMeter3ThThdVc | Meter-3th THD VC | 电表-3次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-3th THD VC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.14 | hwSmartPDUMeter5ThThdVc | Meter-5th THD VC | 电表-5次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-5th THD VC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.15 | hwSmartPDUMeter7ThThdVc | Meter-7th THD VC | 电表-7次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-7th THD VC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.16 | hwSmartPDUMeter9ThThdVc | Meter-9th THD VC | 电表-9次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-9th THD VC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.17 | hwSmartPDUMeter11ThThdVc | Meter-11th THD VC | 电表-11次谐波含量 VC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-11th THD VC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.18 | hwSmartPDUMeterThdIa | Meter-THD IA | 电表-THD IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-THD IA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.19 | hwSmartPDUMeterBasicWaveIa | Meter-basic wave IA | 电表-基波 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-basic wave IA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.20 | hwSmartPDUMeter3ThThdIa | Meter-3th THD IA | 电表-3次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-3th THD IA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.21 | hwSmartPDUMeter5ThThdIa | Meter-5th THD IA | 电表-5次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-5th THD IA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.22 | hwSmartPDUMeter7ThThdIa | Meter-7th THD IA | 电表-7次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-7th THD IA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.23 | hwSmartPDUMeter9ThThdIa | Meter-9th THD IA | 电表-9次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-9th THD IA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.24 | hwSmartPDUMeter11ThThdIa | Meter-11th THD IA | 电表-11次谐波含量 IA | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-11th THD IA of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.25 | hwSmartPDUMeterThdIb | Meter-THD IB | 电表-THD IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-THD IB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.26 | hwSmartPDUMeterBasicWaveIb | Meter-basic wave IB | 电表-基波 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-basic wave IB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.27 | hwSmartPDUMeter3ThThdIb | Meter-3th THD IB | 电表-3次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-3th THD IB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.28 | hwSmartPDUMeter5ThThdIb | Meter-5th THD IB | 电表-5次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-5th THD IB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.29 | hwSmartPDUMeter7ThThdIb | Meter-7th THD IB | 电表-7次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-7th THD IB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.30 | hwSmartPDUMeter9ThThdIb | Meter-9th THD IB | 电表-9次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-9th THD IB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.31 | hwSmartPDUMeter11ThThdIb | Meter-11th THD IB | 电表-11次谐波含量 IB | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-11th THD IB of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.32 | hwSmartPDUMeterThdIc | Meter-THD IC | 电表-THD IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-THD IC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.33 | hwSmartPDUMeterBasicWaveIc | Meter-basic wave IC | 电表-基波 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-basic wave IC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.34 | hwSmartPDUMeter3ThThdIc | Meter-3th THD IC | 电表-3次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-3th THD IC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.35 | hwSmartPDUMeter5ThThdIc | Meter-5th THD IC | 电表-5次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-5th THD IC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.36 | hwSmartPDUMeter7ThThdIc | Meter-7th THD IC | 电表-7次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-7th THD IC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.37 | hwSmartPDUMeter9ThThdIc | Meter-9th THD IC | 电表-9次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-9th THD IC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.38 | hwSmartPDUMeter11ThThdIc | Meter-11th THD IC | 电表-11次谐波含量 IC | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Meter-11th THD IC of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.39 | hwSmartPDUMainInputL1Temperature | Main input-L1 temperature | 主路-L1母排温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input-L1 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.40 | hwSmartPDUMainInputL2Temperature | Main input-L2 temperature | 主路-L2母排温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input-L2 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.41 | hwSmartPDUMainInputL3Temperature | Main input-L3 temperature | 主路-L3母排温度 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main input-L3 temperature of the device config table for the Smart PDU.Multiple:100.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.42 | hwSmartPDUInputSwitchStatus | Input switch status | 输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Input switch status of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.43 | hwSmartPDUUps2InputSwitchStatus | UPS2 input switch status | UPS2输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | UPS2 input switch status of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.44 | hwSmartPDUUps1InputSwitchStatus | UPS1 input switch status | UPS1输入开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | UPS1 input switch status of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.45 | hwSmartPDUUps1OutputSwitchStatus | UPS1 output switch status | UPS1输出开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | UPS1 output switch status of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.46 | hwSmartPDUUps2OutputSwitchStatus | UPS2 output switch status | UPS2输出开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | UPS2 output switch status of the device config table for the Smart PDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.9.82.2.1.100 | hwSmartPDURunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3 | hwSmartPDUConfig3Table | / | / |  |  | / | / | The config table of Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.1 | hwSmartPDUConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.2 | hwSmartPDUDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.3 | hwSmartPDUCurrentHarmonicAlarm | Current harmonic alarm | 电流谐波告警 | 1-Read_Write | 读写 | 0..300 | 0..300 | Current harmonic alarm of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.4 | hwSmartPDUOvervoltage | Overvoltage | 系统过压 | 1-Read_Write | 读写 | 1050..1250 | 1050..1250 | Overvoltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.5 | hwSmartPDUUndervoltage | Undervoltage | 系统欠压 | 1-Read_Write | 读写 | 750..950 | 750..950 | Undervoltage of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.6 | hwSmartPDUOverload | Overload | 负载过载 | 1-Read_Write | 读写 | 1000..1200 | 1000..1200 | Overload of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.7 | hwSmartPDUPhaseOpenVoltage | Phase open voltage | 系统缺相电压 | 1-Read_Write | 读写 | 0..60 | 0..60 | Phase open voltage of the device config table for the Smart PDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.8 | hwSmartPDUEnableHarmonicAlarm | Enable harmonic alarm | 谐波告警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable harmonic alarm of the device config table for the Smart PDU. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.9 | hwSmartPDUVoltageHarmonicAlarm | Voltage harmonic alarm | 电压谐波告警 | 1-Read_Write | 读写 | 10..300 | 10..300 | Voltage harmonic alarm of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.10 | hwSmartPDUOverfrequency | Overfrequency | 系统频率越限 | 1-Read_Write | 读写 | 10..100 | 10..100 | Overfrequency of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.11 | hwSmartPDULoadOvercurrentThreshold | Load overcurrent threshold | 负载电流高阈值 | 1-Read_Write | 读写 | 800..1000 | 800..1000 | Load overcurrent threshold of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.12 | hwSmartPDULoadUndercurrentThreshold | Load undercurrent threshold | 负载电流低阈值 | 1-Read_Write | 读写 | 300..800 | 300..800 | Load undercurrent threshold of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.13 | hwSmartPDUThreePhaseCurrentImbalance | Three-phase current imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..500 | 0..500 | Three-phase current imbalance of the device config table for the Smart PDU.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.14 | hwSmartPDURecordedNumberOfItBranch1MonitoringPoints | Recorded number of IT branch 1 monitoring points | 记录IT路检测点个数 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Recorded number of IT branch 1 monitoring points of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.15 | hwSmartPDUQf7CollectionDisplayFlag | QF7 collection display flag | QF7 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF7 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.16 | hwSmartPDUQf8CollectionDisplayFlag | QF8 collection display flag | QF8 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF8 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.17 | hwSmartPDUQf9CollectionDisplayFlag | QF9 collection display flag | QF9 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF9 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.18 | hwSmartPDUQf10CollectionDisplayFlag | QF10 collection display flag | QF10 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF10 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.19 | hwSmartPDUQf11CollectionDisplayFlag | QF11 collection display flag | QF11 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF11 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.20 | hwSmartPDUQf12CollectionDisplayFlag | QF12 collection display flag | QF12 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF12 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.21 | hwSmartPDUQf13CollectionDisplayFlag | QF13 collection display flag | QF13 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF13 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.22 | hwSmartPDUQf14CollectionDisplayFlag | QF14 collection display flag | QF14 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF14 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.23 | hwSmartPDUQf15CollectionDisplayFlag | QF15 collection display flag | QF15 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF15 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.24 | hwSmartPDUQf16CollectionDisplayFlag | QF16 collection display flag | QF16 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF16 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.25 | hwSmartPDUQf17CollectionDisplayFlag | QF17 collection display flag | QF17 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF17 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.26 | hwSmartPDUQf18CollectionDisplayFlag | QF18 collection display flag | QF18 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF18 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.27 | hwSmartPDUQf19CollectionDisplayFlag | QF19 collection display flag | QF19 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF19 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.28 | hwSmartPDUQf20CollectionDisplayFlag | QF20 collection display flag | QF20 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF20 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.29 | hwSmartPDUQf21CollectionDisplayFlag | QF21 collection display flag | QF21 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF21 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.30 | hwSmartPDUQf22CollectionDisplayFlag | QF22 collection display flag | QF22 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF22 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.31 | hwSmartPDUQf23CollectionDisplayFlag | QF23 collection display flag | QF23 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF23 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.32 | hwSmartPDUQf24CollectionDisplayFlag | QF24 collection display flag | QF24 采集显示标志 | 1-Read_Write | 读写 | 0..1 | 0..1 | QF24 collection display flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.33 | hwSmartPDUItBranch7PhaseFlag | IT branch 7 phase flag | IT路-支路7相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 7 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.34 | hwSmartPDUItBranch8PhaseFlag | IT branch 8 phase flag | IT路-支路8相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 8 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.35 | hwSmartPDUItBranch9PhaseFlag | IT branch 9 phase flag | IT路-支路9相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 9 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.36 | hwSmartPDUItBranch10PhaseFlag | IT branch 10 phase flag | IT路-支路10相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 10 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.37 | hwSmartPDUItBranch11PhaseFlag | IT branch 11 phase flag | IT路-支路11相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 11 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.38 | hwSmartPDUItBranch12PhaseFlag | IT branch 12 phase flag | IT路-支路12相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 12 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.39 | hwSmartPDUItBranch13PhaseFlag | IT branch 13 phase flag | IT路-支路13相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 13 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.40 | hwSmartPDUItBranch14PhaseFlag | IT branch 14 phase flag | IT路-支路14相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 14 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.41 | hwSmartPDUItBranch15PhaseFlag | IT branch 15 phase flag | IT路-支路15相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 15 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.42 | hwSmartPDUItBranch16PhaseFlag | IT branch 16 phase flag | IT路-支路16相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 16 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.43 | hwSmartPDUItBranch17PhaseFlag | IT branch 17 phase flag | IT路-支路17相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 17 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.44 | hwSmartPDUItBranch18PhaseFlag | IT branch 18 phase flag | IT路-支路18相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 18 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.45 | hwSmartPDUItBranch19PhaseFlag | IT branch 19 phase flag | IT路-支路19相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 19 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.46 | hwSmartPDUItBranch20PhaseFlag | IT branch 20 phase flag | IT路-支路20相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 20 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.47 | hwSmartPDUItBranch21PhaseFlag | IT branch 21 phase flag | IT路-支路21相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 21 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.48 | hwSmartPDUItBranch22PhaseFlag | IT branch 22 phase flag | IT路-支路22相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 22 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.49 | hwSmartPDUItBranch23PhaseFlag | IT branch 23 phase flag | IT路-支路23相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 23 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.50 | hwSmartPDUItBranch24PhaseFlag | IT branch 24 phase flag | IT路-支路24相位标志 | 1-Read_Write | 读写 | 0..65535 | 0..65535 | IT branch 24 phase flag of the device config table for the Smart PDU.
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.51 | hwSmartPDUElectricMeterType | Electric meter type | 是否有电表 | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Electric meter type of the device config table for the Smart PDU. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.52 | hwSmartPDUNtcType | NTC type | 是否有NTC | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | NTC type of the device config table for the Smart PDU. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.9.82.3.1.101 | hwSmartPDUConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Smart PDU.

## 5G high density embedded power
5G高密度嵌入式电源
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.102 | 5GHighDensityEmbeddedPower | 5G high density embedded power | 5G高密度嵌入式电源 | / | / | / | / | 5G High Density Embedded Power Equipment.
1.3.6.1.4.1.2011.6.178.1.1.102.1 | hw5GHighDensityEmbeddedPowerRunning1Table | / | / |  |  | / | / | The running table of 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.1 | hw5GHighDensityEmbeddedPowerRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.2 | hw5GHighDensityEmbeddedPowerDcOutputVoltage | DC output voltage | 直流电压 | 0-Read_Only | 只读 | -300000..300000 | -300000..300000 | DC Output Voltage of the device config table for the 5G High Density Embedded Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.3 | hw5GHighDensityEmbeddedPowerLoad1Current | Load 1 current | 负载1电流 | 0-Read_Only | 只读 | -300000..300000 | -300000..300000 | Load 1 Current of the device config table for the 5G High Density Embedded Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.4 | hw5GHighDensityEmbeddedPowerLoad2Current | Load 2 current | 负载2电流 | 0-Read_Only | 只读 | -300000..300000 | -300000..300000 | Load 2 Current of the device config table for the 5G High Density Embedded Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.5 | hw5GHighDensityEmbeddedPowerLoadFuseStatus | / | / | 0-Read_Only | 只读 | 0..255 | / | Load Fuse Status of the device config table for the 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.6 | hw5GHighDensityEmbeddedPowerLoadFuse1Status | Load fuse 1 status | 负载熔丝1状态 | 0-Read_Only | 只读 | close(1), broken(2), unknown(255) | [闭合=1]/[断开=2] | Load Fuse 1 Status of the device config table for the 5G High Density Embedded Power. Value 1 indicate close Value 2 indicate Broken
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.7 | hw5GHighDensityEmbeddedPowerLoadFuse2Status | Load fuse 2 status | 负载熔丝2状态 | 0-Read_Only | 只读 | close(1), broken(2), unknown(255) | [闭合=1]/[断开=2] | Load Fuse 2 Status of the device config table for the 5G High Density Embedded Power. Value 1 indicate close Value 2 indicate Broken
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.8 | hw5GHighDensityEmbeddedPowerContactor1Status | Contactor 1 status | 接触器1状态 | 0-Read_Only | 只读 | close(1), broken(2), unknown(255) | [闭合=1]/[断开=2] | Contactor 1 Status of the device config table for the 5G High Density Embedded Power. Value 1 indicate close Value 2 indicate Broken
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.9 | hw5GHighDensityEmbeddedPowerContactor2Status | Contactor 2 status | 接触器2状态 | 0-Read_Only | 只读 | close(1), broken(2), unknown(255) | [闭合=1]/[断开=2] | Contactor 2 Status of the device config table for the 5G High Density Embedded Power. Value 1 indicate close Value 2 indicate Broken
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.10 | hw5GHighDensityEmbeddedPowerTotalLoad1Power | Total load 1 power | 负载1总功率 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Total Load 1 Power of the device config table for the 5G High Density Embedded Power.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.11 | hw5GHighDensityEmbeddedPowerTotalLoad2Power | Total load 2 power | 负载2总功率 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Total Load 2 Power of the device config table for the 5G High Density Embedded Power.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.12 | hw5GHighDensityEmbeddedPowerTotalLoad1EnergyConsumption | Total load 1 energy consumption | 负载1累积功耗 | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Total Load 1 Energy Consumption of the device config table for the 5G High Density Embedded Power.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.13 | hw5GHighDensityEmbeddedPowerTotalLoad2EnergyConsumption | Total load 2 energy consumption | 负载2累积功耗 | 0-Read_Only | 只读 | 0..2147483600 | 0..2147483600 | Total Load 2 Energy Consumption of the device config table for the 5G High Density Embedded Power.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.14 | hw5GHighDensityEmbeddedPowerCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the 5G High Density Embedded Power. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.15 | hw5GHighDensityEmbeddedPowerSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.16 | hw5GHighDensityEmbeddedPowerPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..5 | 1..5 | Port No. of the device config table for the 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.17 | hw5GHighDensityEmbeddedPowerModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus Address of the device config table for the 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.1.1.101 | hw5GHighDensityEmbeddedPowerRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.2 | hw5GHighDensityEmbeddedPowerConfig2Table | / | / |  |  | / | / | The config table of 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.1 | hw5GHighDensityEmbeddedPowerConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.2 | hw5GHighDensityEmbeddedPowerDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the 5G High Density Embedded Power.
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.3 | hw5GHighDensityEmbeddedPowerLlvd1Voltage | LLVD 1 voltage | 负载1下电电压 | 1-Read_Write | 读写 | 360..560 | 360..560 | LLVD 1 Voltage of the device config table for the 5G High Density Embedded Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.4 | hw5GHighDensityEmbeddedPowerLlvd1ReconnectionVoltage | LLVD 1 reconnection voltage | 负载1上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | LLVD 1 Reconnection Voltage of the device config table for the 5G High Density Embedded Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.5 | hw5GHighDensityEmbeddedPowerLlvd2Voltage | LLVD 2 voltage | 负载2下电电压 | 1-Read_Write | 读写 | 360..560 | 360..560 | LLVD 2 Voltage of the device config table for the 5G High Density Embedded Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.6 | hw5GHighDensityEmbeddedPowerLlvd2ReconnectionVoltage | LLVD 2 reconnection voltage | 负载2上电电压 | 1-Read_Write | 读写 | 370..580 | 370..580 | LLVD 2 Reconnection Voltage of the device config table for the 5G High Density Embedded Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.7 | hw5GHighDensityEmbeddedPowerLlvd1Enabled | LLVD 1 enabled | 负载1下电允许 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD 1 Enabled of the device config table for the 5G High Density Embedded Power. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.8 | hw5GHighDensityEmbeddedPowerLlvd2Enabled | LLVD 2 enabled | 负载2下电允许 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | LLVD 2 Enabled of the device config table for the 5G High Density Embedded Power. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.9 | hw5GHighDensityEmbeddedPowerLoad1Control | Load 1 control | 负载1上下电 | 1-Read_Write | 读写 | reconnection(1), disconnect(2), unknown(255) | [上电=1]/[下电=2] | Load 1 Control of the device config table for the 5G High Density Embedded Power. Value 1 indicate reconnection Value 2 indicate disconnect
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.10 | hw5GHighDensityEmbeddedPowerLoad2Control | Load 2 control | 负载2上下电 | 1-Read_Write | 读写 | reconnection(1), disconnect(2), unknown(255) | [上电=1]/[下电=2] | Load 1 Control of the device config table for the 5G High Density Embedded Power. Value 1 indicate reconnection Value 2 indicate disconnect
1.3.6.1.4.1.2011.6.178.1.1.102.2.1.101 | hw5GHighDensityEmbeddedPowerConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of 5G High Density Embedded Power.

## Ac_Hm25rc
Ac_Hm25rc
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.92 | AcHm25rc | Ac_Hm25rc | Ac_Hm25rc | / | / | / | / | Ac_Hm25rc Equipment.
1.3.6.1.4.1.2011.6.178.1.1.92.1 | hwAcHm25rcRunning1Table | / | / |  |  | / | / | The running table of Ac_Hm25rc.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.1 | hwAcHm25rcRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Ac_Hm25rc.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.2 | hwAcHm25rcCrewStatus | Crew status | 机组状态 | 0-Read_Only | 只读 | off(1), on(2), downtime(3), groupcontrolstandby(4), unknown(255) | [关机=1]/[开机=2]/[停机中=3]/[群控待机=4] | Crew status of the device config table for the Ac_Hm25rc. Value 1 indicate off Value 2 indicate on Value 3 indicate downtime Value 4 indicate group control standby
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.3 | hwAcHm25rcInletWaterTemperature | Inlet water temperature | 进水温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet water temperature of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.4 | hwAcHm25rcOutletWaterTemperature | Outlet water temperature | 出水温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Outlet Water temperature of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.5 | hwAcHm25rcReturnAirTemperature1 | Return air temperature 1 | 回风温度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Return air temperature 1 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.6 | hwAcHm25rcReturnAirTemperature2 | Return air temperature 2 | 回风温度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Return air temperature 2 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.7 | hwAcHm25rcAverageReturnAirTemperature | Average return air temperature | 回风温度均值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average return air temperature of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.8 | hwAcHm25rcReturnAirHumidity | Return air humidity | 回风湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Return air humidity of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.9 | hwAcHm25rcSupplyAirTemperature1 | Supply air temperature 1 | 送风温度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Supply air temperature 1 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.10 | hwAcHm25rcSupplyAirTemperature2 | Supply air temperature 2 | 送风温度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Supply air temperature 2 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.11 | hwAcHm25rcAverageSupplyAirTemperature | Average supply air temperature | 送风温度均值 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average supply air temperature of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.12 | hwAcHm25rcSupplyAirHumidity | Supply air humidity | 送风湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Supply air humidity of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.13 | hwAcHm25rcColdAisleTemperature1 | Cold aisle temperature 1 | 冷通道温度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle temperature 1 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.14 | hwAcHm25rcColdAisleTemperature2 | Cold aisle temperature 2 | 冷通道温度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle temperature 2 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.15 | hwAcHm25rcColdAisleTemperature3 | Cold aisle temperature 3 | 冷通道温度3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle temperature 3 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.16 | hwAcHm25rcColdAisleTemperature4 | Cold aisle temperature 4 | 冷通道温度4 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle temperature 4 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.17 | hwAcHm25rcColdAisleTemperature5 | Cold aisle temperature 5 | 冷通道温度5 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle temperature 5 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.18 | hwAcHm25rcHotAisleTemperature1 | Hot aisle temperature 1 | 热通道温度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle temperature 1 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.19 | hwAcHm25rcHotAisleTemperature2 | Hot aisle temperature 2 | 热通道温度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle temperature 2 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.20 | hwAcHm25rcHotAisleTemperature3 | Hot aisle temperature 3 | 热通道温度3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle temperature 3 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.21 | hwAcHm25rcHotAisleTemperature4 | Hot aisle temperature 4 | 热通道温度4 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle temperature 4 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.22 | hwAcHm25rcHotAisleTemperature5 | Hot aisle temperature 5 | 热通道温度5 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle temperature 5 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.23 | hwAcHm25rcColdAisleHumidity1 | Cold aisle humidity 1 | 冷通道湿度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle humidity 1 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.24 | hwAcHm25rcColdAisleHumidity2 | Cold aisle humidity 2 | 冷通道湿度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle humidity 2 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.25 | hwAcHm25rcColdAisleHumidity3 | Cold aisle humidity 3 | 冷通道湿度3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle humidity 3 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.26 | hwAcHm25rcColdAisleHumidity4 | Cold aisle humidity 4 | 冷通道湿度4 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle humidity 4 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.27 | hwAcHm25rcColdAisleHumidity5 | Cold aisle humidity 5 | 冷通道湿度5 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle humidity 5 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.28 | hwAcHm25rcHotAisleHumidity1 | Hot aisle humidity 1 | 热通道湿度1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle humidity 1 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.29 | hwAcHm25rcHotAisleHumidity2 | Hot aisle humidity 2 | 热通道湿度2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle humidity 2 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.30 | hwAcHm25rcHotAisleHumidity3 | Hot aisle humidity 3 | 热通道湿度3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle humidity 3 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.31 | hwAcHm25rcHotAisleHumidity4 | Hot aisle humidity 4 | 热通道湿度4 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle humidity 4 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.32 | hwAcHm25rcHotAisleHumidity5 | Hot aisle humidity 5 | 热通道湿度5 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Hot aisle humidity 5 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.33 | hwAcHm25rcAverageTemperatureOfAllColdAisles | Average temperature of all cold aisles | 冷通道均温 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average temperature of all cold aisles of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.34 | hwAcHm25rcAverageTemperatureOfAllHotAisles | Average temperature of all hot aisles | 热通道均温 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average temperature of all hot aisles of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.35 | hwAcHm25rcColdAisleAvgHumid | Cold aisle avg humid | 冷通道均湿 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Cold aisle avg humid of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.36 | hwAcHm25rcAverageHumidityOfAllHotAisles | Average humidity of all hot aisles | 热通道均湿 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average humidity of all hot aisles of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.37 | hwAcHm25rcOutletWaterPressure | Outlet water pressure | 出水压力 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Outlet water pressure of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Bar.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.38 | hwAcHm25rcInletWaterPressure | Inlet water pressure | 进水压力 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inlet water pressure of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Bar.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.39 | hwAcHm25rcWaterValveOutputPercentage | Water valve output percentage | 水阀输出百分比 | 0-Read_Only | 只读 | 0..100 | 0..100 | Water valve output percentage of the device config table for the Ac_Hm25rc.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.40 | hwAcHm25rcFanOutputPercentage | Fan output percentage | 风机输出百分比 | 0-Read_Only | 只读 | 0..100 | 0..100 | Fan output percentage of the device config table for the Ac_Hm25rc.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.41 | hwAcHm25rcCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Ac_Hm25rc. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.42 | hwAcHm25rcPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Ac_Hm25rc.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.43 | hwAcHm25rcModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Ac_Hm25rc.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.44 | hwAcHm25rcColdAisleSettings | Cold aisle settings | 冷通道设置 | 0-Read_Only | 只读 | 150..250 | 150..250 | Cold aisle settings of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.45 | hwAcHm25rcHotAisleSettings | Hot aisle settings | 热通道设置 | 0-Read_Only | 只读 | 160..400 | 160..400 | Hot aisle settings of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.46 | hwAcHm25rcReturnAirTemperature3 | Return air temperature 3 | 回风温度3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Return air temperature 3 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.47 | hwAcHm25rcSupplyAirTemperature3 | Supply air temperature 3 | 送风温度3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Supply air temperature 3 of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.1.1.101 | hwAcHm25rcRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Ac_Hm25rc.
1.3.6.1.4.1.2011.6.178.1.1.92.2 | hwAcHm25rcConfig2Table | / | / |  |  | / | / | The config table of Ac_Hm25rc.
1.3.6.1.4.1.2011.6.178.1.1.92.2.1.1 | hwAcHm25rcConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Ac_Hm25rc.
1.3.6.1.4.1.2011.6.178.1.1.92.2.1.2 | hwAcHm25rcDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Ac_Hm25rc.
1.3.6.1.4.1.2011.6.178.1.1.92.2.1.3 | hwAcHm25rcSupplyAirSettings | Supply air settings | 送风设置 | 1-Read_Write | 读写 | 150..250 | 150..250 | Supply air settings of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.2.1.4 | hwAcHm25rcReturnAirSetting | Return air setting | 回风设置 | 1-Read_Write | 读写 | 160..400 | 160..400 | Return air setting of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.92.2.1.5 | hwAcHm25rcMonitorSwitch | Monitor switch | 监控开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Monitor switch of the device config table for the Ac_Hm25rc. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.92.2.1.6 | hwAcHm25rcHumiditySetting | Humidity setting | 湿度设置 | 1-Read_Write | 读写 | 200..800 | 200..800 | Humidity setting of the device config table for the Ac_Hm25rc.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.92.2.1.101 | hwAcHm25rcConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Ac_Hm25rc.

## Acrel AMC16ZH Meter
Acrel AMC16ZH Meter
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.128 | AcrelAMC16ZHMeter | Acrel AMC16ZH Meter | Acrel AMC16ZH Meter | / | / | / | / | Acrel AMC16ZH Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.128.1 | hwAcrelAMC16ZHMeterRunning1Table | / | / |  |  | / | / | The running table of Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.1 | hwAcrelAMC16ZHMeterRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.2 | hwAcrelAMC16ZHMeterBranch1SwitchStatusOnSideA | Branch 1 switch status on side A | A面分路1开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 1 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.3 | hwAcrelAMC16ZHMeterBranch2SwitchStatusOnSideA | Branch 2 switch status on side A | A面分路2开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 2 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.4 | hwAcrelAMC16ZHMeterBranch3SwitchStatusOnSideA | Branch 3 switch status on side A | A面分路3开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 3 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.5 | hwAcrelAMC16ZHMeterBranch4SwitchStatusOnSideA | Branch 4 switch status on side A | A面分路4开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 4 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.6 | hwAcrelAMC16ZHMeterBranch5SwitchStatusOnSideA | Branch 5 switch status on side A | A面分路5开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 5 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.7 | hwAcrelAMC16ZHMeterBranch6SwitchStatusOnSideA | Branch 6 switch status on side A | A面分路6开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 6 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.8 | hwAcrelAMC16ZHMeterBranch7SwitchStatusOnSideA | Branch 7 switch status on side A | A面分路7开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 7 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.9 | hwAcrelAMC16ZHMeterBranch8SwitchStatusOnSideA | Branch 8 switch status on side A | A面分路8开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 8 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.10 | hwAcrelAMC16ZHMeterBranch9SwitchStatusOnSideA | Branch 9 switch status on side A | A面分路9开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 9 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.11 | hwAcrelAMC16ZHMeterBranch10SwitchStatusOnSideA | Branch 10 switch status on side A | A面分路10开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 10 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.12 | hwAcrelAMC16ZHMeterBranch11SwitchStatusOnSideA | Branch 11 switch status on side A | A面分路11开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 11 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.13 | hwAcrelAMC16ZHMeterBranch12SwitchStatusOnSideA | Branch 12 switch status on side A | A面分路12开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 12 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.14 | hwAcrelAMC16ZHMeterBranch13SwitchStatusOnSideA | Branch 13 switch status on side A | A面分路13开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 13 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.15 | hwAcrelAMC16ZHMeterBranch14SwitchStatusOnSideA | Branch 14 switch status on side A | A面分路14开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 14 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.16 | hwAcrelAMC16ZHMeterBranch15SwitchStatusOnSideA | Branch 15 switch status on side A | A面分路15开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 15 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.17 | hwAcrelAMC16ZHMeterBranch16SwitchStatusOnSideA | Branch 16 switch status on side A | A面分路16开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 16 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.18 | hwAcrelAMC16ZHMeterBranch17SwitchStatusOnSideA | Branch 17 switch status on side A | A面分路17开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 17 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.19 | hwAcrelAMC16ZHMeterBranch18SwitchStatusOnSideA | Branch 18 switch status on side A | A面分路18开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 18 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.20 | hwAcrelAMC16ZHMeterBranch19SwitchStatusOnSideA | Branch 19 switch status on side A | A面分路19开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 19 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.21 | hwAcrelAMC16ZHMeterBranch20SwitchStatusOnSideA | Branch 20 switch status on side A | A面分路20开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 20 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.22 | hwAcrelAMC16ZHMeterBranch21SwitchStatusOnSideA | Branch 21 switch status on side A | A面分路21开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 21 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.23 | hwAcrelAMC16ZHMeterBranch22SwitchStatusOnSideA | Branch 22 switch status on side A | A面分路22开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 22 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.24 | hwAcrelAMC16ZHMeterBranch23SwitchStatusOnSideA | Branch 23 switch status on side A | A面分路23开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 23 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.25 | hwAcrelAMC16ZHMeterBranch24SwitchStatusOnSideA | Branch 24 switch status on side A | A面分路24开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 24 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.26 | hwAcrelAMC16ZHMeterBranch25SwitchStatusOnSideA | Branch 25 switch status on side A | A面分路25开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 25 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.27 | hwAcrelAMC16ZHMeterBranch26SwitchStatusOnSideA | Branch 26 switch status on side A | A面分路26开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 26 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.28 | hwAcrelAMC16ZHMeterBranch27SwitchStatusOnSideA | Branch 27 switch status on side A | A面分路27开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 27 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.29 | hwAcrelAMC16ZHMeterBranch28SwitchStatusOnSideA | Branch 28 switch status on side A | A面分路28开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 28 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.30 | hwAcrelAMC16ZHMeterBranch29SwitchStatusOnSideA | Branch 29 switch status on side A | A面分路29开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 29 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.31 | hwAcrelAMC16ZHMeterBranch30SwitchStatusOnSideA | Branch 30 switch status on side A | A面分路30开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 30 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.32 | hwAcrelAMC16ZHMeterBranch31SwitchStatusOnSideA | Branch 31 switch status on side A | A面分路31开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 31 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.33 | hwAcrelAMC16ZHMeterBranch32SwitchStatusOnSideA | Branch 32 switch status on side A | A面分路32开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 32 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.34 | hwAcrelAMC16ZHMeterBranch33SwitchStatusOnSideA | Branch 33 switch status on side A | A面分路33开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 33 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.35 | hwAcrelAMC16ZHMeterBranch34SwitchStatusOnSideA | Branch 34 switch status on side A | A面分路34开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 34 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.36 | hwAcrelAMC16ZHMeterBranch35SwitchStatusOnSideA | Branch 35 switch status on side A | A面分路35开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 35 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.37 | hwAcrelAMC16ZHMeterBranch36SwitchStatusOnSideA | Branch 36 switch status on side A | A面分路36开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 36 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.38 | hwAcrelAMC16ZHMeterBranch37SwitchStatusOnSideA | Branch 37 switch status on side A | A面分路37开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 37 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.39 | hwAcrelAMC16ZHMeterBranch38SwitchStatusOnSideA | Branch 38 switch status on side A | A面分路38开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 38 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.40 | hwAcrelAMC16ZHMeterBranch39SwitchStatusOnSideA | Branch 39 switch status on side A | A面分路39开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 39 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.41 | hwAcrelAMC16ZHMeterBranch40SwitchStatusOnSideA | Branch 40 switch status on side A | A面分路40开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 40 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.42 | hwAcrelAMC16ZHMeterBranch41SwitchStatusOnSideA | Branch 41 switch status on side A | A面分路41开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 41 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.43 | hwAcrelAMC16ZHMeterBranch42SwitchStatusOnSideA | Branch 42 switch status on side A | A面分路42开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 42 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.44 | hwAcrelAMC16ZHMeterBranch43SwitchStatusOnSideA | Branch 43 switch status on side A | A面分路43开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 43 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.45 | hwAcrelAMC16ZHMeterBranch44SwitchStatusOnSideA | Branch 44 switch status on side A | A面分路44开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 44 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.46 | hwAcrelAMC16ZHMeterBranch45SwitchStatusOnSideA | Branch 45 switch status on side A | A面分路45开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 45 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.47 | hwAcrelAMC16ZHMeterBranch46SwitchStatusOnSideA | Branch 46 switch status on side A | A面分路46开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 46 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.48 | hwAcrelAMC16ZHMeterBranch47SwitchStatusOnSideA | Branch 47 switch status on side A | A面分路47开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 47 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.49 | hwAcrelAMC16ZHMeterBranch48SwitchStatusOnSideA | Branch 48 switch status on side A | A面分路48开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 48 switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.50 | hwAcrelAMC16ZHMeterBranch1SwitchStatusOnSideB | Branch 1 switch status on side B | B面分路1开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 1 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.51 | hwAcrelAMC16ZHMeterBranch2SwitchStatusOnSideB | Branch 2 switch status on side B | B面分路2开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 2 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.52 | hwAcrelAMC16ZHMeterBranch3SwitchStatusOnSideB | Branch 3 switch status on side B | B面分路3开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 3 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.53 | hwAcrelAMC16ZHMeterBranch4SwitchStatusOnSideB | Branch 4 switch status on side B | B面分路4开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 4 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.54 | hwAcrelAMC16ZHMeterBranch5SwitchStatusOnSideB | Branch 5 switch status on side B | B面分路5开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 5 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.55 | hwAcrelAMC16ZHMeterBranch6SwitchStatusOnSideB | Branch 6 switch status on side B | B面分路6开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 6 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.56 | hwAcrelAMC16ZHMeterBranch7SwitchStatusOnSideB | Branch 7 switch status on side B | B面分路7开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 7 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.57 | hwAcrelAMC16ZHMeterBranch8SwitchStatusOnSideB | Branch 8 switch status on side B | B面分路8开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 8 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.58 | hwAcrelAMC16ZHMeterBranch9SwitchStatusOnSideB | Branch 9 switch status on side B | B面分路9开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 9 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.59 | hwAcrelAMC16ZHMeterBranch10SwitchStatusOnSideB | Branch 10 switch status on side B | B面分路10开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 10 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.60 | hwAcrelAMC16ZHMeterBranch11SwitchStatusOnSideB | Branch 11 switch status on side B | B面分路11开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 11 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.61 | hwAcrelAMC16ZHMeterBranch12SwitchStatusOnSideB | Branch 12 switch status on side B | B面分路12开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 12 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.62 | hwAcrelAMC16ZHMeterBranch13SwitchStatusOnSideB | Branch 13 switch status on side B | B面分路13开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 13 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.63 | hwAcrelAMC16ZHMeterBranch14SwitchStatusOnSideB | Branch 14 switch status on side B | B面分路14开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 14 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.64 | hwAcrelAMC16ZHMeterBranch15SwitchStatusOnSideB | Branch 15 switch status on side B | B面分路15开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 15 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.65 | hwAcrelAMC16ZHMeterBranch16SwitchStatusOnSideB | Branch 16 switch status on side B | B面分路16开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 16 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.66 | hwAcrelAMC16ZHMeterBranch17SwitchStatusOnSideB | Branch 17 switch status on side B | B面分路17开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 17 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.67 | hwAcrelAMC16ZHMeterBranch18SwitchStatusOnSideB | Branch 18 switch status on side B | B面分路18开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 18 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.68 | hwAcrelAMC16ZHMeterBranch19SwitchStatusOnSideB | Branch 19 switch status on side B | B面分路19开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 19 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.69 | hwAcrelAMC16ZHMeterBranch20SwitchStatusOnSideB | Branch 20 switch status on side B | B面分路20开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 20 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.70 | hwAcrelAMC16ZHMeterBranch21SwitchStatusOnSideB | Branch 21 switch status on side B | B面分路21开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 21 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.71 | hwAcrelAMC16ZHMeterBranch22SwitchStatusOnSideB | Branch 22 switch status on side B | B面分路22开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 22 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.72 | hwAcrelAMC16ZHMeterBranch23SwitchStatusOnSideB | Branch 23 switch status on side B | B面分路23开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 23 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.73 | hwAcrelAMC16ZHMeterBranch24SwitchStatusOnSideB | Branch 24 switch status on side B | B面分路24开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 24 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.74 | hwAcrelAMC16ZHMeterBranch25SwitchStatusOnSideB | Branch 25 switch status on side B | B面分路25开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 25 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.75 | hwAcrelAMC16ZHMeterBranch26SwitchStatusOnSideB | Branch 26 switch status on side B | B面分路26开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 26 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.76 | hwAcrelAMC16ZHMeterBranch27SwitchStatusOnSideB | Branch 27 switch status on side B | B面分路27开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 27 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.77 | hwAcrelAMC16ZHMeterBranch28SwitchStatusOnSideB | Branch 28 switch status on side B | B面分路28开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 28 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.78 | hwAcrelAMC16ZHMeterBranch29SwitchStatusOnSideB | Branch 29 switch status on side B | B面分路29开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 29 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.79 | hwAcrelAMC16ZHMeterBranch30SwitchStatusOnSideB | Branch 30 switch status on side B | B面分路30开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 30 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.80 | hwAcrelAMC16ZHMeterBranch31SwitchStatusOnSideB | Branch 31 switch status on side B | B面分路31开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 31 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.81 | hwAcrelAMC16ZHMeterBranch32SwitchStatusOnSideB | Branch 32 switch status on side B | B面分路32开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 32 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.82 | hwAcrelAMC16ZHMeterBranch33SwitchStatusOnSideB | Branch 33 switch status on side B | B面分路33开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 33 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.83 | hwAcrelAMC16ZHMeterBranch34SwitchStatusOnSideB | Branch 34 switch status on side B | B面分路34开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 34 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.84 | hwAcrelAMC16ZHMeterBranch35SwitchStatusOnSideB | Branch 35 switch status on side B | B面分路35开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 35 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.85 | hwAcrelAMC16ZHMeterBranch36SwitchStatusOnSideB | Branch 36 switch status on side B | B面分路36开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 36 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.86 | hwAcrelAMC16ZHMeterBranch37SwitchStatusOnSideB | Branch 37 switch status on side B | B面分路37开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 37 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.87 | hwAcrelAMC16ZHMeterBranch38SwitchStatusOnSideB | Branch 38 switch status on side B | B面分路38开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 38 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.88 | hwAcrelAMC16ZHMeterBranch39SwitchStatusOnSideB | Branch 39 switch status on side B | B面分路39开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 39 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.89 | hwAcrelAMC16ZHMeterBranch40SwitchStatusOnSideB | Branch 40 switch status on side B | B面分路40开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 40 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.90 | hwAcrelAMC16ZHMeterBranch41SwitchStatusOnSideB | Branch 41 switch status on side B | B面分路41开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 41 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.91 | hwAcrelAMC16ZHMeterBranch42SwitchStatusOnSideB | Branch 42 switch status on side B | B面分路42开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 42 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.92 | hwAcrelAMC16ZHMeterBranch43SwitchStatusOnSideB | Branch 43 switch status on side B | B面分路43开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 43 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.93 | hwAcrelAMC16ZHMeterBranch44SwitchStatusOnSideB | Branch 44 switch status on side B | B面分路44开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 44 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.94 | hwAcrelAMC16ZHMeterBranch45SwitchStatusOnSideB | Branch 45 switch status on side B | B面分路45开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 45 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.95 | hwAcrelAMC16ZHMeterBranch46SwitchStatusOnSideB | Branch 46 switch status on side B | B面分路46开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 46 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.96 | hwAcrelAMC16ZHMeterBranch47SwitchStatusOnSideB | Branch 47 switch status on side B | B面分路47开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 47 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.97 | hwAcrelAMC16ZHMeterBranch48SwitchStatusOnSideB | Branch 48 switch status on side B | B面分路48开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch 48 switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.98 | hwAcrelAMC16ZHMeterMainsSwitchStatusOnSideA | Mains switch status on side A | A面主路开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Mains switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.99 | hwAcrelAMC16ZHMeterSpdSwitchStatusOnSideA | SPD switch status on side A | A面防雷器开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | SPD switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.100 | hwAcrelAMC16ZHMeterTrippedSwitchStatusOnSideA | Tripped switch status on side A | A面跳闸开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Tripped switch status on side A of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.101 | hwAcrelAMC16ZHMeterMainsSwitchStatusOnSideB | Mains switch status on side B | B面主路开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Mains switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.102 | hwAcrelAMC16ZHMeterSpdSwitchStatusOnSideB | SPD switch status on side B | B面防雷器开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | SPD switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.103 | hwAcrelAMC16ZHMeterTrippedSwitchStatusOnSideB | Tripped switch status on side B | B面跳闸开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Tripped switch status on side B of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.104 | hwAcrelAMC16ZHMeterInputCableForSideAPhaseAVoltage | Input cable for side A-phase A voltage | A面进线A相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side A-phase A voltage of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.105 | hwAcrelAMC16ZHMeterInputCableForSideAPhaseACurrent | Input cable for side A-phase A current | A面进线A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side A-phase A current of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.106 | hwAcrelAMC16ZHMeterInputCableForSideAPhaseAActivePower | Input cable for side A-phase A active power | A面进线A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side A-phase A active power of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.107 | hwAcrelAMC16ZHMeterInputCableForSideAPhaseAActiveEnergy | Input cable for side A-phase A active energy | A面进线A相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side A-phase A active energy of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.108 | hwAcrelAMC16ZHMeterInputCableForSideAPhaseACtRatio | Input cable for side A-phase A CT ratio | A面进线A相CT变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side A-phase A CT ratio of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.109 | hwAcrelAMC16ZHMeterTemperature | Temperature | 温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Temperature of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:degrees celsius.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.110 | hwAcrelAMC16ZHMeterHumidity | Humidity | 湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Humidity of the device config table for the Acrel AMC16ZH Meter.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.111 | hwAcrelAMC16ZHMeterInputCableForSideBPhaseAVoltage | Input cable for side B-phase A voltage | B面进线A相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side B-phase A voltage of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.112 | hwAcrelAMC16ZHMeterInputCableForSideBPhaseACurrent | Input cable for side B-phase A current | B面进线A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side B-phase A current of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.113 | hwAcrelAMC16ZHMeterInputCableForSideBTotalActivePower | Input cable for side B-total active power | B面进线总有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side B-total active power of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.114 | hwAcrelAMC16ZHMeterInputCableForSideBPhaseAActivePower | Input cable for side B-phase A active power | B面进线A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side B-phase A active power of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.115 | hwAcrelAMC16ZHMeterInputCableForSideBPhaseAActiveEnergy | Input cable for side B-phase A active energy | B面进线A相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side B-phase A active energy of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.116 | hwAcrelAMC16ZHMeterInputCableForSideBPhaseACtRatio | Input cable for side B-phase A CT ratio | B面进线A相CT变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for side B-phase A CT ratio of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.117 | hwAcrelAMC16ZHMeterPositiveToGroundVoltageOfBusA | Positive-to-ground voltage of bus A | A母线正对地电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive-to-ground voltage of bus A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.118 | hwAcrelAMC16ZHMeterNegToGroundVoltageOfBusA | Negative-to-ground voltage of bus A | A母线负对地电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative-to-ground voltage of bus A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.119 | hwAcrelAMC16ZHMeterBusAVoltage | Bus A voltage | A母线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Bus A voltage of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.120 | hwAcrelAMC16ZHMeterPositiveToGroundResOfBusA | Positive-to-ground resistance of bus A | A母线正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive-to-ground resistance of bus A of the device config table for the Acrel AMC16ZH Meter.Multiple:1.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.121 | hwAcrelAMC16ZHMeterNegToGroundResOfBusA | Negative-to-ground resistance of bus A | A母线负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative-to-ground resistance of bus A of the device config table for the Acrel AMC16ZH Meter.Multiple:1.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.122 | hwAcrelAMC16ZHMeterPositiveToGroundVoltageOfBusB | Positive-to-ground voltage of bus B | B母线正对地电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive-to-ground voltage of bus B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.123 | hwAcrelAMC16ZHMeterNegToGroundVoltageOfBusB | Negative-to-ground voltage of bus B | B母线负对地电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative-to-ground voltage of bus B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.124 | hwAcrelAMC16ZHMeterBusBVoltage | Bus B voltage | B母线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Bus B voltage of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.125 | hwAcrelAMC16ZHMeterPositiveToGroundResOfBusB | Positive-to-ground resistance of bus B | B母线正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive-to-ground resistance of bus B of the device config table for the Acrel AMC16ZH Meter.Multiple:1.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.126 | hwAcrelAMC16ZHMeterNegToGroundResOfBusB | Negative-to-ground resistance of bus B | B母线负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative-to-ground resistance of bus B of the device config table for the Acrel AMC16ZH Meter.Multiple:1.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.127 | hwAcrelAMC16ZHMeterBranch1CurrentOnSideA | Branch 1 current on side A | A面分路1电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.128 | hwAcrelAMC16ZHMeterBranch2CurrentOnSideA | Branch 2 current on side A | A面分路2电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.128 | hwAcrelAMC16ZHMeterBranch3CurrentOnSideA | Branch 3 current on side A | A面分路3电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.130 | hwAcrelAMC16ZHMeterBranch4CurrentOnSideA | Branch 4 current on side A | A面分路4电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.131 | hwAcrelAMC16ZHMeterBranch5CurrentOnSideA | Branch 5 current on side A | A面分路5电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.132 | hwAcrelAMC16ZHMeterBranch6CurrentOnSideA | Branch 6 current on side A | A面分路6电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.133 | hwAcrelAMC16ZHMeterBranch7CurrentOnSideA | Branch 7 current on side A | A面分路7电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.134 | hwAcrelAMC16ZHMeterBranch8CurrentOnSideA | Branch 8 current on side A | A面分路8电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.135 | hwAcrelAMC16ZHMeterBranch9CurrentOnSideA | Branch 9 current on side A | A面分路9电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.136 | hwAcrelAMC16ZHMeterBranch10CurrentOnSideA | Branch 10 current on side A | A面分路10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.137 | hwAcrelAMC16ZHMeterBranch11CurrentOnSideA | Branch 11 current on side A | A面分路11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.138 | hwAcrelAMC16ZHMeterBranch12CurrentOnSideA | Branch 12 current on side A | A面分路12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.139 | hwAcrelAMC16ZHMeterBranch13CurrentOnSideA | Branch 13 current on side A | A面分路13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.140 | hwAcrelAMC16ZHMeterBranch14CurrentOnSideA | Branch 14 current on side A | A面分路14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.141 | hwAcrelAMC16ZHMeterBranch15CurrentOnSideA | Branch 15 current on side A | A面分路15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.142 | hwAcrelAMC16ZHMeterBranch16CurrentOnSideA | Branch 16 current on side A | A面分路16电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.143 | hwAcrelAMC16ZHMeterBranch17CurrentOnSideA | Branch 17 current on side A | A面分路17电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.144 | hwAcrelAMC16ZHMeterBranch18CurrentOnSideA | Branch 18 current on side A | A面分路18电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.145 | hwAcrelAMC16ZHMeterBranch19CurrentOnSideA | Branch 19 current on side A | A面分路19电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.146 | hwAcrelAMC16ZHMeterBranch20CurrentOnSideA | Branch 20 current on side A | A面分路20电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.147 | hwAcrelAMC16ZHMeterBranch21CurrentOnSideA | Branch 21 current on side A | A面分路21电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.148 | hwAcrelAMC16ZHMeterBranch22CurrentOnSideA | Branch 22 current on side A | A面分路22电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.149 | hwAcrelAMC16ZHMeterBranch23CurrentOnSideA | Branch 23 current on side A | A面分路23电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.150 | hwAcrelAMC16ZHMeterBranch24CurrentOnSideA | Branch 24 current on side A | A面分路24电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.151 | hwAcrelAMC16ZHMeterBranch25CurrentOnSideA | Branch 25 current on side A | A面分路25电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.152 | hwAcrelAMC16ZHMeterBranch26CurrentOnSideA | Branch 26 current on side A | A面分路26电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.153 | hwAcrelAMC16ZHMeterBranch27CurrentOnSideA | Branch 27 current on side A | A面分路27电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.154 | hwAcrelAMC16ZHMeterBranch28CurrentOnSideA | Branch 28 current on side A | A面分路28电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.155 | hwAcrelAMC16ZHMeterBranch29CurrentOnSideA | Branch 29 current on side A | A面分路29电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.156 | hwAcrelAMC16ZHMeterBranch30CurrentOnSideA | Branch 30 current on side A | A面分路30电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.157 | hwAcrelAMC16ZHMeterBranch31CurrentOnSideA | Branch 31 current on side A | A面分路31电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.158 | hwAcrelAMC16ZHMeterBranch32CurrentOnSideA | Branch 32 current on side A | A面分路32电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.159 | hwAcrelAMC16ZHMeterBranch33CurrentOnSideA | Branch 33 current on side A | A面分路33电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.160 | hwAcrelAMC16ZHMeterBranch34CurrentOnSideA | Branch 34 current on side A | A面分路34电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.161 | hwAcrelAMC16ZHMeterBranch35CurrentOnSideA | Branch 35 current on side A | A面分路35电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.162 | hwAcrelAMC16ZHMeterBranch36CurrentOnSideA | Branch 36 current on side A | A面分路36电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.163 | hwAcrelAMC16ZHMeterBranch37CurrentOnSideA | Branch 37 current on side A | A面分路37电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.164 | hwAcrelAMC16ZHMeterBranch38CurrentOnSideA | Branch 38 current on side A | A面分路38电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.165 | hwAcrelAMC16ZHMeterBranch39CurrentOnSideA | Branch 39 current on side A | A面分路39电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.166 | hwAcrelAMC16ZHMeterBranch40CurrentOnSideA | Branch 40 current on side A | A面分路40电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.167 | hwAcrelAMC16ZHMeterBranch41CurrentOnSideA | Branch 41 current on side A | A面分路41电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.168 | hwAcrelAMC16ZHMeterBranch42CurrentOnSideA | Branch 42 current on side A | A面分路42电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.169 | hwAcrelAMC16ZHMeterBranch43CurrentOnSideA | Branch 43 current on side A | A面分路43电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.170 | hwAcrelAMC16ZHMeterBranch44CurrentOnSideA | Branch 44 current on side A | A面分路44电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.171 | hwAcrelAMC16ZHMeterBranch45CurrentOnSideA | Branch 45 current on side A | A面分路45电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.172 | hwAcrelAMC16ZHMeterBranch46CurrentOnSideA | Branch 46 current on side A | A面分路46电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.173 | hwAcrelAMC16ZHMeterBranch47CurrentOnSideA | Branch 47 current on side A | A面分路47电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.174 | hwAcrelAMC16ZHMeterBranch48CurrentOnSideA | Branch 48 current on side A | A面分路48电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 current on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.175 | hwAcrelAMC16ZHMeterBranch1ActivePowerOnSideA | Branch 1 active power on side A | A面分路1有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.176 | hwAcrelAMC16ZHMeterBranch2ActivePowerOnSideA | Branch 2 active power on side A | A面分路2有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.177 | hwAcrelAMC16ZHMeterBranch3ActivePowerOnSideA | Branch 3 active power on side A | A面分路3有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.178 | hwAcrelAMC16ZHMeterBranch4ActivePowerOnSideA | Branch 4 active power on side A | A面分路4有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.179 | hwAcrelAMC16ZHMeterBranch5ActivePowerOnSideA | Branch 5 active power on side A | A面分路5有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.180 | hwAcrelAMC16ZHMeterBranch6ActivePowerOnSideA | Branch 6 active power on side A | A面分路6有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.181 | hwAcrelAMC16ZHMeterBranch7ActivePowerOnSideA | Branch 7 active power on side A | A面分路7有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.182 | hwAcrelAMC16ZHMeterBranch8ActivePowerOnSideA | Branch 8 active power on side A | A面分路8有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.183 | hwAcrelAMC16ZHMeterBranch9ActivePowerOnSideA | Branch 9 active power on side A | A面分路9有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.184 | hwAcrelAMC16ZHMeterBranch10ActivePowerOnSideA | Branch 10 active power on side A | A面分路10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.185 | hwAcrelAMC16ZHMeterBranch11ActivePowerOnSideA | Branch 11 active power on side A | A面分路11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.186 | hwAcrelAMC16ZHMeterBranch12ActivePowerOnSideA | Branch 12 active power on side A | A面分路12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.187 | hwAcrelAMC16ZHMeterBranch13ActivePowerOnSideA | Branch 13 active power on side A | A面分路13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.188 | hwAcrelAMC16ZHMeterBranch14ActivePowerOnSideA | Branch 14 active power on side A | A面分路14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.189 | hwAcrelAMC16ZHMeterBranch15ActivePowerOnSideA | Branch 15 active power on side A | A面分路15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.190 | hwAcrelAMC16ZHMeterBranch16ActivePowerOnSideA | Branch 16 active power on side A | A面分路16有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.191 | hwAcrelAMC16ZHMeterBranch17ActivePowerOnSideA | Branch 17 active power on side A | A面分路17有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.192 | hwAcrelAMC16ZHMeterBranch18ActivePowerOnSideA | Branch 18 active power on side A | A面分路18有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.193 | hwAcrelAMC16ZHMeterBranch19ActivePowerOnSideA | Branch 19 active power on side A | A面分路19有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.194 | hwAcrelAMC16ZHMeterBranch20ActivePowerOnSideA | Branch 20 active power on side A | A面分路20有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.195 | hwAcrelAMC16ZHMeterBranch21ActivePowerOnSideA | Branch 21 active power on side A | A面分路21有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.196 | hwAcrelAMC16ZHMeterBranch22ActivePowerOnSideA | Branch 22 active power on side A | A面分路22有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.197 | hwAcrelAMC16ZHMeterBranch23ActivePowerOnSideA | Branch 23 active power on side A | A面分路23有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.198 | hwAcrelAMC16ZHMeterBranch24ActivePowerOnSideA | Branch 24 active power on side A | A面分路24有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.199 | hwAcrelAMC16ZHMeterBranch25ActivePowerOnSideA | Branch 25 active power on side A | A面分路25有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.200 | hwAcrelAMC16ZHMeterBranch26ActivePowerOnSideA | Branch 26 active power on side A | A面分路26有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.201 | hwAcrelAMC16ZHMeterBranch27ActivePowerOnSideA | Branch 27 active power on side A | A面分路27有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.202 | hwAcrelAMC16ZHMeterBranch28ActivePowerOnSideA | Branch 28 active power on side A | A面分路28有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.203 | hwAcrelAMC16ZHMeterBranch29ActivePowerOnSideA | Branch 29 active power on side A | A面分路29有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.204 | hwAcrelAMC16ZHMeterBranch30ActivePowerOnSideA | Branch 30 active power on side A | A面分路30有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.205 | hwAcrelAMC16ZHMeterBranch31ActivePowerOnSideA | Branch 31 active power on side A | A面分路31有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.206 | hwAcrelAMC16ZHMeterBranch32ActivePowerOnSideA | Branch 32 active power on side A | A面分路32有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.207 | hwAcrelAMC16ZHMeterBranch33ActivePowerOnSideA | Branch 33 active power on side A | A面分路33有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.208 | hwAcrelAMC16ZHMeterBranch34ActivePowerOnSideA | Branch 34 active power on side A | A面分路34有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.209 | hwAcrelAMC16ZHMeterBranch35ActivePowerOnSideA | Branch 35 active power on side A | A面分路35有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.210 | hwAcrelAMC16ZHMeterBranch36ActivePowerOnSideA | Branch 36 active power on side A | A面分路36有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.211 | hwAcrelAMC16ZHMeterBranch37ActivePowerOnSideA | Branch 37 active power on side A | A面分路37有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.212 | hwAcrelAMC16ZHMeterBranch38ActivePowerOnSideA | Branch 38 active power on side A | A面分路38有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.213 | hwAcrelAMC16ZHMeterBranch39ActivePowerOnSideA | Branch 39 active power on side A | A面分路39有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.214 | hwAcrelAMC16ZHMeterBranch40ActivePowerOnSideA | Branch 40 active power on side A | A面分路40有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.215 | hwAcrelAMC16ZHMeterBranch41ActivePowerOnSideA | Branch 41 active power on side A | A面分路41有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.216 | hwAcrelAMC16ZHMeterBranch42ActivePowerOnSideA | Branch 42 active power on side A | A面分路42有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.217 | hwAcrelAMC16ZHMeterBranch43ActivePowerOnSideA | Branch 43 active power on side A | A面分路43有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.218 | hwAcrelAMC16ZHMeterBranch44ActivePowerOnSideA | Branch 44 active power on side A | A面分路44有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.219 | hwAcrelAMC16ZHMeterBranch45ActivePowerOnSideA | Branch 45 active power on side A | A面分路45有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.220 | hwAcrelAMC16ZHMeterBranch46ActivePowerOnSideA | Branch 46 active power on side A | A面分路46有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.221 | hwAcrelAMC16ZHMeterBranch47ActivePowerOnSideA | Branch 47 active power on side A | A面分路47有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.222 | hwAcrelAMC16ZHMeterBranch48ActivePowerOnSideA | Branch 48 active power on side A | A面分路48有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 active power on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.223 | hwAcrelAMC16ZHMeterBranch1ActiveEnergyOnSideA | Branch 1 active energy on side A | A面分路1有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.224 | hwAcrelAMC16ZHMeterBranch2ActiveEnergyOnSideA | Branch 2 active energy on side A | A面分路2有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.225 | hwAcrelAMC16ZHMeterBranch3ActiveEnergyOnSideA | Branch 3 active energy on side A | A面分路3有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.226 | hwAcrelAMC16ZHMeterBranch4ActiveEnergyOnSideA | Branch 4 active energy on side A | A面分路4有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.227 | hwAcrelAMC16ZHMeterBranch5ActiveEnergyOnSideA | Branch 5 active energy on side A | A面分路5有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.228 | hwAcrelAMC16ZHMeterBranch6ActiveEnergyOnSideA | Branch 6 active energy on side A | A面分路6有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.229 | hwAcrelAMC16ZHMeterBranch7ActiveEnergyOnSideA | Branch 7 active energy on side A | A面分路7有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.230 | hwAcrelAMC16ZHMeterBranch8ActiveEnergyOnSideA | Branch 8 active energy on side A | A面分路8有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.231 | hwAcrelAMC16ZHMeterBranch9ActiveEnergyOnSideA | Branch 9 active energy on side A | A面分路9有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.232 | hwAcrelAMC16ZHMeterBranch10ActiveEnergyOnSideA | Branch 10 active energy on side A | A面分路10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.233 | hwAcrelAMC16ZHMeterBranch11ActiveEnergyOnSideA | Branch 11 active energy on side A | A面分路11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.234 | hwAcrelAMC16ZHMeterBranch12ActiveEnergyOnSideA | Branch 12 active energy on side A | A面分路12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.235 | hwAcrelAMC16ZHMeterBranch13ActiveEnergyOnSideA | Branch 13 active energy on side A | A面分路13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.236 | hwAcrelAMC16ZHMeterBranch14ActiveEnergyOnSideA | Branch 14 active energy on side A | A面分路14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.237 | hwAcrelAMC16ZHMeterBranch15ActiveEnergyOnSideA | Branch 15 active energy on side A | A面分路15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.238 | hwAcrelAMC16ZHMeterBranch16ActiveEnergyOnSideA | Branch 16 active energy on side A | A面分路16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.239 | hwAcrelAMC16ZHMeterBranch17ActiveEnergyOnSideA | Branch 17 active energy on side A | A面分路17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.240 | hwAcrelAMC16ZHMeterBranch18ActiveEnergyOnSideA | Branch 18 active energy on side A | A面分路18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.241 | hwAcrelAMC16ZHMeterBranch19ActiveEnergyOnSideA | Branch 19 active energy on side A | A面分路19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.242 | hwAcrelAMC16ZHMeterBranch20ActiveEnergyOnSideA | Branch 20 active energy on side A | A面分路20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.243 | hwAcrelAMC16ZHMeterBranch21ActiveEnergyOnSideA | Branch 21 active energy on side A | A面分路21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.244 | hwAcrelAMC16ZHMeterBranch22ActiveEnergyOnSideA | Branch 22 active energy on side A | A面分路22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.245 | hwAcrelAMC16ZHMeterBranch23ActiveEnergyOnSideA | Branch 23 active energy on side A | A面分路23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.246 | hwAcrelAMC16ZHMeterBranch24ActiveEnergyOnSideA | Branch 24 active energy on side A | A面分路24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.247 | hwAcrelAMC16ZHMeterBranch25ActiveEnergyOnSideA | Branch 25 active energy on side A | A面分路25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.248 | hwAcrelAMC16ZHMeterBranch26ActiveEnergyOnSideA | Branch 26 active energy on side A | A面分路26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.249 | hwAcrelAMC16ZHMeterBranch27ActiveEnergyOnSideA | Branch 27 active energy on side A | A面分路27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.250 | hwAcrelAMC16ZHMeterBranch28ActiveEnergyOnSideA | Branch 28 active energy on side A | A面分路28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.251 | hwAcrelAMC16ZHMeterBranch29ActiveEnergyOnSideA | Branch 29 active energy on side A | A面分路29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.252 | hwAcrelAMC16ZHMeterBranch30ActiveEnergyOnSideA | Branch 30 active energy on side A | A面分路30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.253 | hwAcrelAMC16ZHMeterBranch31ActiveEnergyOnSideA | Branch 31 active energy on side A | A面分路31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.254 | hwAcrelAMC16ZHMeterBranch32ActiveEnergyOnSideA | Branch 32 active energy on side A | A面分路32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.255 | hwAcrelAMC16ZHMeterBranch33ActiveEnergyOnSideA | Branch 33 active energy on side A | A面分路33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.256 | hwAcrelAMC16ZHMeterBranch34ActiveEnergyOnSideA | Branch 34 active energy on side A | A面分路34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.257 | hwAcrelAMC16ZHMeterBranch35ActiveEnergyOnSideA | Branch 35 active energy on side A | A面分路35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.258 | hwAcrelAMC16ZHMeterBranch36ActiveEnergyOnSideA | Branch 36 active energy on side A | A面分路36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.259 | hwAcrelAMC16ZHMeterBranch37ActiveEnergyOnSideA | Branch 37 active energy on side A | A面分路37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.260 | hwAcrelAMC16ZHMeterBranch38ActiveEnergyOnSideA | Branch 38 active energy on side A | A面分路38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.261 | hwAcrelAMC16ZHMeterBranch39ActiveEnergyOnSideA | Branch 39 active energy on side A | A面分路39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.262 | hwAcrelAMC16ZHMeterBranch40ActiveEnergyOnSideA | Branch 40 active energy on side A | A面分路40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.263 | hwAcrelAMC16ZHMeterBranch41ActiveEnergyOnSideA | Branch 41 active energy on side A | A面分路41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.264 | hwAcrelAMC16ZHMeterBranch42ActiveEnergyOnSideA | Branch 42 active energy on side A | A面分路42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.265 | hwAcrelAMC16ZHMeterBranch43ActiveEnergyOnSideA | Branch 43 active energy on side A | A面分路43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.266 | hwAcrelAMC16ZHMeterBranch44ActiveEnergyOnSideA | Branch 44 active energy on side A | A面分路44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.267 | hwAcrelAMC16ZHMeterBranch45ActiveEnergyOnSideA | Branch 45 active energy on side A | A面分路45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.268 | hwAcrelAMC16ZHMeterBranch46ActiveEnergyOnSideA | Branch 46 active energy on side A | A面分路46有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.269 | hwAcrelAMC16ZHMeterBranch47ActiveEnergyOnSideA | Branch 47 active energy on side A | A面分路47有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.270 | hwAcrelAMC16ZHMeterBranch48ActiveEnergyOnSideA | Branch 48 active energy on side A | A面分路48有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 active energy on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.271 | hwAcrelAMC16ZHMeterBranch1VoltageOnSideA | Branch 1 voltage on side A | A面分路1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.272 | hwAcrelAMC16ZHMeterBranch2VoltageOnSideA | Branch 2 voltage on side A | A面分路2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.273 | hwAcrelAMC16ZHMeterBranch3VoltageOnSideA | Branch 3 voltage on side A | A面分路3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.274 | hwAcrelAMC16ZHMeterBranch4VoltageOnSideA | Branch 4 voltage on side A | A面分路4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.275 | hwAcrelAMC16ZHMeterBranch5VoltageOnSideA | Branch 5 voltage on side A | A面分路5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.276 | hwAcrelAMC16ZHMeterBranch6VoltageOnSideA | Branch 6 voltage on side A | A面分路6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.277 | hwAcrelAMC16ZHMeterBranch7VoltageOnSideA | Branch 7 voltage on side A | A面分路7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.278 | hwAcrelAMC16ZHMeterBranch8VoltageOnSideA | Branch 8 voltage on side A | A面分路8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.279 | hwAcrelAMC16ZHMeterBranch9VoltageOnSideA | Branch 9 voltage on side A | A面分路9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.280 | hwAcrelAMC16ZHMeterBranch10VoltageOnSideA | Branch 10 voltage on side A | A面分路10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.281 | hwAcrelAMC16ZHMeterBranch11VoltageOnSideA | Branch 11 voltage on side A | A面分路11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.282 | hwAcrelAMC16ZHMeterBranch12VoltageOnSideA | Branch 12 voltage on side A | A面分路12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.283 | hwAcrelAMC16ZHMeterBranch13VoltageOnSideA | Branch 13 voltage on side A | A面分路13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.284 | hwAcrelAMC16ZHMeterBranch14VoltageOnSideA | Branch 14 voltage on side A | A面分路14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.285 | hwAcrelAMC16ZHMeterBranch15VoltageOnSideA | Branch 15 voltage on side A | A面分路15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.286 | hwAcrelAMC16ZHMeterBranch16VoltageOnSideA | Branch 16 voltage on side A | A面分路16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.287 | hwAcrelAMC16ZHMeterBranch17VoltageOnSideA | Branch 17 voltage on side A | A面分路17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.288 | hwAcrelAMC16ZHMeterBranch18VoltageOnSideA | Branch 18 voltage on side A | A面分路18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.289 | hwAcrelAMC16ZHMeterBranch19VoltageOnSideA | Branch 19 voltage on side A | A面分路19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.290 | hwAcrelAMC16ZHMeterBranch20VoltageOnSideA | Branch 20 voltage on side A | A面分路20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.291 | hwAcrelAMC16ZHMeterBranch21VoltageOnSideA | Branch 21 voltage on side A | A面分路21电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.292 | hwAcrelAMC16ZHMeterBranch22VoltageOnSideA | Branch 22 voltage on side A | A面分路22电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.293 | hwAcrelAMC16ZHMeterBranch23VoltageOnSideA | Branch 23 voltage on side A | A面分路23电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.294 | hwAcrelAMC16ZHMeterBranch24VoltageOnSideA | Branch 24 voltage on side A | A面分路24电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.295 | hwAcrelAMC16ZHMeterBranch25VoltageOnSideA | Branch 25 voltage on side A | A面分路25电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.296 | hwAcrelAMC16ZHMeterBranch26VoltageOnSideA | Branch 26 voltage on side A | A面分路26电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.297 | hwAcrelAMC16ZHMeterBranch27VoltageOnSideA | Branch 27 voltage on side A | A面分路27电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.298 | hwAcrelAMC16ZHMeterBranch28VoltageOnSideA | Branch 28 voltage on side A | A面分路28电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.299 | hwAcrelAMC16ZHMeterBranch29VoltageOnSideA | Branch 29 voltage on side A | A面分路29电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.1.1.300 | hwAcrelAMC16ZHMeterRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.2 | hwAcrelAMC16ZHMeterRunning2Table | / | / |  |  | / | / | The running table of Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.1 | hwAcrelAMC16ZHMeterRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.2 | hwAcrelAMC16ZHMeterBranch30VoltageOnSideA | Branch 30 voltage on side A | A面分路30电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.3 | hwAcrelAMC16ZHMeterBranch31VoltageOnSideA | Branch 31 voltage on side A | A面分路31电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.4 | hwAcrelAMC16ZHMeterBranch32VoltageOnSideA | Branch 32 voltage on side A | A面分路32电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.5 | hwAcrelAMC16ZHMeterBranch33VoltageOnSideA | Branch 33 voltage on side A | A面分路33电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.6 | hwAcrelAMC16ZHMeterBranch34VoltageOnSideA | Branch 34 voltage on side A | A面分路34电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.7 | hwAcrelAMC16ZHMeterBranch35VoltageOnSideA | Branch 35 voltage on side A | A面分路35电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.8 | hwAcrelAMC16ZHMeterBranch36VoltageOnSideA | Branch 36 voltage on side A | A面分路36电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.9 | hwAcrelAMC16ZHMeterBranch37VoltageOnSideA | Branch 37 voltage on side A | A面分路37电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.10 | hwAcrelAMC16ZHMeterBranch38VoltageOnSideA | Branch 38 voltage on side A | A面分路38电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.11 | hwAcrelAMC16ZHMeterBranch39VoltageOnSideA | Branch 39 voltage on side A | A面分路39电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.12 | hwAcrelAMC16ZHMeterBranch40VoltageOnSideA | Branch 40 voltage on side A | A面分路40电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.13 | hwAcrelAMC16ZHMeterBranch41VoltageOnSideA | Branch 41 voltage on side A | A面分路41电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.14 | hwAcrelAMC16ZHMeterBranch42VoltageOnSideA | Branch 42 voltage on side A | A面分路42电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.15 | hwAcrelAMC16ZHMeterBranch43VoltageOnSideA | Branch 43 voltage on side A | A面分路43电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.16 | hwAcrelAMC16ZHMeterBranch44VoltageOnSideA | Branch 44 voltage on side A | A面分路44电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.17 | hwAcrelAMC16ZHMeterBranch45VoltageOnSideA | Branch 45 voltage on side A | A面分路45电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.18 | hwAcrelAMC16ZHMeterBranch46VoltageOnSideA | Branch 46 voltage on side A | A面分路46电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.19 | hwAcrelAMC16ZHMeterBranch47VoltageOnSideA | Branch 47 voltage on side A | A面分路47电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.20 | hwAcrelAMC16ZHMeterBranch48VoltageOnSideA | Branch 48 voltage on side A | A面分路48电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 voltage on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.21 | hwAcrelAMC16ZHMeterBranch1CurrentChangeRatioOnSideA | Branch 1 current change ratio on side A | A面分路1电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.22 | hwAcrelAMC16ZHMeterBranch2CurrentChangeRatioOnSideA | Branch 2 current change ratio on side A | A面分路2电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.23 | hwAcrelAMC16ZHMeterBranch3CurrentChangeRatioOnSideA | Branch 3 current change ratio on side A | A面分路3电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.24 | hwAcrelAMC16ZHMeterBranch4CurrentChangeRatioOnSideA | Branch 4 current change ratio on side A | A面分路4电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.25 | hwAcrelAMC16ZHMeterBranch5CurrentChangeRatioOnSideA | Branch 5 current change ratio on side A | A面分路5电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.26 | hwAcrelAMC16ZHMeterBranch6CurrentChangeRatioOnSideA | Branch 6 current change ratio on side A | A面分路6电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.27 | hwAcrelAMC16ZHMeterBranch7CurrentChangeRatioOnSideA | Branch 7 current change ratio on side A | A面分路7电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.28 | hwAcrelAMC16ZHMeterBranch8CurrentChangeRatioOnSideA | Branch 8 current change ratio on side A | A面分路8电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.29 | hwAcrelAMC16ZHMeterBranch9CurrentChangeRatioOnSideA | Branch 9 current change ratio on side A | A面分路9电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.30 | hwAcrelAMC16ZHMeterBranch10CurrentChangeRatioOnSideA | Branch 10 current change ratio on side A | A面分路10电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.31 | hwAcrelAMC16ZHMeterBranch11CurrentChangeRatioOnSideA | Branch 11 current change ratio on side A | A面分路11电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.32 | hwAcrelAMC16ZHMeterBranch12CurrentChangeRatioOnSideA | Branch 12 current change ratio on side A | A面分路12电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.33 | hwAcrelAMC16ZHMeterBranch13CurrentChangeRatioOnSideA | Branch 13 current change ratio on side A | A面分路13电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.34 | hwAcrelAMC16ZHMeterBranch14CurrentChangeRatioOnSideA | Branch 14 current change ratio on side A | A面分路14电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.35 | hwAcrelAMC16ZHMeterBranch15CurrentChangeRatioOnSideA | Branch 15 current change ratio on side A | A面分路15电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.36 | hwAcrelAMC16ZHMeterBranch16CurrentChangeRatioOnSideA | Branch 16 current change ratio on side A | A面分路16电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.37 | hwAcrelAMC16ZHMeterBranch17CurrentChangeRatioOnSideA | Branch 17 current change ratio on side A | A面分路17电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.38 | hwAcrelAMC16ZHMeterBranch18CurrentChangeRatioOnSideA | Branch 18 current change ratio on side A | A面分路18电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.39 | hwAcrelAMC16ZHMeterBranch19CurrentChangeRatioOnSideA | Branch 19 current change ratio on side A | A面分路19电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.40 | hwAcrelAMC16ZHMeterBranch20CurrentChangeRatioOnSideA | Branch 20 current change ratio on side A | A面分路20电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.41 | hwAcrelAMC16ZHMeterBranch21CurrentChangeRatioOnSideA | Branch 21 current change ratio on side A | A面分路21电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.42 | hwAcrelAMC16ZHMeterBranch22CurrentChangeRatioOnSideA | Branch 22 current change ratio on side A | A面分路22电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.43 | hwAcrelAMC16ZHMeterBranch23CurrentChangeRatioOnSideA | Branch 23 current change ratio on side A | A面分路23电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.44 | hwAcrelAMC16ZHMeterBranch24CurrentChangeRatioOnSideA | Branch 24 current change ratio on side A | A面分路24电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.45 | hwAcrelAMC16ZHMeterBranch25CurrentChangeRatioOnSideA | Branch 25 current change ratio on side A | A面分路25电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.46 | hwAcrelAMC16ZHMeterBranch26CurrentChangeRatioOnSideA | Branch 26 current change ratio on side A | A面分路26电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.47 | hwAcrelAMC16ZHMeterBranch27CurrentChangeRatioOnSideA | Branch 27 current change ratio on side A | A面分路27电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.48 | hwAcrelAMC16ZHMeterBranch28CurrentChangeRatioOnSideA | Branch 28 current change ratio on side A | A面分路28电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.49 | hwAcrelAMC16ZHMeterBranch29CurrentChangeRatioOnSideA | Branch 29 current change ratio on side A | A面分路29电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.50 | hwAcrelAMC16ZHMeterBranch30CurrentChangeRatioOnSideA | Branch 30 current change ratio on side A | A面分路30电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.51 | hwAcrelAMC16ZHMeterBranch31CurrentChangeRatioOnSideA | Branch 31 current change ratio on side A | A面分路31电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.52 | hwAcrelAMC16ZHMeterBranch32CurrentChangeRatioOnSideA | Branch 32 current change ratio on side A | A面分路32电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.53 | hwAcrelAMC16ZHMeterBranch33CurrentChangeRatioOnSideA | Branch 33 current change ratio on side A | A面分路33电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.54 | hwAcrelAMC16ZHMeterBranch34CurrentChangeRatioOnSideA | Branch 34 current change ratio on side A | A面分路34电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.55 | hwAcrelAMC16ZHMeterBranch35CurrentChangeRatioOnSideA | Branch 35 current change ratio on side A | A面分路35电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.56 | hwAcrelAMC16ZHMeterBranch36CurrentChangeRatioOnSideA | Branch 36 current change ratio on side A | A面分路36电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.57 | hwAcrelAMC16ZHMeterBranch37CurrentChangeRatioOnSideA | Branch 37 current change ratio on side A | A面分路37电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.58 | hwAcrelAMC16ZHMeterBranch38CurrentChangeRatioOnSideA | Branch 38 current change ratio on side A | A面分路38电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.59 | hwAcrelAMC16ZHMeterBranch39CurrentChangeRatioOnSideA | Branch 39 current change ratio on side A | A面分路39电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.60 | hwAcrelAMC16ZHMeterBranch40CurrentChangeRatioOnSideA | Branch 40 current change ratio on side A | A面分路40电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.61 | hwAcrelAMC16ZHMeterBranch41CurrentChangeRatioOnSideA | Branch 41 current change ratio on side A | A面分路41电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.62 | hwAcrelAMC16ZHMeterBranch42CurrentChangeRatioOnSideA | Branch 42 current change ratio on side A | A面分路42电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.63 | hwAcrelAMC16ZHMeterBranch43CurrentChangeRatioOnSideA | Branch 43 current change ratio on side A | A面分路43电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.64 | hwAcrelAMC16ZHMeterBranch44CurrentChangeRatioOnSideA | Branch 44 current change ratio on side A | A面分路44电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.65 | hwAcrelAMC16ZHMeterBranch45CurrentChangeRatioOnSideA | Branch 45 current change ratio on side A | A面分路45电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.66 | hwAcrelAMC16ZHMeterBranch46CurrentChangeRatioOnSideA | Branch 46 current change ratio on side A | A面分路46电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.67 | hwAcrelAMC16ZHMeterBranch47CurrentChangeRatioOnSideA | Branch 47 current change ratio on side A | A面分路47电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.68 | hwAcrelAMC16ZHMeterBranch48CurrentChangeRatioOnSideA | Branch 48 current change ratio on side A | A面分路48电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 current change ratio on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.69 | hwAcrelAMC16ZHMeterInsulation1PositiveToGroundResOnSideA | Insulation 1 positive-to-ground resistance on side A | A面绝缘1正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 1 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.70 | hwAcrelAMC16ZHMeterInsulation2PositiveToGroundResOnSideA | Insulation 2 positive-to-ground resistance on side A | A面绝缘2正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 2 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.71 | hwAcrelAMC16ZHMeterInsulation3PositiveToGroundResOnSideA | Insulation 3 positive-to-ground resistance on side A | A面绝缘3正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 3 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.72 | hwAcrelAMC16ZHMeterInsulation4PositiveToGroundResOnSideA | Insulation 4 positive-to-ground resistance on side A | A面绝缘4正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 4 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.73 | hwAcrelAMC16ZHMeterInsulation5PositiveToGroundResOnSideA | Insulation 5 positive-to-ground resistance on side A | A面绝缘5正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 5 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.74 | hwAcrelAMC16ZHMeterInsulation6PositiveToGroundResOnSideA | Insulation 6 positive-to-ground resistance on side A | A面绝缘6正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 6 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.75 | hwAcrelAMC16ZHMeterInsulation7PositiveToGroundResOnSideA | Insulation 7 positive-to-ground resistance on side A | A面绝缘7正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 7 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.76 | hwAcrelAMC16ZHMeterInsulation8PositiveToGroundResOnSideA | Insulation 8 positive-to-ground resistance on side A | A面绝缘8正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 8 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.77 | hwAcrelAMC16ZHMeterInsulation9PositiveToGroundResOnSideA | Insulation 9 positive-to-ground resistance on side A | A面绝缘9正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 9 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.78 | hwAcrelAMC16ZHMeterInsulation10PositiveToGroundResOnSideA | Insulation 10 positive-to-ground resistance on side A | A面绝缘10正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 10 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.79 | hwAcrelAMC16ZHMeterInsulation11PositiveToGroundResOnSideA | Insulation 11 positive-to-ground resistance on side A | A面绝缘11正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 11 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.80 | hwAcrelAMC16ZHMeterInsulation12PositiveToGroundResOnSideA | Insulation 12 positive-to-ground resistance on side A | A面绝缘12正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 12 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.81 | hwAcrelAMC16ZHMeterInsulation13PositiveToGroundResOnSideA | Insulation 13 positive-to-ground resistance on side A | A面绝缘13正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 13 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.82 | hwAcrelAMC16ZHMeterInsulation14PositiveToGroundResOnSideA | Insulation 14 positive-to-ground resistance on side A | A面绝缘14正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 14 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.83 | hwAcrelAMC16ZHMeterInsulation15PositiveToGroundResOnSideA | Insulation 15 positive-to-ground resistance on side A | A面绝缘15正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 15 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.84 | hwAcrelAMC16ZHMeterInsulation16PositiveToGroundResOnSideA | Insulation 16 positive-to-ground resistance on side A | A面绝缘16正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 16 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.85 | hwAcrelAMC16ZHMeterInsulation17PositiveToGroundResOnSideA | Insulation 17 positive-to-ground resistance on side A | A面绝缘17正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 17 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.86 | hwAcrelAMC16ZHMeterInsulation18PositiveToGroundResOnSideA | Insulation 18 positive-to-ground resistance on side A | A面绝缘18正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 18 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.87 | hwAcrelAMC16ZHMeterInsulation19PositiveToGroundResOnSideA | Insulation 19 positive-to-ground resistance on side A | A面绝缘19正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 19 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.88 | hwAcrelAMC16ZHMeterInsulation20PositiveToGroundResOnSideA | Insulation 20 positive-to-ground resistance on side A | A面绝缘20正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 20 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.89 | hwAcrelAMC16ZHMeterInsulation21PositiveToGroundResOnSideA | Insulation 21 positive-to-ground resistance on side A | A面绝缘21正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 21 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.90 | hwAcrelAMC16ZHMeterInsulation22PositiveToGroundResOnSideA | Insulation 22 positive-to-ground resistance on side A | A面绝缘22正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 22 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.91 | hwAcrelAMC16ZHMeterInsulation23PositiveToGroundResOnSideA | Insulation 23 positive-to-ground resistance on side A | A面绝缘23正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 23 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.92 | hwAcrelAMC16ZHMeterInsulation24PositiveToGroundResOnSideA | Insulation 24 positive-to-ground resistance on side A | A面绝缘24正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 24 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.93 | hwAcrelAMC16ZHMeterInsulation25PositiveToGroundResOnSideA | Insulation 25 positive-to-ground resistance on side A | A面绝缘25正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 25 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.94 | hwAcrelAMC16ZHMeterInsulation26PositiveToGroundResOnSideA | Insulation 26 positive-to-ground resistance on side A | A面绝缘26正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 26 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.95 | hwAcrelAMC16ZHMeterInsulation27PositiveToGroundResOnSideA | Insulation 27 positive-to-ground resistance on side A | A面绝缘27正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 27 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.96 | hwAcrelAMC16ZHMeterInsulation28PositiveToGroundResOnSideA | Insulation 28 positive-to-ground resistance on side A | A面绝缘28正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 28 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.97 | hwAcrelAMC16ZHMeterInsulation29PositiveToGroundResOnSideA | Insulation 29 positive-to-ground resistance on side A | A面绝缘29正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 29 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.98 | hwAcrelAMC16ZHMeterInsulation30PositiveToGroundResOnSideA | Insulation 30 positive-to-ground resistance on side A | A面绝缘30正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 30 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.99 | hwAcrelAMC16ZHMeterInsulation31PositiveToGroundResOnSideA | Insulation 31 positive-to-ground resistance on side A | A面绝缘31正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 31 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.100 | hwAcrelAMC16ZHMeterInsulation32PositiveToGroundResOnSideA | Insulation 32 positive-to-ground resistance on side A | A面绝缘32正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 32 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.101 | hwAcrelAMC16ZHMeterInsulation33PositiveToGroundResOnSideA | Insulation 33 positive-to-ground resistance on side A | A面绝缘33正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 33 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.102 | hwAcrelAMC16ZHMeterInsulation34PositiveToGroundResOnSideA | Insulation 34 positive-to-ground resistance on side A | A面绝缘34正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 34 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.103 | hwAcrelAMC16ZHMeterInsulation35PositiveToGroundResOnSideA | Insulation 35 positive-to-ground resistance on side A | A面绝缘35正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 35 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.104 | hwAcrelAMC16ZHMeterInsulation36PositiveToGroundResOnSideA | Insulation 36 positive-to-ground resistance on side A | A面绝缘36正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 36 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.105 | hwAcrelAMC16ZHMeterInsulation37PositiveToGroundResOnSideA | Insulation 37 positive-to-ground resistance on side A | A面绝缘37正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 37 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.106 | hwAcrelAMC16ZHMeterInsulation38PositiveToGroundResOnSideA | Insulation 38 positive-to-ground resistance on side A | A面绝缘38正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 38 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.107 | hwAcrelAMC16ZHMeterInsulation39PositiveToGroundResOnSideA | Insulation 39 positive-to-ground resistance on side A | A面绝缘39正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 39 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.108 | hwAcrelAMC16ZHMeterInsulation40PositiveToGroundResOnSideA | Insulation 40 positive-to-ground resistance on side A | A面绝缘40正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 40 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.109 | hwAcrelAMC16ZHMeterInsulation41PositiveToGroundResOnSideA | Insulation 41 positive-to-ground resistance on side A | A面绝缘41正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 41 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.110 | hwAcrelAMC16ZHMeterInsulation42PositiveToGroundResOnSideA | Insulation 42 positive-to-ground resistance on side A | A面绝缘42正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 42 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.111 | hwAcrelAMC16ZHMeterInsulation43PositiveToGroundResOnSideA | Insulation 43 positive-to-ground resistance on side A | A面绝缘43正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 43 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.112 | hwAcrelAMC16ZHMeterInsulation44PositiveToGroundResOnSideA | Insulation 44 positive-to-ground resistance on side A | A面绝缘44正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 44 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.113 | hwAcrelAMC16ZHMeterInsulation45PositiveToGroundResOnSideA | Insulation 45 positive-to-ground resistance on side A | A面绝缘45正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 45 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.114 | hwAcrelAMC16ZHMeterInsulation46PositiveToGroundResOnSideA | Insulation 46 positive-to-ground resistance on side A | A面绝缘46正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 46 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.115 | hwAcrelAMC16ZHMeterInsulation47PositiveToGroundResOnSideA | Insulation 47 positive-to-ground resistance on side A | A面绝缘47正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 47 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.116 | hwAcrelAMC16ZHMeterInsulation48PositiveToGroundResOnSideA | Insulation 48 positive-to-ground resistance on side A | A面绝缘48正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 48 positive-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.117 | hwAcrelAMC16ZHMeterInsulation1NegToGroundResOnSideA | Insulation 1 negative-to-ground resistance on side A | A面绝缘1负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 1 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.118 | hwAcrelAMC16ZHMeterInsulation2NegToGroundResOnSideA | Insulation 2 negative-to-ground resistance on side A | A面绝缘2负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 2 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.119 | hwAcrelAMC16ZHMeterInsulation3NegToGroundResOnSideA | Insulation 3 negative-to-ground resistance on side A | A面绝缘3负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 3 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.120 | hwAcrelAMC16ZHMeterInsulation4NegToGroundResOnSideA | Insulation 4 negative-to-ground resistance on side A | A面绝缘4负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 4 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.121 | hwAcrelAMC16ZHMeterInsulation5NegToGroundResOnSideA | Insulation 5 negative-to-ground resistance on side A | A面绝缘5负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 5 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.122 | hwAcrelAMC16ZHMeterInsulation6NegToGroundResOnSideA | Insulation 6 negative-to-ground resistance on side A | A面绝缘6负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 6 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.123 | hwAcrelAMC16ZHMeterInsulation7NegToGroundResOnSideA | Insulation 7 negative-to-ground resistance on side A | A面绝缘7负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 7 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.124 | hwAcrelAMC16ZHMeterInsulation8NegToGroundResOnSideA | Insulation 8 negative-to-ground resistance on side A | A面绝缘8负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 8 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.125 | hwAcrelAMC16ZHMeterInsulation9NegToGroundResOnSideA | Insulation 9 negative-to-ground resistance on side A | A面绝缘9负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 9 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.126 | hwAcrelAMC16ZHMeterInsulation10NegToGroundResOnSideA | Insulation 10 negative-to-ground resistance on side A | A面绝缘10负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 10 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.127 | hwAcrelAMC16ZHMeterInsulation11NegToGroundResOnSideA | Insulation 11 negative-to-ground resistance on side A | A面绝缘11负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 11 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.128 | hwAcrelAMC16ZHMeterInsulation12NegToGroundResOnSideA | Insulation 12 negative-to-ground resistance on side A | A面绝缘12负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 12 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.128 | hwAcrelAMC16ZHMeterInsulation13NegToGroundResOnSideA | Insulation 13 negative-to-ground resistance on side A | A面绝缘13负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 13 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.130 | hwAcrelAMC16ZHMeterInsulation14NegToGroundResOnSideA | Insulation 14 negative-to-ground resistance on side A | A面绝缘14负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 14 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.131 | hwAcrelAMC16ZHMeterInsulation15NegToGroundResOnSideA | Insulation 15 negative-to-ground resistance on side A | A面绝缘15负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 15 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.132 | hwAcrelAMC16ZHMeterInsulation16NegToGroundResOnSideA | Insulation 16 negative-to-ground resistance on side A | A面绝缘16负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 16 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.133 | hwAcrelAMC16ZHMeterInsulation17NegToGroundResOnSideA | Insulation 17 negative-to-ground resistance on side A | A面绝缘17负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 17 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.134 | hwAcrelAMC16ZHMeterInsulation18NegToGroundResOnSideA | Insulation 18 negative-to-ground resistance on side A | A面绝缘18负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 18 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.135 | hwAcrelAMC16ZHMeterInsulation19NegToGroundResOnSideA | Insulation 19 negative-to-ground resistance on side A | A面绝缘19负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 19 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.136 | hwAcrelAMC16ZHMeterInsulation20NegToGroundResOnSideA | Insulation 20 negative-to-ground resistance on side A | A面绝缘20负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 20 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.137 | hwAcrelAMC16ZHMeterInsulation21NegToGroundResOnSideA | Insulation 21 negative-to-ground resistance on side A | A面绝缘21负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 21 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.138 | hwAcrelAMC16ZHMeterInsulation22NegToGroundResOnSideA | Insulation 22 negative-to-ground resistance on side A | A面绝缘22负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 22 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.139 | hwAcrelAMC16ZHMeterInsulation23NegToGroundResOnSideA | Insulation 23 negative-to-ground resistance on side A | A面绝缘23负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 23 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.140 | hwAcrelAMC16ZHMeterInsulation24NegToGroundResOnSideA | Insulation 24 negative-to-ground resistance on side A | A面绝缘24负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 24 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.141 | hwAcrelAMC16ZHMeterInsulation25NegToGroundResOnSideA | Insulation 25 negative-to-ground resistance on side A | A面绝缘25负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 25 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.142 | hwAcrelAMC16ZHMeterInsulation26NegToGroundResOnSideA | Insulation 26 negative-to-ground resistance on side A | A面绝缘26负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 26 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.143 | hwAcrelAMC16ZHMeterInsulation27NegToGroundResOnSideA | Insulation 27 negative-to-ground resistance on side A | A面绝缘27负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 27 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.144 | hwAcrelAMC16ZHMeterInsulation28NegToGroundResOnSideA | Insulation 28 negative-to-ground resistance on side A | A面绝缘28负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 28 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.145 | hwAcrelAMC16ZHMeterInsulation29NegToGroundResOnSideA | Insulation 29 negative-to-ground resistance on side A | A面绝缘29负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 29 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.146 | hwAcrelAMC16ZHMeterInsulation30NegToGroundResOnSideA | Insulation 30 negative-to-ground resistance on side A | A面绝缘30负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 30 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.147 | hwAcrelAMC16ZHMeterInsulation31NegToGroundResOnSideA | Insulation 31 negative-to-ground resistance on side A | A面绝缘31负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 31 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.148 | hwAcrelAMC16ZHMeterInsulation32NegToGroundResOnSideA | Insulation 32 negative-to-ground resistance on side A | A面绝缘32负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 32 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.149 | hwAcrelAMC16ZHMeterInsulation33NegToGroundResOnSideA | Insulation 33 negative-to-ground resistance on side A | A面绝缘33负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 33 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.150 | hwAcrelAMC16ZHMeterInsulation34NegToGroundResOnSideA | Insulation 34 negative-to-ground resistance on side A | A面绝缘34负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 34 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.151 | hwAcrelAMC16ZHMeterInsulation35NegToGroundResOnSideA | Insulation 35 negative-to-ground resistance on side A | A面绝缘35负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 35 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.152 | hwAcrelAMC16ZHMeterInsulation36NegToGroundResOnSideA | Insulation 36 negative-to-ground resistance on side A | A面绝缘36负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 36 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.153 | hwAcrelAMC16ZHMeterInsulation37NegToGroundResOnSideA | Insulation 37 negative-to-ground resistance on side A | A面绝缘37负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 37 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.154 | hwAcrelAMC16ZHMeterInsulation38NegToGroundResOnSideA | Insulation 38 negative-to-ground resistance on side A | A面绝缘38负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 38 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.155 | hwAcrelAMC16ZHMeterInsulation39NegToGroundResOnSideA | Insulation 39 negative-to-ground resistance on side A | A面绝缘39负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 39 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.156 | hwAcrelAMC16ZHMeterInsulation40NegToGroundResOnSideA | Insulation 40 negative-to-ground resistance on side A | A面绝缘40负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 40 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.157 | hwAcrelAMC16ZHMeterInsulation41NegToGroundResOnSideA | Insulation 41 negative-to-ground resistance on side A | A面绝缘41负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 41 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.158 | hwAcrelAMC16ZHMeterInsulation42NegToGroundResOnSideA | Insulation 42 negative-to-ground resistance on side A | A面绝缘42负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 42 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.159 | hwAcrelAMC16ZHMeterInsulation43NegToGroundResOnSideA | Insulation 43 negative-to-ground resistance on side A | A面绝缘43负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 43 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.160 | hwAcrelAMC16ZHMeterInsulation44NegToGroundResOnSideA | Insulation 44 negative-to-ground resistance on side A | A面绝缘44负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 44 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.161 | hwAcrelAMC16ZHMeterInsulation45NegToGroundResOnSideA | Insulation 45 negative-to-ground resistance on side A | A面绝缘45负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 45 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.162 | hwAcrelAMC16ZHMeterInsulation46NegToGroundResOnSideA | Insulation 46 negative-to-ground resistance on side A | A面绝缘46负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 46 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.163 | hwAcrelAMC16ZHMeterInsulation47NegToGroundResOnSideA | Insulation 47 negative-to-ground resistance on side A | A面绝缘47负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 47 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.164 | hwAcrelAMC16ZHMeterInsulation48NegToGroundResOnSideA | Insulation 48 negative-to-ground resistance on side A | A面绝缘48负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 48 negative-to-ground resistance on side A of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.165 | hwAcrelAMC16ZHMeterBranch1CurrentOnSideB | Branch 1 current on side B | B面分路1电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.166 | hwAcrelAMC16ZHMeterBranch2CurrentOnSideB | Branch 2 current on side B | B面分路2电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.167 | hwAcrelAMC16ZHMeterBranch3CurrentOnSideB | Branch 3 current on side B | B面分路3电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.168 | hwAcrelAMC16ZHMeterBranch4CurrentOnSideB | Branch 4 current on side B | B面分路4电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.169 | hwAcrelAMC16ZHMeterBranch5CurrentOnSideB | Branch 5 current on side B | B面分路5电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.170 | hwAcrelAMC16ZHMeterBranch6CurrentOnSideB | Branch 6 current on side B | B面分路6电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.171 | hwAcrelAMC16ZHMeterBranch7CurrentOnSideB | Branch 7 current on side B | B面分路7电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.172 | hwAcrelAMC16ZHMeterBranch8CurrentOnSideB | Branch 8 current on side B | B面分路8电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.173 | hwAcrelAMC16ZHMeterBranch9CurrentOnSideB | Branch 9 current on side B | B面分路9电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.174 | hwAcrelAMC16ZHMeterBranch10CurrentOnSideB | Branch 10 current on side B | B面分路10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.175 | hwAcrelAMC16ZHMeterBranch11CurrentOnSideB | Branch 11 current on side B | B面分路11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.176 | hwAcrelAMC16ZHMeterBranch12CurrentOnSideB | Branch 12 current on side B | B面分路12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.177 | hwAcrelAMC16ZHMeterBranch13CurrentOnSideB | Branch 13 current on side B | B面分路13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.178 | hwAcrelAMC16ZHMeterBranch14CurrentOnSideB | Branch 14 current on side B | B面分路14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.179 | hwAcrelAMC16ZHMeterBranch15CurrentOnSideB | Branch 15 current on side B | B面分路15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.180 | hwAcrelAMC16ZHMeterBranch16CurrentOnSideB | Branch 16 current on side B | B面分路16电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.181 | hwAcrelAMC16ZHMeterBranch17CurrentOnSideB | Branch 17 current on side B | B面分路17电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.182 | hwAcrelAMC16ZHMeterBranch18CurrentOnSideB | Branch 18 current on side B | B面分路18电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.183 | hwAcrelAMC16ZHMeterBranch19CurrentOnSideB | Branch 19 current on side B | B面分路19电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.184 | hwAcrelAMC16ZHMeterBranch20CurrentOnSideB | Branch 20 current on side B | B面分路20电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.185 | hwAcrelAMC16ZHMeterBranch21CurrentOnSideB | Branch 21 current on side B | B面分路21电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.186 | hwAcrelAMC16ZHMeterBranch22CurrentOnSideB | Branch 22 current on side B | B面分路22电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.187 | hwAcrelAMC16ZHMeterBranch23CurrentOnSideB | Branch 23 current on side B | B面分路23电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.188 | hwAcrelAMC16ZHMeterBranch24CurrentOnSideB | Branch 24 current on side B | B面分路24电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.189 | hwAcrelAMC16ZHMeterBranch25CurrentOnSideB | Branch 25 current on side B | B面分路25电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.190 | hwAcrelAMC16ZHMeterBranch26CurrentOnSideB | Branch 26 current on side B | B面分路26电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.191 | hwAcrelAMC16ZHMeterBranch27CurrentOnSideB | Branch 27 current on side B | B面分路27电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.192 | hwAcrelAMC16ZHMeterBranch28CurrentOnSideB | Branch 28 current on side B | B面分路28电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.193 | hwAcrelAMC16ZHMeterBranch29CurrentOnSideB | Branch 29 current on side B | B面分路29电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.194 | hwAcrelAMC16ZHMeterBranch30CurrentOnSideB | Branch 30 current on side B | B面分路30电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.195 | hwAcrelAMC16ZHMeterBranch31CurrentOnSideB | Branch 31 current on side B | B面分路31电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.196 | hwAcrelAMC16ZHMeterBranch32CurrentOnSideB | Branch 32 current on side B | B面分路32电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.197 | hwAcrelAMC16ZHMeterBranch33CurrentOnSideB | Branch 33 current on side B | B面分路33电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.198 | hwAcrelAMC16ZHMeterBranch34CurrentOnSideB | Branch 34 current on side B | B面分路34电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.199 | hwAcrelAMC16ZHMeterBranch35CurrentOnSideB | Branch 35 current on side B | B面分路35电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.200 | hwAcrelAMC16ZHMeterBranch36CurrentOnSideB | Branch 36 current on side B | B面分路36电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.201 | hwAcrelAMC16ZHMeterBranch37CurrentOnSideB | Branch 37 current on side B | B面分路37电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.202 | hwAcrelAMC16ZHMeterBranch38CurrentOnSideB | Branch 38 current on side B | B面分路38电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.203 | hwAcrelAMC16ZHMeterBranch39CurrentOnSideB | Branch 39 current on side B | B面分路39电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.204 | hwAcrelAMC16ZHMeterBranch40CurrentOnSideB | Branch 40 current on side B | B面分路40电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.205 | hwAcrelAMC16ZHMeterBranch41CurrentOnSideB | Branch 41 current on side B | B面分路41电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.206 | hwAcrelAMC16ZHMeterBranch42CurrentOnSideB | Branch 42 current on side B | B面分路42电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.207 | hwAcrelAMC16ZHMeterBranch43CurrentOnSideB | Branch 43 current on side B | B面分路43电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.208 | hwAcrelAMC16ZHMeterBranch44CurrentOnSideB | Branch 44 current on side B | B面分路44电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.209 | hwAcrelAMC16ZHMeterBranch45CurrentOnSideB | Branch 45 current on side B | B面分路45电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.210 | hwAcrelAMC16ZHMeterBranch46CurrentOnSideB | Branch 46 current on side B | B面分路46电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.211 | hwAcrelAMC16ZHMeterBranch47CurrentOnSideB | Branch 47 current on side B | B面分路47电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.212 | hwAcrelAMC16ZHMeterBranch48CurrentOnSideB | Branch 48 current on side B | B面分路48电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 current on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.213 | hwAcrelAMC16ZHMeterBranch1ActivePowerOnSideB | Branch 1 active power on side B | B面分路1有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.214 | hwAcrelAMC16ZHMeterBranch2ActivePowerOnSideB | Branch 2 active power on side B | B面分路2有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.215 | hwAcrelAMC16ZHMeterBranch3ActivePowerOnSideB | Branch 3 active power on side B | B面分路3有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.216 | hwAcrelAMC16ZHMeterBranch4ActivePowerOnSideB | Branch 4 active power on side B | B面分路4有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.217 | hwAcrelAMC16ZHMeterBranch5ActivePowerOnSideB | Branch 5 active power on side B | B面分路5有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.218 | hwAcrelAMC16ZHMeterBranch6ActivePowerOnSideB | Branch 6 active power on side B | B面分路6有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.219 | hwAcrelAMC16ZHMeterBranch7ActivePowerOnSideB | Branch 7 active power on side B | B面分路7有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.220 | hwAcrelAMC16ZHMeterBranch8ActivePowerOnSideB | Branch 8 active power on side B | B面分路8有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.221 | hwAcrelAMC16ZHMeterBranch9ActivePowerOnSideB | Branch 9 active power on side B | B面分路9有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.222 | hwAcrelAMC16ZHMeterBranch10ActivePowerOnSideB | Branch 10 active power on side B | B面分路10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.223 | hwAcrelAMC16ZHMeterBranch11ActivePowerOnSideB | Branch 11 active power on side B | B面分路11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.224 | hwAcrelAMC16ZHMeterBranch12ActivePowerOnSideB | Branch 12 active power on side B | B面分路12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.225 | hwAcrelAMC16ZHMeterBranch13ActivePowerOnSideB | Branch 13 active power on side B | B面分路13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.226 | hwAcrelAMC16ZHMeterBranch14ActivePowerOnSideB | Branch 14 active power on side B | B面分路14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.227 | hwAcrelAMC16ZHMeterBranch15ActivePowerOnSideB | Branch 15 active power on side B | B面分路15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.228 | hwAcrelAMC16ZHMeterBranch16ActivePowerOnSideB | Branch 16 active power on side B | B面分路16有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.229 | hwAcrelAMC16ZHMeterBranch17ActivePowerOnSideB | Branch 17 active power on side B | B面分路17有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.230 | hwAcrelAMC16ZHMeterBranch18ActivePowerOnSideB | Branch 18 active power on side B | B面分路18有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.231 | hwAcrelAMC16ZHMeterBranch19ActivePowerOnSideB | Branch 19 active power on side B | B面分路19有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.232 | hwAcrelAMC16ZHMeterBranch20ActivePowerOnSideB | Branch 20 active power on side B | B面分路20有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.233 | hwAcrelAMC16ZHMeterBranch21ActivePowerOnSideB | Branch 21 active power on side B | B面分路21有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.234 | hwAcrelAMC16ZHMeterBranch22ActivePowerOnSideB | Branch 22 active power on side B | B面分路22有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.235 | hwAcrelAMC16ZHMeterBranch23ActivePowerOnSideB | Branch 23 active power on side B | B面分路23有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.236 | hwAcrelAMC16ZHMeterBranch24ActivePowerOnSideB | Branch 24 active power on side B | B面分路24有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.237 | hwAcrelAMC16ZHMeterBranch25ActivePowerOnSideB | Branch 25 active power on side B | B面分路25有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.238 | hwAcrelAMC16ZHMeterBranch26ActivePowerOnSideB | Branch 26 active power on side B | B面分路26有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.239 | hwAcrelAMC16ZHMeterBranch27ActivePowerOnSideB | Branch 27 active power on side B | B面分路27有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.240 | hwAcrelAMC16ZHMeterBranch28ActivePowerOnSideB | Branch 28 active power on side B | B面分路28有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.241 | hwAcrelAMC16ZHMeterBranch29ActivePowerOnSideB | Branch 29 active power on side B | B面分路29有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.242 | hwAcrelAMC16ZHMeterBranch30ActivePowerOnSideB | Branch 30 active power on side B | B面分路30有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.243 | hwAcrelAMC16ZHMeterBranch31ActivePowerOnSideB | Branch 31 active power on side B | B面分路31有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.244 | hwAcrelAMC16ZHMeterBranch32ActivePowerOnSideB | Branch 32 active power on side B | B面分路32有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.245 | hwAcrelAMC16ZHMeterBranch33ActivePowerOnSideB | Branch 33 active power on side B | B面分路33有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.246 | hwAcrelAMC16ZHMeterBranch34ActivePowerOnSideB | Branch 34 active power on side B | B面分路34有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.247 | hwAcrelAMC16ZHMeterBranch35ActivePowerOnSideB | Branch 35 active power on side B | B面分路35有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.248 | hwAcrelAMC16ZHMeterBranch36ActivePowerOnSideB | Branch 36 active power on side B | B面分路36有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.249 | hwAcrelAMC16ZHMeterBranch37ActivePowerOnSideB | Branch 37 active power on side B | B面分路37有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.250 | hwAcrelAMC16ZHMeterBranch38ActivePowerOnSideB | Branch 38 active power on side B | B面分路38有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.251 | hwAcrelAMC16ZHMeterBranch39ActivePowerOnSideB | Branch 39 active power on side B | B面分路39有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.252 | hwAcrelAMC16ZHMeterBranch40ActivePowerOnSideB | Branch 40 active power on side B | B面分路40有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.253 | hwAcrelAMC16ZHMeterBranch41ActivePowerOnSideB | Branch 41 active power on side B | B面分路41有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.254 | hwAcrelAMC16ZHMeterBranch42ActivePowerOnSideB | Branch 42 active power on side B | B面分路42有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.255 | hwAcrelAMC16ZHMeterBranch43ActivePowerOnSideB | Branch 43 active power on side B | B面分路43有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.256 | hwAcrelAMC16ZHMeterBranch44ActivePowerOnSideB | Branch 44 active power on side B | B面分路44有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.257 | hwAcrelAMC16ZHMeterBranch45ActivePowerOnSideB | Branch 45 active power on side B | B面分路45有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.258 | hwAcrelAMC16ZHMeterBranch46ActivePowerOnSideB | Branch 46 active power on side B | B面分路46有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.259 | hwAcrelAMC16ZHMeterBranch47ActivePowerOnSideB | Branch 47 active power on side B | B面分路47有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.260 | hwAcrelAMC16ZHMeterBranch48ActivePowerOnSideB | Branch 48 active power on side B | B面分路48有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 active power on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.261 | hwAcrelAMC16ZHMeterBranch1ActiveEnergyOnSideB | Branch 1 active energy on side B | B面分路1有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.262 | hwAcrelAMC16ZHMeterBranch2ActiveEnergyOnSideB | Branch 2 active energy on side B | B面分路2有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.263 | hwAcrelAMC16ZHMeterBranch3ActiveEnergyOnSideB | Branch 3 active energy on side B | B面分路3有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.264 | hwAcrelAMC16ZHMeterBranch4ActiveEnergyOnSideB | Branch 4 active energy on side B | B面分路4有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.265 | hwAcrelAMC16ZHMeterBranch5ActiveEnergyOnSideB | Branch 5 active energy on side B | B面分路5有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.266 | hwAcrelAMC16ZHMeterBranch6ActiveEnergyOnSideB | Branch 6 active energy on side B | B面分路6有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.267 | hwAcrelAMC16ZHMeterBranch7ActiveEnergyOnSideB | Branch 7 active energy on side B | B面分路7有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.268 | hwAcrelAMC16ZHMeterBranch8ActiveEnergyOnSideB | Branch 8 active energy on side B | B面分路8有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.269 | hwAcrelAMC16ZHMeterBranch9ActiveEnergyOnSideB | Branch 9 active energy on side B | B面分路9有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.270 | hwAcrelAMC16ZHMeterBranch10ActiveEnergyOnSideB | Branch 10 active energy on side B | B面分路10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.271 | hwAcrelAMC16ZHMeterBranch11ActiveEnergyOnSideB | Branch 11 active energy on side B | B面分路11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.272 | hwAcrelAMC16ZHMeterBranch12ActiveEnergyOnSideB | Branch 12 active energy on side B | B面分路12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.273 | hwAcrelAMC16ZHMeterBranch13ActiveEnergyOnSideB | Branch 13 active energy on side B | B面分路13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.274 | hwAcrelAMC16ZHMeterBranch14ActiveEnergyOnSideB | Branch 14 active energy on side B | B面分路14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.275 | hwAcrelAMC16ZHMeterBranch15ActiveEnergyOnSideB | Branch 15 active energy on side B | B面分路15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.276 | hwAcrelAMC16ZHMeterBranch16ActiveEnergyOnSideB | Branch 16 active energy on side B | B面分路16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.277 | hwAcrelAMC16ZHMeterBranch17ActiveEnergyOnSideB | Branch 17 active energy on side B | B面分路17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.278 | hwAcrelAMC16ZHMeterBranch18ActiveEnergyOnSideB | Branch 18 active energy on side B | B面分路18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.279 | hwAcrelAMC16ZHMeterBranch19ActiveEnergyOnSideB | Branch 19 active energy on side B | B面分路19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.280 | hwAcrelAMC16ZHMeterBranch20ActiveEnergyOnSideB | Branch 20 active energy on side B | B面分路20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.281 | hwAcrelAMC16ZHMeterBranch21ActiveEnergyOnSideB | Branch 21 active energy on side B | B面分路21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.282 | hwAcrelAMC16ZHMeterBranch22ActiveEnergyOnSideB | Branch 22 active energy on side B | B面分路22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.283 | hwAcrelAMC16ZHMeterBranch23ActiveEnergyOnSideB | Branch 23 active energy on side B | B面分路23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.284 | hwAcrelAMC16ZHMeterBranch24ActiveEnergyOnSideB | Branch 24 active energy on side B | B面分路24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.285 | hwAcrelAMC16ZHMeterBranch25ActiveEnergyOnSideB | Branch 25 active energy on side B | B面分路25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.286 | hwAcrelAMC16ZHMeterBranch26ActiveEnergyOnSideB | Branch 26 active energy on side B | B面分路26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.287 | hwAcrelAMC16ZHMeterBranch27ActiveEnergyOnSideB | Branch 27 active energy on side B | B面分路27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.288 | hwAcrelAMC16ZHMeterBranch28ActiveEnergyOnSideB | Branch 28 active energy on side B | B面分路28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.289 | hwAcrelAMC16ZHMeterBranch29ActiveEnergyOnSideB | Branch 29 active energy on side B | B面分路29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.290 | hwAcrelAMC16ZHMeterBranch30ActiveEnergyOnSideB | Branch 30 active energy on side B | B面分路30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.291 | hwAcrelAMC16ZHMeterBranch31ActiveEnergyOnSideB | Branch 31 active energy on side B | B面分路31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.292 | hwAcrelAMC16ZHMeterBranch32ActiveEnergyOnSideB | Branch 32 active energy on side B | B面分路32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.293 | hwAcrelAMC16ZHMeterBranch33ActiveEnergyOnSideB | Branch 33 active energy on side B | B面分路33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.294 | hwAcrelAMC16ZHMeterBranch34ActiveEnergyOnSideB | Branch 34 active energy on side B | B面分路34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.295 | hwAcrelAMC16ZHMeterBranch35ActiveEnergyOnSideB | Branch 35 active energy on side B | B面分路35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.296 | hwAcrelAMC16ZHMeterBranch36ActiveEnergyOnSideB | Branch 36 active energy on side B | B面分路36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.297 | hwAcrelAMC16ZHMeterBranch37ActiveEnergyOnSideB | Branch 37 active energy on side B | B面分路37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.298 | hwAcrelAMC16ZHMeterBranch38ActiveEnergyOnSideB | Branch 38 active energy on side B | B面分路38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.299 | hwAcrelAMC16ZHMeterBranch39ActiveEnergyOnSideB | Branch 39 active energy on side B | B面分路39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.2.1.300 | hwAcrelAMC16ZHMeterRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.3 | hwAcrelAMC16ZHMeterRunning3Table | / | / |  |  | / | / | The running table of Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.1 | hwAcrelAMC16ZHMeterRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.2 | hwAcrelAMC16ZHMeterBranch40ActiveEnergyOnSideB | Branch 40 active energy on side B | B面分路40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.3 | hwAcrelAMC16ZHMeterBranch41ActiveEnergyOnSideB | Branch 41 active energy on side B | B面分路41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.4 | hwAcrelAMC16ZHMeterBranch42ActiveEnergyOnSideB | Branch 42 active energy on side B | B面分路42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.5 | hwAcrelAMC16ZHMeterBranch43ActiveEnergyOnSideB | Branch 43 active energy on side B | B面分路43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.6 | hwAcrelAMC16ZHMeterBranch44ActiveEnergyOnSideB | Branch 44 active energy on side B | B面分路44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.7 | hwAcrelAMC16ZHMeterBranch45ActiveEnergyOnSideB | Branch 45 active energy on side B | B面分路45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.8 | hwAcrelAMC16ZHMeterBranch46ActiveEnergyOnSideB | Branch 46 active energy on side B | B面分路46有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.9 | hwAcrelAMC16ZHMeterBranch47ActiveEnergyOnSideB | Branch 47 active energy on side B | B面分路47有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.10 | hwAcrelAMC16ZHMeterBranch48ActiveEnergyOnSideB | Branch 48 active energy on side B | B面分路48有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 active energy on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.11 | hwAcrelAMC16ZHMeterBranch1VoltageOnSideB | Branch 1 voltage on side B | B面分路1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.12 | hwAcrelAMC16ZHMeterBranch2VoltageOnSideB | Branch 2 voltage on side B | B面分路2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.13 | hwAcrelAMC16ZHMeterBranch3VoltageOnSideB | Branch 3 voltage on side B | B面分路3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.14 | hwAcrelAMC16ZHMeterBranch4VoltageOnSideB | Branch 4 voltage on side B | B面分路4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.15 | hwAcrelAMC16ZHMeterBranch5VoltageOnSideB | Branch 5 voltage on side B | B面分路5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.16 | hwAcrelAMC16ZHMeterBranch6VoltageOnSideB | Branch 6 voltage on side B | B面分路6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.17 | hwAcrelAMC16ZHMeterBranch7VoltageOnSideB | Branch 7 voltage on side B | B面分路7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.18 | hwAcrelAMC16ZHMeterBranch8VoltageOnSideB | Branch 8 voltage on side B | B面分路8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.19 | hwAcrelAMC16ZHMeterBranch9VoltageOnSideB | Branch 9 voltage on side B | B面分路9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.20 | hwAcrelAMC16ZHMeterBranch10VoltageOnSideB | Branch 10 voltage on side B | B面分路10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.21 | hwAcrelAMC16ZHMeterBranch11VoltageOnSideB | Branch 11 voltage on side B | B面分路11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.22 | hwAcrelAMC16ZHMeterBranch12VoltageOnSideB | Branch 12 voltage on side B | B面分路12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.23 | hwAcrelAMC16ZHMeterBranch13VoltageOnSideB | Branch 13 voltage on side B | B面分路13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.24 | hwAcrelAMC16ZHMeterBranch14VoltageOnSideB | Branch 14 voltage on side B | B面分路14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.25 | hwAcrelAMC16ZHMeterBranch15VoltageOnSideB | Branch 15 voltage on side B | B面分路15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.26 | hwAcrelAMC16ZHMeterBranch16VoltageOnSideB | Branch 16 voltage on side B | B面分路16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.27 | hwAcrelAMC16ZHMeterBranch17VoltageOnSideB | Branch 17 voltage on side B | B面分路17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.28 | hwAcrelAMC16ZHMeterBranch18VoltageOnSideB | Branch 18 voltage on side B | B面分路18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.29 | hwAcrelAMC16ZHMeterBranch19VoltageOnSideB | Branch 19 voltage on side B | B面分路19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.30 | hwAcrelAMC16ZHMeterBranch20VoltageOnSideB | Branch 20 voltage on side B | B面分路20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.31 | hwAcrelAMC16ZHMeterBranch21VoltageOnSideB | Branch 21 voltage on side B | B面分路21电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.32 | hwAcrelAMC16ZHMeterBranch22VoltageOnSideB | Branch 22 voltage on side B | B面分路22电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.33 | hwAcrelAMC16ZHMeterBranch23VoltageOnSideB | Branch 23 voltage on side B | B面分路23电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.34 | hwAcrelAMC16ZHMeterBranch24VoltageOnSideB | Branch 24 voltage on side B | B面分路24电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.35 | hwAcrelAMC16ZHMeterBranch25VoltageOnSideB | Branch 25 voltage on side B | B面分路25电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.36 | hwAcrelAMC16ZHMeterBranch26VoltageOnSideB | Branch 26 voltage on side B | B面分路26电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.37 | hwAcrelAMC16ZHMeterBranch27VoltageOnSideB | Branch 27 voltage on side B | B面分路27电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.38 | hwAcrelAMC16ZHMeterBranch28VoltageOnSideB | Branch 28 voltage on side B | B面分路28电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.39 | hwAcrelAMC16ZHMeterBranch29VoltageOnSideB | Branch 29 voltage on side B | B面分路29电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.40 | hwAcrelAMC16ZHMeterBranch30VoltageOnSideB | Branch 30 voltage on side B | B面分路30电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.41 | hwAcrelAMC16ZHMeterBranch31VoltageOnSideB | Branch 31 voltage on side B | B面分路31电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.42 | hwAcrelAMC16ZHMeterBranch32VoltageOnSideB | Branch 32 voltage on side B | B面分路32电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.43 | hwAcrelAMC16ZHMeterBranch33VoltageOnSideB | Branch 33 voltage on side B | B面分路33电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.44 | hwAcrelAMC16ZHMeterBranch34VoltageOnSideB | Branch 34 voltage on side B | B面分路34电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.45 | hwAcrelAMC16ZHMeterBranch35VoltageOnSideB | Branch 35 voltage on side B | B面分路35电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.46 | hwAcrelAMC16ZHMeterBranch36VoltageOnSideB | Branch 36 voltage on side B | B面分路36电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.47 | hwAcrelAMC16ZHMeterBranch37VoltageOnSideB | Branch 37 voltage on side B | B面分路37电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.48 | hwAcrelAMC16ZHMeterBranch38VoltageOnSideB | Branch 38 voltage on side B | B面分路38电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.49 | hwAcrelAMC16ZHMeterBranch39VoltageOnSideB | Branch 39 voltage on side B | B面分路39电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.50 | hwAcrelAMC16ZHMeterBranch40VoltageOnSideB | Branch 40 voltage on side B | B面分路40电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.51 | hwAcrelAMC16ZHMeterBranch41VoltageOnSideB | Branch 41 voltage on side B | B面分路41电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.52 | hwAcrelAMC16ZHMeterBranch42VoltageOnSideB | Branch 42 voltage on side B | B面分路42电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.53 | hwAcrelAMC16ZHMeterBranch43VoltageOnSideB | Branch 43 voltage on side B | B面分路43电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.54 | hwAcrelAMC16ZHMeterBranch44VoltageOnSideB | Branch 44 voltage on side B | B面分路44电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.55 | hwAcrelAMC16ZHMeterBranch45VoltageOnSideB | Branch 45 voltage on side B | B面分路45电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.56 | hwAcrelAMC16ZHMeterBranch46VoltageOnSideB | Branch 46 voltage on side B | B面分路46电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.57 | hwAcrelAMC16ZHMeterBranch47VoltageOnSideB | Branch 47 voltage on side B | B面分路47电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.58 | hwAcrelAMC16ZHMeterBranch48VoltageOnSideB | Branch 48 voltage on side B | B面分路48电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 voltage on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.59 | hwAcrelAMC16ZHMeterBranch1CurrentChangeRatioOnSideB | Branch 1 current change ratio on side B | B面分路1电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 1 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.60 | hwAcrelAMC16ZHMeterBranch2CurrentChangeRatioOnSideB | Branch 2 current change ratio on side B | B面分路2电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 2 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.61 | hwAcrelAMC16ZHMeterBranch3CurrentChangeRatioOnSideB | Branch 3 current change ratio on side B | B面分路3电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 3 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.62 | hwAcrelAMC16ZHMeterBranch4CurrentChangeRatioOnSideB | Branch 4 current change ratio on side B | B面分路4电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 4 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.63 | hwAcrelAMC16ZHMeterBranch5CurrentChangeRatioOnSideB | Branch 5 current change ratio on side B | B面分路5电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 5 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.64 | hwAcrelAMC16ZHMeterBranch6CurrentChangeRatioOnSideB | Branch 6 current change ratio on side B | B面分路6电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 6 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.65 | hwAcrelAMC16ZHMeterBranch7CurrentChangeRatioOnSideB | Branch 7 current change ratio on side B | B面分路7电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 7 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.66 | hwAcrelAMC16ZHMeterBranch8CurrentChangeRatioOnSideB | Branch 8 current change ratio on side B | B面分路8电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 8 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.67 | hwAcrelAMC16ZHMeterBranch9CurrentChangeRatioOnSideB | Branch 9 current change ratio on side B | B面分路9电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 9 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.68 | hwAcrelAMC16ZHMeterBranch10CurrentChangeRatioOnSideB | Branch 10 current change ratio on side B | B面分路10电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 10 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.69 | hwAcrelAMC16ZHMeterBranch11CurrentChangeRatioOnSideB | Branch 11 current change ratio on side B | B面分路11电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 11 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.70 | hwAcrelAMC16ZHMeterBranch12CurrentChangeRatioOnSideB | Branch 12 current change ratio on side B | B面分路12电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 12 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.71 | hwAcrelAMC16ZHMeterBranch13CurrentChangeRatioOnSideB | Branch 13 current change ratio on side B | B面分路13电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 13 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.72 | hwAcrelAMC16ZHMeterBranch14CurrentChangeRatioOnSideB | Branch 14 current change ratio on side B | B面分路14电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 14 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.73 | hwAcrelAMC16ZHMeterBranch15CurrentChangeRatioOnSideB | Branch 15 current change ratio on side B | B面分路15电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 15 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.74 | hwAcrelAMC16ZHMeterBranch16CurrentChangeRatioOnSideB | Branch 16 current change ratio on side B | B面分路16电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 16 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.75 | hwAcrelAMC16ZHMeterBranch17CurrentChangeRatioOnSideB | Branch 17 current change ratio on side B | B面分路17电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 17 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.76 | hwAcrelAMC16ZHMeterBranch18CurrentChangeRatioOnSideB | Branch 18 current change ratio on side B | B面分路18电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 18 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.77 | hwAcrelAMC16ZHMeterBranch19CurrentChangeRatioOnSideB | Branch 19 current change ratio on side B | B面分路19电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 19 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.78 | hwAcrelAMC16ZHMeterBranch20CurrentChangeRatioOnSideB | Branch 20 current change ratio on side B | B面分路20电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 20 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.79 | hwAcrelAMC16ZHMeterBranch21CurrentChangeRatioOnSideB | Branch 21 current change ratio on side B | B面分路21电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 21 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.80 | hwAcrelAMC16ZHMeterBranch22CurrentChangeRatioOnSideB | Branch 22 current change ratio on side B | B面分路22电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 22 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.81 | hwAcrelAMC16ZHMeterBranch23CurrentChangeRatioOnSideB | Branch 23 current change ratio on side B | B面分路23电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 23 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.82 | hwAcrelAMC16ZHMeterBranch24CurrentChangeRatioOnSideB | Branch 24 current change ratio on side B | B面分路24电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 24 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.83 | hwAcrelAMC16ZHMeterBranch25CurrentChangeRatioOnSideB | Branch 25 current change ratio on side B | B面分路25电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 25 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.84 | hwAcrelAMC16ZHMeterBranch26CurrentChangeRatioOnSideB | Branch 26 current change ratio on side B | B面分路26电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 26 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.85 | hwAcrelAMC16ZHMeterBranch27CurrentChangeRatioOnSideB | Branch 27 current change ratio on side B | B面分路27电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 27 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.86 | hwAcrelAMC16ZHMeterBranch28CurrentChangeRatioOnSideB | Branch 28 current change ratio on side B | B面分路28电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 28 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.87 | hwAcrelAMC16ZHMeterBranch29CurrentChangeRatioOnSideB | Branch 29 current change ratio on side B | B面分路29电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 29 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.88 | hwAcrelAMC16ZHMeterBranch30CurrentChangeRatioOnSideB | Branch 30 current change ratio on side B | B面分路30电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 30 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.89 | hwAcrelAMC16ZHMeterBranch31CurrentChangeRatioOnSideB | Branch 31 current change ratio on side B | B面分路31电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 31 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.90 | hwAcrelAMC16ZHMeterBranch32CurrentChangeRatioOnSideB | Branch 32 current change ratio on side B | B面分路32电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 32 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.91 | hwAcrelAMC16ZHMeterBranch33CurrentChangeRatioOnSideB | Branch 33 current change ratio on side B | B面分路33电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 33 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.92 | hwAcrelAMC16ZHMeterBranch34CurrentChangeRatioOnSideB | Branch 34 current change ratio on side B | B面分路34电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 34 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.93 | hwAcrelAMC16ZHMeterBranch35CurrentChangeRatioOnSideB | Branch 35 current change ratio on side B | B面分路35电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 35 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.94 | hwAcrelAMC16ZHMeterBranch36CurrentChangeRatioOnSideB | Branch 36 current change ratio on side B | B面分路36电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 36 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.95 | hwAcrelAMC16ZHMeterBranch37CurrentChangeRatioOnSideB | Branch 37 current change ratio on side B | B面分路37电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 37 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.96 | hwAcrelAMC16ZHMeterBranch38CurrentChangeRatioOnSideB | Branch 38 current change ratio on side B | B面分路38电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 38 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.97 | hwAcrelAMC16ZHMeterBranch39CurrentChangeRatioOnSideB | Branch 39 current change ratio on side B | B面分路39电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 39 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.98 | hwAcrelAMC16ZHMeterBranch40CurrentChangeRatioOnSideB | Branch 40 current change ratio on side B | B面分路40电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 40 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.99 | hwAcrelAMC16ZHMeterBranch41CurrentChangeRatioOnSideB | Branch 41 current change ratio on side B | B面分路41电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 41 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.100 | hwAcrelAMC16ZHMeterBranch42CurrentChangeRatioOnSideB | Branch 42 current change ratio on side B | B面分路42电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 42 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.101 | hwAcrelAMC16ZHMeterBranch43CurrentChangeRatioOnSideB | Branch 43 current change ratio on side B | B面分路43电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 43 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.102 | hwAcrelAMC16ZHMeterBranch44CurrentChangeRatioOnSideB | Branch 44 current change ratio on side B | B面分路44电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 44 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.103 | hwAcrelAMC16ZHMeterBranch45CurrentChangeRatioOnSideB | Branch 45 current change ratio on side B | B面分路45电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 45 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.104 | hwAcrelAMC16ZHMeterBranch46CurrentChangeRatioOnSideB | Branch 46 current change ratio on side B | B面分路46电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 46 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.105 | hwAcrelAMC16ZHMeterBranch47CurrentChangeRatioOnSideB | Branch 47 current change ratio on side B | B面分路47电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 47 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.106 | hwAcrelAMC16ZHMeterBranch48CurrentChangeRatioOnSideB | Branch 48 current change ratio on side B | B面分路48电流变比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch 48 current change ratio on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.107 | hwAcrelAMC16ZHMeterInsulation1PositiveToGroundResOnSideB | Insulation 1 positive-to-ground resistance on side B | B面绝缘1正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 1 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.108 | hwAcrelAMC16ZHMeterInsulation2PositiveToGroundResOnSideB | Insulation 2 positive-to-ground resistance on side B | B面绝缘2正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 2 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.109 | hwAcrelAMC16ZHMeterInsulation3PositiveToGroundResOnSideB | Insulation 3 positive-to-ground resistance on side B | B面绝缘3正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 3 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.110 | hwAcrelAMC16ZHMeterInsulation4PositiveToGroundResOnSideB | Insulation 4 positive-to-ground resistance on side B | B面绝缘4正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 4 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.111 | hwAcrelAMC16ZHMeterInsulation5PositiveToGroundResOnSideB | Insulation 5 positive-to-ground resistance on side B | B面绝缘5正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 5 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.112 | hwAcrelAMC16ZHMeterInsulation6PositiveToGroundResOnSideB | Insulation 6 positive-to-ground resistance on side B | B面绝缘6正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 6 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.113 | hwAcrelAMC16ZHMeterInsulation7PositiveToGroundResOnSideB | Insulation 7 positive-to-ground resistance on side B | B面绝缘7正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 7 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.114 | hwAcrelAMC16ZHMeterInsulation8PositiveToGroundResOnSideB | Insulation 8 positive-to-ground resistance on side B | B面绝缘8正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 8 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.115 | hwAcrelAMC16ZHMeterInsulation9PositiveToGroundResOnSideB | Insulation 9 positive-to-ground resistance on side B | B面绝缘9正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 9 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.116 | hwAcrelAMC16ZHMeterInsulation10PositiveToGroundResOnSideB | Insulation 10 positive-to-ground resistance on side B | B面绝缘10正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 10 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.117 | hwAcrelAMC16ZHMeterInsulation11PositiveToGroundResOnSideB | Insulation 11 positive-to-ground resistance on side B | B面绝缘11正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 11 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.118 | hwAcrelAMC16ZHMeterInsulation12PositiveToGroundResOnSideB | Insulation 12 positive-to-ground resistance on side B | B面绝缘12正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 12 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.119 | hwAcrelAMC16ZHMeterInsulation13PositiveToGroundResOnSideB | Insulation 13 positive-to-ground resistance on side B | B面绝缘13正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 13 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.120 | hwAcrelAMC16ZHMeterInsulation14PositiveToGroundResOnSideB | Insulation 14 positive-to-ground resistance on side B | B面绝缘14正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 14 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.121 | hwAcrelAMC16ZHMeterInsulation15PositiveToGroundResOnSideB | Insulation 15 positive-to-ground resistance on side B | B面绝缘15正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 15 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.122 | hwAcrelAMC16ZHMeterInsulation16PositiveToGroundResOnSideB | Insulation 16 positive-to-ground resistance on side B | B面绝缘16正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 16 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.123 | hwAcrelAMC16ZHMeterInsulation17PositiveToGroundResOnSideB | Insulation 17 positive-to-ground resistance on side B | B面绝缘17正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 17 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.124 | hwAcrelAMC16ZHMeterInsulation18PositiveToGroundResOnSideB | Insulation 18 positive-to-ground resistance on side B | B面绝缘18正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 18 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.125 | hwAcrelAMC16ZHMeterInsulation19PositiveToGroundResOnSideB | Insulation 19 positive-to-ground resistance on side B | B面绝缘19正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 19 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.126 | hwAcrelAMC16ZHMeterInsulation20PositiveToGroundResOnSideB | Insulation 20 positive-to-ground resistance on side B | B面绝缘20正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 20 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.127 | hwAcrelAMC16ZHMeterInsulation21PositiveToGroundResOnSideB | Insulation 21 positive-to-ground resistance on side B | B面绝缘21正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 21 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.128 | hwAcrelAMC16ZHMeterInsulation22PositiveToGroundResOnSideB | Insulation 22 positive-to-ground resistance on side B | B面绝缘22正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 22 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.128 | hwAcrelAMC16ZHMeterInsulation23PositiveToGroundResOnSideB | Insulation 23 positive-to-ground resistance on side B | B面绝缘23正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 23 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.130 | hwAcrelAMC16ZHMeterInsulation24PositiveToGroundResOnSideB | Insulation 24 positive-to-ground resistance on side B | B面绝缘24正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 24 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.131 | hwAcrelAMC16ZHMeterInsulation25PositiveToGroundResOnSideB | Insulation 25 positive-to-ground resistance on side B | B面绝缘25正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 25 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.132 | hwAcrelAMC16ZHMeterInsulation26PositiveToGroundResOnSideB | Insulation 26 positive-to-ground resistance on side B | B面绝缘26正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 26 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.133 | hwAcrelAMC16ZHMeterInsulation27PositiveToGroundResOnSideB | Insulation 27 positive-to-ground resistance on side B | B面绝缘27正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 27 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.134 | hwAcrelAMC16ZHMeterInsulation28PositiveToGroundResOnSideB | Insulation 28 positive-to-ground resistance on side B | B面绝缘28正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 28 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.135 | hwAcrelAMC16ZHMeterInsulation29PositiveToGroundResOnSideB | Insulation 29 positive-to-ground resistance on side B | B面绝缘29正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 29 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.136 | hwAcrelAMC16ZHMeterInsulation30PositiveToGroundResOnSideB | Insulation 30 positive-to-ground resistance on side B | B面绝缘30正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 30 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.137 | hwAcrelAMC16ZHMeterInsulation31PositiveToGroundResOnSideB | Insulation 31 positive-to-ground resistance on side B | B面绝缘31正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 31 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.138 | hwAcrelAMC16ZHMeterInsulation32PositiveToGroundResOnSideB | Insulation 32 positive-to-ground resistance on side B | B面绝缘32正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 32 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.139 | hwAcrelAMC16ZHMeterInsulation33PositiveToGroundResOnSideB | Insulation 33 positive-to-ground resistance on side B | B面绝缘33正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 33 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.140 | hwAcrelAMC16ZHMeterInsulation34PositiveToGroundResOnSideB | Insulation 34 positive-to-ground resistance on side B | B面绝缘34正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 34 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.141 | hwAcrelAMC16ZHMeterInsulation35PositiveToGroundResOnSideB | Insulation 35 positive-to-ground resistance on side B | B面绝缘35正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 35 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.142 | hwAcrelAMC16ZHMeterInsulation36PositiveToGroundResOnSideB | Insulation 36 positive-to-ground resistance on side B | B面绝缘36正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 36 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.143 | hwAcrelAMC16ZHMeterInsulation37PositiveToGroundResOnSideB | Insulation 37 positive-to-ground resistance on side B | B面绝缘37正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 37 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.144 | hwAcrelAMC16ZHMeterInsulation38PositiveToGroundResOnSideB | Insulation 38 positive-to-ground resistance on side B | B面绝缘38正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 38 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.145 | hwAcrelAMC16ZHMeterInsulation39PositiveToGroundResOnSideB | Insulation 39 positive-to-ground resistance on side B | B面绝缘39正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 39 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.146 | hwAcrelAMC16ZHMeterInsulation40PositiveToGroundResOnSideB | Insulation 40 positive-to-ground resistance on side B | B面绝缘40正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 40 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.147 | hwAcrelAMC16ZHMeterInsulation41PositiveToGroundResOnSideB | Insulation 41 positive-to-ground resistance on side B | B面绝缘41正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 41 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.148 | hwAcrelAMC16ZHMeterInsulation42PositiveToGroundResOnSideB | Insulation 42 positive-to-ground resistance on side B | B面绝缘42正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 42 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.149 | hwAcrelAMC16ZHMeterInsulation43PositiveToGroundResOnSideB | Insulation 43 positive-to-ground resistance on side B | B面绝缘43正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 43 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.150 | hwAcrelAMC16ZHMeterInsulation44PositiveToGroundResOnSideB | Insulation 44 positive-to-ground resistance on side B | B面绝缘44正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 44 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.151 | hwAcrelAMC16ZHMeterInsulation45PositiveToGroundResOnSideB | Insulation 45 positive-to-ground resistance on side B | B面绝缘45正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 45 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.152 | hwAcrelAMC16ZHMeterInsulation46PositiveToGroundResOnSideB | Insulation 46 positive-to-ground resistance on side B | B面绝缘46正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 46 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.153 | hwAcrelAMC16ZHMeterInsulation47PositiveToGroundResOnSideB | Insulation 47 positive-to-ground resistance on side B | B面绝缘47正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 47 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.154 | hwAcrelAMC16ZHMeterInsulation48PositiveToGroundResOnSideB | Insulation 48 positive-to-ground resistance on side B | B面绝缘48正对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 48 positive-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.155 | hwAcrelAMC16ZHMeterInsulation1NegToGroundResOnSideB | Insulation 1 negative-to-ground resistance on side B | B面绝缘1负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 1 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.156 | hwAcrelAMC16ZHMeterInsulation2NegToGroundResOnSideB | Insulation 2 negative-to-ground resistance on side B | B面绝缘2负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 2 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.157 | hwAcrelAMC16ZHMeterInsulation3NegToGroundResOnSideB | Insulation 3 negative-to-ground resistance on side B | B面绝缘3负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 3 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.158 | hwAcrelAMC16ZHMeterInsulation4NegToGroundResOnSideB | Insulation 4 negative-to-ground resistance on side B | B面绝缘4负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 4 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.159 | hwAcrelAMC16ZHMeterInsulation5NegToGroundResOnSideB | Insulation 5 negative-to-ground resistance on side B | B面绝缘5负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 5 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.160 | hwAcrelAMC16ZHMeterInsulation6NegToGroundResOnSideB | Insulation 6 negative-to-ground resistance on side B | B面绝缘6负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 6 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.161 | hwAcrelAMC16ZHMeterInsulation7NegToGroundResOnSideB | Insulation 7 negative-to-ground resistance on side B | B面绝缘7负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 7 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.162 | hwAcrelAMC16ZHMeterInsulation8NegToGroundResOnSideB | Insulation 8 negative-to-ground resistance on side B | B面绝缘8负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 8 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.163 | hwAcrelAMC16ZHMeterInsulation9NegToGroundResOnSideB | Insulation 9 negative-to-ground resistance on side B | B面绝缘9负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 9 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.164 | hwAcrelAMC16ZHMeterInsulation10NegToGroundResOnSideB | Insulation 10 negative-to-ground resistance on side B | B面绝缘10负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 10 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.165 | hwAcrelAMC16ZHMeterInsulation11NegToGroundResOnSideB | Insulation 11 negative-to-ground resistance on side B | B面绝缘11负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 11 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.166 | hwAcrelAMC16ZHMeterInsulation12NegToGroundResOnSideB | Insulation 12 negative-to-ground resistance on side B | B面绝缘12负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 12 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.167 | hwAcrelAMC16ZHMeterInsulation13NegToGroundResOnSideB | Insulation 13 negative-to-ground resistance on side B | B面绝缘13负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 13 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.168 | hwAcrelAMC16ZHMeterInsulation14NegToGroundResOnSideB | Insulation 14 negative-to-ground resistance on side B | B面绝缘14负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 14 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.169 | hwAcrelAMC16ZHMeterInsulation15NegToGroundResOnSideB | Insulation 15 negative-to-ground resistance on side B | B面绝缘15负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 15 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.170 | hwAcrelAMC16ZHMeterInsulation16NegToGroundResOnSideB | Insulation 16 negative-to-ground resistance on side B | B面绝缘16负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 16 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.171 | hwAcrelAMC16ZHMeterInsulation17NegToGroundResOnSideB | Insulation 17 negative-to-ground resistance on side B | B面绝缘17负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 17 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.172 | hwAcrelAMC16ZHMeterInsulation18NegToGroundResOnSideB | Insulation 18 negative-to-ground resistance on side B | B面绝缘18负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 18 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.173 | hwAcrelAMC16ZHMeterInsulation19NegToGroundResOnSideB | Insulation 19 negative-to-ground resistance on side B | B面绝缘19负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 19 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.174 | hwAcrelAMC16ZHMeterInsulation20NegToGroundResOnSideB | Insulation 20 negative-to-ground resistance on side B | B面绝缘20负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 20 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.175 | hwAcrelAMC16ZHMeterInsulation21NegToGroundResOnSideB | Insulation 21 negative-to-ground resistance on side B | B面绝缘21负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 21 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.176 | hwAcrelAMC16ZHMeterInsulation22NegToGroundResOnSideB | Insulation 22 negative-to-ground resistance on side B | B面绝缘22负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 22 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.177 | hwAcrelAMC16ZHMeterInsulation23NegToGroundResOnSideB | Insulation 23 negative-to-ground resistance on side B | B面绝缘23负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 23 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.178 | hwAcrelAMC16ZHMeterInsulation24NegToGroundResOnSideB | Insulation 24 negative-to-ground resistance on side B | B面绝缘24负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 24 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.179 | hwAcrelAMC16ZHMeterInsulation25NegToGroundResOnSideB | Insulation 25 negative-to-ground resistance on side B | B面绝缘25负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 25 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.180 | hwAcrelAMC16ZHMeterInsulation26NegToGroundResOnSideB | Insulation 26 negative-to-ground resistance on side B | B面绝缘26负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 26 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.181 | hwAcrelAMC16ZHMeterInsulation27NegToGroundResOnSideB | Insulation 27 negative-to-ground resistance on side B | B面绝缘27负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 27 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.182 | hwAcrelAMC16ZHMeterInsulation28NegToGroundResOnSideB | Insulation 28 negative-to-ground resistance on side B | B面绝缘28负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 28 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.183 | hwAcrelAMC16ZHMeterInsulation29NegToGroundResOnSideB | Insulation 29 negative-to-ground resistance on side B | B面绝缘29负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 29 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.184 | hwAcrelAMC16ZHMeterInsulation30NegToGroundResOnSideB | Insulation 30 negative-to-ground resistance on side B | B面绝缘30负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 30 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.185 | hwAcrelAMC16ZHMeterInsulation31NegToGroundResOnSideB | Insulation 31 negative-to-ground resistance on side B | B面绝缘31负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 31 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.186 | hwAcrelAMC16ZHMeterInsulation32NegToGroundResOnSideB | Insulation 32 negative-to-ground resistance on side B | B面绝缘32负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 32 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.187 | hwAcrelAMC16ZHMeterInsulation33NegToGroundResOnSideB | Insulation 33 negative-to-ground resistance on side B | B面绝缘33负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 33 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.188 | hwAcrelAMC16ZHMeterInsulation34NegToGroundResOnSideB | Insulation 34 negative-to-ground resistance on side B | B面绝缘34负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 34 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.189 | hwAcrelAMC16ZHMeterInsulation35NegToGroundResOnSideB | Insulation 35 negative-to-ground resistance on side B | B面绝缘35负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 35 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.190 | hwAcrelAMC16ZHMeterInsulation36NegToGroundResOnSideB | Insulation 36 negative-to-ground resistance on side B | B面绝缘36负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 36 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.191 | hwAcrelAMC16ZHMeterInsulation37NegToGroundResOnSideB | Insulation 37 negative-to-ground resistance on side B | B面绝缘37负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 37 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.192 | hwAcrelAMC16ZHMeterInsulation38NegToGroundResOnSideB | Insulation 38 negative-to-ground resistance on side B | B面绝缘38负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 38 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.193 | hwAcrelAMC16ZHMeterInsulation39NegToGroundResOnSideB | Insulation 39 negative-to-ground resistance on side B | B面绝缘39负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 39 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.194 | hwAcrelAMC16ZHMeterInsulation40NegToGroundResOnSideB | Insulation 40 negative-to-ground resistance on side B | B面绝缘40负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 40 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.195 | hwAcrelAMC16ZHMeterInsulation41NegToGroundResOnSideB | Insulation 41 negative-to-ground resistance on side B | B面绝缘41负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 41 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.196 | hwAcrelAMC16ZHMeterInsulation42NegToGroundResOnSideB | Insulation 42 negative-to-ground resistance on side B | B面绝缘42负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 42 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.197 | hwAcrelAMC16ZHMeterInsulation43NegToGroundResOnSideB | Insulation 43 negative-to-ground resistance on side B | B面绝缘43负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 43 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.198 | hwAcrelAMC16ZHMeterInsulation44NegToGroundResOnSideB | Insulation 44 negative-to-ground resistance on side B | B面绝缘44负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 44 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.199 | hwAcrelAMC16ZHMeterInsulation45NegToGroundResOnSideB | Insulation 45 negative-to-ground resistance on side B | B面绝缘45负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 45 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.200 | hwAcrelAMC16ZHMeterInsulation46NegToGroundResOnSideB | Insulation 46 negative-to-ground resistance on side B | B面绝缘46负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 46 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.201 | hwAcrelAMC16ZHMeterInsulation47NegToGroundResOnSideB | Insulation 47 negative-to-ground resistance on side B | B面绝缘47负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 47 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.202 | hwAcrelAMC16ZHMeterInsulation48NegToGroundResOnSideB | Insulation 48 negative-to-ground resistance on side B | B面绝缘48负对地电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Insulation 48 negative-to-ground resistance on side B of the device config table for the Acrel AMC16ZH Meter.Multiple:10.SigUnitInfo:thousand ohms.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.203 | hwAcrelAMC16ZHMeterCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the Acrel AMC16ZH Meter. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.204 | hwAcrelAMC16ZHMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.205 | hwAcrelAMC16ZHMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.3.1.300 | hwAcrelAMC16ZHMeterRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.4 | hwAcrelAMC16ZHMeterConfig4Table | / | / |  |  | / | / | The config table of Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.4.1.1 | hwAcrelAMC16ZHMeterConfig4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.4.1.2 | hwAcrelAMC16ZHMeterDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.4.1.3 | hwAcrelAMC16ZHMeterNumberOfBranches | Number of branches | 支路个数 | 1-Read_Write | 读写 | 1..48 | 1..48 | Number of branches of the device config table for the Acrel AMC16ZH Meter.
1.3.6.1.4.1.2011.6.178.1.1.128.4.1.300 | hwAcrelAMC16ZHMeterConfig4Status | / | / | 2-Read_Create | 读构建 | / | / | The row status of Acrel AMC16ZH Meter.

## AC_PDC_MA01C
MA01C交流配电柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.86 | ACPDCMA01C | AC_PDC_MA01C | MA01C交流配电柜 | / | / | / | / | AC_PDC_MA01C Equipment.
1.3.6.1.4.1.2011.6.178.1.1.86.1 | hwACPDCMA01CRunning1Table | / | / |  |  | / | / | The running table of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.1 | hwACPDCMA01CRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.2 | hwACPDCMA01CCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the AC_PDC_MA01C. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.3 | hwACPDCMA01CInputCableForRouteASpdStatus | Input cable for route A - SPD status | A路进线-防雷器状态 | 0-Read_Only | 只读 | normal(1), alarm(2), notenabled(3), unknown(255) | [正常=1]/[告警=2]/[未启用=3] | Input cable for route A - SPD status of the device config table for the AC_PDC_MA01C. Value 1 indicate normal Value 2 indicate alarm Value 3 indicate not enabled
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.4 | hwACPDCMA01CInputCableForRouteAVoltageLineFrequency | Input cable for route A - voltage line frequency | A路进线-电压线频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - voltage line frequency of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.5 | hwACPDCMA01CInputCableForRouteAPhaseAVoltage | Input cable for route A - phase A voltage | A路进线-A相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase A voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.6 | hwACPDCMA01CInputCableForRouteAPhaseBVoltage | Input cable for route A - phase B voltage | A路进线-B相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase B voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.7 | hwACPDCMA01CInputCableForRouteAPhaseCVoltage | Input cable for route A - phase C voltage | A路进线-C相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase C voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.8 | hwACPDCMA01CInputCableForRouteAPhaseABVoltage | Input cable for route A - phase A-B voltage | A路进线-AB线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase A-B voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.9 | hwACPDCMA01CInputCableForRouteAPhaseBCVoltage | Input cable for route A - phase B-C voltage | A路进线-BC线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase B-C voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.10 | hwACPDCMA01CInputCableForRouteAPhaseCAVoltage | Input cable for route A - phase C-A voltage | A路进线-CA线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase C-A voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.11 | hwACPDCMA01CInputCableForRouteAPhaseACurrent | Input cable for route A - phase A current | A路进线-A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase A current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.12 | hwACPDCMA01CInputCableForRouteAPhaseBCurrent | Input cable for route A - phase B current | A路进线-B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase B current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.13 | hwACPDCMA01CInputCableForRouteAPhaseCCurrent | Input cable for route A - phase C current | A路进线-C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase C current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.14 | hwACPDCMA01CInputCableForRouteAPhaseAActivePower | Input cable for route A - phase A active power | A路进线-A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase A active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.15 | hwACPDCMA01CInputCableForRouteAPhaseBActivePower | Input cable for route A - phase B active power | A路进线-B相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase B active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.16 | hwACPDCMA01CInputCableForRouteAPhaseCActivePower | Input cable for route A - phase C active power | A路进线-C相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase C active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.17 | hwACPDCMA01CInputCableForRouteACombinedPhaseActivePower | Input cable for route A - combined phase active power | A路进线-合相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - combined phase active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.18 | hwACPDCMA01CInputCableForRouteAPhaseAActiveEnergy | Input cable for route A - phase A active energy | A路进线-A相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase A active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.19 | hwACPDCMA01CInputCableForRouteAPhaseBActiveEnergy | Input cable for route A - phase B active energy | A路进线-B相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase B active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.20 | hwACPDCMA01CInputCableForRouteAPhaseCActiveEnergy | Input cable for route A - phase C active energy | A路进线-C相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - phase C active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.21 | hwACPDCMA01CInputCableForRouteACombinedPhaseActiveEnergy | Input cable for route A - combined phase active energy | A路进线-合相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route A - combined phase active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.22 | hwACPDCMA01CInputCableForRouteBVoltageLineFrequency | Input cable for route B - voltage line frequency | B路进线-电压线频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - voltage line frequency of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.23 | hwACPDCMA01CInputCableForRouteBPhaseAVoltage | Input cable for route B - phase A voltage | B路进线-A相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase A voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.24 | hwACPDCMA01CInputCableForRouteBPhaseBVoltage | Input cable for route B - phase B voltage | B路进线-B相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase B voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.25 | hwACPDCMA01CInputCableForRouteBPhaseCVoltage | Input cable for route B - phase C voltage | B路进线-C相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase C voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.26 | hwACPDCMA01CInputCableForRouteBPhaseABVoltage | Input cable for route B - phase A-B voltage | B路进线-AB线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase A-B voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.27 | hwACPDCMA01CInputCableForRouteBPhaseBCVoltage | Input cable for route B - phase B-C voltage | B路进线-BC线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase B-C voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.28 | hwACPDCMA01CInputCableForRouteBPhaseCAVoltage | Input cable for route B - phase C-A voltage | B路进线-CA线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase C-A voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.29 | hwACPDCMA01CInputCableForRouteBPhaseACurrent | Input cable for route B - phase A current | B路进线-A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase A current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.30 | hwACPDCMA01CInputCableForRouteBPhaseBCurrent | Input cable for route B - phase B current | B路进线-B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase B current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.31 | hwACPDCMA01CInputCableForRouteBPhaseCCurrent | Input cable for route B - phase C current | B路进线-C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase C current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.32 | hwACPDCMA01CInputCableForRouteBPhaseAActivePower | Input cable for route B - phase A active power | B路进线-A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase A active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.33 | hwACPDCMA01CInputCableForRouteBPhaseBActivePower | Input cable for route B - phase B active power | B路进线-B相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase B active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.34 | hwACPDCMA01CInputCableForRouteBPhaseCActivePower | Input cable for route B - phase C active power | B路进线-C相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase C active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.35 | hwACPDCMA01CInputCableForRouteBCombinedPhaseActivePower | Input cable for route B - combined phase active power | B路进线-合相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - combined phase active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.36 | hwACPDCMA01CInputCableForRouteBPhaseAActiveEnergy | Input cable for route B - phase A active energy | B路进线-A相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase A active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.37 | hwACPDCMA01CInputCableForRouteBPhaseBActiveEnergy | Input cable for route B - phase B active energy | B路进线-B相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase B active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.38 | hwACPDCMA01CInputCableForRouteBPhaseCActiveEnergy | Input cable for route B - phase C active energy | B路进线-C相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - phase C active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.39 | hwACPDCMA01CInputCableForRouteBCombinedPhaseActiveEnergy | Input cable for route B - combined phase active energy | B路进线-合相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable for route B - combined phase active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.40 | hwACPDCMA01CA01Voltage | A01 Voltage | A01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A01 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.41 | hwACPDCMA01CA02Voltage | A02 Voltage | A02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A02 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.42 | hwACPDCMA01CA03Voltage | A03 Voltage | A03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A03 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.43 | hwACPDCMA01CA01Current | A01 Current | A01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A01 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.44 | hwACPDCMA01CA02Current | A02 Current | A02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A02 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.45 | hwACPDCMA01CA03Current | A03 Current | A03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A03 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.46 | hwACPDCMA01CA01ActivePower | A01 Active power | A01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A01 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.47 | hwACPDCMA01CA02ActivePower | A02 Active power | A02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A02 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.48 | hwACPDCMA01CA03ActivePower | A03 Active power | A03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A03 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.49 | hwACPDCMA01CA01ActiveElectricEnergy | A01 Active electric energy | A01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A01 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.50 | hwACPDCMA01CA02ActiveElectricEnergy | A02 Active electric energy | A02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A02 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.51 | hwACPDCMA01CA03ActiveElectricEnergy | A03 Active electric energy | A03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A03 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.52 | hwACPDCMA01CA04Voltage | A04 Voltage | A04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A04 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.53 | hwACPDCMA01CA05Voltage | A05 Voltage | A05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A05 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.54 | hwACPDCMA01CA06Voltage | A06 Voltage | A06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A06 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.55 | hwACPDCMA01CA04Current | A04 Current | A04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A04 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.56 | hwACPDCMA01CA05Current | A05 Current | A05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A05 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.57 | hwACPDCMA01CA06Current | A06 Current | A06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A06 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.58 | hwACPDCMA01CA04ActivePower | A04 Active power | A04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A04 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.59 | hwACPDCMA01CA05ActivePower | A05 Active power | A05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A05 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.60 | hwACPDCMA01CA06ActivePower | A06 Active power | A06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A06 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.61 | hwACPDCMA01CA04ActiveElectricEnergy | A04 Active electric energy | A04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A04 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.62 | hwACPDCMA01CA05ActiveElectricEnergy | A05 Active electric energy | A05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A05 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.63 | hwACPDCMA01CA06ActiveElectricEnergy | A06 Active electric energy | A06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A06 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.64 | hwACPDCMA01CA07Voltage | A07 Voltage | A07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A07 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.65 | hwACPDCMA01CA08Voltage | A08 Voltage | A08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A08 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.66 | hwACPDCMA01CA09Voltage | A09 Voltage | A09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A09 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.67 | hwACPDCMA01CA07Current | A07 Current | A07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A07 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.68 | hwACPDCMA01CA08Current | A08 Current | A08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A08 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.69 | hwACPDCMA01CA09Current | A09 Current | A09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A09 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.70 | hwACPDCMA01CA07ActivePower | A07 Active power | A07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A07 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.71 | hwACPDCMA01CA08ActivePower | A08 Active power | A08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A08 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.72 | hwACPDCMA01CA09ActivePower | A09 Active power | A09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A09 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.73 | hwACPDCMA01CA07ActiveElectricEnergy | A07 Active electric energy | A07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A07 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.74 | hwACPDCMA01CA08ActiveElectricEnergy | A08 Active electric energy | A08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A08 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.75 | hwACPDCMA01CA09ActiveElectricEnergy | A09 Active electric energy | A09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A09 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.76 | hwACPDCMA01CA10Voltage | A10 Voltage | A10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A10 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.77 | hwACPDCMA01CA11Voltage | A11 Voltage | A11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A11 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.78 | hwACPDCMA01CA12Voltage | A12 Voltage | A12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A12 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.79 | hwACPDCMA01CA10Current | A10 Current | A10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A10 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.80 | hwACPDCMA01CA11Current | A11 Current | A11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A11 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.81 | hwACPDCMA01CA12Current | A12 Current | A12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A12 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.82 | hwACPDCMA01CA10ActivePower | A10 Active power | A10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A10 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.83 | hwACPDCMA01CA11ActivePower | A11 Active power | A11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A11 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.84 | hwACPDCMA01CA12ActivePower | A12 Active power | A12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A12 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.85 | hwACPDCMA01CA10ActiveElectricEnergy | A10 Active electric energy | A10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A10 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.86 | hwACPDCMA01CA11ActiveElectricEnergy | A11 Active electric energy | A11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A11 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.87 | hwACPDCMA01CA12ActiveElectricEnergy | A12 Active electric energy | A12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A12 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.88 | hwACPDCMA01CA13Voltage | A13 Voltage | A13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A13 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.89 | hwACPDCMA01CA14Voltage | A14 Voltage | A14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A14 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.90 | hwACPDCMA01CA15Voltage | A15 Voltage | A15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A15 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.91 | hwACPDCMA01CA13Current | A13 Current | A13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A13 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.92 | hwACPDCMA01CA14Current | A14 Current | A14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A14 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.93 | hwACPDCMA01CA15Current | A15 Current | A15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A15 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.94 | hwACPDCMA01CA13ActivePower | A13 Active power | A13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A13 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.95 | hwACPDCMA01CA14ActivePower | A14 Active power | A14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A14 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.96 | hwACPDCMA01CA15ActivePower | A15 Active power | A15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A15 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.97 | hwACPDCMA01CA13ActiveElectricEnergy | A13 Active electric energy | A13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A13 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.98 | hwACPDCMA01CA14ActiveElectricEnergy | A14 Active electric energy | A14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A14 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.99 | hwACPDCMA01CA15ActiveElectricEnergy | A15 Active electric energy | A15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A15 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.100 | hwACPDCMA01CA16Voltage | A16 Voltage | A16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A16 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.101 | hwACPDCMA01CA17Voltage | A17 Voltage | A17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A17 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.102 | hwACPDCMA01CA18Voltage | A18 Voltage | A18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A18 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.103 | hwACPDCMA01CA16Current | A16 Current | A16电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A16 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.104 | hwACPDCMA01CA17Current | A17 Current | A17电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A17 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.105 | hwACPDCMA01CA18Current | A18 Current | A18电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A18 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.106 | hwACPDCMA01CA16ActivePower | A16 Active power | A16有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A16 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.107 | hwACPDCMA01CA17ActivePower | A17 Active power | A17有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A17 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.108 | hwACPDCMA01CA18ActivePower | A18 Active power | A18有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A18 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.109 | hwACPDCMA01CA16ActiveElectricEnergy | A16 Active electric energy | A16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A16 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.110 | hwACPDCMA01CA17ActiveElectricEnergy | A17 Active electric energy | A17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A17 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.111 | hwACPDCMA01CA18ActiveElectricEnergy | A18 Active electric energy | A18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A18 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.112 | hwACPDCMA01CA19Voltage | A19 Voltage | A19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A19 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.113 | hwACPDCMA01CA19Current | A19 Current | A19电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A19 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.114 | hwACPDCMA01CA19ActivePower | A19 Active power | A19有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A19 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.115 | hwACPDCMA01CA19ActiveElectricEnergy | A19 Active electric energy | A19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A19 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.116 | hwACPDCMA01CA20Voltage | A20 Voltage | A20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A20 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.117 | hwACPDCMA01CA21Voltage | A21 Voltage | A21电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A21 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.118 | hwACPDCMA01CA20Current | A20 Current | A20电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A20 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.119 | hwACPDCMA01CA21Current | A21 Current | A21电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A21 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.120 | hwACPDCMA01CA20ActivePower | A20 Active power | A20有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A20 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.121 | hwACPDCMA01CA21ActivePower | A21 Active power | A21有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A21 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.122 | hwACPDCMA01CA20ActiveElectricEnergy | A20 Active electric energy | A20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A20 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.123 | hwACPDCMA01CA21ActiveElectricEnergy | A21 Active electric energy | A21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A21 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.124 | hwACPDCMA01CA22Voltage | A22 Voltage | A22电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A22 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.125 | hwACPDCMA01CA23Voltage | A23 Voltage | A23电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A23 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.126 | hwACPDCMA01CA24Voltage | A24 Voltage | A24电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A24 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.127 | hwACPDCMA01CA22Current | A22 Current | A22电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A22 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.128 | hwACPDCMA01CA23Current | A23 Current | A23电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A23 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.129 | hwACPDCMA01CA24Current | A24 Current | A24电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A24 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.130 | hwACPDCMA01CA22ActivePower | A22 Active power | A22有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A22 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.131 | hwACPDCMA01CA23ActivePower | A23 Active power | A23有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A23 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.132 | hwACPDCMA01CA24ActivePower | A24 Active power | A24有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A24 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.133 | hwACPDCMA01CA22ActiveElectricEnergy | A22 Active electric energy | A22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A22 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.134 | hwACPDCMA01CA23ActiveElectricEnergy | A23 Active electric energy | A23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A23 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.135 | hwACPDCMA01CA24ActiveElectricEnergy | A24 Active electric energy | A24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A24 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.136 | hwACPDCMA01CA25Voltage | A25 Voltage | A25电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A25 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.137 | hwACPDCMA01CA26Voltage | A26 Voltage | A26电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A26 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.138 | hwACPDCMA01CA27Voltage | A27 Voltage | A27电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A27 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.139 | hwACPDCMA01CA25Current | A25 Current | A25电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A25 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.140 | hwACPDCMA01CA26Current | A26 Current | A26电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A26 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.141 | hwACPDCMA01CA27Current | A27 Current | A27电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A27 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.142 | hwACPDCMA01CA25ActivePower | A25 Active power | A25有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A25 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.143 | hwACPDCMA01CA26ActivePower | A26 Active power | A26有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A26 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.144 | hwACPDCMA01CA27ActivePower | A27 Active power | A27有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A27 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.145 | hwACPDCMA01CA25ActiveElectricEnergy | A25 Active electric energy | A25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A25 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.146 | hwACPDCMA01CA26ActiveElectricEnergy | A26 Active electric energy | A26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A26 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.147 | hwACPDCMA01CA27ActiveElectricEnergy | A27 Active electric energy | A27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A27 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.148 | hwACPDCMA01CA28Voltage | A28 Voltage | A28电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A28 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.149 | hwACPDCMA01CA29Voltage | A29 Voltage | A29电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A29 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.150 | hwACPDCMA01CA28Current | A28 Current | A28电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A28 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.151 | hwACPDCMA01CA29Current | A29 Current | A29电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A29 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.152 | hwACPDCMA01CA28ActivePower | A28 Active power | A28有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A28 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.153 | hwACPDCMA01CA29ActivePower | A29 Active power | A29有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A29 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.154 | hwACPDCMA01CA28ActiveElectricEnergy | A28 Active electric energy | A28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A28 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.155 | hwACPDCMA01CA29ActiveElectricEnergy | A29 Active electric energy | A29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A29 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.156 | hwACPDCMA01CA30Voltage | A30 Voltage | A30电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A30 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.157 | hwACPDCMA01CA30Current | A30 Current | A30电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A30 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.158 | hwACPDCMA01CA30ActivePower | A30 Active power | A30有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A30 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.159 | hwACPDCMA01CA30ActiveElectricEnergy | A30 Active electric energy | A30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A30 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.160 | hwACPDCMA01CA31Voltage | A31 Voltage | A31电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A31 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.161 | hwACPDCMA01CA32Voltage | A32 Voltage | A32电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A32 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.162 | hwACPDCMA01CA33Voltage | A33 Voltage | A33电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A33 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.163 | hwACPDCMA01CA31Current | A31 Current | A31电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A31 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.164 | hwACPDCMA01CA32Current | A32 Current | A32电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A32 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.165 | hwACPDCMA01CA33Current | A33 Current | A33电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A33 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.166 | hwACPDCMA01CA31ActivePower | A31 Active power | A31有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A31 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.167 | hwACPDCMA01CA32ActivePower | A32 Active power | A32有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A32 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.168 | hwACPDCMA01CA33ActivePower | A33 Active power | A33有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A33 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.169 | hwACPDCMA01CA31ActiveElectricEnergy | A31 Active electric energy | A31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A31 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.170 | hwACPDCMA01CA32ActiveElectricEnergy | A32 Active electric energy | A32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A32 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.171 | hwACPDCMA01CA33ActiveElectricEnergy | A33 Active electric energy | A33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A33 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.172 | hwACPDCMA01CA34Voltage | A34 Voltage | A34电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A34 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.173 | hwACPDCMA01CA35Voltage | A35 Voltage | A35电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A35 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.174 | hwACPDCMA01CA36Voltage | A36 Voltage | A36电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A36 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.175 | hwACPDCMA01CA34Current | A34 Current | A34电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A34 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.176 | hwACPDCMA01CA35Current | A35 Current | A35电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A35 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.177 | hwACPDCMA01CA36Current | A36 Current | A36电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A36 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.178 | hwACPDCMA01CA34ActivePower | A34 Active power | A34有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A34 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.179 | hwACPDCMA01CA35ActivePower | A35 Active power | A35有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A35 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.180 | hwACPDCMA01CA36ActivePower | A36 Active power | A36有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A36 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.181 | hwACPDCMA01CA34ActiveElectricEnergy | A34 Active electric energy | A34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A34 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.182 | hwACPDCMA01CA35ActiveElectricEnergy | A35 Active electric energy | A35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A35 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.183 | hwACPDCMA01CA36ActiveElectricEnergy | A36 Active electric energy | A36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A36 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.184 | hwACPDCMA01CA37Voltage | A37 Voltage | A37电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A37 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.185 | hwACPDCMA01CA38Voltage | A38 Voltage | A38电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A38 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.186 | hwACPDCMA01CA39Voltage | A39 Voltage | A39电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A39 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.187 | hwACPDCMA01CA37Current | A37 Current | A37电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A37 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.188 | hwACPDCMA01CA38Current | A38 Current | A38电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A38 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.189 | hwACPDCMA01CA39Current | A39 Current | A39电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A39 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.190 | hwACPDCMA01CA37ActivePower | A37 Active power | A37有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A37 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.191 | hwACPDCMA01CA38ActivePower | A38 Active power | A38有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A38 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.192 | hwACPDCMA01CA39ActivePower | A39 Active power | A39有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A39 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.193 | hwACPDCMA01CA37ActiveElectricEnergy | A37 Active electric energy | A37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A37 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.194 | hwACPDCMA01CA38ActiveElectricEnergy | A38 Active electric energy | A38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A38 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.195 | hwACPDCMA01CA39ActiveElectricEnergy | A39 Active electric energy | A39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A39 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.196 | hwACPDCMA01CA40Voltage | A40 Voltage | A40电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A40 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.197 | hwACPDCMA01CA41Voltage | A41 Voltage | A41电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A41 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.198 | hwACPDCMA01CA42Voltage | A42 Voltage | A42电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A42 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.199 | hwACPDCMA01CA40Current | A40 Current | A40电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A40 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.200 | hwACPDCMA01CA41Current | A41 Current | A41电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A41 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.1.1.201 | hwACPDCMA01CRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.2 | hwACPDCMA01CRunning2Table | / | / |  |  | / | / | The running table of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.1 | hwACPDCMA01CRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.2 | hwACPDCMA01CA42Current | A42 Current | A42电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A42 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.3 | hwACPDCMA01CA40ActivePower | A40 Active power | A40有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A40 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.4 | hwACPDCMA01CA41ActivePower | A41 Active power | A41有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A41 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.5 | hwACPDCMA01CA42ActivePower | A42 Active power | A42有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A42 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.6 | hwACPDCMA01CA40ActiveElectricEnergy | A40 Active electric energy | A40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A40 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.7 | hwACPDCMA01CA41ActiveElectricEnergy | A41 Active electric energy | A41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A41 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.8 | hwACPDCMA01CA42ActiveElectricEnergy | A42 Active electric energy | A42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A42 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.9 | hwACPDCMA01CA43Voltage | A43 Voltage | A43电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A43 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.10 | hwACPDCMA01CA44Voltage | A44 Voltage | A44电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A44 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.11 | hwACPDCMA01CA45Voltage | A45 Voltage | A45电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A45 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.12 | hwACPDCMA01CA43Current | A43 Current | A43电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A43 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.13 | hwACPDCMA01CA44Current | A44 Current | A44电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A44 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.14 | hwACPDCMA01CA45Current | A45 Current | A45电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A45 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.15 | hwACPDCMA01CA43ActivePower | A43 Active power | A43有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A43 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.16 | hwACPDCMA01CA44ActivePower | A44 Active power | A44有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A44 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.17 | hwACPDCMA01CA45ActivePower | A45 Active power | A45有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A45 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.18 | hwACPDCMA01CA43ActiveElectricEnergy | A43 Active electric energy | A43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A43 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.19 | hwACPDCMA01CA44ActiveElectricEnergy | A44 Active electric energy | A44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A44 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.20 | hwACPDCMA01CA45ActiveElectricEnergy | A45 Active electric energy | A45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A45 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.21 | hwACPDCMA01CA46Voltage | A46 Voltage | A46电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A46 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.22 | hwACPDCMA01CA47Voltage | A47 Voltage | A47电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A47 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.23 | hwACPDCMA01CA48Voltage | A48 Voltage | A48电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A48 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.24 | hwACPDCMA01CA46Current | A46 Current | A46电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A46 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.25 | hwACPDCMA01CA47Current | A47 Current | A47电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A47 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.26 | hwACPDCMA01CA48Current | A48 Current | A48电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A48 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.27 | hwACPDCMA01CA46ActivePower | A46 Active power | A46有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A46 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.28 | hwACPDCMA01CA47ActivePower | A47 Active power | A47有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A47 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.29 | hwACPDCMA01CA48ActivePower | A48 Active power | A48有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A48 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.30 | hwACPDCMA01CA46ActiveElectricEnergy | A46 Active electric energy | A46有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A46 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.31 | hwACPDCMA01CA47ActiveElectricEnergy | A47 Active electric energy | A47有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A47 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.32 | hwACPDCMA01CA48ActiveElectricEnergy | A48 Active electric energy | A48有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A48 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.33 | hwACPDCMA01CB01Voltage | B01 Voltage | B01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B01 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.34 | hwACPDCMA01CB02Voltage | B02 Voltage | B02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B02 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.35 | hwACPDCMA01CB03Voltage | B03 Voltage | B03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B03 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.36 | hwACPDCMA01CB01Current | B01 Current | B01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B01 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.37 | hwACPDCMA01CB02Current | B02 Current | B02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B02 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.38 | hwACPDCMA01CB03Current | B03 Current | B03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B03 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.39 | hwACPDCMA01CB01ActivePower | B01 Active power | B01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B01 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.40 | hwACPDCMA01CB02ActivePower | B02 Active power | B02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B02 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.41 | hwACPDCMA01CB03ActivePower | B03 Active power | B03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B03 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.42 | hwACPDCMA01CB01ActiveElectricEnergy | B01 Active electric energy | B01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B01 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.43 | hwACPDCMA01CB02ActiveElectricEnergy | B02 Active electric energy | B02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B02 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.44 | hwACPDCMA01CB03ActiveElectricEnergy | B03 Active electric energy | B03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B03 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.45 | hwACPDCMA01CB04Voltage | B04 Voltage | B04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B04 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.46 | hwACPDCMA01CB05Voltage | B05 Voltage | B05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B05 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.47 | hwACPDCMA01CB06Voltage | B06 Voltage | B06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B06 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.48 | hwACPDCMA01CB04Current | B04 Current | B04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B04 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.49 | hwACPDCMA01CB05Current | B05 Current | B05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B05 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.50 | hwACPDCMA01CB06Current | B06 Current | B06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B06 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.51 | hwACPDCMA01CB04ActivePower | B04 Active power | B04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B04 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.52 | hwACPDCMA01CB05ActivePower | B05 Active power | B05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B05 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.53 | hwACPDCMA01CB06ActivePower | B06 Active power | B06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B06 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.54 | hwACPDCMA01CB04ActiveElectricEnergy | B04 Active electric energy | B04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B04 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.55 | hwACPDCMA01CB05ActiveElectricEnergy | B05 Active electric energy | B05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B05 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.56 | hwACPDCMA01CB06ActiveElectricEnergy | B06 Active electric energy | B06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B06 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.57 | hwACPDCMA01CB07Voltage | B07 Voltage | B07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B07 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.58 | hwACPDCMA01CB08Voltage | B08 Voltage | B08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B08 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.59 | hwACPDCMA01CB09Voltage | B09 Voltage | B09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B09 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.60 | hwACPDCMA01CB07Current | B07 Current | B07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B07 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.61 | hwACPDCMA01CB08Current | B08 Current | B08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B08 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.62 | hwACPDCMA01CB09Current | B09 Current | B09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B09 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.63 | hwACPDCMA01CB07ActivePower | B07 Active power | B07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B07 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.64 | hwACPDCMA01CB08ActivePower | B08 Active power | B08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B08 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.65 | hwACPDCMA01CB09ActivePower | B09 Active power | B09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B09 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.66 | hwACPDCMA01CB07ActiveElectricEnergy | B07 Active electric energy | B07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B07 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.67 | hwACPDCMA01CB08ActiveElectricEnergy | B08 Active electric energy | B08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B08 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.68 | hwACPDCMA01CB09ActiveElectricEnergy | B09 Active electric energy | B09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B09 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.69 | hwACPDCMA01CB10Voltage | B10 Voltage | B10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B10 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.70 | hwACPDCMA01CB11Voltage | B11 Voltage | B11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B11 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.71 | hwACPDCMA01CB12Voltage | B12 Voltage | B12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B12 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.72 | hwACPDCMA01CB10Current | B10 Current | B10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B10 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.73 | hwACPDCMA01CB11Current | B11 Current | B11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B11 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.74 | hwACPDCMA01CB12Current | B12 Current | B12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B12 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.75 | hwACPDCMA01CB10ActivePower | B10 Active power | B10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B10 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.76 | hwACPDCMA01CB11ActivePower | B11 Active power | B11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B11 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.77 | hwACPDCMA01CB12ActivePower | B12 Active power | B12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B12 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.78 | hwACPDCMA01CB10ActiveElectricEnergy | B10 Active electric energy | B10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B10 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.79 | hwACPDCMA01CB11ActiveElectricEnergy | B11 Active electric energy | B11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B11 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.80 | hwACPDCMA01CB12ActiveElectricEnergy | B12 Active electric energy | B12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B12 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.81 | hwACPDCMA01CB13Voltage | B13 Voltage | B13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B13 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.82 | hwACPDCMA01CB14Voltage | B14 Voltage | B14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B14 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.83 | hwACPDCMA01CB15Voltage | B15 Voltage | B15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B15 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.84 | hwACPDCMA01CB13Current | B13 Current | B13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B13 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.85 | hwACPDCMA01CB14Current | B14 Current | B14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B14 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.86 | hwACPDCMA01CB15Current | B15 Current | B15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B15 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.87 | hwACPDCMA01CB13ActivePower | B13 Active power | B13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B13 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.88 | hwACPDCMA01CB14ActivePower | B14 Active power | B14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B14 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.89 | hwACPDCMA01CB15ActivePower | B15 Active power | B15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B15 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.90 | hwACPDCMA01CB13ActiveElectricEnergy | B13 Active electric energy | B13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B13 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.91 | hwACPDCMA01CB14ActiveElectricEnergy | B14 Active electric energy | B14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B14 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.92 | hwACPDCMA01CB15ActiveElectricEnergy | B15 Active electric energy | B15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B15 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.93 | hwACPDCMA01CB16Voltage | B16 Voltage | B16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B16 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.94 | hwACPDCMA01CB17Voltage | B17 Voltage | B17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B17 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.95 | hwACPDCMA01CB18Voltage | B18 Voltage | B18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B18 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.96 | hwACPDCMA01CB16Current | B16 Current | B16电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B16 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.97 | hwACPDCMA01CB17Current | B17 Current | B17电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B17 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.98 | hwACPDCMA01CB18Current | B18 Current | B18电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B18 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.99 | hwACPDCMA01CB16ActivePower | B16 Active power | B16有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B16 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.100 | hwACPDCMA01CB17ActivePower | B17 Active power | B17有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B17 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.101 | hwACPDCMA01CB18ActivePower | B18 Active power | B18有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B18 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.102 | hwACPDCMA01CB16ActiveElectricEnergy | B16 Active electric energy | B16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B16 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.103 | hwACPDCMA01CB17ActiveElectricEnergy | B17 Active electric energy | B17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B17 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.104 | hwACPDCMA01CB18ActiveElectricEnergy | B18 Active electric energy | B18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B18 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.105 | hwACPDCMA01CB19Voltage | B19 Voltage | B19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B19 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.106 | hwACPDCMA01CB20Voltage | B20 Voltage | B20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B20 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.107 | hwACPDCMA01CB21Voltage | B21 Voltage | B21电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B21 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.108 | hwACPDCMA01CB19Current | B19 Current | B19电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B19 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.109 | hwACPDCMA01CB20Current | B20 Current | B20电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B20 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.110 | hwACPDCMA01CB21Current | B21 Current | B21电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B21 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.111 | hwACPDCMA01CB19ActivePower | B19 Active power | B19有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B19 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.112 | hwACPDCMA01CB20ActivePower | B20 Active power | B20有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B20 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.113 | hwACPDCMA01CB21ActivePower | B21 Active power | B21有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B21 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.114 | hwACPDCMA01CB19ActiveElectricEnergy | B19 Active electric energy | B19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B19 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.115 | hwACPDCMA01CB20ActiveElectricEnergy | B20 Active electric energy | B20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B20 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.116 | hwACPDCMA01CB21ActiveElectricEnergy | B21 Active electric energy | B21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B21 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.117 | hwACPDCMA01CB22Voltage | B22 Voltage | B22电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B22 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.118 | hwACPDCMA01CB23Voltage | B23 Voltage | B23电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B23 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.119 | hwACPDCMA01CB24Voltage | B24 Voltage | B24电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B24 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.120 | hwACPDCMA01CB22Current | B22 Current | B22电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B22 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.121 | hwACPDCMA01CB23Current | B23 Current | B23电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B23 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.122 | hwACPDCMA01CB24Current | B24 Current | B24电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B24 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.123 | hwACPDCMA01CB22ActivePower | B22 Active power | B22有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B22 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.124 | hwACPDCMA01CB23ActivePower | B23 Active power | B23有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B23 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.125 | hwACPDCMA01CB24ActivePower | B24 Active power | B24有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B24 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.126 | hwACPDCMA01CB22ActiveElectricEnergy | B22 Active electric energy | B22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B22 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.127 | hwACPDCMA01CB23ActiveElectricEnergy | B23 Active electric energy | B23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B23 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.128 | hwACPDCMA01CB24ActiveElectricEnergy | B24 Active electric energy | B24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B24 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.129 | hwACPDCMA01CB25Voltage | B25 Voltage | B25电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B25 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.130 | hwACPDCMA01CB26Voltage | B26 Voltage | B26电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B26 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.131 | hwACPDCMA01CB27Voltage | B27 Voltage | B27电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B27 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.132 | hwACPDCMA01CB25Current | B25 Current | B25电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B25 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.133 | hwACPDCMA01CB26Current | B26 Current | B26电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B26 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.134 | hwACPDCMA01CB27Current | B27 Current | B27电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B27 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.135 | hwACPDCMA01CB25ActivePower | B25 Active power | B25有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B25 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.136 | hwACPDCMA01CB26ActivePower | B26 Active power | B26有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B26 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.137 | hwACPDCMA01CB27ActivePower | B27 Active power | B27有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B27 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.138 | hwACPDCMA01CB25ActiveElectricEnergy | B25 Active electric energy | B25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B25 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.139 | hwACPDCMA01CB26ActiveElectricEnergy | B26 Active electric energy | B26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B26 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.140 | hwACPDCMA01CB27ActiveElectricEnergy | B27 Active electric energy | B27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B27 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.141 | hwACPDCMA01CB28Voltage | B28 Voltage | B28电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B28 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.142 | hwACPDCMA01CB29Voltage | B29 Voltage | B29电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B29 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.143 | hwACPDCMA01CB30Voltage | B30 Voltage | B30电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B30 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.144 | hwACPDCMA01CB28Current | B28 Current | B28电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B28 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.145 | hwACPDCMA01CB29Current | B29 Current | B29电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B29 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.146 | hwACPDCMA01CB30Current | B30 Current | B30电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B30 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.147 | hwACPDCMA01CB28ActivePower | B28 Active power | B28有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B28 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.148 | hwACPDCMA01CB29ActivePower | B29 Active power | B29有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B29 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.149 | hwACPDCMA01CB30ActivePower | B30 Active power | B30有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B30 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.150 | hwACPDCMA01CB28ActiveElectricEnergy | B28 Active electric energy | B28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B28 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.151 | hwACPDCMA01CB29ActiveElectricEnergy | B29 Active electric energy | B29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B29 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.152 | hwACPDCMA01CB30ActiveElectricEnergy | B30 Active electric energy | B30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B30 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.153 | hwACPDCMA01CB31Voltage | B31 Voltage | B31电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B31 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.154 | hwACPDCMA01CB32Voltage | B32 Voltage | B32电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B32 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.155 | hwACPDCMA01CB33Voltage | B33 Voltage | B33电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B33 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.156 | hwACPDCMA01CB31Current | B31 Current | B31电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B31 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.157 | hwACPDCMA01CB32Current | B32 Current | B32电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B32 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.158 | hwACPDCMA01CB33Current | B33 Current | B33电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B33 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.159 | hwACPDCMA01CB31ActivePower | B31 Active power | B31有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B31 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.160 | hwACPDCMA01CB32ActivePower | B32 Active power | B32有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B32 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.161 | hwACPDCMA01CB33ActivePower | B33 Active power | B33有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B33 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.162 | hwACPDCMA01CB31ActiveElectricEnergy | B31 Active electric energy | B31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B31 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.163 | hwACPDCMA01CB32ActiveElectricEnergy | B32 Active electric energy | B32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B32 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.164 | hwACPDCMA01CB33ActiveElectricEnergy | B33 Active electric energy | B33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B33 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.165 | hwACPDCMA01CB34Voltage | B34 Voltage | B34电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B34 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.166 | hwACPDCMA01CB35Voltage | B35 Voltage | B35电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B35 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.167 | hwACPDCMA01CB36Voltage | B36 Voltage | B36电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B36 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.168 | hwACPDCMA01CB34Current | B34 Current | B34电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B34 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.169 | hwACPDCMA01CB35Current | B35 Current | B35电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B35 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.170 | hwACPDCMA01CB36Current | B36 Current | B36电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B36 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.171 | hwACPDCMA01CB34ActivePower | B34 Active power | B34有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B34 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.172 | hwACPDCMA01CB35ActivePower | B35 Active power | B35有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B35 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.173 | hwACPDCMA01CB36ActivePower | B36 Active power | B36有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B36 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.174 | hwACPDCMA01CB34ActiveElectricEnergy | B34 Active electric energy | B34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B34 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.175 | hwACPDCMA01CB35ActiveElectricEnergy | B35 Active electric energy | B35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B35 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.176 | hwACPDCMA01CB36ActiveElectricEnergy | B36 Active electric energy | B36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B36 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.177 | hwACPDCMA01CB37Voltage | B37 Voltage | B37电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B37 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.178 | hwACPDCMA01CB38Voltage | B38 Voltage | B38电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B38 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.179 | hwACPDCMA01CB39Voltage | B39 Voltage | B39电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B39 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.180 | hwACPDCMA01CB37Current | B37 Current | B37电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B37 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.181 | hwACPDCMA01CB38Current | B38 Current | B38电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B38 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.182 | hwACPDCMA01CB39Current | B39 Current | B39电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B39 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.183 | hwACPDCMA01CB37ActivePower | B37 Active power | B37有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B37 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.184 | hwACPDCMA01CB38ActivePower | B38 Active power | B38有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B38 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.185 | hwACPDCMA01CB39ActivePower | B39 Active power | B39有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B39 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.186 | hwACPDCMA01CB37ActiveElectricEnergy | B37 Active electric energy | B37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B37 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.187 | hwACPDCMA01CB38ActiveElectricEnergy | B38 Active electric energy | B38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B38 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.188 | hwACPDCMA01CB39ActiveElectricEnergy | B39 Active electric energy | B39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B39 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.189 | hwACPDCMA01CB40Voltage | B40 Voltage | B40电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B40 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.190 | hwACPDCMA01CB41Voltage | B41 Voltage | B41电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B41 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.191 | hwACPDCMA01CB42Voltage | B42 Voltage | B42电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B42 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.192 | hwACPDCMA01CB40Current | B40 Current | B40电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B40 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.193 | hwACPDCMA01CB41Current | B41 Current | B41电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B41 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.194 | hwACPDCMA01CB42Current | B42 Current | B42电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B42 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.195 | hwACPDCMA01CB40ActivePower | B40 Active power | B40有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B40 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.196 | hwACPDCMA01CB41ActivePower | B41 Active power | B41有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B41 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.197 | hwACPDCMA01CB42ActivePower | B42 Active power | B42有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B42 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.198 | hwACPDCMA01CB40ActiveElectricEnergy | B40 Active electric energy | B40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B40 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.199 | hwACPDCMA01CB41ActiveElectricEnergy | B41 Active electric energy | B41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B41 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.200 | hwACPDCMA01CB42ActiveElectricEnergy | B42 Active electric energy | B42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B42 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.2.1.201 | hwACPDCMA01CRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.3 | hwACPDCMA01CRunning3Table | / | / |  |  | / | / | The running table of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.1 | hwACPDCMA01CRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.2 | hwACPDCMA01CB43Voltage | B43 Voltage | B43电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B43 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.3 | hwACPDCMA01CB44Voltage | B44 Voltage | B44电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B44 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.4 | hwACPDCMA01CB45Voltage | B45 Voltage | B45电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B45 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.5 | hwACPDCMA01CB43Current | B43 Current | B43电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B43 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.6 | hwACPDCMA01CB44Current | B44 Current | B44电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B44 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.7 | hwACPDCMA01CB45Current | B45 Current | B45电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B45 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.8 | hwACPDCMA01CB43ActivePower | B43 Active power | B43有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B43 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.9 | hwACPDCMA01CB44ActivePower | B44 Active power | B44有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B44 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.10 | hwACPDCMA01CB45ActivePower | B45 Active power | B45有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B45 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.11 | hwACPDCMA01CB43ActiveElectricEnergy | B43 Active electric energy | B43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B43 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.12 | hwACPDCMA01CB44ActiveElectricEnergy | B44 Active electric energy | B44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B44 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.13 | hwACPDCMA01CB45ActiveElectricEnergy | B45 Active electric energy | B45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B45 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.14 | hwACPDCMA01CB46Voltage | B46 Voltage | B46电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B46 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.15 | hwACPDCMA01CB47Voltage | B47 Voltage | B47电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B47 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.16 | hwACPDCMA01CB48Voltage | B48 Voltage | B48电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B48 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.17 | hwACPDCMA01CB46Current | B46 Current | B46电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B46 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.18 | hwACPDCMA01CB47Current | B47 Current | B47电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B47 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.19 | hwACPDCMA01CB48Current | B48 Current | B48电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B48 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.20 | hwACPDCMA01CB46ActivePower | B46 Active power | B46有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B46 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.21 | hwACPDCMA01CB47ActivePower | B47 Active power | B47有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B47 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.22 | hwACPDCMA01CB48ActivePower | B48 Active power | B48有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B48 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.23 | hwACPDCMA01CB46ActiveElectricEnergy | B46 Active electric energy | B46有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B46 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.24 | hwACPDCMA01CB47ActiveElectricEnergy | B47 Active electric energy | B47有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B47 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.25 | hwACPDCMA01CB48ActiveElectricEnergy | B48 Active electric energy | B48有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B48 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.26 | hwACPDCMA01CInputCableForRouteBSpdStatus | Input cable for route B - SPD status | B路进线-防雷器状态 | 0-Read_Only | 只读 | normal(1), alarm(2), notenabled(3), unknown(255) | [正常=1]/[告警=2]/[未启用=3] | Input cable for route B - SPD status of the device config table for the AC_PDC_MA01C. Value 1 indicate normal Value 2 indicate alarm Value 3 indicate not enabled
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.27 | hwACPDCMA01CModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..254 | 1..254 | Modbus address of the device config table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.28 | hwACPDCMA01CPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.29 | hwACPDCMA01CInputCableVoltageLineFrequency | Input cable - voltage line frequency | 进线-电压线频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - voltage line frequency of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.30 | hwACPDCMA01CInputCablePhaseAVoltage | Input cable - phase A voltage | 进线-A相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable -phase A voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.31 | hwACPDCMA01CInputCablePhaseBVoltage | Input cable - phase B voltage | 进线-B相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase B voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.32 | hwACPDCMA01CInputCablePhaseCVoltage | Input cable - phase C voltage | 进线-C相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase C voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.33 | hwACPDCMA01CInputCablePhaseABVoltage | Input cable - phase A-B voltage | 进线-AB线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase AB voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.34 | hwACPDCMA01CInputCablePhaseBCVoltage | Input cable - phase B-C voltage | 进线-BC线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase BC voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.35 | hwACPDCMA01CInputCablePhaseCAVoltage | Input cable - phase C-A voltage | 进线-CA线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase CA voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.36 | hwACPDCMA01CInputCablePhaseACurrent | Input cable - phase A current | 进线-A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase A current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.37 | hwACPDCMA01CInputCablePhaseBCurrent | Input cable - phase B current | 进线-B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase B current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.38 | hwACPDCMA01CInputCablePhaseCCurrent | Input cable - phase C current | 进线-C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase C current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.39 | hwACPDCMA01CInputCablePhaseAActivePower | Input cable - phase A active power | 进线-A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase A active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.40 | hwACPDCMA01CInputCablePhaseABctivePower | Input cable - phase B active power | 进线-B相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase B active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.41 | hwACPDCMA01CInputCablePhaseCActivePower | Input cable - phase C active power | 进线-C相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase C active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.42 | hwACPDCMA01CInputCableCombinedPhaseActivePower | Input cable - combined phase active power | 进线-合相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - combined phase active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.43 | hwACPDCMA01CInputCablePhaseAActiveEnergy | Input cable - phase A active energy | 进线-A相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase A active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.44 | hwACPDCMA01CInputCablePhaseBActiveEnergy | Input cable - phase B active energy | 进线-B相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase B active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.45 | hwACPDCMA01CInputCablePhaseCActiveEnergy | Input cable - phase C active energy | 进线-C相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - phase C active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.46 | hwACPDCMA01CInputCableCombinedPhaseActiveEnergy | Input cable - combined phase active energy | 进线-合相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Input cable - combined phase active energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.47 | hwACPDCMA01CBranch1Voltage | Branch1 Voltage | 支路1电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch1 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.48 | hwACPDCMA01CBranch2Voltage | Branch2 Voltage | 支路2电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch2 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.49 | hwACPDCMA01CBranch3Voltage | Branch3 Voltage | 支路3电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch3 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.50 | hwACPDCMA01CBranch1Current | Branch1 Current | 支路1电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch1 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.51 | hwACPDCMA01CBranch2Current | Branch2 Current | 支路2电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch2 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.52 | hwACPDCMA01CBranch3Current | Branch3 Current | 支路3电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch3 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.53 | hwACPDCMA01CBranch1ActivePower | Branch1 Active power | 支路1有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch1 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.54 | hwACPDCMA01CBranch2ActivePower | Branch2 Active power | 支路2有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch2 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.55 | hwACPDCMA01CBranch3ActivePower | Branch3 Active power | 支路3有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch3 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.56 | hwACPDCMA01CBranch1ActiveElectricEnergy | Branch1 Active electric energy | 支路1有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch1 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.57 | hwACPDCMA01CBranch2ActiveElectricEnergy | Branch2 Active electric energy | 支路2有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch2 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.58 | hwACPDCMA01CBranch3ActiveElectricEnergy | Branch3 Active electric energy | 支路3有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch3 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.59 | hwACPDCMA01CBranch4Voltage | Branch4 Voltage | 支路4电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch4 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.60 | hwACPDCMA01CBranch5Voltage | Branch5 Voltage | 支路5电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch5 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.61 | hwACPDCMA01CBranch6Voltage | Branch6 Voltage | 支路6电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch6 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.62 | hwACPDCMA01CBranch4Current | Branch4 Current | 支路4电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch4 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.63 | hwACPDCMA01CBranch5Current | Branch5 Current | 支路5电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch5 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.64 | hwACPDCMA01CBranch6Current | Branch6 Current | 支路6电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch6 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.65 | hwACPDCMA01CBranch4ActivePower | Branch4 Active power | 支路4有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch4 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.66 | hwACPDCMA01CBranch5ActivePower | Branch5 Active power | 支路5有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch5 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.67 | hwACPDCMA01CBranch6ActivePower | Branch6 Active power | 支路6有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch6 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.68 | hwACPDCMA01CBranch4ActiveElectricEnergy | Branch4 Active electric energy | 支路4有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch4 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.69 | hwACPDCMA01CBranch5ActiveElectricEnergy | Branch5 Active electric energy | 支路5有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch5 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.70 | hwACPDCMA01CBranch6ActiveElectricEnergy | Branch6 Active electric energy | 支路6有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch6 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.71 | hwACPDCMA01CBranch7Voltage | Branch7 Voltage | 支路7电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch7 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.72 | hwACPDCMA01CBranch8Voltage | Branch8 Voltage | 支路8电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch8 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.73 | hwACPDCMA01CBranch9Voltage | Branch9 Voltage | 支路9电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch9 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.74 | hwACPDCMA01CBranch7Current | Branch7 Current | 支路7电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch7 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.75 | hwACPDCMA01CBranch8Current | Branch8 Current | 支路8电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch8 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.76 | hwACPDCMA01CBranch9Current | Branch9 Current | 支路9电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch9 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.77 | hwACPDCMA01CBranch7ActivePower | Branch7 Active power | 支路7有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch7 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.78 | hwACPDCMA01CBranch8ActivePower | Branch8 Active power | 支路8有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch8 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.79 | hwACPDCMA01CBranch9ActivePower | Branch9 Active power | 支路9有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch9 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.80 | hwACPDCMA01CBranch7ActiveElectricEnergy | Branch7 Active electric energy | 支路7有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch7 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.81 | hwACPDCMA01CBranch8ActiveElectricEnergy | Branch8 Active electric energy | 支路8有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch8 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.82 | hwACPDCMA01CBranch9ActiveElectricEnergy | Branch9 Active electric energy | 支路9有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch9 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.83 | hwACPDCMA01CBranch10Voltage | Branch10 Voltage | 支路10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch10 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.84 | hwACPDCMA01CBranch11Voltage | Branch11 Voltage | 支路11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch11 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.85 | hwACPDCMA01CBranch12Voltage | Branch12 Voltage | 支路12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch12 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.86 | hwACPDCMA01CBranch10Current | Branch10 Current | 支路10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch10 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.87 | hwACPDCMA01CBranch11Current | Branch11 Current | 支路11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch11 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.88 | hwACPDCMA01CBranch12Current | Branch12 Current | 支路12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch12 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.89 | hwACPDCMA01CBranch10ActivePower | Branch10 Active power | 支路10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch10 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.90 | hwACPDCMA01CBranch11ActivePower | Branch11 Active power | 支路11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch11 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.91 | hwACPDCMA01CBranch12ActivePower | Branch12 Active power | 支路12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch12 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.92 | hwACPDCMA01CBranch10ActiveElectricEnergy | Branch10 Active electric energy | 支路10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch10 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.93 | hwACPDCMA01CBranch11ActiveElectricEnergy | Branch11 Active electric energy | 支路11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch11 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.94 | hwACPDCMA01CBranch12ActiveElectricEnergy | Branch12 Active electric energy | 支路12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch12 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.95 | hwACPDCMA01CBranch13Voltage | Branch13 Voltage | 支路13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch13 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.96 | hwACPDCMA01CBranch14Voltage | Branch14 Voltage | 支路14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch14 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.97 | hwACPDCMA01CBranch15Voltage | Branch15 Voltage | 支路15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch15 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.98 | hwACPDCMA01CBranch13Current | Branch13 Current | 支路13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch13 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.99 | hwACPDCMA01CBranch14Current | Branch14 Current | 支路14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch14 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.100 | hwACPDCMA01CBranch15Current | Branch15 Current | 支路15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch15 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.101 | hwACPDCMA01CBranch13ActivePower | Branch13 Active power | 支路13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch13 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.102 | hwACPDCMA01CBranch14ActivePower | Branch14 Active power | 支路14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch14 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.103 | hwACPDCMA01CBranch15ActivePower | Branch15 Active power | 支路15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch15 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.104 | hwACPDCMA01CBranch13ActiveElectricEnergy | Branch13 Active electric energy | 支路13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch13 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.105 | hwACPDCMA01CBranch14ActiveElectricEnergy | Branch14 Active electric energy | 支路14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch14 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.106 | hwACPDCMA01CBranch15ActiveElectricEnergy | Branch15 Active electric energy | 支路15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch15 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.107 | hwACPDCMA01CBranch16Voltage | Branch16 Voltage | 支路16电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch16 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.108 | hwACPDCMA01CBranch17Voltage | Branch17 Voltage | 支路17电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch17 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.109 | hwACPDCMA01CBranch18Voltage | Branch18 Voltage | 支路18电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch18 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.110 | hwACPDCMA01CBranch16Current | Branch16 Current | 支路16电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch16 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.111 | hwACPDCMA01CBranch17Current | Branch17 Current | 支路17电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch17 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.112 | hwACPDCMA01CBranch18Current | Branch18 Current | 支路18电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch18 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.113 | hwACPDCMA01CBranch16ActivePower | Branch16 Active power | 支路16有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch16 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.114 | hwACPDCMA01CBranch17ActivePower | Branch17 Active power | 支路17有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch17 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.115 | hwACPDCMA01CBranch18ActivePower | Branch18 Active power | 支路18有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch18 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.116 | hwACPDCMA01CBranch16ActiveElectricEnergy | Branch16 Active electric energy | 支路16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch16 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.117 | hwACPDCMA01CBranch17ActiveElectricEnergy | Branch17 Active electric energy | 支路17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch17 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.118 | hwACPDCMA01CBranch18ActiveElectricEnergy | Branch18 Active electric energy | 支路18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch18 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.119 | hwACPDCMA01CBranch19Voltage | Branch19 Voltage | 支路19电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch19 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.120 | hwACPDCMA01CBranch20Voltage | Branch20 Voltage | 支路20电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch20 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.121 | hwACPDCMA01CBranch21Voltage | Branch21 Voltage | 支路21电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch21 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.122 | hwACPDCMA01CBranch19Current | Branch19 Current | 支路19电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch19 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.123 | hwACPDCMA01CBranch20Current | Branch20 Current | 支路20电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch20 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.124 | hwACPDCMA01CBranch21Current | Branch21 Current | 支路21电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch21 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.125 | hwACPDCMA01CBranch19ActivePower | Branch19 Active power | 支路19有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch19 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.126 | hwACPDCMA01CBranch20ActivePower | Branch20 Active power | 支路20有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch20 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.127 | hwACPDCMA01CBranch21ActivePower | Branch21 Active power | 支路21有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch21 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.128 | hwACPDCMA01CBranch19ActiveElectricEnergy | Branch19 Active electric energy | 支路19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch19 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.129 | hwACPDCMA01CBranch20ActiveElectricEnergy | Branch20 Active electric energy | 支路20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch20 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.130 | hwACPDCMA01CBranch21ActiveElectricEnergy | Branch21 Active electric energy | 支路21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch21 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.131 | hwACPDCMA01CBranch22Voltage | Branch22 Voltage | 支路22电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch22 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.132 | hwACPDCMA01CBranch23Voltage | Branch23 Voltage | 支路23电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch23 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.133 | hwACPDCMA01CBranch24Voltage | Branch24 Voltage | 支路24电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch24 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.134 | hwACPDCMA01CBranch22Current | Branch22 Current | 支路22电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch22 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.135 | hwACPDCMA01CBranch23Current | Branch23 Current | 支路23电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch23 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.136 | hwACPDCMA01CBranch24Current | Branch24 Current | 支路24电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch24 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.137 | hwACPDCMA01CBranch22ActivePower | Branch22 Active power | 支路22有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch22 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.138 | hwACPDCMA01CBranch23ActivePower | Branch23 Active power | 支路23有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch23 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.139 | hwACPDCMA01CBranch24ActivePower | Branch24 Active power | 支路24有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch24 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.140 | hwACPDCMA01CBranch22ActiveElectricEnergy | Branch22 Active electric energy | 支路22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch22 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.141 | hwACPDCMA01CBranch23ActiveElectricEnergy | Branch23 Active electric energy | 支路23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch23 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.142 | hwACPDCMA01CBranch24ActiveElectricEnergy | Branch24 Active electric energy | 支路24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch24 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.143 | hwACPDCMA01CBranch25Voltage | Branch25 Voltage | 支路25电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch25 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.144 | hwACPDCMA01CBranch26Voltage | Branch26 Voltage | 支路26电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch26 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.145 | hwACPDCMA01CBranch27Voltage | Branch27 Voltage | 支路27电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch27 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.146 | hwACPDCMA01CBranch25Current | Branch25 Current | 支路25电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch25 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.147 | hwACPDCMA01CBranch26Current | Branch26 Current | 支路26电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch26 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.148 | hwACPDCMA01CBranch27Current | Branch27 Current | 支路27电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch27 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.149 | hwACPDCMA01CBranch25ActivePower | Branch25 Active power | 支路25有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch25 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.150 | hwACPDCMA01CBranch26ActivePower | Branch26 Active power | 支路26有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch26 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.151 | hwACPDCMA01CBranch27ActivePower | Branch27 Active power | 支路27有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch27 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.152 | hwACPDCMA01CBranch25ActiveElectricEnergy | Branch25 Active electric energy | 支路25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch25 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.153 | hwACPDCMA01CBranch26ActiveElectricEnergy | Branch26 Active electric energy | 支路26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch26 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.154 | hwACPDCMA01CBranch27ActiveElectricEnergy | Branch27 Active electric energy | 支路27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch27 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.155 | hwACPDCMA01CBranch28Voltage | Branch28 Voltage | 支路28电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch28 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.156 | hwACPDCMA01CBranch29Voltage | Branch29 Voltage | 支路29电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch29 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.157 | hwACPDCMA01CBranch30Voltage | Branch30 Voltage | 支路30电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch30 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.158 | hwACPDCMA01CBranch28Current | Branch28 Current | 支路28电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch28 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.159 | hwACPDCMA01CBranch29Current | Branch29 Current | 支路29电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch29 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.160 | hwACPDCMA01CBranch30Current | Branch30 Current | 支路30电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch30 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.161 | hwACPDCMA01CBranch28ActivePower | Branch28 Active power | 支路28有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch28 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.162 | hwACPDCMA01CBranch29ActivePower | Branch29 Active power | 支路29有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch29 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.163 | hwACPDCMA01CBranch30ActivePower | Branch30 Active power | 支路30有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch30 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.164 | hwACPDCMA01CBranch28ActiveElectricEnergy | Branch28 Active electric energy | 支路28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch28 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.165 | hwACPDCMA01CBranch29ActiveElectricEnergy | Branch29 Active electric energy | 支路29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch29 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.166 | hwACPDCMA01CBranch30ActiveElectricEnergy | Branch30 Active electric energy | 支路30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch30 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.167 | hwACPDCMA01CBranch31Voltage | Branch31 Voltage | 支路31电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch31 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.168 | hwACPDCMA01CBranch32Voltage | Branch32 Voltage | 支路32电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch32 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.169 | hwACPDCMA01CBranch33Voltage | Branch33 Voltage | 支路33电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch33 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.170 | hwACPDCMA01CBranch31Current | Branch31 Current | 支路31电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch31 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.171 | hwACPDCMA01CBranch32Current | Branch32 Current | 支路32电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch32 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.172 | hwACPDCMA01CBranch33Current | Branch33 Current | 支路33电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch33 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.173 | hwACPDCMA01CBranch31ActivePower | Branch31 Active power | 支路31有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch31 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.174 | hwACPDCMA01CBranch32ActivePower | Branch32 Active power | 支路32有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch32 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.175 | hwACPDCMA01CBranch33ActivePower | Branch33 Active power | 支路33有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch33 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.176 | hwACPDCMA01CBranch31ActiveElectricEnergy | Branch31 Active electric energy | 支路31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch31 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.177 | hwACPDCMA01CBranch32ActiveElectricEnergy | Branch32 Active electric energy | 支路32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch32 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.178 | hwACPDCMA01CBranch33ActiveElectricEnergy | Branch33 Active electric energy | 支路33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch33 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.179 | hwACPDCMA01CBranch34Voltage | Branch34 Voltage | 支路34电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch34 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.180 | hwACPDCMA01CBranch35Voltage | Branch35 Voltage | 支路35电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch35 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.181 | hwACPDCMA01CBranch36Voltage | Branch36 Voltage | 支路36电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch36 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.182 | hwACPDCMA01CBranch34Current | Branch34 Current | 支路34电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch34 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.183 | hwACPDCMA01CBranch35Current | Branch35 Current | 支路35电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch35 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.184 | hwACPDCMA01CBranch36Current | Branch36 Current | 支路36电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch36 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.185 | hwACPDCMA01CBranch34ActivePower | Branch34 Active power | 支路34有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch34 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.186 | hwACPDCMA01CBranch35ActivePower | Branch35 Active power | 支路35有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch35 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.187 | hwACPDCMA01CBranch36ActivePower | Branch36 Active power | 支路36有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch36 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.188 | hwACPDCMA01CBranch34ActiveElectricEnergy | Branch34 Active electric energy | 支路34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch34 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.189 | hwACPDCMA01CBranch35ActiveElectricEnergy | Branch35 Active electric energy | 支路35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch35 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.190 | hwACPDCMA01CBranch36ActiveElectricEnergy | Branch36 Active electric energy | 支路36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch36 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.191 | hwACPDCMA01CBranch37Voltage | Branch37 Voltage | 支路37电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch37 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.192 | hwACPDCMA01CBranch38Voltage | Branch38 Voltage | 支路38电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch38 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.193 | hwACPDCMA01CBranch39Voltage | Branch39 Voltage | 支路39电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch39 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.194 | hwACPDCMA01CBranch37Current | Branch37 Current | 支路37电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch37 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.195 | hwACPDCMA01CBranch38Current | Branch38 Current | 支路38电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch38 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.196 | hwACPDCMA01CBranch39Current | Branch39 Current | 支路39电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch39 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.197 | hwACPDCMA01CBranch37ActivePower | Branch37 Active power | 支路37有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch37 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.198 | hwACPDCMA01CBranch38ActivePower | Branch38 Active power | 支路38有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch38 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.199 | hwACPDCMA01CBranch39ActivePower | Branch39 Active power | 支路39有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch39 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.200 | hwACPDCMA01CBranch37ActiveElectricEnergy | Branch37 Active electric energy | 支路37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch37 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.3.1.201 | hwACPDCMA01CRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.4 | hwACPDCMA01CRunning4Table | / | / |  |  | / | / | The running table of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.1 | hwACPDCMA01CRunning4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.2 | hwACPDCMA01CBranch38ActiveElectricEnergy | Branch38 Active electric energy | 支路38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch38 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.3 | hwACPDCMA01CBranch39ActiveElectricEnergy | Branch39 Active electric energy | 支路39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch39 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.4 | hwACPDCMA01CBranch40Voltage | Branch40 Voltage | 支路40电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch40 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.5 | hwACPDCMA01CBranch41Voltage | Branch41 Voltage | 支路41电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch41 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.6 | hwACPDCMA01CBranch42Voltage | Branch42 Voltage | 支路42电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch42 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.7 | hwACPDCMA01CBranch40Current | Branch40 Current | 支路40电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch40 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.8 | hwACPDCMA01CBranch41Current | Branch41 Current | 支路41电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch41 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.9 | hwACPDCMA01CBranch42Current | Branch42 Current | 支路42电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch42 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.10 | hwACPDCMA01CBranch40ActivePower | Branch40 Active power | 支路40有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch40 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.11 | hwACPDCMA01CBranch41ActivePower | Branch41 Active power | 支路41有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch41 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.12 | hwACPDCMA01CBranch42ActivePower | Branch42 Active power | 支路42有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch42 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.13 | hwACPDCMA01CBranch40ActiveElectricEnergy | Branch40 Active electric energy | 支路40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch40 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.14 | hwACPDCMA01CBranch41ActiveElectricEnergy | Branch41 Active electric energy | 支路41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch41 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.15 | hwACPDCMA01CBranch42ActiveElectricEnergy | Branch42 Active electric energy | 支路42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch42 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.16 | hwACPDCMA01CBranch43Voltage | Branch43 Voltage | 支路43电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch43 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.17 | hwACPDCMA01CBranch44Voltage | Branch44 Voltage | 支路44电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch44 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.18 | hwACPDCMA01CBranch45Voltage | Branch45 Voltage | 支路45电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch45 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.19 | hwACPDCMA01CBranch43Current | Branch43 Current | 支路43电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch43 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.20 | hwACPDCMA01CBranch44Current | Branch44 Current | 支路44电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch44 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.21 | hwACPDCMA01CBranch45Current | Branch45 Current | 支路45电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch45 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.22 | hwACPDCMA01CBranch43ActivePower | Branch43 Active power | 支路43有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch43 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.23 | hwACPDCMA01CBranch44ActivePower | Branch44 Active power | 支路44有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch44 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.24 | hwACPDCMA01CBranch45ActivePower | Branch45 Active power | 支路45有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch45 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.25 | hwACPDCMA01CBranch43ActiveElectricEnergy | Branch43 Active electric energy | 支路43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch43 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.26 | hwACPDCMA01CBranch44ActiveElectricEnergy | Branch44 Active electric energy | 支路44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch44 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.27 | hwACPDCMA01CBranch45ActiveElectricEnergy | Branch45 Active electric energy | 支路45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch45 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.28 | hwACPDCMA01CBranch46Voltage | Branch46 Voltage | 支路46电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch46 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.29 | hwACPDCMA01CBranch47Voltage | Branch47 Voltage | 支路47电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch47 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.30 | hwACPDCMA01CBranch48Voltage | Branch48 Voltage | 支路48电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch48 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.31 | hwACPDCMA01CBranch46Current | Branch46 Current | 支路46电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch46 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.32 | hwACPDCMA01CBranch47Current | Branch47 Current | 支路47电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch47 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.33 | hwACPDCMA01CBranch48Current | Branch48 Current | 支路48电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch48 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.34 | hwACPDCMA01CBranch46ActivePower | Branch46 Active power | 支路46有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch46 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.35 | hwACPDCMA01CBranch47ActivePower | Branch47 Active power | 支路47有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch47 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.36 | hwACPDCMA01CBranch48ActivePower | Branch48 Active power | 支路48有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch48 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.37 | hwACPDCMA01CBranch46ActiveElectricEnergy | Branch46 Active electric energy | 支路46有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch46 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.38 | hwACPDCMA01CBranch47ActiveElectricEnergy | Branch47 Active electric energy | 支路47有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch47 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.39 | hwACPDCMA01CBranch48ActiveElectricEnergy | Branch48 Active electric energy | 支路48有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch48 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.40 | hwACPDCMA01CBranch49Voltage | Branch49 Voltage | 支路49电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch49 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.41 | hwACPDCMA01CBranch50Voltage | Branch50 Voltage | 支路50电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch50 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.42 | hwACPDCMA01CBranch51Voltage | Branch51 Voltage | 支路51电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch51 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.43 | hwACPDCMA01CBranch49Current | Branch49 Current | 支路49电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch49 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.44 | hwACPDCMA01CBranch50Current | Branch50 Current | 支路50电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch50 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.45 | hwACPDCMA01CBranch51Current | Branch51 Current | 支路51电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch51 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.46 | hwACPDCMA01CBranch49ActivePower | Branch49 Active power | 支路49有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch49 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.47 | hwACPDCMA01CBranch50ActivePower | Branch50 Active power | 支路50有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch50 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.48 | hwACPDCMA01CBranch51ActivePower | Branch51 Active power | 支路51有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch51 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.49 | hwACPDCMA01CBranch49ActiveElectricEnergy | Branch49 Active electric energy | 支路49有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch49 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.50 | hwACPDCMA01CBranch50ActiveElectricEnergy | Branch50 Active electric energy | 支路50有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch50 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.51 | hwACPDCMA01CBranch51ActiveElectricEnergy | Branch51 Active electric energy | 支路51有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch51 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.52 | hwACPDCMA01CBranch52Voltage | Branch52 Voltage | 支路52电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch52 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.53 | hwACPDCMA01CBranch53Voltage | Branch53 Voltage | 支路53电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch53 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.54 | hwACPDCMA01CBranch54Voltage | Branch54 Voltage | 支路54电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch54 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.55 | hwACPDCMA01CBranch52Current | Branch52 Current | 支路52电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch52 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.56 | hwACPDCMA01CBranch53Current | Branch53 Current | 支路53电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch53 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.57 | hwACPDCMA01CBranch54Current | Branch54 Current | 支路54电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch54 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.58 | hwACPDCMA01CBranch52ActivePower | Branch52 Active power | 支路52有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch52 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.59 | hwACPDCMA01CBranch53ActivePower | Branch53 Active power | 支路53有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch53 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.60 | hwACPDCMA01CBranch54ActivePower | Branch54 Active power | 支路54有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch54 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.61 | hwACPDCMA01CBranch52ActiveElectricEnergy | Branch52 Active electric energy | 支路52有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch52 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.62 | hwACPDCMA01CBranch53ActiveElectricEnergy | Branch53 Active electric energy | 支路53有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch53 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.63 | hwACPDCMA01CBranch54ActiveElectricEnergy | Branch54 Active electric energy | 支路54有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch54 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.64 | hwACPDCMA01CBranch55Voltage | Branch55 Voltage | 支路55电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch55 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.65 | hwACPDCMA01CBranch56Voltage | Branch56 Voltage | 支路56电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch56 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.66 | hwACPDCMA01CBranch57Voltage | Branch57 Voltage | 支路57电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch57 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.67 | hwACPDCMA01CBranch55Current | Branch55 Current | 支路55电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch55 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.68 | hwACPDCMA01CBranch56Current | Branch56 Current | 支路56电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch56 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.69 | hwACPDCMA01CBranch57Current | Branch57 Current | 支路57电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch57 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.70 | hwACPDCMA01CBranch55ActivePower | Branch55 Active power | 支路55有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch55 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.71 | hwACPDCMA01CBranch56ActivePower | Branch56 Active power | 支路56有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch56 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.72 | hwACPDCMA01CBranch57ActivePower | Branch57 Active power | 支路57有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch57 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.73 | hwACPDCMA01CBranch55ActiveElectricEnergy | Branch55 Active electric energy | 支路55有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch55 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.74 | hwACPDCMA01CBranch56ActiveElectricEnergy | Branch56 Active electric energy | 支路56有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch56 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.75 | hwACPDCMA01CBranch57ActiveElectricEnergy | Branch57 Active electric energy | 支路57有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch57 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.76 | hwACPDCMA01CBranch58Voltage | Branch58 Voltage | 支路58电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch58 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.77 | hwACPDCMA01CBranch59Voltage | Branch59 Voltage | 支路59电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch59 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.78 | hwACPDCMA01CBranch60Voltage | Branch60 Voltage | 支路60电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch60 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.79 | hwACPDCMA01CBranch58Current | Branch58 Current | 支路58电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch58 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.80 | hwACPDCMA01CBranch59Current | Branch59 Current | 支路59电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch59 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.81 | hwACPDCMA01CBranch60Current | Branch60 Current | 支路60电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch60 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.82 | hwACPDCMA01CBranch58ActivePower | Branch58 Active power | 支路58有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch58 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.83 | hwACPDCMA01CBranch59ActivePower | Branch59 Active power | 支路59有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch59 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.84 | hwACPDCMA01CBranch60ActivePower | Branch60 Active power | 支路60有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch60 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.85 | hwACPDCMA01CBranch58ActiveElectricEnergy | Branch58 Active electric energy | 支路58有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch58 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.86 | hwACPDCMA01CBranch59ActiveElectricEnergy | Branch59 Active electric energy | 支路59有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch59 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.87 | hwACPDCMA01CBranch60ActiveElectricEnergy | Branch60 Active electric energy | 支路60有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch60 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.88 | hwACPDCMA01CBranch61Voltage | Branch61 Voltage | 支路61电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch61 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.89 | hwACPDCMA01CBranch62Voltage | Branch62 Voltage | 支路62电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch62 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.90 | hwACPDCMA01CBranch63Voltage | Branch63 Voltage | 支路63电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch63 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.91 | hwACPDCMA01CBranch61Current | Branch61 Current | 支路61电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch61 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.92 | hwACPDCMA01CBranch62Current | Branch62 Current | 支路62电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch62 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.93 | hwACPDCMA01CBranch63Current | Branch63 Current | 支路63电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch63 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.94 | hwACPDCMA01CBranch61ActivePower | Branch61 Active power | 支路61有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch61 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.95 | hwACPDCMA01CBranch62ActivePower | Branch62 Active power | 支路62有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch62 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.96 | hwACPDCMA01CBranch63ActivePower | Branch63 Active power | 支路63有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch63 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.97 | hwACPDCMA01CBranch61ActiveElectricEnergy | Branch61 Active electric energy | 支路61有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch61 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.98 | hwACPDCMA01CBranch62ActiveElectricEnergy | Branch62 Active electric energy | 支路62有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch62 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.99 | hwACPDCMA01CBranch63ActiveElectricEnergy | Branch63 Active electric energy | 支路63有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch63 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.100 | hwACPDCMA01CBranch64Voltage | Branch64 Voltage | 支路64电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch64 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.101 | hwACPDCMA01CBranch65Voltage | Branch65 Voltage | 支路65电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch65 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.102 | hwACPDCMA01CBranch66Voltage | Branch66 Voltage | 支路66电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch66 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.103 | hwACPDCMA01CBranch64Current | Branch64 Current | 支路64电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch64 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.104 | hwACPDCMA01CBranch65Current | Branch65 Current | 支路65电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch65 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.105 | hwACPDCMA01CBranch66Current | Branch66 Current | 支路66电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch66 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.106 | hwACPDCMA01CBranch64ActivePower | Branch64 Active power | 支路64有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch64 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.107 | hwACPDCMA01CBranch65ActivePower | Branch65 Active power | 支路65有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch65 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.108 | hwACPDCMA01CBranch66ActivePower | Branch66 Active power | 支路66有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch66 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.109 | hwACPDCMA01CBranch64ActiveElectricEnergy | Branch64 Active electric energy | 支路64有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch64 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.110 | hwACPDCMA01CBranch65ActiveElectricEnergy | Branch65 Active electric energy | 支路65有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch65 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.111 | hwACPDCMA01CBranch66ActiveElectricEnergy | Branch66 Active electric energy | 支路66有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch66 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.112 | hwACPDCMA01CBranch67Voltage | Branch67 Voltage | 支路67电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch67 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.113 | hwACPDCMA01CBranch68Voltage | Branch68 Voltage | 支路68电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch68 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.114 | hwACPDCMA01CBranch69Voltage | Branch69 Voltage | 支路69电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch69 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.115 | hwACPDCMA01CBranch67Current | Branch67 Current | 支路67电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch67 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.116 | hwACPDCMA01CBranch68Current | Branch68 Current | 支路68电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch68 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.117 | hwACPDCMA01CBranch69Current | Branch69 Current | 支路69电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch69 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.118 | hwACPDCMA01CBranch67ActivePower | Branch67 Active power | 支路67有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch67 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.119 | hwACPDCMA01CBranch68ActivePower | Branch68 Active power | 支路68有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch68 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.120 | hwACPDCMA01CBranch69ActivePower | Branch69 Active power | 支路69有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch69 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.121 | hwACPDCMA01CBranch67ActiveElectricEnergy | Branch67 Active electric energy | 支路67有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch67 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.122 | hwACPDCMA01CBranch68ActiveElectricEnergy | Branch68 Active electric energy | 支路68有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch68 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.123 | hwACPDCMA01CBranch69ActiveElectricEnergy | Branch69 Active electric energy | 支路69有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch69 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.124 | hwACPDCMA01CBranch70Voltage | Branch70 Voltage | 支路70电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch70 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.125 | hwACPDCMA01CBranch71Voltage | Branch71 Voltage | 支路71电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch71 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.126 | hwACPDCMA01CBranch72Voltage | Branch72 Voltage | 支路72电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch72 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.127 | hwACPDCMA01CBranch70Current | Branch70 Current | 支路70电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch70 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.128 | hwACPDCMA01CBranch71Current | Branch71 Current | 支路71电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch71 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.129 | hwACPDCMA01CBranch72Current | Branch72 Current | 支路72电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch72 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.130 | hwACPDCMA01CBranch70ActivePower | Branch70 Active power | 支路70有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch70 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.131 | hwACPDCMA01CBranch71ActivePower | Branch71 Active power | 支路71有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch71 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.132 | hwACPDCMA01CBranch72ActivePower | Branch72 Active power | 支路72有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch72 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.133 | hwACPDCMA01CBranch70ActiveElectricEnergy | Branch70 Active electric energy | 支路70有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch70 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.134 | hwACPDCMA01CBranch71ActiveElectricEnergy | Branch71 Active electric energy | 支路71有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch71 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.135 | hwACPDCMA01CBranch72ActiveElectricEnergy | Branch72 Active electric energy | 支路72有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch72 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.136 | hwACPDCMA01CBranch73Voltage | Branch73 Voltage | 支路73电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch73 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.137 | hwACPDCMA01CBranch74Voltage | Branch74 Voltage | 支路74电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch74 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.138 | hwACPDCMA01CBranch75Voltage | Branch75 Voltage | 支路75电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch75 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.139 | hwACPDCMA01CBranch73Current | Branch73 Current | 支路73电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch73 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.140 | hwACPDCMA01CBranch74Current | Branch74 Current | 支路74电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch74 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.141 | hwACPDCMA01CBranch75Current | Branch75 Current | 支路75电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch75 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.142 | hwACPDCMA01CBranch73ActivePower | Branch73 Active power | 支路73有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch73 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.143 | hwACPDCMA01CBranch74ActivePower | Branch74 Active power | 支路74有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch74 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.144 | hwACPDCMA01CBranch75ActivePower | Branch75 Active power | 支路75有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch75 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.145 | hwACPDCMA01CBranch73ActiveElectricEnergy | Branch73 Active electric energy | 支路73有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch73 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.146 | hwACPDCMA01CBranch74ActiveElectricEnergy | Branch74 Active electric energy | 支路74有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch74 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.147 | hwACPDCMA01CBranch75ActiveElectricEnergy | Branch75 Active electric energy | 支路75有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch75 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.148 | hwACPDCMA01CBranch76Voltage | Branch76 Voltage | 支路76电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch76 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.149 | hwACPDCMA01CBranch77Voltage | Branch77 Voltage | 支路77电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch77 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.150 | hwACPDCMA01CBranch78Voltage | Branch78 Voltage | 支路78电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch78 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.151 | hwACPDCMA01CBranch76Current | Branch76 Current | 支路76电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch76 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.152 | hwACPDCMA01CBranch77Current | Branch77 Current | 支路77电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch77 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.153 | hwACPDCMA01CBranch78Current | Branch78 Current | 支路78电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch78 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.154 | hwACPDCMA01CBranch76ActivePower | Branch76 Active power | 支路76有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch76 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.155 | hwACPDCMA01CBranch77ActivePower | Branch77 Active power | 支路77有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch77 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.156 | hwACPDCMA01CBranch78ActivePower | Branch78 Active power | 支路78有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch78 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.157 | hwACPDCMA01CBranch76ActiveElectricEnergy | Branch76 Active electric energy | 支路76有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch76 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.158 | hwACPDCMA01CBranch77ActiveElectricEnergy | Branch77 Active electric energy | 支路77有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch77 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.159 | hwACPDCMA01CBranch78ActiveElectricEnergy | Branch78 Active electric energy | 支路78有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch78 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.160 | hwACPDCMA01CBranch79Voltage | Branch79 Voltage | 支路79电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch79 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.161 | hwACPDCMA01CBranch80Voltage | Branch80 Voltage | 支路80电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch80 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.162 | hwACPDCMA01CBranch81Voltage | Branch81 Voltage | 支路81电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch81 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.163 | hwACPDCMA01CBranch79Current | Branch79 Current | 支路79电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch79 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.164 | hwACPDCMA01CBranch80Current | Branch80 Current | 支路80电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch80 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.165 | hwACPDCMA01CBranch81Current | Branch81 Current | 支路81电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch81 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.166 | hwACPDCMA01CBranch79ActivePower | Branch79 Active power | 支路79有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch79 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.167 | hwACPDCMA01CBranch80ActivePower | Branch80 Active power | 支路80有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch80 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.168 | hwACPDCMA01CBranch81ActivePower | Branch81 Active power | 支路81有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch81 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.169 | hwACPDCMA01CBranch79ActiveElectricEnergy | Branch79 Active electric energy | 支路79有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch79 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.170 | hwACPDCMA01CBranch80ActiveElectricEnergy | Branch80 Active electric energy | 支路80有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch80 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.171 | hwACPDCMA01CBranch81ActiveElectricEnergy | Branch81 Active electric energy | 支路81有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch81 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.172 | hwACPDCMA01CBranch82Voltage | Branch82 Voltage | 支路82电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch82 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.173 | hwACPDCMA01CBranch83Voltage | Branch83 Voltage | 支路83电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch83 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.174 | hwACPDCMA01CBranch84Voltage | Branch84 Voltage | 支路84电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch84 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.175 | hwACPDCMA01CBranch82Current | Branch82 Current | 支路82电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch82 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.176 | hwACPDCMA01CBranch83Current | Branch83 Current | 支路83电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch83 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.177 | hwACPDCMA01CBranch84Current | Branch84 Current | 支路84电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch84 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.178 | hwACPDCMA01CBranch82ActivePower | Branch82 Active power | 支路82有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch82 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.179 | hwACPDCMA01CBranch83ActivePower | Branch83 Active power | 支路83有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch83 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.180 | hwACPDCMA01CBranch84ActivePower | Branch84 Active power | 支路84有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch84 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.181 | hwACPDCMA01CBranch82ActiveElectricEnergy | Branch82 Active electric energy | 支路82有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch82 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.182 | hwACPDCMA01CBranch83ActiveElectricEnergy | Branch83 Active electric energy | 支路83有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch83 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.183 | hwACPDCMA01CBranch84ActiveElectricEnergy | Branch84 Active electric energy | 支路84有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch84 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.184 | hwACPDCMA01CBranch85Voltage | Branch85 Voltage | 支路85电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch85 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.185 | hwACPDCMA01CBranch86Voltage | Branch86 Voltage | 支路86电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch86 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.186 | hwACPDCMA01CBranch87Voltage | Branch87 Voltage | 支路87电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch87 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.187 | hwACPDCMA01CBranch85Current | Branch85 Current | 支路85电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch85 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.188 | hwACPDCMA01CBranch86Current | Branch86 Current | 支路86电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch86 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.189 | hwACPDCMA01CBranch87Current | Branch87 Current | 支路87电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch87 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.190 | hwACPDCMA01CBranch85ActivePower | Branch85 Active power | 支路85有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch85 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.191 | hwACPDCMA01CBranch86ActivePower | Branch86 Active power | 支路86有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch86 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.192 | hwACPDCMA01CBranch87ActivePower | Branch87 Active power | 支路87有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch87 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.193 | hwACPDCMA01CBranch85ActiveElectricEnergy | Branch85 Active electric energy | 支路85有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch85 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.194 | hwACPDCMA01CBranch86ActiveElectricEnergy | Branch86 Active electric energy | 支路86有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch86 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.195 | hwACPDCMA01CBranch87ActiveElectricEnergy | Branch87 Active electric energy | 支路87有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch87 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.196 | hwACPDCMA01CBranch88Voltage | Branch88 Voltage | 支路88电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch88 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.197 | hwACPDCMA01CBranch89Voltage | Branch89 Voltage | 支路89电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch89 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.198 | hwACPDCMA01CBranch90Voltage | Branch90 Voltage | 支路90电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch90 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.199 | hwACPDCMA01CBranch88Current | Branch88 Current | 支路88电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch88 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.200 | hwACPDCMA01CBranch89Current | Branch89 Current | 支路89电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch89 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.4.1.201 | hwACPDCMA01CRunning4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.5 | hwACPDCMA01CRunning5Table | / | / |  |  | / | / | The running table of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.1 | hwACPDCMA01CRunning5Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.2 | hwACPDCMA01CBranch90Current | Branch90 Current | 支路90电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch90 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.3 | hwACPDCMA01CBranch88ActivePower | Branch88 Active power | 支路88有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch88 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.4 | hwACPDCMA01CBranch89ActivePower | Branch89 Active power | 支路89有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch89 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.5 | hwACPDCMA01CBranch90ActivePower | Branch90 Active power | 支路90有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch90 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.6 | hwACPDCMA01CBranch88ActiveElectricEnergy | Branch88 Active electric energy | 支路88有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch88 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.7 | hwACPDCMA01CBranch89ActiveElectricEnergy | Branch89 Active electric energy | 支路89有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch89 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.8 | hwACPDCMA01CBranch90ActiveElectricEnergy | Branch90 Active electric energy | 支路90有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch90 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.9 | hwACPDCMA01CBranch91Voltage | Branch91 Voltage | 支路91电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch91 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.10 | hwACPDCMA01CBranch92Voltage | Branch92 Voltage | 支路92电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch92 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.11 | hwACPDCMA01CBranch93Voltage | Branch93 Voltage | 支路93电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch93 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.12 | hwACPDCMA01CBranch91Current | Branch91 Current | 支路91电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch91 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.13 | hwACPDCMA01CBranch92Current | Branch92 Current | 支路92电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch92 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.14 | hwACPDCMA01CBranch93Current | Branch93 Current | 支路93电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch93 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.15 | hwACPDCMA01CBranch91ActivePower | Branch91 Active power | 支路91有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch91 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.16 | hwACPDCMA01CBranch92ActivePower | Branch92 Active power | 支路92有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch92 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.17 | hwACPDCMA01CBranch93ActivePower | Branch93 Active power | 支路93有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch93 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.18 | hwACPDCMA01CBranch91ActiveElectricEnergy | Branch91 Active electric energy | 支路91有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch91 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.19 | hwACPDCMA01CBranch92ActiveElectricEnergy | Branch92 Active electric energy | 支路92有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch92 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.20 | hwACPDCMA01CBranch93ActiveElectricEnergy | Branch93 Active electric energy | 支路93有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch93 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.21 | hwACPDCMA01CBranch94Voltage | Branch94 Voltage | 支路94电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch94 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.22 | hwACPDCMA01CBranch95Voltage | Branch95 Voltage | 支路95电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch95 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.23 | hwACPDCMA01CBranch96Voltage | Branch96 Voltage | 支路96电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch96 Voltage of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.24 | hwACPDCMA01CBranch94Current | Branch94 Current | 支路94电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch94 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.25 | hwACPDCMA01CBranch95Current | Branch95 Current | 支路95电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch95 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.26 | hwACPDCMA01CBranch96Current | Branch96 Current | 支路96电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch96 Current of the device config table for the AC_PDC_MA01C.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.27 | hwACPDCMA01CBranch94ActivePower | Branch94 Active power | 支路94有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch94 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.28 | hwACPDCMA01CBranch95ActivePower | Branch95 Active power | 支路95有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch95 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.29 | hwACPDCMA01CBranch96ActivePower | Branch96 Active power | 支路96有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch96 Active power of the device config table for the AC_PDC_MA01C.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.30 | hwACPDCMA01CBranch94ActiveElectricEnergy | Branch94 Active electric energy | 支路94有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch94 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.31 | hwACPDCMA01CBranch95ActiveElectricEnergy | Branch95 Active electric energy | 支路95有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch95 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.32 | hwACPDCMA01CBranch96ActiveElectricEnergy | Branch96 Active electric energy | 支路96有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Branch96 Active electric energy of the device config table for the AC_PDC_MA01C.Multiple:10.SigUnitInfo:KWh.
1.3.6.1.4.1.2011.6.178.1.1.86.5.1.101 | hwACPDCMA01CRunning5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.6 | hwACPDCMA01CConfig6Table | / | / |  |  | / | / | The config table of AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.6.1.1 | hwACPDCMA01CConfig6Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.6.1.2 | hwACPDCMA01CDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.6.1.3 | hwACPDCMA01CInputCableMode | Input cable mode | 进线模式 | 1-Read_Write | 读写 | singlepowersupply(1), dualpowersupply(2), unknown(255) | [单路供电=1]/[双路供电=2] | Input cable mode of the device config table for the AC_PDC_MA01C. Value 1 indicate single power supply Value 2 indicate dual power supply
1.3.6.1.4.1.2011.6.178.1.1.86.6.1.4 | hwACPDCMA01CSinglePowerSupplyBranchNum | Branch num | 支路路数 | 1-Read_Write | 读写 | 0..96 | 0..96 | branch num of the device config table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.6.1.5 | hwACPDCMA01CInputCableSpdStatus | Input cable - SPD status | 进线-防雷器状态 | 0-Read_Only | 只读 | normal(1), alarm(2), notenabled(3), unknown(255) | [正常=1]/[告警=2]/[未启用=3] | Input cable SPD status of the device config table for the AC_PDC_MA01C. Value 1 indicate normal Value 2 indicate alarm Value 3 indicate not enabled
1.3.6.1.4.1.2011.6.178.1.1.86.6.1.6 | hwACPDCMA01CDualPowerSupplyBranchNum | Branch num | 支路路数 | 1-Read_Write | 读写 | 0..48 | 0..48 | branch num of the device config table for the AC_PDC_MA01C.
1.3.6.1.4.1.2011.6.178.1.1.86.6.1.101 | hwACPDCMA01CConfig6RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of AC_PDC_MA01C.

## ATS cabinet
ATS柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.8.2 | ATScabinet | ATS cabinet | ATS柜 | / | / | / | / | ATS cabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1 | hwATScabinetRunningAndConfigTable | / | / |  |  | / | / | The running table of ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.1 | hwATScabinetRunningAndConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.2 | hwATScabinetS1Feedback | S1 Feedback | S1开关/触头状态 | 0-Read_Only | 只读 | open(1), close(2), tripping(3), unknown(255) | [分闸=1]/[合闸=2]/[脱扣=3] | S1 Feedback of the device config table for the ATS cabinet. Value 1 indicate open Value 2 indicate close Value 3 indicate tripping
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.3 | hwATScabinetS2Feedback | S2 Feedback | S2开关/触头状态 | 0-Read_Only | 只读 | open(1), close(2), tripping(3), unknown(255) | [分闸=1]/[合闸=2]/[脱扣=3] | S2 Feedback of the device config table for the ATS cabinet. Value 1 indicate open Value 2 indicate close Value 3 indicate tripping
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.4 | hwATScabinetS1Uab | S1 UAB | S1UAB线电压 | 0-Read_Only | 只读 | 0..418 | 0..418 | S1 UAB of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.5 | hwATScabinetS1Ubc | S1 UBC | S1UBC线电压 | 0-Read_Only | 只读 | 0..418 | 0..418 | S1 UBC of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.6 | hwATScabinetS1Uca | S1 UCA | S1UCA线电压 | 0-Read_Only | 只读 | 0..418 | 0..418 | S1 UCA of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.7 | hwATScabinetS2Uab | S2 UAB | S2UAB线电压 | 0-Read_Only | 只读 | 0..418 | 0..418 | S2 UAB of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.8 | hwATScabinetS2Ubc | S2 UBC | S2UBC线电压 | 0-Read_Only | 只读 | 0..418 | 0..418 | S2 UBC of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.9 | hwATScabinetS2Uca | S2 UCA | S2UCA线电压 | 0-Read_Only | 只读 | 0..418 | 0..418 | S2 UCA of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.10 | hwATScabinetAlarm | Alarm | 报警 | 0-Read_Only | 只读 | noalarm(1), alarm(2), unknown(255) | [不报警=1]/[报警=2] | Alarm of the device config table for the ATS cabinet. Value 1 indicate no alarm Value 2 indicate alarm
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.11 | hwATScabinetS1PowerStatus | S1 power status | S1电压状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [不正常=1]/[正常=2] | S1 power status of the device config table for the ATS cabinet. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.12 | hwATScabinetS2PowerStatus | S2 power status | S2电压状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [不正常=1]/[正常=2] | S2 power status of the device config table for the ATS cabinet. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.13 | hwATScabinet001ActionOrFaultCode | 001 Action or fault code | 记录一 动作或故障码 | 0-Read_Only | 只读 | s1tos2(1), s2tos1(2), s1tobipartition(3), s2tobipartition(4), bipartitiontos1(5), bipartitiontos2(6), s1switchtrip(7), s2switchtrip(8), reserved(9), conversiontimeout(10), dualcombinationfault(11), doublesplitfault(12), frequentlyswitchover6timespermin(13), unknown(255) | [S1转至S2=1]/[S2转至S1=2]/[S1转至双分=3]/[S2转至双分=4]/[双分转至S1=5]/[双分转至S2=6]/[S1开关脱扣=7]/[S2开关脱扣=8]/[保留=9]/[转换超时=10]/[双合故障=11]/[双分故障=12]/[频繁切换>6次/min=13] | 001 Action or fault code of the device config table for the ATS cabinet. Value 1 indicate s1 to s2 Value 2 indicate s2 to s1 Value 3 indicate s1 to bi partition Value 4 indicate s2 to bi partition Value 5 indicate bi partition to s1 Value 6 indicate bi partition to s2 Value 7 indicate s1 switch trip Value 8 indicate s2 switch trip Value 9 indicate reserved Value 10 indicate conversion timeout Value 11 indicate dual-combination fault Value 12 indicate double split fault Value 13 frequently switch over 6 times/min
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.14 | hwATScabinet002ActionOrFaultCode | 002 Action or fault code | 记录二 动作或故障码 | 0-Read_Only | 只读 | s1tos2(1), s2tos1(2), s1tobipartition(3), s2tobipartition(4), bipartitiontos1(5), bipartitiontos2(6), s1switchtrip(7), s2switchtrip(8), reserved(9), conversiontimeout(10), dualcombinationfault(11), doublesplitfault(12), frequentlyswitchover6timespermin(13), unknown(255) | [S1转至S2=1]/[S2转至S1=2]/[S1转至双分=3]/[S2转至双分=4]/[双分转至S1=5]/[双分转至S2=6]/[S1开关脱扣=7]/[S2开关脱扣=8]/[保留=9]/[转换超时=10]/[双合故障=11]/[双分故障=12]/[频繁切换>6次/min=13] | 002 Action or fault code of the device config table for the ATS cabinet. Value 1 indicate s1 to s2 Value 2 indicate s2 to s1 Value 3 indicate s1 to bi partition Value 4 indicate s2 to bi partition Value 5 indicate bi partition to s1 Value 6 indicate bi partition to s2 Value 7 indicate s1 switch trip Value 8 indicate s2 switch trip Value 9 indicate reserved Value 10 indicate conversion timeout Value 11 indicate dual-combination fault Value 12 indicate double split fault Value 13 frequently switch over 6 times/min
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.15 | hwATScabinet003ActionOrFaultCode | 003 Action or fault code | 记录三 动作或故障码 | 0-Read_Only | 只读 | s1tos2(1), s2tos1(2), s1tobipartition(3), s2tobipartition(4), bipartitiontos1(5), bipartitiontos2(6), s1switchtrip(7), s2switchtrip(8), reserved(9), conversiontimeout(10), dualcombinationfault(11), doublesplitfault(12), frequentlyswitchover6timespermin(13), unknown(255) | [S1转至S2=1]/[S2转至S1=2]/[S1转至双分=3]/[S2转至双分=4]/[双分转至S1=5]/[双分转至S2=6]/[S1开关脱扣=7]/[S2开关脱扣=8]/[保留=9]/[转换超时=10]/[双合故障=11]/[双分故障=12]/[频繁切换>6次/min=13] | 003 Action or fault code of the device config table for the ATS cabinet. Value 1 indicate s1 to s2 Value 2 indicate s2 to s1 Value 3 indicate s1 to bi partition Value 4 indicate s2 to bi partition Value 5 indicate bi partition to s1 Value 6 indicate bi partition to s2 Value 7 indicate s1 switch trip Value 8 indicate s2 switch trip Value 9 indicate reserved Value 10 indicate conversion timeout Value 11 indicate dual-combination fault Value 12 indicate double split fault Value 13 frequently switch over 6 times/min
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.16 | hwATScabinet004ActionOrFaultCode | 004 Action or fault code | 记录四 动作或故障码 | 0-Read_Only | 只读 | s1tos2(1), s2tos1(2), s1tobipartition(3), s2tobipartition(4), bipartitiontos1(5), bipartitiontos2(6), s1switchtrip(7), s2switchtrip(8), reserved(9), conversiontimeout(10), dualcombinationfault(11), doublesplitfault(12), frequentlyswitchover6timespermin(13), unknown(255) | [S1转至S2=1]/[S2转至S1=2]/[S1转至双分=3]/[S2转至双分=4]/[双分转至S1=5]/[双分转至S2=6]/[S1开关脱扣=7]/[S2开关脱扣=8]/[保留=9]/[转换超时=10]/[双合故障=11]/[双分故障=12]/[频繁切换>6次/min=13] | 004 Action or fault code of the device config table for the ATS cabinet. Value 1 indicate s1 to s2 Value 2 indicate s2 to s1 Value 3 indicate s1 to bi partition Value 4 indicate s2 to bi partition Value 5 indicate bi partition to s1 Value 6 indicate bi partition to s2 Value 7 indicate s1 switch trip Value 8 indicate s2 switch trip Value 9 indicate reserved Value 10 indicate conversion timeout Value 11 indicate dual-combination fault Value 12 indicate double split fault Value 13 frequently switch over 6 times/min
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.17 | hwATScabinet005ActionOrFaultCode | 005 Action or fault code | 记录五 动作或故障码 | 0-Read_Only | 只读 | s1tos2(1), s2tos1(2), s1tobipartition(3), s2tobipartition(4), bipartitiontos1(5), bipartitiontos2(6), s1switchtrip(7), s2switchtrip(8), reserved(9), conversiontimeout(10), dualcombinationfault(11), doublesplitfault(12), frequentlyswitchover6timespermin(13), unknown(255) | [S1转至S2=1]/[S2转至S1=2]/[S1转至双分=3]/[S2转至双分=4]/[双分转至S1=5]/[双分转至S2=6]/[S1开关脱扣=7]/[S2开关脱扣=8]/[保留=9]/[转换超时=10]/[双合故障=11]/[双分故障=12]/[频繁切换>6次/min=13] | 005 Action or fault code of the device config table for the ATS cabinet. Value 1 indicate s1 to s2 Value 2 indicate s2 to s1 Value 3 indicate s1 to bi partition Value 4 indicate s2 to bi partition Value 5 indicate bi partition to s1 Value 6 indicate bi partition to s2 Value 7 indicate s1 switch trip Value 8 indicate s2 switch trip Value 9 indicate reserved Value 10 indicate conversion timeout Value 11 indicate dual-combination fault Value 12 indicate double split fault Value 13 frequently switch over 6 times/min
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.18 | hwATScabinetControllerStatus | Controller status | 控制器状态 | 0-Read_Only | 只读 | auto(1), communication(2), remote(3), pushbutton(4), forbidden(5), fireprotection(6), exit(7), unknown(255) | [自动=1]/[通讯=2]/[远程=3]/[按键=4]/[禁止=5]/[消防=6]/[退出=7] | Controller status of the device config table for the ATS cabinet. Value 1 indicate auto Value 2 indicate communication Value 3 indicate remote Value 4 indicate push button Value 5 indicate forbidden Value 6 indicate fire protection Value 7 indicate exit
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.19 | hwATScabinetCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the ATS cabinet. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.20 | hwATScabinetPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.21 | hwATScabinetModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.22 | hwATScabinetRecord1Time | Record 1 time | 记录1时间 | 0-Read_Only | 只读 | 0..20 | 0..20 | Record 1 time of the device config table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.23 | hwATScabinetRecord2Time | Record 2 time | 记录2时间 | 0-Read_Only | 只读 | 0..20 | 0..20 | Record 2 time of the device config table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.24 | hwATScabinetRecord3Time | Record 3 time | 记录3时间 | 0-Read_Only | 只读 | 0..20 | 0..20 | Record 3 time of the device config table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.25 | hwATScabinetRecord4Time | Record 4 time | 记录4时间 | 0-Read_Only | 只读 | 0..20 | 0..20 | Record 4 time of the device config table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.26 | hwATScabinetRecord5Time | Record 5 time | 记录5时间 | 0-Read_Only | 只读 | 0..20 | 0..20 | Record 5 time of the device config table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.27 | hwATScabinetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the ATS cabinet.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.28 | hwATScabinetS1UvDropOut | S1 UV drop out | S1欠压阈值 | 1-Read_Write | 读写 | 290..330 | 290..330 | S1 UV drop out of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.29 | hwATScabinetS1OvDropOut | S1 OV drop out | S1过压阈值 | 1-Read_Write | 读写 | 420..460 | 420..460 | S1 OV drop out of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.30 | hwATScabinetS2UvDropOut | S2 UV drop out | S2欠压阈值 | 1-Read_Write | 读写 | 290..330 | 290..330 | S2 UV drop out of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.31 | hwATScabinetS2OvDropOut | S2 OV drop out | S2过压阈值 | 1-Read_Write | 读写 | 420..460 | 420..460 | S2 OV drop out of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.32 | hwATScabinetTdNET1 | TD N-E | 市电-市电延时T1 | 1-Read_Write | 读写 | 0..300 | 0..300 | TD N-E of the device config table for the ATS cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.33 | hwATScabinetTdENT2 | TD E-N | 市电-市电延时T2 | 1-Read_Write | 读写 | 0..30 | 0..30 | TD E-N of the device config table for the ATS cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.34 | hwATScabinetTdPtT3 | TD PT | 市电-市电延时T3 | 1-Read_Write | 读写 | 0..60 | 0..60 | TD PT of the device config table for the ATS cabinet.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.35 | hwATScabinetTdNE | TD N-E | 市电-发电机延时T1 | 1-Read_Write | 读写 | 0..300 | 0..300 | TD N-E of the device config table for the ATS cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.36 | hwATScabinetTdEN | TD E-N | 市电-发电机延时T2 | 1-Read_Write | 读写 | 0..30 | 0..30 | TD E-N of the device config table for the ATS cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.37 | hwATScabinetTdPt | TD PT | 市电-发电机延时T3 | 1-Read_Write | 读写 | 0..60 | 0..60 | TD PT of the device config table for the ATS cabinet.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.38 | hwATScabinetTdEs | TD ES | 市电-发电机延时T5 | 1-Read_Write | 读写 | 0..300 | 0..300 | TD ES of the device config table for the ATS cabinet.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.39 | hwATScabinetTdEc | TD EC | 市电-发电机延时T6 | 1-Read_Write | 读写 | 0..60 | 0..60 | TD EC of the device config table for the ATS cabinet.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.40 | hwATScabinetPowerType | Power type | 电源类型设置 | 1-Read_Write | 读写 | mainsandmains(1), mainsandgenerator(2), unknown(255) | [市电-市电=1]/[市电-发电机=2] | Power type of the device config table for the ATS cabinet. Value 1 indicate mains-mains Value 2 indicate mains-generator
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.41 | hwATScabinetWorkMode | Work mode | 工作模式 | 1-Read_Write | 读写 | selfinjectionsandselfrecovery(1), selfinjectionwithoutselfrecovery(2), standbyforeachother(3), unknown(255) | [自投自复=1]/[自投不自复=2]/[互为备用=3] | Work mode of the device config table for the ATS cabinet. Value 1 indicate self-injections and self-recovery Value 2 indicate self-injection with out self-recovery Value 3 indicate standby for each other
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.42 | hwATScabinetYear | Year | 设置年 | 1-Read_Write | 读写 | 1999..2037 | 1999..2037 | Year of the device config table for the ATS cabinet.SigUnitInfo:year.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.43 | hwATScabinetMonth | Month | 设置月 | 1-Read_Write | 读写 | 1..12 | 1..12 | Month of the device config table for the ATS cabinet.SigUnitInfo:month.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.44 | hwATScabinetDay | Day | 设置日 | 1-Read_Write | 读写 | 1..31 | 1..31 | Day of the device config table for the ATS cabinet.SigUnitInfo:day.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.45 | hwATScabinetHour | Hour | 设置时 | 1-Read_Write | 读写 | 0..24 | 0..24 | Hour of the device config table for the ATS cabinet.SigUnitInfo:hour.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.46 | hwATScabinetMin | Min | 设置分 | 1-Read_Write | 读写 | 0..60 | 0..60 | Min of the device config table for the ATS cabinet.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.47 | hwATScabinetMainPower | Main power | 主电选择 | 1-Read_Write | 读写 | mainpowersupplys1(1), mainpowersupplys2(2), unknown(255) | [S1为主电源=1]/[S2为主电源=2] | Main power of the device config table for the ATS cabinet. Value 1 indicate main power supply s1 Value 2 indicate main power supply s2
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.48 | hwATScabinetS1UvPickUp | S1 UV pick up | S1欠压返回值 | 1-Read_Write | 读写 | 10..30 | 10..30 | S1 UV pick up of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.49 | hwATScabinetS1OvPickUp | S1 OV pick up | S1过压返回值 | 1-Read_Write | 读写 | 10..30 | 10..30 | S1 OV pick up of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.50 | hwATScabinetS2UvPickUp | S2 UV pick up | S2欠压返回值 | 1-Read_Write | 读写 | 10..30 | 10..30 | S2 UV pick up of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.51 | hwATScabinetS2OvPickUp | S2 OV pick up | S2过压返回值 | 1-Read_Write | 读写 | 10..30 | 10..30 | S2 OV pick up of the device config table for the ATS cabinet.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.52 | hwATScabinetExitComMode | Exit com mode | 退出通讯控制 | 1-Read_Write | 读写 | exitcommunicationcontrol(1) | [退出通讯控制=1] | Exit com mode of the device config table for the ATS cabinet. Value 1 indicate exit communication control
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.53 | hwATScabinetComMode | Com mode | 通讯控制 | 1-Read_Write | 读写 | bipartition(1), switchtos1(2), switchtos2(3), unknown(255) | [双分=1]/[投S1=2]/[投S2=3] | Com mode of the device config table for the ATS cabinet. Value 1 indicate bi partition Value 2 indicate switch to s1 Value 3 indicate switch to s2
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.54 | hwATScabinetLanguage | Language | 显示语言 | 1-Read_Write | 读写 | chinese(1), english(2), unknown(255) | [中文=1]/[英文=2] | Language of the device config table for the ATS cabinet. Value 1 indicate Chinese Value 2 indicate English
1.3.6.1.4.1.2011.6.178.1.1.8.2.1.1.300 | hwATScabinetRunningAndConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of ATS cabinet.

## ATS Abb-mx250
ATS Abb-mx250
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.8.3 | ATSAbbmx250 | ATS Abb-mx250 | ATS Abb-mx250 | / | / | / | / | ATS Abb-mx250 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1 | hwATSAbbMx250RunningAndConfig1Table | / | / |  |  | / | / | The running table of ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.1 | hwATSAbbMx250RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.2 | hwATSAbbMx250ContactWear | Contact wear | 触点磨损 | 0-Read_Only | 只读 | 0..100 | 0..100 | Contact wear of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.3 | hwATSAbbMx250TotalOpearations | Total opearations | 总操作次数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Total opearations of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.4 | hwATSAbbMx250NumberOfLoadTransfers | Number of load transfers | 负载转换次数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Number of load transfers of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.5 | hwATSAbbMx250TransferTime | Transfer time | 转换时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Transfer time of the device config table for the ATS Abb-mx250.SigUnitInfo:ms.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.6 | hwATSAbbMx250SourceFailTransfers | Source fail transfers | 电源失效转换次数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source fail transfers of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.7 | hwATSAbbMx250DaysEnergized | Days energized | 通电天数 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Days energized of the device config table for the ATS Abb-mx250.SigUnitInfo:d.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.8 | hwATSAbbMx250Source1Connected | Source 1 connected | 电源1已连接 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Switch in position I of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.9 | hwATSAbbMx250ManualRetransferRequired | Manual retransfer required | 需要自投不自复 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Manual retransfer required of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.10 | hwATSAbbMx250ControlAlarm | Control alarm | 控制单元告警 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Alarm active of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.11 | hwATSAbbMx250Source1OK | Source 1 OK | 电源1正常 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Source 1 OK of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.12 | hwATSAbbMx250AutoConfigActive | Auto config active | 自动配置激活 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Active of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.13 | hwATSAbbMx250AutoConfigReady | Auto config ready | 自动配置就绪 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Configuration ready of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.14 | hwATSAbbMx250AutomaticMode | Automatic mode | 自动模式 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Automatic of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.15 | hwATSAbbMx250Source2Connected | Source 2 connected | 电源2已连接 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Switch in position II of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.16 | hwATSAbbMx250LocalOrRemote | Local / Remote | 本地/远程 | 0-Read_Only | 只读 | local(1), remote(2), unknown(255) | [本地=1]/[远程=2] | Remote of the device config table for the ATS Abb-mx250. Value 1 indicate local Value 2 indicate remote
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.17 | hwATSAbbMx250Source2Ok | Source 2 OK | 电源2正常 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Source 2 OK of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.18 | hwATSAbbMx250SupplyFromAuxiliaryVoltageOn | Supply from auxiliary voltage on | 辅助电压供电打开 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Supply from auxiliary voltage on of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.19 | hwATSAbbMx250SupplyFromPowerModuleOn | Supply from power module on | 电源模块供电打开 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Supply from power module on of the device config table for the ATS Abb-mx250. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.20 | hwATSAbbMx250GeneratorUsage | Generator usage | 发电机使用 | 0-Read_Only | 只读 | noGenerator(1), generatorInUse(2), unknown(255) | [无发电机=1]/[发电机在使用中=2] | Generator usage of the device config table for the ATS Abb-mx250. Value 1 indicate no generator Value 2 indicate generator in use
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.21 | hwATSAbbMx250GeneratorStatus | Generator status | 发电机状态 | 0-Read_Only | 只读 | generatorStopped(1), generatorStarted(2), unknown(255) | [发电机停止=1]/[发电机启动 =2] | Generator status of the device config table for the ATS Abb-mx250. Value 1 indicate generator stopped Value 2 indicate generator started
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.22 | hwATSAbbMx250L1Current | L1 current | L1电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | L1 current of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.23 | hwATSAbbMx250L2Current | L2 current | L2电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | L2 current of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.24 | hwATSAbbMx250L3Current | L3 current | L3电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | L3 current of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.25 | hwATSAbbMx250NeCurrent | Ne current | Ne电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Ne current of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.26 | hwATSAbbMx250InternalGroundCurrent | Internal ground current | 内部接地电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Internal ground current of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.27 | hwATSAbbMx250MaximumCurrent | Maximum current | 最大电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Maximum current of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.28 | hwATSAbbMx250MaximumCurrentPhase | Maximum current phase | 最大电流相位 | 0-Read_Only | 只读 | l1(1), l2(2), l3(3), ne(4), unknown(255) | [L1=1]/[L2=2]/[L3=3]/[Ne=4] | Maximum current phase of the device config table for the ATS Abb-mx250. Value 1 indicate L1 Value 2 indicate L2 Value 3 indicate L3 Value 4 indicate Ne
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.29 | hwATSAbbMx250Source1U1 | Source 1 U1 | 电源1 U1 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 1 U1 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.30 | hwATSAbbMx250Source1U2 | Source 1 U2 | 电源1 U2 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 1 U2 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.31 | hwATSAbbMx250Source1U3 | Source 1 U3 | 电源1 U3 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 1 U3 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.32 | hwATSAbbMx250Source1U0 | Source 1 U0 | 电源1 U0 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 1 U0 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.33 | hwATSAbbMx250Source1U12 | Source 1 U12 | 电源1 U12 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 1 U12 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.34 | hwATSAbbMx250Source1U23 | Source 1 U23 | 电源1 U23 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 1 U23 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.35 | hwATSAbbMx250Source1U31 | Source 1 U31 | 电源1 U31 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 1 U31 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.36 | hwATSAbbMx250Source1Umax | Source 1 Umax | 电源1 Umax | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 1 Umax of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.37 | hwATSAbbMx250Source1MaxPhase | Source 1 max phase | 电源1最大相位 | 0-Read_Only | 只读 | u1OrU12(1), u2OrU23(2), u3OrU31(3), unknown(255) | [U1/U12=1]/[U2/U23=2]/[U3/U31=3] | Source 1 max phase of the device config table for the ATS Abb-mx250. Value 1 indicate U1/U12 Value 2 indicate U2/U23 Value 3 indicate U3/U31
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.38 | hwATSAbbMx250Source2U1 | Source 2 U1 | 电源2 U1 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 2 U1 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.39 | hwATSAbbMx250Source2U2 | Source 2 U2 | 电源2 U2 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 2 U2 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.40 | hwATSAbbMx250Source2U3 | Source 2 U3 | 电源2 U3 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 2 U3 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.41 | hwATSAbbMx250Source2U0 | Source 2 U0 | 电源2 U0 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 2 U0 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.42 | hwATSAbbMx250Source2U12 | Source 2 U12 | 电源2 U12 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 2 U12 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.43 | hwATSAbbMx250Source2U23 | Source 2 U23 | 电源2 U23 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 2 U23 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.44 | hwATSAbbMx250Source2U31 | Source 2 U31 | 电源2 U31 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 2 U31 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.45 | hwATSAbbMx250Source2Umax | Source 2 umax | 电源2 Umax | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Source 2 umax of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.46 | hwATSAbbMx250Source2MaxPhase | Source 2 max phase | 电源2最大相位 | 0-Read_Only | 只读 | u1OrU12(1), u2OrU23(2), u3OrU31(3), unknown(255) | [U1/U12=1]/[U2/U23=2]/[U3/U31=3] | Source 2 max phase of the device config table for the ATS Abb-mx250. Value 1 indicate U1/U12 Value 2 indicate U2/U23 Value 3 indicate U3/U31
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.47 | hwATSAbbMx250ActivePowerL1 | Active power L1 | 有功功率L1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active power L1 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.48 | hwATSAbbMx250ActivePowerL2 | Active power L2 | 有功功率L2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active power L2 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.49 | hwATSAbbMx250ActivePowerL3 | Active power L3 | 有功功率L3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active power L3 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.50 | hwATSAbbMx250ActivePowerTotal | Active power total | 总有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active power total of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.51 | hwATSAbbMx250ReactivePowerL1 | Reactive power L1 | 无功功率L1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Reactive power L1 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.52 | hwATSAbbMx250ReactivePowerL2 | Reactive power L2 | 无功功率L2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Reactive power L2 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.53 | hwATSAbbMx250ReactivePowerL3 | Reactive power L3 | 无功功率L3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Reactive power L3 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.54 | hwATSAbbMx250ReactivePowerTotal | Reactive power total | 总无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Reactive power total of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.55 | hwATSAbbMx250ApparentPowerL1 | Apparent power L1 | 视在功率L1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Apparent power L1 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.56 | hwATSAbbMx250ApparentPowerL2 | Apparent power L2 | 视在功率L2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Apparent power L2 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.57 | hwATSAbbMx250ApparentPowerL3 | Apparent power L3 | 视在功率L3 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Apparent power L3 of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.58 | hwATSAbbMx250ApparentPowerTotal | Apparent power total | 总视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Apparent power total of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.59 | hwATSAbbMx250PowerFactorTotal | Power factor total | 总功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Power factor total of the device config table for the ATS Abb-mx250.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.60 | hwATSAbbMx250Source1Frequency | Source 1 frequency | 电源1频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Source 1 frequency of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.61 | hwATSAbbMx250Source2Frequency | Source 2 frequency | 电源2频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Source 2 frequency of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.62 | hwATSAbbMx250TemperaturePole1 | Temperature pole 1 | 电极温度1 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Temperature pole 1 of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.63 | hwATSAbbMx250TemperaturePole2 | Temperature pole 2 | 电极温度2 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Temperature pole 2 of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.64 | hwATSAbbMx250TemperaturePole3 | Temperature pole 3 | 电极温度3 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Temperature pole 3 of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.65 | hwATSAbbMx250TemperaturePole4 | Temperature pole 4 | 电极温度4 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Temperature pole 4 of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.66 | hwATSAbbMx250GeneratorStartingTime | Generator starting time | 发电机启动时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Generator starting time of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.67 | hwATSAbbMx250InPhaseTime | In-phase time | 同相时间 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | In-phase time of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.68 | hwATSAbbMx250TimeNormalAvailable | Time normal available | 正常可用时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Time normal available of the device config table for the ATS Abb-mx250.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.69 | hwATSAbbMx250TotalTimeOnNormal | Total time on normal | 正常态总时长 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total time on normal of the device config table for the ATS Abb-mx250.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.70 | hwATSAbbMx250TimeEmergencyAvailable | Time emergency available | 紧急态可用时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Time emergency available of the device config table for the ATS Abb-mx250.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.71 | hwATSAbbMx250TotalTimeOnEmergency | Total time on emergency | 紧急态总时长 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total time on emergency of the device config table for the ATS Abb-mx250.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.72 | hwATSAbbMx250ActiveEnergyS1 | Active energy S1 | 有功电能S1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active energy S1 of the device config table for the ATS Abb-mx250.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.73 | hwATSAbbMx250ActiveEnergyS2 | Active energy S2 | 有功电能S2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active energy S2 of the device config table for the ATS Abb-mx250.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.74 | hwATSAbbMx250ReactiveEnergyS1 | Reactive energy S1 | 无功电能S1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Reactive energy S1 of the device config table for the ATS Abb-mx250.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.75 | hwATSAbbMx250ReactiveEnergyS2 | Reactive energy S2 | 无功电能S2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Reactive energy S2 of the device config table for the ATS Abb-mx250.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.76 | hwATSAbbMx250ApparentEnergyS1 | Apparent energy S1 | 视在电能S1 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Apparent energy S1 of the device config table for the ATS Abb-mx250.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.77 | hwATSAbbMx250ApparentEnergyS2 | Apparent energy S2 | 视在电能S2 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Apparent energy S2 of the device config table for the ATS Abb-mx250.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.78 | hwATSAbbMx250ActiveEnergyTotal | Active energy total | 总有功电能 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Active energy total of the device config table for the ATS Abb-mx250.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.79 | hwATSAbbMx250ReactiveEnergyTotal | Reactive energy total | 总无功电能 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Reactive energy total of the device config table for the ATS Abb-mx250.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.80 | hwATSAbbMx250ApparentEnergyTotal | Apparent energy total | 总视在电能 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Apparent energy total of the device config table for the ATS Abb-mx250.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.81 | hwATSAbbMx250VoltageSource1U1orU12Thd | Voltage source 1 U1/U12 THD | 电压源1 U1/U12 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage source 1 U1/U12 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.82 | hwATSAbbMx250VoltageSource1U2orU23Thd | Voltage source 1 U2/U23 THD | 电压源1 U2/U23 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage source 1 U2/U23 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.83 | hwATSAbbMx250VoltageSource1U3orU31Thd | Voltage source 1 U3/U31 THD | 电压源1 U3/U31 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage source 1 U3/U31 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.84 | hwATSAbbMx250VoltageSource2U1orU12Thd | Voltage source 2 U1/U12 THD | 电压源2 U1/U12 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage source 2 U1/U12 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.85 | hwATSAbbMx250VoltageSource2U2orU23Thd | Voltage source 2 U2/U23 THD | 电压源2 U2/U23 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage source 2 U2/U23 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.86 | hwATSAbbMx250VoltageSource2U3orU31Thd | Voltage source 2 U3/U31 THD | 电压源2 U3/U31 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage source 2 U3/U31 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.87 | hwATSAbbMx250CurrentI1Thd | Current I1 THD | 电流I1 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current I1 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.88 | hwATSAbbMx250CurrentI2Thd | Current I2 THD | 电流I2 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current I2 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.89 | hwATSAbbMx250CurrentI3Thd | Current I3 THD | 电流I3 THD | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Current I3 THD of the device config table for the ATS Abb-mx250.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.90 | hwATSAbbMx250SoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Software version of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.91 | hwATSAbbMx250NominalCurrent | Nominal current | 标称电流 | 0-Read_Only | 只读 | 30..4000 | 30..4000 | Nominal current of the device config table for the ATS Abb-mx250.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.92 | hwATSAbbMx250NumberOfSwitchPositions | Number of switch positions | 开关位置数 | 0-Read_Only | 只读 | iAndOAndII(1), iAndII(2), unknown(255) | [I-O-II=1]/[I-II=2] | Number of switch positions of the device config table for the ATS Abb-mx250. Value 1 indicate I-O-II Value 2 indicate I-II
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.93 | hwATSAbbMx250SerialNumber | Serial number | 序列号 | 0-Read_Only | 只读 | 0..16 | 0..16 | Serial number of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.94 | hwATSAbbMx250TypeDesignation | Type designation | 类型名称 | 0-Read_Only | 只读 | 0..16 | 0..16 | Type designation of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.95 | hwATSAbbMx250NumberOfPoles | Number of poles | 极数 | 0-Read_Only | 只读 | 2..4 | 2..4 | Number of poles of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.96 | hwATSAbbMx250CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the ATS Abb-mx250. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.97 | hwATSAbbMx250PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.98 | hwATSAbbMx250ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.99 | hwATSAbbMx250SetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the ATS Abb-mx250.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.100 | hwATSAbbMx250SetSource1PowerDistributionSystem | Source 1 power distribution system | 电源1配电系统 | 1-Read_Write | 读写 | onepPhaseTowWire(1), towPhaseThreeWire(2), threePhaseNotWithN(3), threePhaseWithN(4), threePhaseFourWireHighLegDelta(5), unknown(255) | [1相2线=1]/[2相3线=2]/[3相不含N=3]/[3相含N=4]/[3相4线高段=5] | Source 1 power distribution system of the device config table for the ATS Abb-mx250. Value 1 indicate 1 phase 2 wire Value 2 indicate 2 phase 3 wire Value 3 indicate 3 phase w/o n Value 4 indicate 3 phase with n Value 5 indicate 3 phase 4 wire high leg delta
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.101 | hwATSAbbMx250SetSource2PowerDistributionSystem | Source 2 power distribution system | 电源2配电系统 | 1-Read_Write | 读写 | onepPhaseTowWire(1), towPhaseThreeWire(2), threePhaseNotWithN(3), threePhaseWithN(4), threePhaseFourWireHighLegDelta(5), unknown(255) | [1相2线=1]/[2相3线=2]/[3相不含N=3]/[3相含N=4]/[3相4线高段=5] | Source 2 power distribution system of the device config table for the ATS Abb-mx250. Value 1 indicate 1 phase 2 wire Value 2 indicate 2 phase 3 wire Value 3 indicate 3 phase w/o n Value 4 indicate 3 phase with n Value 5 indicate 3 phase 4 wire high leg delta
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.102 | hwATSAbbMx250SetOverrideS1FailureDelay | Override S1 failure delay | S1断电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | Override S1 failure delay of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.103 | hwATSAbbMx250SetTransferFromS1ToS2Delay | Transfer from S1 to S2 delay | S1到S2的转换延时 | 1-Read_Write | 读写 | 0..300 | 0..300 | Transfer from S1 to S2 delay of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.104 | hwATSAbbMx250SetOverrideS2FailureDelay | Override S2 failure delay | S2断电延时 | 1-Read_Write | 读写 | 0..3600 | 0..3600 | Override S2 failure delay of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.105 | hwATSAbbMx250SetRatedVoltage | Rated voltage | 额定电压 | 1-Read_Write | 读写 | twoHundredV(1), twoHundredAndEightV(2), twoHundredAndTwentyV(3), twoHundredAndThirtyV(4), twoHundredAndFortyV(5), twoHundredAndSeventySevenV(6), threeHundredAndFortySevenV(7), threeHundredAndEightyV(8), fourHundredV(9), fourHundredAndFifteenV(10), fourHundredAndFortyV(11), fourHundredAndSixtyV(12), fourHundredAndEightyV(13), unknown(255) | [200 V=1]/[208 V=2]/[220 V=3]/[230 V=4]/[240 V=5]/[277 V=6]/[347 V=7]/[380 V=8]/[400 V=9]/[415 V=10]/[440 V=11]/[460 V=12]/[480 V=13] | Rated voltage of the device config table for the ATS Abb-mx250. Value 1 indicate 200v Value 2 indicate 208v Value 3 indicate 220v Value 4 indicate 230v Value 5 indicate 240v Value 6 indicate 277v Value 7 indicate 347v Value 8 indicate 380v Value 9 indicate 400v Value 10 indicate 415v Value 11 indicate 440v Value 12 indicate 460v Value 13 indicate 480v
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.106 | hwATSAbbMx250SetTransferFromS2ToS1Delay | Transfer from S2 to S1 delay | S2到S1的转换延时 | 1-Read_Write | 读写 | 0..3600 | 0..3600 | Transfer from S2 to S1 delay of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.107 | hwATSAbbMx250SetGeneratorStopDelay | Generator stop delay | 发电机停止延时 | 1-Read_Write | 读写 | 0..60 | 0..60 | Generator stop delay of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.108 | hwATSAbbMx250SetCenterOffDelay | Center-off delay | 中间双分位断开延时 | 1-Read_Write | 读写 | 0..600 | 0..600 | Center-off delay of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.109 | hwATSAbbMx250SetLoadShedDelay | Load shed delay | 负载卸载延时 | 1-Read_Write | 读写 | 0..60 | 0..60 | Load shed delay of the device config table for the ATS Abb-mx250.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.110 | hwATSAbbMx250SetOperationMode | Operation mode | 操作模式 | 1-Read_Write | 读写 | auto(1), man(2), testOffLoad(3), testOnLoad(4), unknown(255) | [自动=1]/[人工=2]/[空载测试=3]/[负载测试=4] | Operation mode of the device config table for the ATS Abb-mx250. Value 1 indicate auto Value 2 indicate man Value 3 indicate test off load Value 4 indicate test on load
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.111 | hwATSAbbMx250SetAutomaticMode | Automatic mode | 自动模式 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关=1]/[开=2] | Automatic mode of the device config table for the ATS Abb-mx250. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.112 | hwATSAbbMx250SetS1DropoutVoltageHigh | S1 dropout voltage high | 电源1恢复电压高 | 1-Read_Write | 读写 | 102..120 | 102..120 | S1 dropout voltage high of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.113 | hwATSAbbMx250SetS1DropoutVoltageLow | S1 dropout voltage low | 电源1恢复电压低 | 1-Read_Write | 读写 | 85..100 | 85..100 | S1 dropout voltage low of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.114 | hwATSAbbMx250SetS1PickupVoltageHigh | S1 pickup voltage high | 电源1动作电压高 | 1-Read_Write | 读写 | 101..119 | 101..119 | S1 pickup voltage high of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.115 | hwATSAbbMx250SetS1PickupVoltageLow | S1 pickup voltage low | 电源1动作电压低 | 1-Read_Write | 读写 | 75..99 | 75..99 | S1 pickup voltage low of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.116 | hwATSAbbMx250SetS1DropoutFrequencyHigh | S1 dropout frequency high | 电源1恢复频率高 | 1-Read_Write | 读写 | 102..104 | 102..104 | S1 dropout frequency high of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.117 | hwATSAbbMx250SetS1DropoutFrequencyLow | S1 dropout frequency low | 电源1恢复频率低 | 1-Read_Write | 读写 | 90..100 | 90..100 | S1 dropout frequency low of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.118 | hwATSAbbMx250SetS1PickupFrequencyHigh | S1 pickup frequency high | 电源1动作频率高 | 1-Read_Write | 读写 | 1030..1050 | 1030..1050 | S1 pickup frequency high of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.119 | hwATSAbbMx250SetS1PickupFrequencyLow | S1 pickup frequency low | 电源1动作频率低 | 1-Read_Write | 读写 | 880..980 | 880..980 | S1 pickup frequency low of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.120 | hwATSAbbMx250SetS2DropoutVoltageHigh | S2 dropout voltage high | 电源2恢复电压高 | 1-Read_Write | 读写 | 103..105 | 103..105 | S2 dropout voltage high of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.121 | hwATSAbbMx250SetS2DropoutVoltageLow | S2 dropout voltage low | 电源2恢复电压低 | 1-Read_Write | 读写 | 80..100 | 80..100 | S2 dropout voltage low of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.122 | hwATSAbbMx250SetS2PickupVoltageHigh | S2 pickup voltage high | 电源2动作电压高 | 1-Read_Write | 读写 | 105..110 | 105..110 | S2 pickup voltage high of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.123 | hwATSAbbMx250SetS2PickupVoltageLow | S2 pickup voltage low | 电源2动作电压低 | 1-Read_Write | 读写 | 85..100 | 85..100 | S2 pickup voltage low of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.124 | hwATSAbbMx250SetS2DropoutFrequencyHigh | S2 dropout frequency high | 电源2恢复频率高 | 1-Read_Write | 读写 | 102..104 | 102..104 | S2 dropout frequency high of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.125 | hwATSAbbMx250SetS2DropoutFrequencyLow | S2 dropout frequency low | 电源2恢复频率低 | 1-Read_Write | 读写 | 90..100 | 90..100 | S2 dropout frequency low of the device config table for the ATS Abb-mx250.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.126 | hwATSAbbMx250SetS2PickupFrequencyHigh | S2 pickup frequency high | 电源2动作频率高 | 1-Read_Write | 读写 | 1030..1050 | 1030..1050 | S2 pickup frequency high of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.127 | hwATSAbbMx250SetS2PickupFrequencyLow | S2 pickup frequency low | 电源2动作频率低 | 1-Read_Write | 读写 | 880..980 | 880..980 | S2 pickup frequency low of the device config table for the ATS Abb-mx250.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.8.3.1.1.300 | hwATSAbbMx250RunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of ATS Abb-mx250.

## ATS-HW
ATS-HW
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.74 | ATSHW | ATS-HW | ATS-HW | / | / | / | / | ats_so Equipment.
1.3.6.1.4.1.2011.6.178.1.1.74.1 | hwATSHWRunning1Table | / | / |  |  | / | / | The running table of ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.1 | hwATSHWRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.2 | hwATSHWMainsPhaseAVoltage | Mains phase A voltage | 主路A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase A voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.3 | hwATSHWMainsPhaseBVoltage | Mains phase B voltage | 主路B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase B voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.4 | hwATSHWMainsPhaseCVoltage | Mains phase C voltage | 主路C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase C voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.5 | hwATSHWMainsLineAVoltage | Mains line A voltage | 主路A线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Mains line A voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.6 | hwATSHWMainsLineBVoltage | Mains line B voltage | 主路B线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Mains line B voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.7 | hwATSHWMainsLineCVoltage | Mains line C voltage | 主路C线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Mains line C voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.8 | hwATSHWMainsPhaseACurrent | Mains phase A current | 主路A相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Mains phase A current of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.9 | hwATSHWMainsPhaseBCurrent | Mains phase B current | 主路B相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Mains phase B current of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.10 | hwATSHWMainsPhaseCCurrent | Mains phase C current | 主路C相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Mains phase C current of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.11 | hwATSHWMainsPhaseNCurrent | Mains phase N current | 主路N相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Mains phase N current of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.12 | hwATSHWMainsFrequency | Mains frequency | 主路频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Mains frequency of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.13 | hwATSHWStandbyPhaseAVoltage | Standby phase A voltage | 备路A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase A voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.14 | hwATSHWStandbyPhaseBVoltage | Standby phase B voltage | 备路B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase B voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.15 | hwATSHWStandbyPhaseCVoltage | Standby phase C voltage | 备路C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase C voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.16 | hwATSHWStandbyLineAVoltage | Standby line A voltage | 备路A线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Standby line A voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.17 | hwATSHWStandbyLineBVoltage | Standby line B voltage | 备路B线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Standby line B voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.18 | hwATSHWStandbyLineCVoltage | Standby line C voltage | 备路C线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Standby line C voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.19 | hwATSHWStandbyPhaseACurrent | Standby phase A current | 备路A相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Standby phase A current of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.20 | hwATSHWStandbyPhaseBCurrent | Standby phase B current | 备路B相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Standby phase B current of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.21 | hwATSHWStandbyPhaseCCurrent | Standby phase C current | 备路C相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Standby phase C current of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.22 | hwATSHWStandbyPhaseNCurrent | Standby phase N current | 备路N相电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Standby phase N current of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.23 | hwATSHWStandbyFrequency | Standby frequency | 备路频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Standby frequency of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.24 | hwATSHWMainsPhaseVoltageImbalanceDegree | Mains phase voltage imbalance degree | 主路相电压不平衡度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Mains phase voltage imbalance degree of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.25 | hwATSHWStandbyPhaseVoltageImbalanceDegree | Standby phase voltage imbalance degree | 备路相电压不平衡度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Standby phase voltage imbalance degree of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.26 | hwATSHWMainsNeutralGroundVoltage | Mains neutral-ground voltage | 主路零地电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains neutral-ground voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.27 | hwATSHWStandbyNeutralGroundVoltage | Standby neutral-ground voltage | 备路零地电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby neutral-ground voltage of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.28 | hwATSHWMainsSwitchStatus | Mains switch status | 主路开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [断开=1]/[闭合=2] | Mains switch status of the device config table for the ATS-HW. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.29 | hwATSHWStandbySwitchStatus | Standby switch status | 备路开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [断开=1]/[闭合=2] | Standby switch status of the device config table for the ATS-HW. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.30 | hwATSHWManualorAutomaticStatus | Manual/Automatic status | 手动自动状态 | 0-Read_Only | 只读 | automatic(1), manualmode(2), fireextinguishingsystemabnormal(3), unknown(255) | [自动模式=1]/[手动模式=2]/[消防异常=3] | Manual/Automatic status of the device config table for the ATS-HW. Value 1 indicate automatic Value 2 indicate manual mode Value 3 indicate fire extinguishing system abnormal
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.31 | hwATSHWCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the ATS-HW. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.32 | hwATSHWSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.33 | hwATSHWPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.34 | hwATSHWModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.35 | hwATSHWMainsPhaseAApparentPower | Mains phase A apparent power | 主路A相视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Mains phase A apparent power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:KVA.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.36 | hwATSHWMainsPhaseBApparentPower | Mains phase B apparent power | 主路B相视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Mains phase B apparent power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:KVA.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.37 | hwATSHWMainsPhaseCApparentPower | Mains phase C apparent power | 主路C相视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Mains phase C apparent power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:KVA.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.38 | hwATSHWMainsPhaseAActivePower | Mains phase A active power | 主路A相有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Mains phase A active power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.39 | hwATSHWMainsPhaseBActivePower | Mains phase B active power | 主路B相有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Mains phase B active power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.40 | hwATSHWMainsPhaseCActivePower | Mains phase C active power | 主路C相有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Mains phase C active power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.41 | hwATSHWMainsPhaseAPowerFactor | Mains phase A power factor | 主路A相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Mains phase A power factor of the device config table for the ATS-HW.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.42 | hwATSHWMainsPhaseBPowerFactor | Mains phase B power factor | 主路B相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Mains phase B power factor of the device config table for the ATS-HW.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.43 | hwATSHWMainsPhaseCPowerFactor | Mains phase C power factor | 主路C相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Mains phase C power factor of the device config table for the ATS-HW.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.44 | hwATSHWMainsPhaseAActiveEnergy | Mains phase A active energy | 主路A相有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Mains phase A active energy of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.45 | hwATSHWMainsPhaseBActiveEnergy | Mains phase B active energy | 主路B相有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Mains phase B active energy of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.46 | hwATSHWMainsPhaseCActiveEnergy | Mains phase C active energy | 主路C相有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Mains phase C active energy of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.47 | hwATSHWMainsPhaseAHarmonicVoltageDistortion | Mains phase A harmonic voltage distortion | 主路A相电压谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase A harmonic voltage distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.48 | hwATSHWMainsPhaseBHarmonicVoltageDistortion | Mains phase B harmonic voltage distortion | 主路B相电压谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase B harmonic voltage distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.49 | hwATSHWMainsPhaseCHarmonicVoltageDistortion | Mains phase C harmonic voltage distortion | 主路C相电压谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase C harmonic voltage distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.50 | hwATSHWMainsPhaseAHarmonicCurrentDistortion | Mains phase A harmonic current distortion | 主路A相电流谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase A harmonic current distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.51 | hwATSHWMainsPhaseBHarmonicCurrentDistortion | Mains phase B harmonic current distortion | 主路B相电流谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase B harmonic current distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.52 | hwATSHWMainsPhaseCHarmonicCurrentDistortion | Mains phase C harmonic current distortion | 主路C相电流谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Mains phase C harmonic current distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.53 | hwATSHWStandbyPhaseAApparentPower | Standby phase A apparent power | 备路A相视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Standby phase A apparent power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:KVA.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.54 | hwATSHWStandbyPhaseBApparentPower | Standby phase B apparent power | 备路B相视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Standby phase B apparent power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:KVA.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.55 | hwATSHWStandbyPhaseCApparentPower | Standby phase C apparent power | 备路C相视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Standby phase C apparent power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:KVA.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.56 | hwATSHWStandbyPhaseAActivePower | Standby phase A active power | 备路A相有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Standby phase A active power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.57 | hwATSHWStandbyPhaseBActivePower | Standby phase B active power | 备路B相有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Standby phase B active power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.58 | hwATSHWStandbyPhaseCActivePower | Standby phase C active power | 备路C相有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Standby phase C active power of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.59 | hwATSHWStandbyPhaseAPowerFactor | Standby phase A power factor | 备路A相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Standby phase A power factor of the device config table for the ATS-HW.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.60 | hwATSHWStandbyPhaseBPowerFactor | Standby phase B power factor | 备路B相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Standby phase B power factor of the device config table for the ATS-HW.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.61 | hwATSHWStandbyPhaseCPowerFactor | Standby phase C power factor | 备路C相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Standby phase C power factor of the device config table for the ATS-HW.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.62 | hwATSHWStandbyPhaseAActiveEnergy | Standby phase A active energy | 备路A相有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Standby phase A active energy of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.63 | hwATSHWStandbyPhaseBActiveEnergy | Standby phase B active energy | 备路B相有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Standby phase B active energy of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.64 | hwATSHWStandbyPhaseCActiveEnergy | Standby phase C active energy | 备路C相有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Standby phase C active energy of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.65 | hwATSHWStandbyPhaseAHarmonicVoltageDistortion | Standby phase A harmonic voltage distortion | 备路A相电压谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase A harmonic voltage distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.66 | hwATSHWStandbyPhaseBHarmonicVoltageDistortion | Standby phase B harmonic voltage distortion | 备路B相电压谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase B harmonic voltage distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.67 | hwATSHWStandbyPhaseCHarmonicVoltageDistortion | Standby phase C harmonic voltage distortion | 备路C相电压谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase C harmonic voltage distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.68 | hwATSHWStandbyPhaseAHarmonicCurrentDistortion | Standby phase A harmonic current distortion | 备路A相电流谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase A harmonic current distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.69 | hwATSHWStandbyPhaseBHarmonicCurrentDistortion | Standby phase B harmonic current distortion | 备路B相电流谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase B harmonic current distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.70 | hwATSHWStandbyPhaseCHarmonicCurrentDistortion | Standby phase C harmonic current distortion | 备路C相电流谐波畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Standby phase C harmonic current distortion of the device config table for the ATS-HW.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.71 | hwATSHWMainsPhaseALoadRate | Mains phase A load rate | 主路A相带载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Mains phase A load rate of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.72 | hwATSHWMainsPhaseBLoadRate | Mains phase B load rate | 主路B相带载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Mains phase B load rate of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.73 | hwATSHWMainsPhaseCLoadRate | Mains phase C load rate | 主路C相带载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Mains phase C load rate of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.74 | hwATSHWStandbyPhaseALoadRate | Standby phase A load rate | 备路A相带载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Standby phase A load rate of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.75 | hwATSHWStandbyPhaseBLoadRate | Standby phase B load rate | 备路B相带载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Standby phase B load rate of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.76 | hwATSHWStandbyPhaseCLoadRate | Standby phase C load rate | 备路C相带载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Standby phase C load rate of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.1.1.101 | hwATSHWRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.2 | hwATSHWConfig2Table | / | / |  |  | / | / | The config table of ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.1 | hwATSHWConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.2 | hwATSHWDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.3 | hwATSHWWorkingMode | Working mode | 工作模式 | 1-Read_Write | 读写 | mainsMainsautomaticswitchingback(1), mainsMainsmutualbackup(2), mainsMainsnotswitchingback(3), mainsDgautomaticswitchingback(4), mainsDgmutualbackup(5), manualmode(6), nonFireextinguishingpowerdisconnection(7), unknown(255) | [市电市电自投自复=1]/[市电市电互为备用=2]/[市电市电自投不自复=3]/[市电油机自投自复=4]/[市电油机互为备用=5]/[手动模式=6]/[消防切非=7] | Working mode of the device config table for the ATS-HW. Value 1 indicate mains-mains automatic switching back Value 2 indicate mains-mains mutual backup Value 3 indicate mains-mains not switching back Value 4 indicate mains-dg automatic switching back Value 5 indicate mains-dg mutual backup Value 6 indicate manual mode Value 7 indicate non-fire extinguishing power disconnection
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.4 | hwATSHWMainsRatedVoltage | Mains rated voltage | 主路额定电压 | 1-Read_Write | 读写 | 50..500 | 50..500 | Mains rated voltage of the device config table for the ATS-HW.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.5 | hwATSHWMainsOvervoltageAlarmThreshold | Mains overvoltage alarm threshold | 主路过压告警阈值 | 1-Read_Write | 读写 | 105..130 | 105..130 | Mains overvoltage alarm threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.6 | hwATSHWMainsUndervoltageAlarmThreshold | Mains undervoltage alarm threshold | 主路欠压告警阈值 | 1-Read_Write | 读写 | 70..95 | 70..95 | Mains undervoltage alarm threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.7 | hwATSHWMainsOvervoltageRecoveryThreshold | Mains overvoltage recovery threshold | 主路过压恢复阈值 | 1-Read_Write | 读写 | 1..10 | 1..10 | Mains overvoltage recovery threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.8 | hwATSHWMainsUndervoltageRecoveryThreshold | Mains undervoltage recovery threshold | 主路欠压恢复阈值 | 1-Read_Write | 读写 | 1..10 | 1..10 | Mains undervoltage recovery threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.9 | hwATSHWStandbyRatedVoltage | Standby rated voltage | 备路额定电压 | 1-Read_Write | 读写 | 50..500 | 50..500 | Standby rated voltage of the device config table for the ATS-HW.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.10 | hwATSHWStandbyOvervoltageAlarmThreshold | Standby overvoltage alarm threshold | 备路过压告警阈值 | 1-Read_Write | 读写 | 105..130 | 105..130 | Standby overvoltage alarm threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.11 | hwATSHWStandbyUndervoltageAlarmThreshold | Standby undervoltage alarm threshold | 备路欠压告警阈值 | 1-Read_Write | 读写 | 70..95 | 70..95 | Standby undervoltage alarm threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.12 | hwATSHWStandbyOvervoltageRecoveryThreshold | Standby overvoltage recovery threshold | 备路过压恢复阈值 | 1-Read_Write | 读写 | 1..10 | 1..10 | Standby overvoltage recovery threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.13 | hwATSHWStandbyUndervoltageRecoveryThreshold | Standby undervoltage recovery threshold | 备路欠压恢复阈值 | 1-Read_Write | 读写 | 1..10 | 1..10 | Standby undervoltage recovery threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.14 | hwATSHWMainsRatedFrequency | Mains rated frequency | 主路额定频率 | 1-Read_Write | 读写 | 45..65 | 45..65 | Mains rated frequency of the device config table for the ATS-HW.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.15 | hwATSHWMainsOverfrequencyAlarmThreshold | Mains overfrequency alarm threshold | 主路过频告警阈值 | 1-Read_Write | 读写 | 1010..1100 | 1010..1100 | Mains overfrequency alarm threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.16 | hwATSHWMainsUnderfrequencyAlarmThreshold | Mains underfrequency alarm threshold | 主路欠频告警阈值 | 1-Read_Write | 读写 | 800..990 | 800..990 | Mains underfrequency alarm threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.17 | hwATSHWMainsOverfrequencyRecoveryThreshold | Mains overfrequency recovery threshold | 主路过频恢复阈值 | 1-Read_Write | 读写 | 1..50 | 1..50 | Mains overfrequency recovery threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.18 | hwATSHWMainsUnderfrequencyRecoveryThreshold | Mains underfrequency recovery threshold | 主路欠频恢复阈值 | 1-Read_Write | 读写 | 1..50 | 1..50 | Mains underfrequency recovery threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.19 | hwATSHWStandbyRatedFrequency | Standby rated frequency | 备路额定频率 | 1-Read_Write | 读写 | 45..65 | 45..65 | Standby rated frequency of the device config table for the ATS-HW.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.20 | hwATSHWStandbyOverfrequencyAlarmThreshold | Standby overfrequency alarm threshold | 备路过频告警阈值 | 1-Read_Write | 读写 | 1010..1100 | 1010..1100 | Standby overfrequency alarm threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.21 | hwATSHWStandbyUnderfrequencyAlarmThreshold | Standby underfrequency alarm threshold | 备路欠频告警阈值 | 1-Read_Write | 读写 | 800..990 | 800..990 | Standby underfrequency alarm threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.22 | hwATSHWStandbyOverfrequencyRecoveryThreshold | Standby overfrequency recovery threshold | 备路过频恢复阈值 | 1-Read_Write | 读写 | 1..50 | 1..50 | Standby overfrequency recovery threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.23 | hwATSHWStandbyUnderfrequencyRecoveryThreshold | Standby underfrequency recovery threshold | 备路欠频恢复阈值 | 1-Read_Write | 读写 | 1..50 | 1..50 | Standby underfrequency recovery threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.24 | hwATSHWMainsPhaseVoltageImbalanceAlarmThreshold | Mains phase voltage imbalance alarm threshold | 主路相电压不平衡告警阈值 | 1-Read_Write | 读写 | 5..30 | 5..30 | Mains phase voltage imbalance alarm threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.25 | hwATSHWStandbyPhaseVoltageImbalanceAlarmThreshold | Standby phase voltage imbalance alarm threshold | 备路相电压不平衡告警阈值 | 1-Read_Write | 读写 | 5..30 | 5..30 | Standby phase voltage imbalance alarm threshold of the device config table for the ATS-HW.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.26 | hwATSHWAlarmAckDelayForSwitchMainsToBothDisconn | Alarm ack delay for switch mains to both disconn | 主路切双分告警确认延时 | 1-Read_Write | 读写 | 1..120 | 1..120 | Alarm acknowledgment delay for switching mains to both disconnected of the device config table for the ATS-HW.SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.27 | hwATSHWAlarmAckDelayForSwitchStandbyToBothDisconn | Alarm ack delay for switch standby to both disconn | 备路切双分告警确认延时 | 1-Read_Write | 读写 | 1..120 | 1..120 | Alarm acknowledgment delay for switching standby to both disconnected of the device config table for the ATS-HW.SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.28 | hwATSHWAlarmAckDelayForSwitchBothDisconnToMains | Alarm ack delay for switch both disconn to mains | 双分切主路告警确认延时 | 1-Read_Write | 读写 | 0..120 | 0..120 | Alarm acknowledgment delay for switching both disconnected to mains of the device config table for the ATS-HW.SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.29 | hwATSHWAlarmAckDelayForSwitchBothDisconnToStandby | Alarm ack delay for switch both disconn to standby | 双分切备路告警确认延时 | 1-Read_Write | 读写 | 0..120 | 0..120 | Alarm acknowledgment delay for switching both disconnected to standby of the device config table for the ATS-HW.SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.30 | hwATSHWManualModeContactStatus | Manual mode contact status | 手动模式触点状态 | 1-Read_Write | 读写 | maincircuit(1), standbycircuit(2), bothdisconnected(3), unknown(255) | [主路=1]/[备路=2]/[双分=3] | Manual mode contact status of the device config table for the ATS-HW. Value 1 indicate main circuit Value 2 indicate standby circuit Value 3 indicate both disconnected
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.31 | hwATSHWDgStabilityDelay | DG stability delay | 油机稳定延时 | 1-Read_Write | 读写 | 1..1800 | 1..1800 | DG stability delay of the device config table for the ATS-HW.SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.32 | hwATSHWDgShutdownAcknowledgmentDelay | DG shutdown acknowledgment delay | 关油机确认延时 | 1-Read_Write | 读写 | 1..1800 | 1..1800 | DG shutdown acknowledgment delay of the device config table for the ATS-HW.SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.33 | hwATSHWAlarmClearing | Alarm clearing | 故障清除 | 1-Read_Write | 读写 | yes(1) | [是=1] | Alarm clearing of the device config table for the ATS-HW. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.34 | hwATSHWBodyType | Body type | 本体类型 | 1-Read_Write | 读写 | nader(1), taiyong(2), unknown(255) | [良信=1]/[泰永=2] | Body type of the device config table for the ATS-HW. Value 1 indicate nader Value 2 indicate taiyong
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.35 | hwATSHWPowerSupplyPriority | Power supply priority | 电源优先级 | 1-Read_Write | 读写 | circuitifirst(1), circuitiifirst(2), unknown(255) | [I路优先=1]/[II路优先=2] | Power supply priority of the device config table for the ATS-HW. Value 1 indicate circuit i first Value 2 indicate circuit ii first
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.36 | hwATSHWRouteIRatedCurrent | Route I rated current | I路额定电流 | 1-Read_Write | 读写 | 125..1600 | 125..1600 | Route I rated current of the device config table for the ATS-HW.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.37 | hwATSHWRouteIiRatedCurrent | Route II rated current | II路额定电流 | 1-Read_Write | 读写 | 125..1600 | 125..1600 | Route II rated current of the device config table for the ATS-HW.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.38 | hwATSHWRouteIRatedCtChange | Route I rated CT change | I路额定CT变比 | 1-Read_Write | 读写 | 50..1600 | 50..1600 | Route I rated CT change of the device config table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.39 | hwATSHWRouteIiRatedCtChange | Route II rated CT change | II路额定CT变比 | 1-Read_Write | 读写 | 50..1600 | 50..1600 | Route II rated CT change of the device config table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.40 | hwATSHWRecheckFireExtinguishingSystem | Recheck fire extinguishing system | 消防复检 | 1-Read_Write | 读写 | check(1), checkandreset(2), unknown(255) | [检测=1]/[检测复位=2] | Recheck fire extinguishing system of the device config table for the ATS-HW. Value 1 indicate check Value 2 indicate check and reset
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.41 | hwATSHWHarmonicDistortionDisplayTimes | Harmonic distortion display times | 谐波畸变率显示次数 | 1-Read_Write | 读写 | 2..31 | 2..31 | Harmonic distortion display times of the device config table for the ATS-HW.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.42 | hwATSHWCurrentOverloadAlarmThreshold | Current overload alarm threshold | 电流过载告警阈值 | 1-Read_Write | 读写 | 1000..1200 | 1000..1200 | Current overload alarm threshold of the device config table for the ATS-HW.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.74.2.1.101 | hwATSHWConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of ATS-HW.

## Battery System
电池系统
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.98 | BatterySystem | Battery System | 电池系统 | / | / | / | / | Battery System Equipment.
1.3.6.1.4.1.2011.6.178.1.1.98.1 | hwBatterySystemRunning1Table | / | / |  |  | / | / | The running table of Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.1 | hwBatterySystemRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.2 | hwBatterySystemRunningStatus | Running status | 运行状态 | 0-Read_Only | 只读 | standby(1), charging(2), discharging(3), fault(4), unknown(255) | [待机=1]/[充电=2]/[放电=3]/[故障=4] | Running status of the device config table for the Battery System. Value 1 indicate standby Value 2 indicate charging Value 3 indicate discharging Value 4 indicate fault
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.3 | hwBatterySystemCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Battery System. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.4 | hwBatterySystemESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.5 | hwBatterySystemMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.6 | hwBatterySystemIp | IP | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IP of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.7 | hwBatterySystemBatterySystemId | Battery system id | 电池系统编号 | 0-Read_Only | 只读 | 0..7 | 0..7 | Battery system id of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.8 | hwBatterySystemBatteryCabinetQuantity | Battery cabinet quantity | 电池柜数量 | 0-Read_Only | 只读 | 0..15 | 0..15 | Battery cabinet quantity of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.9 | hwBatterySystemBatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Battery voltage of the device config table for the Battery System.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.10 | hwBatterySystemBatteryCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -10000..10000 | -10000..10000 | Battery current of the device config table for the Battery System.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.11 | hwBatterySystemSoc | SOC | SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | SOC of the device config table for the Battery System.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.12 | hwBatterySystemSoh | SOH | SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | SOH of the device config table for the Battery System.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.13 | hwBatterySystemMaximumCellVoltage | Maximum cell voltage | 电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Maximum cell voltage of the device config table for the Battery System.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.14 | hwBatterySystemMinimumCellVoltage | Minimum cell voltage | 电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Minimum cell voltage of the device config table for the Battery System.Multiple:1000.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.15 | hwBatterySystemMaximumCellTemperature | Maximum cell temperature | 电芯最高温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Maximum cell temperature of the device config table for the Battery System.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.16 | hwBatterySystemMinimumCellTemperature | Minimum cell temperature | 电芯最低温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Minimum cell temperature of the device config table for the Battery System.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.17 | hwBatterySystemTotalDischargeTimes | Total discharge times | 累计放电次数 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Total discharge times of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.18 | hwBatterySystemTotalDischargeCapacity | Total discharge capacity | 累计放电容量 | 0-Read_Only | 只读 | 0..100000000 | 0..100000000 | Total discharge capacity of the device config table for the Battery System.Multiple:10.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.19 | hwBatterySystemBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery capacity of the device config table for the Battery System.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.20 | hwBatterySystemMonitoringSoftwareVersion | Monitoring software version | 监控软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Monitoring software version of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.21 | hwBatterySystemPowerSoftwareVersion | Power software version | 功率软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Power software version of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.34 | hwBatterySystemBatteryCurrentInt32 | Battery current | 电池电流 | 0-Read_Only | 只读 | -200000..200000 | -200000..200000 | Battery current of the device config table for the Battery System.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.35 | hwBatterySystemBackupTime | Backup time | 备电时间 | 0-Read_Only | 只读 | 0..999 | 0..999 | Backup time of the device config table for the Battery System.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.36 | hwBatterySystemPortVoltage | Port voltage | 端口电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Port voltage of the device config table for the Battery System.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.37 | hwBatterySystemPortCurrent | Port current | 端口电流 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Port current of the device config table for the Battery System.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.98.1.1.101 | hwBatterySystemRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.2 | hwBatterySystemConfig2Table | / | / |  |  | / | / | The config table of Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.2.1.1 | hwBatterySystemConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.2.1.2 | hwBatterySystemDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Battery System.
1.3.6.1.4.1.2011.6.178.1.1.98.2.1.101 | hwBatterySystemConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Battery System.

## Cabinet Electronic Clasp Lock
机柜电子扣锁
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.84 | CabinetElectronicClaspLock | Cabinet Electronic Clasp Lock | 机柜电子扣锁 | / | / | / | / | CabinetElectronicClaspLock Equipment.
1.3.6.1.4.1.2011.6.178.1.1.84.1 | hwCabinetElectronicClaspLockRunning1Table | / | / |  |  | / | / | The running table of CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.1 | hwCabinetElectronicClaspLockRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.2 | hwCabinetElectronicClaspLockCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the CabinetElectronicClaspLock. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.3 | hwCabinetElectronicClaspLockPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.4 | hwCabinetElectronicClaspLockModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..247 | 1..247 | Modbus address of the device config table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.5 | hwCabinetElectronicClaspLockDeviceModel | Device model | 设备型号 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Device model of the device config table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.6 | hwCabinetElectronicClaspLockSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.7 | hwCabinetElectronicClaspLockHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.8 | hwCabinetElectronicClaspLockESN | ESN | ESN | 0-Read_Only | 只读 | 0..20 | 0..20 | ESN of the device config table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.9 | hwCabinetElectronicClaspLockDoorState | Door state | 门状态 | 0-Read_Only | 只读 | doorclose(1), dooropen(2), unknown(255) | [门关=1]/[门开=2] | Door state of the device config table for the CabinetElectronicClaspLock. Value 1 indicate door close Value 2 indicate door open
1.3.6.1.4.1.2011.6.178.1.1.84.1.1.101 | hwCabinetElectronicClaspLockRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.2 | hwCabinetElectronicClaspLockConfig2Table | / | / |  |  | / | / | The config table of CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.2.1.1 | hwCabinetElectronicClaspLockConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.2.1.2 | hwCabinetElectronicClaspLockDoorOpen | Door open | 开门 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Door open of the device config table for the CabinetElectronicClaspLock. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.84.2.1.3 | hwCabinetElectronicClaspLockDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the CabinetElectronicClaspLock.
1.3.6.1.4.1.2011.6.178.1.1.84.2.1.101 | hwCabinetElectronicClaspLockConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of CabinetElectronicClaspLock.

## Cantal_Ms19_Row_Mb
列间变频空调
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.104 | Ms19RowMb | Cantal_Ms19_Row_Mb | 列间变频空调 | / | / | / | / | Ms19_Row_Mb Equipment.
1.3.6.1.4.1.2011.6.178.1.1.104.1 | hwMs19RowMbRunning1Table | / | / |  |  | / | / | The running table of Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.1 | hwMs19RowMbRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.2 | hwMs19RowMbReturnAirTemperature | Return air temperature | 回风温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Return air temperature of the device config table for the Ms19_Row_Mb.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.3 | hwMs19RowMbReturnAirHumidity | Return air humidity | 回风湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Return air humidity of the device config table for the Ms19_Row_Mb.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.4 | hwMs19RowMbSupplyAirTemperature | Supply air temperature | 送风温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Supply air temperature of the device config table for the Ms19_Row_Mb.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.5 | hwMs19RowMbSupplyAirHumidity | Supply air humidity | 送风湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Supply air humidity of the device config table for the Ms19_Row_Mb.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.6 | hwMs19RowMbFanRelay | Fan relay | 风机继电器 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | Fan relay of the device config table for the Ms19_Row_Mb. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.7 | hwMs19RowMbCompressor1Relay | Compressor 1 relay | 压缩机1继电器 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | Compressor 1 relay of the device config table for the Ms19_Row_Mb. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.8 | hwMs19RowMbAirConditionerStartuporShutdown | Air conditioner startup/shutdown | 本机开关机 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Air conditioner startup/shutdown of the device config table for the Ms19_Row_Mb. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.9 | hwMs19RowMbTotalFanRuntime | Total fan runtime | 风机运行累加时 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Total fan runtime of the device config table for the Ms19_Row_Mb.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.10 | hwMs19RowMbTotalCoolingRuntime | Total cooling runtime | 制冷累加时 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Total cooling runtime of the device config table for the Ms19_Row_Mb.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.11 | hwMs19RowMbEcFan0To10VOutput | EC fan 0–10 V output | EC风机0-10V输出 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | EC fan 0-10 V output of the device config table for the Ms19_Row_Mb.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.12 | hwMs19RowMbWaterValve0To10VOutput | Water valve 0–10 V output | 水阀0-10V输出 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Water valve 0-10 V output of the device config table for the Ms19_Row_Mb.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.13 | hwMs19RowMbActualRotationalSpeedOfTheCompressor | [Mainboard] Actual rotational speed of the compressor | [主板]压机实际转速 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Actual rotational speed of the compressor of the device config table for the Ms19_Row_Mb.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.14 | hwMs19RowMbCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Ms19_Row_Mb. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.15 | hwMs19RowMbPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.16 | hwMs19RowMbModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.17 | hwMs19RowMbSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | The Software version of Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.1.1.101 | hwMs19RowMbRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.2 | hwMs19RowMbConfig2Table | / | / |  |  | / | / | The config table of Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.2.1.1 | hwMs19RowMbConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.2.1.2 | hwMs19RowMbDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Ms19_Row_Mb.
1.3.6.1.4.1.2011.6.178.1.1.104.2.1.3 | hwMs19RowMbTemperatureSetpoint | Temperature setpoint | 温度设定值 | 1-Read_Write | 读写 | 50..450 | 50..450 | Temperature setpoint of the device config table for the Ms19_Row_Mb.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.104.2.1.4 | hwMs19RowMbHumiditySetpoint | Humidity setpoint | 湿度设定值 | 1-Read_Write | 读写 | 30..80 | 30..80 | Humidity setpoint of the device config table for the Ms19_Row_Mb.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.104.2.1.101 | hwMs19RowMbConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Ms19_Row_Mb.

## NetCol5000CF-110HALF
NetCol5000CF_110HALF
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.66 | NetCol5000CF110HALF | NetCol5000CF_110HALF | NetCol5000CF_110HALF | / | / | / | / | NetCol Equipments.
1.3.6.1.4.1.2011.6.178.1.1.66.1 | hwNetCol5000CF110HALFRunning1Table | / | / |  |  | / | / | The running table of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.1 | hwNetCol5000CF110HALFRunning1Index | / | / | 0-Read_Only | 只读 | / | / | The Index of running table of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.2 | hwNetCol5000CF110HALFCommstate | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The Commstate of the NetCol5000CF110HALF. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.3 | hwNetCol5000CF110HALFCurrentTemp | Current temperature | 当前温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The CurrentTemp of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.4 | hwNetCol5000CF110HALFCurrentHumid | Current humidity | 当前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The CurrentHumid of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.5 | hwNetCol5000CF110HALFSupplywaterTemp | Supply-water temperature | 供水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The SupplywaterTemp of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.6 | hwNetCol5000CF110HALFReturnwaterTemp | Return-water temperature | 回水温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The ReturnwaterTemp of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.7 | hwNetCol5000CF110HALFCoolOutp | Cool output | 制冷输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The CoolOutp of the NetCol5000CF110HALF. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.8 | hwNetCol5000CF110HALFFanOutp | Indoor fan output | 室内风机输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The FanOutp of the NetCol5000CF110HALF. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.9 | hwNetCol5000CF110HALFHeatOutp | Heat output | 加热输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The HeatOutp of the NetCol5000CF110HALF. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.10 | hwNetCol5000CF110HALFHumidOutp | Humidity output | 加湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The HumidOutp of the NetCol5000CF110HALF. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.11 | hwNetCol5000CF110HALFIndoorfanCtrlStatus | Indoor fan control status | 室内风机控制状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The IndoorfanCtrlStatus of the NetCol5000CF110HALF. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.12 | hwNetCol5000CF110HALFCwvalveRunStatus | CW valve run status | 冷冻水阀运行状态 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The CwvalveRunStatus of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.13 | hwNetCol5000CF110HALFCondpumpRunStatus | Drain pump run status | 排水水泵运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The CondpumpRunStatus of the NetCol5000CF110HALF. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.14 | hwNetCol5000CF110HALFUnitOnOffStatus | On/Off status of air conditioner | 机组开关机状态 | 0-Read_Only | 只读 | poweroff(1), poweron(2), unknown(255) | [关机=1]/[开机=2] | The UnitOnOffStatus of the NetCol5000CF110HALF. Value 1 indicates poweroff. Value 2 indicates poweron.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.15 | hwNetCol5000CF110HALFBestWaterTemp | Recommended supply water temperature | 供水温度建议值 | 0-Read_Only | 只读 | 7..19 | 7..19 | The BestWaterTemp of the NetCol5000CF110HALF. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.16 | hwNetCol5000CF110HALFCurCool | Cooling capacity | 制冷量 | 0-Read_Only | 只读 | 0..200000 | 0..200000 | The CurCool of the NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.17 | hwNetCol5000CF110HALFCurLoad | Cooling load factor | 制冷负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The CurLoad of the NetCol5000CF110HALF. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.18 | hwNetCol5000CF110HALFIpAddr | IP address | IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IpAddr of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.19 | hwNetCol5000CF110HALFEquipEsn | ESN No. | ESN号 | 0-Read_Only | 只读 | 1..50 | 1..50 | The EquipEsn of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.20 | hwNetCol5000CF110HALFEquipElabel | E-label | 电子标签 | 0-Read_Only | 只读 | 1..2048 | 1..2048 | The EquipElabel of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.21 | hwNetCol5000CF110HALFPortMac | / | / | 0-Read_Only | 只读 | 1..50 | / | The PortMac of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.22 | hwNetCol5000CF110HALFSoftVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | The SoftVersion of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.23 | hwNetCol5000CF110HALFIndoorFan1TotalRuntime | Indoor fan 1 total runtime | 室内风机1累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan1TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.24 | hwNetCol5000CF110HALFIndoorFan2TotalRuntime | Indoor fan 2 total runtime | 室内风机2累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan2TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.25 | hwNetCol5000CF110HALFIndoorFan3TotalRuntime | Indoor fan 3 total runtime | 室内风机3累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan3TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.26 | hwNetCol5000CF110HALFIndoorFan4TotalRuntime | Indoor fan 4 total runtime | 室内风机4累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan4TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.27 | hwNetCol5000CF110HALFIndoorFan5TotalRuntime | Indoor fan 5 total runtime | 室内风机5累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan5TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.28 | hwNetCol5000CF110HALFIndoorFan6TotalRuntime | Indoor fan 6 total runtime | 室内风机6累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan6TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.29 | hwNetCol5000CF110HALFIndoorFan7TotalRuntime | Indoor fan 7 total runtime | 室内风机7累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan7TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.30 | hwNetCol5000CF110HALFIndoorFan8TotalRuntime | Indoor fan 8 total runtime | 室内风机8累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan8TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.31 | hwNetCol5000CF110HALFIndoorFan9TotalRuntime | Indoor fan 9 total runtime | 室内风机9累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan9TotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.32 | hwNetCol5000CF110HALFIndoorFan10totalRuntime | Indoor fan 10 total runtime | 室内风机10累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan10totalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.33 | hwNetCol5000CF110HALFIndoorFan11totalRuntime | Indoor fan 11 total runtime | 室内风机11累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan11totalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.34 | hwNetCol5000CF110HALFIndoorFan12totalRuntime | Indoor fan 12 total runtime | 室内风机12累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan12totalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.35 | hwNetCol5000CF110HALFHumidifierPumpTotalRuntime | Humidifier pump total runtime | 加湿水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The HumidifierPumpTotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.36 | hwNetCol5000CF110HALFHumidifierWetTotalRuntime | Humidifier total runtime | 加湿器累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The HumidifierWetTotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.37 | hwNetCol5000CF110HALFCondpumpTotalRuntime | Drain pump total runtime | 排水水泵累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The CondpumpTotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.38 | hwNetCol5000CF110HALFAirfilterTotalRuntime | Return air filter total runtime | 回风过滤网累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The AirfilterTotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.39 | hwNetCol5000CF110HALFCwvalveTotalRuntime | CW valve total runtime | 冷冻水阀累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The CwvalveTotalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.40 | hwNetCol5000CF110HALFTotalNumberOfUnits | Total number of units | 本群组机组数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | The TotalNumberOfUnits of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.41 | hwNetCol5000CF110HALFNumberOfRunningUnits | Number of running units | 本群组运行机数目 | 0-Read_Only | 只读 | 1..32 | 1..32 | The NumberOfRunningUnits of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.42 | hwNetCol5000CF110HALFTeamWorkStatus | Teamwork status | 群控状态 | 0-Read_Only | 只读 | single(1), intelligentTeamworkControl(2), iCooling(3), unknown(255) | [单机=1]/[智能群控=2]/[iCooling=3] | The TeamWorkStatus of the NetCol5000CF110HALF. Value 1 indicates single. Value 2 indicates intelligent teamwork control. Value 3 indicates iCooling.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.43 | hwNetCol5000CF110HALFPowerVolt | Power 1 input voltage | 电源1输入电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The PowerVolt of the NetCol5000CF110HALF. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.44 | hwNetCol5000CF110HALFElectricSupplyRate | Power frequency | 电源频率 | 0-Read_Only | 只读 | 0..200 | 0..200 | The ElectricSupplyRate of the NetCol5000CF110HALF. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.45 | hwNetCol5000CF110HALFSupplyAirAvgTemp | Supply-air average temperature | 送风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The SupplyAirAvgTemp of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.46 | hwNetCol5000CF110HALFReturnAirAvgTemp | Return-air average temperature | 回风平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The ReturnAirAvgTemp of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.47 | hwNetCol5000CF110HALFColdAisleAvgTemp | Cold-aisle average temperature | 冷通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The ColdAisleAvgTemp of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.48 | hwNetCol5000CF110HALFHotAisleAvgTemp | Hot-aisle average temperature | 热通道平均温度 | 0-Read_Only | 只读 | -500..1500 | -500..1500 | The HotAisleAvgTemp of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.49 | hwNetCol5000CF110HALFSupplyAirAvgHumid | Supply-air average humidity | 送风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The SupplyAirAvgHumid of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.50 | hwNetCol5000CF110HALFReturnAirAvgHumid | Return-air average humidity | 回风平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The ReturnAirAvgHumid of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.51 | hwNetCol5000CF110HALFColdAisleAvgHumid | Cold-aisle average humidity | 冷通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The ColdAisleAvgHumid of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.52 | hwNetCol5000CF110HALFHotAisleAvgHumid | Hot-aisle average humidity | 热通道平均湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The HotAisleAvgHumid of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.53 | hwNetCol5000CF110HALFSidePressureDiff | Side pressure difference | 风侧压差 | 0-Read_Only | 只读 | 0..500 | 0..500 | The SidePressureDiff of the NetCol5000CF110HALF. SigUnitInfo:Pa
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.54 | hwNetCol5000CF110HALFTHControlType | Temperature and humidity control type | 温湿度控制类型 | 0-Read_Only | 只读 | returnair(1), supplyair(2), coldaisle(3), hotaisle(4), unknown(255) | [回风=1]/[送风=2]/[冷通道=3]/[热通道=4] | The THControlType of the NetCol5000CF110HALF. Value 1 indicates returnair. Value 2 indicates supplyair. Value 3 indicates coldaisle. Value 4 indicates hotaisle.
1.3.6.1.4.1.2011.6.178.1.1.66.1.1.200 | hwNetCol5000CF110HALFRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The unning row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.66.2 | hwNetCol5000CF110HALFRunning2Table | / | / |  |  | / | / | The running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.1 | hwNetCol5000CF110HALFRunning2Index | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.2 | hwNetCol5000CF110HALFSetEmsStatus | Startup/Shutdown control | 控制开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | The SetEmsStatus of the NetCol5000CF110HALF. Value 1 indicates on. Value 2 indicates off.
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.3 | hwNetCol5000CF110HALFSetTemperatureSetpoint | Temperature setpoint | 温度设定点 | 1-Read_Write | 读写 | 150..450 | 150..450 | The value range of the temperature setting point is related to the temperature and humidity control type. 1. When the temperature and humidity control type is return air; 2. When the temperature and humidity control type is used for air supply; 3. When the temperature and humidity control type is cold aisle; 4. When the temperature and humidity control type is hot aisle. Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.4 | hwNetCol5000CF110HALFSetHumiditySetpoint | Humidity setpoint | 湿度设定点 | 1-Read_Write | 读写 | 150..800 | 150..800 | The SetHumiditySetpoint of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.5 | hwNetCol5000CF110HALFSetRetWaterTempDiff | Supply/return water temp difference setpoint | 供回水温差设定点 | 1-Read_Write | 读写 | 5..7 | 5..7 | The SetRetWaterTempDiff of the NetCol5000CF110HALF. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.6 | hwNetCol5000CF110HALFSetCoolManager | Cooling capacity management function | 冷量管理功能 | 1-Read_Write | 读写 | disable(1), enable(2) | [禁止=1]/[使能=2] | The SetCoolManager of the NetCol5000CF110HALF. Value 1 indicates disable. Value 2 indicates enable.
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.7 | hwNetCol5000CF110HALFSetLoadFactorTarget | Target cooling load factor | 制冷负载率目标值 | 1-Read_Write | 读写 | 50..90 | 50..90 | The SetLoadFactorTarget of the NetCol5000CF110HALF. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.8 | hwNetCol5000CF110HALFSetSupplyWaterTempUpper | Upper limit of water supply temperature | 供水温度上限 | 1-Read_Write | 读写 | 10..19 | 10..19 | The SetSupplyWaterTempUpper of the NetCol5000CF110HALF. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.9 | hwNetCol5000CF110HALFSetSupplyWaterTempLower | Lower limit of water supply temperature | 供水温度下限 | 1-Read_Write | 读写 | 10..19 | 10..19 | The SetSupplyWaterTempLower of the NetCol5000CF110HALF. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.10 | hwNetCol5000CF110HALFSetRetAirHTempAlmThreshold | Return air high temperature alarm threshold | 回风高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | The SetRetAirHTempAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.11 | hwNetCol5000CF110HALFSetRetAirLTempAlmThreshold | Return air low temperature alarm threshold | 回风低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | The SetRetAirLTempAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.12 | hwNetCol5000CF110HALFSetSupplyAirHTempAlmThreshold | Supply air high temperature alarm threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The SetSupplyAirHTempAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.13 | hwNetCol5000CF110HALFSetSupplyAirLTempAlmThreshold | Supply air low temperature alarm threshold | 送风低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | The SetSupplyAirLTempAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.14 | hwNetCol5000CF110HALFSetColdAisleHTempAlmThreshold | Cold aisle high temperature alarm threshold | 冷通道高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The SetColdAisleHTempAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.15 | hwNetCol5000CF110HALFSetColdAisleLTempAlmThreshold | Cold aisle low temperature alarm threshold | 冷通道低温告警阈值 | 1-Read_Write | 读写 | 50..150 | 50..150 | The SetColdAisleLTempAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.16 | hwNetCol5000CF110HALFSetHotAisleHTempAlmThreshold | Hot aisle high temperature alarm threshold | 热通道高温告警阈值 | 1-Read_Write | 读写 | 350..550 | 350..550 | The SetHotAisleHTempAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.17 | hwNetCol5000CF110HALFSetHotAisleLTempAlmThreshold | Hot aisle low temperature alarm threshold | 热通道低温告警阈值 | 1-Read_Write | 读写 | 50..200 | 50..200 | The SetHotAisleLTempAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.18 | hwNetCol5000CF110HALFSetHotHumAlmThreshold | High humidity alarm threshold | 高湿告警阈值 | 1-Read_Write | 读写 | 650..950 | 650..950 | The SetHotHumAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.19 | hwNetCol5000CF110HALFSetLowHumAlmThreshold | Low humidity alarm threshold | 低湿告警阈值 | 1-Read_Write | 读写 | 50..350 | 50..350 | The SetLowHumAlmThreshold of the NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.20 | hwNetCol5000CF110HALFDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The devicename of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.2.1.200 | hwNetCol5000CF110HALFRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The running row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.66.3 | hwNetCol5000CF110HALFRunning3Table | / | / |  |  | / | / | The running table of NetColCF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.1 | hwNetCol5000CF110HALFRunning3Index | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.2 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity1 | Calculated rated cooling capacity 1 | 额定制冷量计算值1 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 1 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.3 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity2 | Calculated rated cooling capacity 2 | 额定制冷量计算值2 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 2 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.4 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity3 | Calculated rated cooling capacity 3 | 额定制冷量计算值3 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 3 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.5 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity4 | Calculated rated cooling capacity 4 | 额定制冷量计算值4 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 4 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.6 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity5 | Calculated rated cooling capacity 5 | 额定制冷量计算值5 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 5 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.7 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity6 | Calculated rated cooling capacity 6 | 额定制冷量计算值6 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 6 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.8 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity7 | Calculated rated cooling capacity 7 | 额定制冷量计算值7 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 7 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.9 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity8 | Calculated rated cooling capacity 8 | 额定制冷量计算值8 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 8 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.10 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity9 | Calculated rated cooling capacity 9 | 额定制冷量计算值9 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 9 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.11 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity10 | Calculated rated cooling capacity 10 | 额定制冷量计算值10 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 10 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.12 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity11 | Calculated rated cooling capacity 11 | 额定制冷量计算值11 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 11 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.13 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity12 | Calculated rated cooling capacity 12 | 额定制冷量计算值12 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 12 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.14 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity13 | Calculated rated cooling capacity 13 | 额定制冷量计算值13 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 13 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.15 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity14 | Calculated rated cooling capacity 14 | 额定制冷量计算值14 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 14 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.16 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity15 | Calculated rated cooling capacity 15 | 额定制冷量计算值15 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 15 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.17 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity16 | Calculated rated cooling capacity 16 | 额定制冷量计算值16 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 16 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.18 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity17 | Calculated rated cooling capacity 17 | 额定制冷量计算值17 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 17 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.19 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity18 | Calculated rated cooling capacity 18 | 额定制冷量计算值18 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 18 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.20 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity19 | Calculated rated cooling capacity 19 | 额定制冷量计算值19 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 19 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.21 | hwNetCol5000CF110HALFCalculatedratedcoolingcapacity20 | Calculated rated cooling capacity 20 | 额定制冷量计算值20 | 0-Read_Only | 只读 | 0..2000000 | 0..2000000 | The Calculated rated cooling capacity 20 of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.22 | hwNetCol5000CF110HALFHeatMode | Heat mode | 加热方式 | 0-Read_Only | 只读 | dehumidheat(1), lowtempheat(2), dehumidltheat(3) | [除湿补热=1]/[低温加热=2]/[除湿补热且低温加热=3] | The Heat Mode of NetCol5000CF110HALF. Value 1 indicates dehumidheat. Value 2 indicates lowtempheat. Value 3 indicates dehumidltheat.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.23 | hwNetCol5000CF110HALFHeatFunc | Heat | 加热功能 | 0-Read_Only | 只读 | disable(1), enable(2), enableinactivepowersupply(3), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The Heat Func of NetCol5000CF110HALF. Value 1 indicates Disable. Value 2 indicates Enable. Value 3 indicates enable in active power supply.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.24 | hwNetCol5000CF110HALFHumidFunc | Humidity | 加湿功能 | 0-Read_Only | 只读 | disable(1), enable(2), enableinactivepowersupply(3), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The Heat Func of NetCol5000CF110HALF. Value 1 indicates Disable. Value 2 indicates Enable. Value 3 indicates enable in active power supply.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.25 | hwNetCol5000CF110HALFDehumidFunc | Dehumidity | 除湿功能 | 0-Read_Only | 只读 | disable(1), enable(2), enableinactivepowersupply(3), unknown(255) | [禁止=1]/[使能=2]/[主路供电时使能=3] | The Heat Func of NetCol5000CF110HALF. Value 1 indicates Disable. Value 2 indicates Enable. Value 3 indicates enable in active power supply.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.26 | hwNetCol5000CF110HALFTeamworkFunction | Teamwork function | 群控功能 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | The Teamwork Function of NetCol5000CF110HALF. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.27 | hwNetCol5000CF110HALFTotalnumberofactualunits | Total number of actual units | 本群组实际机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The Total number of actual units of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.28 | hwNetCol5000CF110HALFNumberofactiveunits | Number of active units | 本群组实际运行机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The Number of active units of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.29 | hwNetCol5000CF110HALFNumberofstandbyunits | Number of standby units | 本群组实际备机机组数目 | 0-Read_Only | 只读 | 0..32 | 0..32 | The Number of standby units of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.30 | hwNetCol5000CF110HALFTeamworkMode | Teamwork mode | 群控模式 | 0-Read_Only | 只读 | smart(1), iCooling(2), unknown(255) | [智能=1]/[iCooling=2] | The Teamwork Mode of NetCol5000CF110HALF. Value 1 indicates Smart. Value 2 indicates iCooling.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.31 | hwNetCol5000CF110HALFIndoorFanCtrlType | Indoor fan control type | 室内风机控制类型 | 0-Read_Only | 只读 | randsairtempdiffratecontrol(1), pressurediffcontrol(2), supairtempcontrol(3), unknown(255) | [回送风温差比例控制=1]/[压差控制=2]/[送风温度控制=3] | The Indoor Fan Ctrl Type of NetCol5000CF110HALF. Value 1 indicates R/S air temp diff rate control. Value 2 indicates Pressure diff control. Value 3 indicates Sup air temp control.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.32 | hwNetCol5000CF110HALFElectric | Electricity | 电量 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The Electric of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.33 | hwNetCol5000CF110HALFPower | Power | 功率 | 0-Read_Only | 只读 | 0..1000000 | 0..1000000 | The Power of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.34 | hwNetCol5000CF110HALFNumberofcondpumps | Number of cond pumps | 水泵数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Number of condpumps of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.35 | hwNetCol5000CF110HALFNumberofindoorfans | Number of indoor fans | 风机数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Number of indoorfans of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.36 | hwNetCol5000CF110HALFNumberofCWvalves | Number of CW valves | 冷冻水阀数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The Number of CWvalves of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.37 | hwNetCol5000CF110HALFNumberofPSU | Number of PSU | PSU数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The Number of PSU of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.38 | hwNetCol5000CF110HALFNumberofHumidifiers | Number of humidifiers | 加湿器数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The Number of Humidifiers of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.39 | hwNetCol5000CF110HALFNumberofHeaters | Number of heaters | 加热器数量 | 0-Read_Only | 只读 | 0..255 | 0..255 | The Number of Heaters of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.40 | hwNetCol5000CF110HALFTeamworkUnitAddress | Air conditioner address | 机组地址 | 0-Read_Only | 只读 | 1..32 | 1..32 | The Teamwork UnitAddress of NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.41 | hwNetCol5000CF110HALFCurr | Current | 电流 | 0-Read_Only | 只读 | -100000..100000 | -100000..100000 | The Curr of NetCol5000CF110HALF.Multiple:100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.42 | hwNetCol5000CF110HALFiCoolingRunningStatus | iCooling run status | iCooling运行状态 | 0-Read_Only | 只读 | normal(1), abnormalairconditioner(2), invalidcabinettemperature(3), invalidcabinetpower(4), dataupdatingtimeout(5), inconsistentnumberofteamworkunits(6), notcoldaislecontainment(7), unknown(255) | [正常=1]/[空调异常=2]/[机柜温度无效=3]/[机柜功率无效=4]/[数据更新超时=5]/[群控机组数目不一致=6]/[封闭通道非冷通道=7] | The iCooling Running Status of NetCol5000CF110HALF. Value 1 indicates Normal. Value 2 indicates Abnormal air conditioner. Value 3 indicates Invalid cabinet temperature. Value 4 indicates Invalid cabinet power. Value 5 indicates Data updating timeout. Value 6 indicates Inconsistent number of teamwork units. Value 7 indicates Not cold aisle containment.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.43 | hwNetCol5000CF110HALFSupplyAirHighTemperatureAlarmThreshold | Supply air high temperature alarm threshold | 送风高温告警阈值 | 1-Read_Write | 读写 | 200..500 | 200..500 | The Supply Air High Temperature Alarm Threshold of NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.44 | hwNetCol5000CF110HALFL1L2linkagetemperature | L1/L2 linkage target temperature | L1/L2联动目标温度 | 1-Read_Write | 读写 | 150..450 | 150..450 | The L1 L2 linkage temperature of NetCol5000CF110HALF.Multiple:10. SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.45 | hwNetCol5000CF110HALFL1L2linkagehumdity | L1/L2 linkage target humidity | L1/L2联动目标湿度 | 1-Read_Write | 读写 | 20..800 | 20..800 | The L1 L2 linkage humidity of NetCol5000CF110HALF.Multiple:10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.46 | hwNetCol5000CF110HALFhardwareversion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | The hardware version of the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.47 | hwNetCol5000CF110HALFHostFlag | Host identity | 主机标志 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | The Host Flag of the NetCol5000CF110HALF. value 1 indicates slave, value 2 indicates master,
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.48 | hwNetCol5000CF110HALFIndoorFan1RunStatus | Indoor fan 1 run status | 室内风机1运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan1 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.49 | hwNetCol5000CF110HALFIndoorFan2RunStatus | Indoor fan 2 run status | 室内风机2运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan2 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.50 | hwNetCol5000CF110HALFIndoorFan3RunStatus | Indoor fan 3 run status | 室内风机3运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan3 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.51 | hwNetCol5000CF110HALFIndoorFan4RunStatus | Indoor fan 4 run status | 室内风机4运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan4 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.52 | hwNetCol5000CF110HALFIndoorFan5RunStatus | Indoor fan 5 run status | 室内风机5运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan5 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.53 | hwNetCol5000CF110HALFIndoorFan6RunStatus | Indoor fan 6 run status | 室内风机6运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan6 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.54 | hwNetCol5000CF110HALFIndoorFan7RunStatus | Indoor fan 7 run status | 室内风机7运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan7 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.55 | hwNetCol5000CF110HALFIndoorFan8RunStatus | Indoor fan 8 run status | 室内风机8运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan8 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.56 | hwNetCol5000CF110HALFIndoorFan9RunStatus | Indoor fan 9 run status | 室内风机9运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan9 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.57 | hwNetCol5000CF110HALFIndoorFan10RunStatus | Indoor fan 10 run status | 室内风机10运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan10 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.58 | hwNetCol5000CF110HALFIndoorFan11RunStatus | Indoor fan 11 run status | 室内风机11运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan11 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.59 | hwNetCol5000CF110HALFIndoorFan12RunStatus | Indoor fan 12 run status | 室内风机12运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan12 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.60 | hwNetCol5000CF110HALFDehumid | Dehumid | 除湿输出 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Dehumid of the NetCol5000CF110HALF.SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.61 | hwNetCol5000CF110HALFMasterSlaveFlag | Master/Slave flag | 主从机标志 | 0-Read_Only | 只读 | slave(1), master(2), unknown(255) | [从机=1]/[主机=2] | The Master Slave flag of the NetCol5000CF110HALF. Value 1 indicates Slave. Value 2 indicates Master.
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.62 | hwNetCol5000CF110HALFIndoorFanPressureDifferenceSetPoint | Indoor fan pressure difference setpoint | 室内风机压差设定点 | 0-Read_Only | 只读 | 5..45 | 5..45 | The Indoor fan pressure difference setpoint of the NetCol5000CF110HALF.SigUnitInfo:Pa
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.63 | hwNetCol5000CF110HALFIndoorFanSupplyAirTemperatureSetPoint | Indoor fan supply air temperature setpoint | 室内风机送风温度设定点 | 0-Read_Only | 只读 | 150..350 | 150..350 | The Indoor fan supply air temperature setpoint of the NetCol5000CF110HALF.SigUnitInfo:Degrees Celcius
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.64 | hwNetCol5000CF110HALFWetFilmHumidifierRunningStatus | Wet film humidifier running status | 湿膜加湿运行状态 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Wet film humidifier running status of the NetCol5000CF110HALF.SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.65 | hwNetCol5000CF110HALFWetFilmHumidifierControlStatus | Wet film humidifier control status | 湿膜加湿控制状态 | 1-Read_Only |  | 0..100 | 0..100 | The Wet film humidifier control status of the NetCol5000CF110HALF.SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.66.3.1.100 | hwNetCol5000CF110HALFRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the NetCol5000CF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.4 | hwNetCol5000CF110HALFConfig1Table | / | / |  |  | / | / | The config table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.66.4.1.1 | hwNetCol5000CF110HALFConfig1Index | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.66.4.1.2 | hwNetCol5000CF110HALFIndoorFanMaxReturnSupplyAirTempDiff | Indoor fan max return/supply air temperature difference | 室内风机回送风最大温差 | 1-Read_Write | 读写 | 10..200 | 10..200 | The Indoor fan max return/supply air temperature difference of the NetCol5000CF110HALF.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.66.4.1.3 | hwNetCol5000CF110HALFIndoorFanTempDiffrence | Indoor fan temperature difference set point | 室内风机温差设定点 | 1-Read_Write | 读写 | 0..450 | 0..450 | The Indoor fan temperature difference set point of the NetCol5000CF110HALF.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.66.4.1.4 | hwNetCol5000CF110HALFTempsetpointhigh | Indoor fan pressure difference setpoint | 室内风机压差设定点 | 1-Read_Write | 读写 | 5..45 | 5..45 | Temp set point high of the NetCol5000CF110HALF.SigUnitInfo:Pa.
1.3.6.1.4.1.2011.6.178.1.1.66.4.1.100 | hwNetCol5000CF110HALFHALFConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The config row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.66.5 | hwNetCol5000CF110HALFRunning5Table | / | / |  |  | / | / | The running table of NetColCF110HALF.
1.3.6.1.4.1.2011.6.178.1.1.66.5.1.1 | hwNetCol5000CF110HALFRunning5Index | / | / | 0-Read_Only | 只读 | / | / | The ndex of running table of NetCol.
1.3.6.1.4.1.2011.6.178.1.1.66.5.1.2 | hwNetCol5000CF110HALFIndoorFan13totalRuntime | Indoor fan 13 total runtime | 室内风机13累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan13totalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.5.1.3 | hwNetCol5000CF110HALFIndoorFan14totalRuntime | Indoor fan 14 total runtime | 室内风机14累计运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | The IndoorFan14totalRuntime of the NetCol5000CF110HALF. SigUnitInfo:h
1.3.6.1.4.1.2011.6.178.1.1.66.5.1.4 | hwNetCol5000CF110HALFIndoorFan13RunStatus | Indoor fan 13 run status | 室内风机13运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan13 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.5.1.5 | hwNetCol5000CF110HALFIndoorFan14RunStatus | Indoor fan 14 run status | 室内风机14运行状态 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Indoor Fan14 Run Status of the NetCol5000CF110HALF. SigUnitInfo:rpm
1.3.6.1.4.1.2011.6.178.1.1.66.5.1.100 | hwNetCol5000CF110HALFRunning5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the NetCol5000CF110HALF.

## CompensatingCabinet
补偿柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.124 | CompensatingCabinet | CompensatingCabinet | 补偿柜 | / | / | / | / | CompensatingCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.124.1 | hwCompensatingCabinetRunning1Table | / | / |  |  | / | / | The running table of CompensatingCabinet.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.1 | hwCompensatingCabinetRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the CompensatingCabinet.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.2 | hwCompensatingCabinetDeviceStatus | Device status | 装置状态 | 0-Read_Only | 只读 | fault(1), run(2), suspended(3), unknown(255) | [故障=1]/[运行=2]/[停机=3] | Device status of the device config table for the CompensatingCabinet. Value 1 indicate fault Value 2 indicate run Value 3 indicate suspended
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.3 | hwCompensatingCabinetCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the CompensatingCabinet. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.4 | hwCompensatingCabinetPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the CompensatingCabinet.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.5 | hwCompensatingCabinetModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..247 | 1..247 | Modbus address of the device config table for the CompensatingCabinet.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.6 | hwCompensatingCabinetDeviceCompensationCurrentA | Device compensation current A | 装置补偿电流A | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Device compensation current A of the device config table for the CompensatingCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.7 | hwCompensatingCabinetDeviceCompensationCurrentB | Device compensation current B | 装置补偿电流B | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Device compensation current B of the device config table for the CompensatingCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.8 | hwCompensatingCabinetDeviceCompensationCurrentC | Device compensation current C | 装置补偿电流C | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Device compensation current C of the device config table for the CompensatingCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.9 | hwCompensatingCabinetTemperatureOfTheDevice | Temperature of the device | 装置温度 | 0-Read_Only | 只读 | -100..200 | -100..200 | Temperature of the device of the device config table for the CompensatingCabinet.SigUnitInfo:Celcius.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.10 | hwCompensatingCabinetEffectiveValueOfLoadCurrentA | Effective value of load current A | 负载电流有效值A | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current A of the device config table for the CompensatingCabinet.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.11 | hwCompensatingCabinetEffectiveValueOfLoadCurrentB | Effective value of load current B | 负载电流有效值B | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current B of the device config table for the CompensatingCabinet.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.12 | hwCompensatingCabinetEffectiveValueOfLoadCurrentC | Effective value of load current C | 负载电流有效值C | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current C of the device config table for the CompensatingCabinet.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.13 | hwCompensatingCabinetEffectiveValueOfLineVoltageAb | Effective value of line voltage AB | 线电压有效值AB | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Effective value of line voltage AB of the device config table for the CompensatingCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.14 | hwCompensatingCabinetEffectiveValueOfLineVoltageBc | Effective value of line voltage BC | 线电压有效值BC | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Effective value of line voltage BC of the device config table for the CompensatingCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.15 | hwCompensatingCabinetEffectiveValueOfLineVoltageCa | Effective value of line voltage CA | 线电压有效值CA | 0-Read_Only | 只读 | 0..32767 | 0..32767 | Effective value of line voltage CA of the device config table for the CompensatingCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.16 | hwCompensatingCabinetSystemCurrentDistortionRate | System current distortion rate | 系统电流畸变率 | 0-Read_Only | 只读 | 0..32767 | 0..32767 | System current distortion rate of the device config table for the CompensatingCabinet.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.17 | hwCompensatingCabinetSystemPowerFactor | System power factor | 系统功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | System power factor of the device config table for the CompensatingCabinet.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.18 | hwCompensatingCabinetEquipmentLoadRate | Equipment load rate | 设备负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Equipment load rate of the device config table for the CompensatingCabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.124.1.1.300 | hwCompensatingCabinetRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of CompensatingCabinet.
1.3.6.1.4.1.2011.6.178.1.1.124.2 | hwCompensatingCabinetConfig2Table | / | / |  |  | / | / | The config table of CompensatingCabinet.
1.3.6.1.4.1.2011.6.178.1.1.124.2.1.1 | hwCompensatingCabinetConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the CompensatingCabinet.
1.3.6.1.4.1.2011.6.178.1.1.124.2.1.2 | hwCompensatingCabinetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the CompensatingCabinet.
1.3.6.1.4.1.2011.6.178.1.1.124.2.1.3 | hwCompensatingCabinetStartAndStopControl | Start and stop control | 启停控制 | 1-Read_Write | 读写 | localControl(1), startFromAfar(2), stopFromAfar(3), unknown(255) | [就地控制=1]/[远方启动=2]/[远方停止=3] | Start and stop control of the device config table for the CompensatingCabinet. Value 1 indicate local control Value 2 indicate start from afar Value 3 indicate stop from afar
1.3.6.1.4.1.2011.6.178.1.1.124.2.1.300 | hwCompensatingCabinetConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of CompensatingCabinet.

## TP483000D DC PDF
TP483000D直流配电柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.68 | dcpdc | TP483000D DC PDF | TP483000D直流配电柜 | / | / | / | / | DC pdc Equipment.
1.3.6.1.4.1.2011.6.178.1.1.68.1 | hwdcpdcRunningTable | / | / |  |  | / | / | The running table of DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.1 | hwdcpdcRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.2 | hwdcpdcCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the DC pdc. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.3 | hwdcpdcSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | The Software version of the DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.4 | hwdcpdcHardVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | The Hard version of the DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.5 | hwdcpdcPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The Port No. of the DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.6 | hwdcpdcModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Modbus address of the DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.7 | hwdcpdcDCvolt | DC volt | 直流电压 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The DC volt of the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.8 | hwdcpdcLoadcurrent | Load current | 负载电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Load currentof the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.9 | hwdcpdcLoadpower | Load power | 负载功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The Load powerof the DC pdc.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.10 | hwdcpdcNumberofloadfuse | Load fuse | 负载熔丝路数 | 0-Read_Only | 只读 | 0..42 | 0..42 | The Number of load fuse of the DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.11 | hwdcpdcESN | ESN No. | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | The ESN of the DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.12 | hwdcpdcDevicename | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device name for the DC pdc.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.13 | hwdcpdcDu1DcVoltage | DU1 DC voltage | 配电单元1直流电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | DU1 DC voltage of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.14 | hwdcpdcDu1TotalLoadCurrent | DU1 total load current | 配电单元1总负载电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 total load current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.15 | hwdcpdcDu1BatteryCurrent1 | DU1 battery current 1 | 配电单元1电池电流1 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current1 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.16 | hwdcpdcDu1BatteryCurrent2 | DU1 battery current 2 | 配电单元1电池电流2 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current2 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.17 | hwdcpdcDu1BatteryCurrent3 | DU1 battery current 3 | 配电单元1电池电流3 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current3 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.18 | hwdcpdcDu1BatteryCurrent4 | DU1 battery current 4 | 配电单元1电池电流4 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current4 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.19 | hwdcpdcDu1BatteryCurrent5 | DU1 battery current 5 | 配电单元1电池电流5 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current5 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.20 | hwdcpdcDu1BatteryCurrent6 | DU1 battery current 6 | 配电单元1电池电流6 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current6 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.21 | hwdcpdcDu1BatteryCurrent7 | DU1 battery current 7 | 配电单元1电池电流7 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current7 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.22 | hwdcpdcDu1BatteryCurrent8 | DU1 battery current 8 | 配电单元1电池电流8 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current8 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.23 | hwdcpdcDu1BatteryCurrent9 | DU1 battery current 9 | 配电单元1电池电流9 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current9 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.24 | hwdcpdcDu1BatteryCurrent10 | DU1 battery current 10 | 配电单元1电池电流10 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU1 battery current10 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.25 | hwdcpdcDu1BatteryMidpointVoltage1 | DU1 battery midpoint voltage 1 | 配电单元1电池串1中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 1 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.26 | hwdcpdcDu1BatteryMidpointVoltage2 | DU1 battery midpoint voltage 2 | 配电单元1电池串2中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 2 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.27 | hwdcpdcDu1BatteryMidpointVoltage3 | DU1 battery midpoint voltage 3 | 配电单元1电池串3中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 3 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.28 | hwdcpdcDu1BatteryMidpointVoltage4 | DU1 battery midpoint voltage 4 | 配电单元1电池串4中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 4 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.29 | hwdcpdcDu1BatteryMidpointVoltage5 | DU1 battery midpoint voltage 5 | 配电单元1电池串5中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 5 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.30 | hwdcpdcDu1BatteryMidpointVoltage6 | DU1 battery midpoint voltage 6 | 配电单元1电池串6中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 6 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.31 | hwdcpdcDu1BatteryMidpointVoltage7 | DU1 battery midpoint voltage 7 | 配电单元1电池串7中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 7 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.32 | hwdcpdcDu1BatteryMidpointVoltage8 | DU1 battery midpoint voltage 8 | 配电单元1电池串8中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 8 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.33 | hwdcpdcDu1BatteryMidpointVoltage9 | DU1 battery midpoint voltage 9 | 配电单元1电池串9中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 9 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.34 | hwdcpdcDu1BatteryMidpointVoltage10 | DU1 battery midpoint voltage 10 | 配电单元1电池串10中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU1 battery midpoint voltage 10 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.35 | hwdcpdcDu1Load1Current | DU1 load 1 current | 配电单元1负载1电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load1 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.36 | hwdcpdcDu1Load2Current | DU1 load 2 current | 配电单元1负载2电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load2 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.37 | hwdcpdcDu1Load3Current | DU1 load 3 current | 配电单元1负载3电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load3 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.38 | hwdcpdcDu1Load4Current | DU1 load 4 current | 配电单元1负载4电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load4 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.39 | hwdcpdcDu1Load5Current | DU1 load 5 current | 配电单元1负载5电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load5 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.40 | hwdcpdcDu1Load6Current | DU1 load 6 current | 配电单元1负载6电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load6 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.41 | hwdcpdcDu1Load7Current | DU1 load 7 current | 配电单元1负载7电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load7 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.42 | hwdcpdcDu1Load8Current | DU1 load 8 current | 配电单元1负载8电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load8 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.43 | hwdcpdcDu1Load9Current | DU1 load 9 current | 配电单元1负载9电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load9 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.44 | hwdcpdcDu1Load10Current | DU1 load 10 current | 配电单元1负载10电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load10 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.45 | hwdcpdcDu1Load11Current | DU1 load 11 current | 配电单元1负载11电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load11 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.46 | hwdcpdcDu1Load12Current | DU1 load 12 current | 配电单元1负载12电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load12 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.47 | hwdcpdcDu1Load13Current | DU1 load 13 current | 配电单元1负载13电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load13 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.48 | hwdcpdcDu1Load14Current | DU1 load 14 current | 配电单元1负载14电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load14 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.49 | hwdcpdcDu1Load15Current | DU1 load 15 current | 配电单元1负载15电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load15 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.50 | hwdcpdcDu1Load16Current | DU1 load 16 current | 配电单元1负载16电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load16 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.51 | hwdcpdcDu1Load17Current | DU1 load 17 current | 配电单元1负载17电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load17 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.52 | hwdcpdcDu1Load18Current | DU1 load 18 current | 配电单元1负载18电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load18 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.53 | hwdcpdcDu1Load19Current | DU1 load 19 current | 配电单元1负载19电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load19 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.54 | hwdcpdcDu1Load20Current | DU1 load 20 current | 配电单元1负载20电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load20 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.55 | hwdcpdcDu1Load21Current | DU1 load 21 current | 配电单元1负载21电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load21 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.56 | hwdcpdcDu1Load22Current | DU1 load 22 current | 配电单元1负载22电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load22 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.57 | hwdcpdcDu1Load23Current | DU1 load 23 current | 配电单元1负载23电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load23 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.58 | hwdcpdcDu1Load24Current | DU1 load 24 current | 配电单元1负载24电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load24 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.59 | hwdcpdcDu1Load25Current | DU1 load 25 current | 配电单元1负载25电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load25 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.60 | hwdcpdcDu1Load26Current | DU1 load 26 current | 配电单元1负载26电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load26 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.61 | hwdcpdcDu1Load27Current | DU1 load 27 current | 配电单元1负载27电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load27 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.62 | hwdcpdcDu1Load28Current | DU1 load 28 current | 配电单元1负载28电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load28 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.63 | hwdcpdcDu1Load29Current | DU1 load 29 current | 配电单元1负载29电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load29 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.64 | hwdcpdcDu1Load30Current | DU1 load 30 current | 配电单元1负载30电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 load30 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.65 | hwdcpdcDu1DcLoad1Power | DU1 DC load 1 power | 配电单元1直流负载1功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load1 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.66 | hwdcpdcDu1DcLoad2Power | DU1 DC load 2 power | 配电单元1直流负载2功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load2 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.67 | hwdcpdcDu1DcLoad3Power | DU1 DC load 3 power | 配电单元1直流负载3功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load3 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.68 | hwdcpdcDu1DcLoad4Power | DU1 DC load 4 power | 配电单元1直流负载4功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load4 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.69 | hwdcpdcDu1DcLoad5Power | DU1 DC load 5 power | 配电单元1直流负载5功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load5 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.70 | hwdcpdcDu1DcLoad6Power | DU1 DC load 6 power | 配电单元1直流负载6功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load6 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.71 | hwdcpdcDu1DcLoad7Power | DU1 DC load 7 power | 配电单元1直流负载7功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load7 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.72 | hwdcpdcDu1DcLoad8Power | DU1 DC load 8 power | 配电单元1直流负载8功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load8 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.73 | hwdcpdcDu1DcLoad9Power | DU1 DC load 9 power | 配电单元1直流负载9功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load9 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.74 | hwdcpdcDu1DcLoad10Power | DU1 DC load 10 power | 配电单元1直流负载10功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load10 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.75 | hwdcpdcDu1DcLoad11Power | DU1 DC load 11 power | 配电单元1直流负载11功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load11 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.76 | hwdcpdcDu1DcLoad12Power | DU1 DC load 12 power | 配电单元1直流负载12功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load12 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.77 | hwdcpdcDu1DcLoad13Power | DU1 DC load 13 power | 配电单元1直流负载13功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load13 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.78 | hwdcpdcDu1DcLoad14Power | DU1 DC load 14 power | 配电单元1直流负载14功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load14 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.79 | hwdcpdcDu1DcLoad15Power | DU1 DC load 15 power | 配电单元1直流负载15功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load15 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.80 | hwdcpdcDu1DcLoad16Power | DU1 DC load 16 power | 配电单元1直流负载16功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load16 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.81 | hwdcpdcDu1DcLoad17Power | DU1 DC load 17 power | 配电单元1直流负载17功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load17 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.82 | hwdcpdcDu1DcLoad18Power | DU1 DC load 18 power | 配电单元1直流负载18功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load18 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.83 | hwdcpdcDu1DcLoad19Power | DU1 DC load 19 power | 配电单元1直流负载19功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load19 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.84 | hwdcpdcDu1DcLoad20Power | DU1 DC load 20 power | 配电单元1直流负载20功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load20 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.85 | hwdcpdcDu1DcLoad21Power | DU1 DC load 21 power | 配电单元1直流负载21功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load21 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.86 | hwdcpdcDu1DcLoad22Power | DU1 DC load 22 power | 配电单元1直流负载22功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load22 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.87 | hwdcpdcDu1DcLoad23Power | DU1 DC load 23 power | 配电单元1直流负载23功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load23 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.88 | hwdcpdcDu1DcLoad24Power | DU1 DC load 24 power | 配电单元1直流负载24功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load24 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.89 | hwdcpdcDu1DcLoad25Power | DU1 DC load 25 power | 配电单元1直流负载25功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load25 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.90 | hwdcpdcDu1DcLoad26Power | DU1 DC load 26 power | 配电单元1直流负载26功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load26 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.91 | hwdcpdcDu1DcLoad27Power | DU1 DC load 27 power | 配电单元1直流负载27功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load27 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.92 | hwdcpdcDu1DcLoad28Power | DU1 DC load 28 power | 配电单元1直流负载28功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load28 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.93 | hwdcpdcDu1DcLoad29Power | DU1 DC load 29 power | 配电单元1直流负载29功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load29 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.94 | hwdcpdcDu1DcLoad30Power | DU1 DC load 30 power | 配电单元1直流负载30功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU1 DC load30 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.95 | hwdcpdcDu2DcVoltage | DU2 DC voltage | 配电单元2直流电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | DU2 DC voltage of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.96 | hwdcpdcDu2TotalLoadCurrent | DU2 total load current | 配电单元2总负载电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 total load current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.97 | hwdcpdcDu2BatteryCurrent1 | DU2 battery current 1 | 配电单元2电池电流1 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current1 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.98 | hwdcpdcDu2BatteryCurrent2 | DU2 battery current 2 | 配电单元2电池电流2 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current2 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.99 | hwdcpdcDu2BatteryCurrent3 | DU2 battery current 3 | 配电单元2电池电流3 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current3 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.100 | hwdcpdcDu2BatteryCurrent4 | DU2 battery current 4 | 配电单元2电池电流4 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current4 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.101 | hwdcpdcDu2BatteryCurrent5 | DU2 battery current 5 | 配电单元2电池电流5 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current5 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.102 | hwdcpdcDu2BatteryCurrent6 | DU2 battery current 6 | 配电单元2电池电流6 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current6 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.103 | hwdcpdcDu2BatteryCurrent7 | DU2 battery current 7 | 配电单元2电池电流7 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current7 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.104 | hwdcpdcDu2BatteryCurrent8 | DU2 battery current 8 | 配电单元2电池电流8 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current8 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.105 | hwdcpdcDu2BatteryCurrent9 | DU2 battery current 9 | 配电单元2电池电流9 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current9 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.106 | hwdcpdcDu2BatteryCurrent10 | DU2 battery current 10 | 配电单元2电池电流10 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU2 battery current10 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.107 | hwdcpdcDu2BatteryMidpointVoltage1 | DU2 battery midpoint voltage 1 | 配电单元2电池串1中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 1 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.108 | hwdcpdcDu2BatteryMidpointVoltage2 | DU2 battery midpoint voltage 2 | 配电单元2电池串2中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 2 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.109 | hwdcpdcDu2BatteryMidpointVoltage3 | DU2 battery midpoint voltage 3 | 配电单元2电池串3中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 3 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.110 | hwdcpdcDu2BatteryMidpointVoltage4 | DU2 battery midpoint voltage 4 | 配电单元2电池串4中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 4 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.111 | hwdcpdcDu2BatteryMidpointVoltage5 | DU2 battery midpoint voltage 5 | 配电单元2电池串5中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 5 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.112 | hwdcpdcDu2BatteryMidpointVoltage6 | DU2 battery midpoint voltage 6 | 配电单元2电池串6中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 6 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.113 | hwdcpdcDu2BatteryMidpointVoltage7 | DU2 battery midpoint voltage 7 | 配电单元2电池串7中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 7 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.114 | hwdcpdcDu2BatteryMidpointVoltage8 | DU2 battery midpoint voltage 8 | 配电单元2电池串8中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 8 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.115 | hwdcpdcDu2BatteryMidpointVoltage9 | DU2 battery midpoint voltage 9 | 配电单元2电池串9中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 9 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.116 | hwdcpdcDu2BatteryMidpointVoltage10 | DU2 battery midpoint voltage 10 | 配电单元2电池串10中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU2 battery midpoint voltage 10 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.117 | hwdcpdcDu2Load1Current | DU2 load 1 current | 配电单元2负载1电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load1 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.118 | hwdcpdcDu2Load2Current | DU2 load 2 current | 配电单元2负载2电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load2 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.119 | hwdcpdcDu2Load3Current | DU2 load 3 current | 配电单元2负载3电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load3 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.120 | hwdcpdcDu2Load4Current | DU2 load 4 current | 配电单元2负载4电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load4 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.121 | hwdcpdcDu2Load5Current | DU2 load 5 current | 配电单元2负载5电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load5 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.122 | hwdcpdcDu2Load6Current | DU2 load 6 current | 配电单元2负载6电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load6 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.123 | hwdcpdcDu2Load7Current | DU2 load 7 current | 配电单元2负载7电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load7 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.124 | hwdcpdcDu2Load8Current | DU2 load 8 current | 配电单元2负载8电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load8 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.125 | hwdcpdcDu2Load9Current | DU2 load 9 current | 配电单元2负载9电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load9 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.126 | hwdcpdcDu2Load10Current | DU2 load 10 current | 配电单元2负载10电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load10 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.127 | hwdcpdcDu2Load11Current | DU2 load 11 current | 配电单元2负载11电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load11 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.128 | hwdcpdcDu2Load12Current | DU2 load 12 current | 配电单元2负载12电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load12 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.129 | hwdcpdcDu2Load13Current | DU2 load 13 current | 配电单元2负载13电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load13 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.130 | hwdcpdcDu2Load14Current | DU2 load 14 current | 配电单元2负载14电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load14 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.131 | hwdcpdcDu2Load15Current | DU2 load 15 current | 配电单元2负载15电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load15 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.132 | hwdcpdcDu2Load16Current | DU2 load 16 current | 配电单元2负载16电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load16 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.133 | hwdcpdcDu2Load17Current | DU2 load 17 current | 配电单元2负载17电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load17 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.134 | hwdcpdcDu2Load18Current | DU2 load 18 current | 配电单元2负载18电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load18 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.135 | hwdcpdcDu2Load19Current | DU2 load 19 current | 配电单元2负载19电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load19 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.136 | hwdcpdcDu2Load20Current | DU2 load 20 current | 配电单元2负载20电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load20 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.137 | hwdcpdcDu2Load21Current | DU2 load 21 current | 配电单元2负载21电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load21 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.138 | hwdcpdcDu2Load22Current | DU2 load 22 current | 配电单元2负载22电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load22 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.139 | hwdcpdcDu2Load23Current | DU2 load 23 current | 配电单元2负载23电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load23 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.140 | hwdcpdcDu2Load24Current | DU2 load 24 current | 配电单元2负载24电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load24 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.141 | hwdcpdcDu2Load25Current | DU2 load 25 current | 配电单元2负载25电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load25 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.142 | hwdcpdcDu2Load26Current | DU2 load 26 current | 配电单元2负载26电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load26 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.143 | hwdcpdcDu2Load27Current | DU2 load 27 current | 配电单元2负载27电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load27 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.144 | hwdcpdcDu2Load28Current | DU2 load 28 current | 配电单元2负载28电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load28 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.145 | hwdcpdcDu2Load29Current | DU2 load 29 current | 配电单元2负载29电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load29 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.146 | hwdcpdcDu2Load30Current | DU2 load 30 current | 配电单元2负载30电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 load30 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.147 | hwdcpdcDu2DcLoad1Power | DU2 DC load 1 power | 配电单元2直流负载1功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load1 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.148 | hwdcpdcDu2DcLoad2Power | DU2 DC load 2 power | 配电单元2直流负载2功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load2 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.149 | hwdcpdcDu2DcLoad3Power | DU2 DC load 3 power | 配电单元2直流负载3功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load3 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.150 | hwdcpdcDu2DcLoad4Power | DU2 DC load 4 power | 配电单元2直流负载4功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load4 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.151 | hwdcpdcDu2DcLoad5Power | DU2 DC load 5 power | 配电单元2直流负载5功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load5 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.152 | hwdcpdcDu2DcLoad6Power | DU2 DC load 6 power | 配电单元2直流负载6功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load6 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.153 | hwdcpdcDu2DcLoad7Power | DU2 DC load 7 power | 配电单元2直流负载7功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load7 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.154 | hwdcpdcDu2DcLoad8Power | DU2 DC load 8 power | 配电单元2直流负载8功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load8 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.155 | hwdcpdcDu2DcLoad9Power | DU2 DC load 9 power | 配电单元2直流负载9功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load9 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.156 | hwdcpdcDu2DcLoad10Power | DU2 DC load 10 power | 配电单元2直流负载10功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load10 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.157 | hwdcpdcDu2DcLoad11Power | DU2 DC load 11 power | 配电单元2直流负载11功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load11 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.158 | hwdcpdcDu2DcLoad12Power | DU2 DC load 12 power | 配电单元2直流负载12功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load12 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.159 | hwdcpdcDu2DcLoad13Power | DU2 DC load 13 power | 配电单元2直流负载13功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load13 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.160 | hwdcpdcDu2DcLoad14Power | DU2 DC load 14 power | 配电单元2直流负载14功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load14 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.161 | hwdcpdcDu2DcLoad15Power | DU2 DC load 15 power | 配电单元2直流负载15功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load15 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.162 | hwdcpdcDu2DcLoad16Power | DU2 DC load 16 power | 配电单元2直流负载16功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load16 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.163 | hwdcpdcDu2DcLoad17Power | DU2 DC load 17 power | 配电单元2直流负载17功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load17 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.164 | hwdcpdcDu2DcLoad18Power | DU2 DC load 18 power | 配电单元2直流负载18功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load18 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.165 | hwdcpdcDu2DcLoad19Power | DU2 DC load 19 power | 配电单元2直流负载19功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load19 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.166 | hwdcpdcDu2DcLoad20Power | DU2 DC load 20 power | 配电单元2直流负载20功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load20 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.167 | hwdcpdcDu2DcLoad21Power | DU2 DC load 21 power | 配电单元2直流负载21功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load21 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.168 | hwdcpdcDu2DcLoad22Power | DU2 DC load 22 power | 配电单元2直流负载22功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load22 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.169 | hwdcpdcDu2DcLoad23Power | DU2 DC load 23 power | 配电单元2直流负载23功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load23 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.170 | hwdcpdcDu2DcLoad24Power | DU2 DC load 24 power | 配电单元2直流负载24功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load24 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.171 | hwdcpdcDu2DcLoad25Power | DU2 DC load 25 power | 配电单元2直流负载25功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load25 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.172 | hwdcpdcDu2DcLoad26Power | DU2 DC load 26 power | 配电单元2直流负载26功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load26 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.173 | hwdcpdcDu2DcLoad27Power | DU2 DC load 27 power | 配电单元2直流负载27功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load27 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.174 | hwdcpdcDu2DcLoad28Power | DU2 DC load 28 power | 配电单元2直流负载28功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load28 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.175 | hwdcpdcDu2DcLoad29Power | DU2 DC load 29 power | 配电单元2直流负载29功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load29 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.176 | hwdcpdcDu2DcLoad30Power | DU2 DC load 30 power | 配电单元2直流负载30功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU2 DC load30 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.177 | hwdcpdcDu3DcVoltage | DU3 DC voltage | 配电单元3直流电压 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | DU3 DC voltage of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.178 | hwdcpdcDu3TotalLoadCurrent | DU3 total load current | 配电单元3总负载电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 total load current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.179 | hwdcpdcDu3BatteryCurrent1 | DU3 battery current 1 | 配电单元3电池电流1 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current1 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.180 | hwdcpdcDu3BatteryCurrent2 | DU3 battery current 2 | 配电单元3电池电流2 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current2 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.181 | hwdcpdcDu3BatteryCurrent3 | DU3 battery current 3 | 配电单元3电池电流3 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current3 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.182 | hwdcpdcDu3BatteryCurrent4 | DU3 battery current 4 | 配电单元3电池电流4 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current4 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.183 | hwdcpdcDu3BatteryCurrent5 | DU3 battery current 5 | 配电单元3电池电流5 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current5 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.184 | hwdcpdcDu3BatteryCurrent6 | DU3 battery current 6 | 配电单元3电池电流6 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current6 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.185 | hwdcpdcDu3BatteryCurrent7 | DU3 battery current 7 | 配电单元3电池电流7 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current7 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.186 | hwdcpdcDu3BatteryCurrent8 | DU3 battery current 8 | 配电单元3电池电流8 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current8 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.187 | hwdcpdcDu3BatteryCurrent9 | DU3 battery current 9 | 配电单元3电池电流9 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current9 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.188 | hwdcpdcDu3BatteryCurrent10 | DU3 battery current 10 | 配电单元3电池电流10 | 0-Read_Only | 只读 | -500000..500000 | -500000..500000 | DU3 battery current10 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.189 | hwdcpdcDu3BatteryMidpointVoltage1 | DU3 battery midpoint voltage 1 | 配电单元3电池串1中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 1 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.190 | hwdcpdcDu3BatteryMidpointVoltage2 | DU3 battery midpoint voltage 2 | 配电单元3电池串2中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 2 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.191 | hwdcpdcDu3BatteryMidpointVoltage3 | DU3 battery midpoint voltage 3 | 配电单元3电池串3中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 3 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.192 | hwdcpdcDu3BatteryMidpointVoltage4 | DU3 battery midpoint voltage 4 | 配电单元3电池串4中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 4 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.193 | hwdcpdcDu3BatteryMidpointVoltage5 | DU3 battery midpoint voltage 5 | 配电单元3电池串5中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 5 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.194 | hwdcpdcDu3BatteryMidpointVoltage6 | DU3 battery midpoint voltage 6 | 配电单元3电池串6中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 6 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.195 | hwdcpdcDu3BatteryMidpointVoltage7 | DU3 battery midpoint voltage 7 | 配电单元3电池串7中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 7 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.196 | hwdcpdcDu3BatteryMidpointVoltage8 | DU3 battery midpoint voltage 8 | 配电单元3电池串8中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 8 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.197 | hwdcpdcDu3BatteryMidpointVoltage9 | DU3 battery midpoint voltage 9 | 配电单元3电池串9中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 9 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.198 | hwdcpdcDu3BatteryMidpointVoltage10 | DU3 battery midpoint voltage 10 | 配电单元3电池串10中点电压 | 0-Read_Only | 只读 | -10..600 | -10..600 | DU3 battery midpoint voltage 10 of the device config table for the DC pdc.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.199 | hwdcpdcDu3Load1Current | DU3 load 1 current | 配电单元3负载1电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load1 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.200 | hwdcpdcDu3Load2Current | DU3 load 2 current | 配电单元3负载2电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load2 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.201 | hwdcpdcDu3Load3Current | DU3 load 3 current | 配电单元3负载3电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load3 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.202 | hwdcpdcDu3Load4Current | DU3 load 4 current | 配电单元3负载4电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load4 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.203 | hwdcpdcDu3Load5Current | DU3 load 5 current | 配电单元3负载5电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load5 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.204 | hwdcpdcDu3Load6Current | DU3 load 6 current | 配电单元3负载6电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load6 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.205 | hwdcpdcDu3Load7Current | DU3 load 7 current | 配电单元3负载7电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load7 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.206 | hwdcpdcDu3Load8Current | DU3 load 8 current | 配电单元3负载8电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load8 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.207 | hwdcpdcDu3Load9Current | DU3 load 9 current | 配电单元3负载9电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load9 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.208 | hwdcpdcDu3Load10Current | DU3 load 10 current | 配电单元3负载10电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load10 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.209 | hwdcpdcDu3Load11Current | DU3 load 11 current | 配电单元3负载11电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load11 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.210 | hwdcpdcDu3Load12Current | DU3 load 12 current | 配电单元3负载12电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load12 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.211 | hwdcpdcDu3Load13Current | DU3 load 13 current | 配电单元3负载13电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load13 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.212 | hwdcpdcDu3Load14Current | DU3 load 14 current | 配电单元3负载14电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load14 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.213 | hwdcpdcDu3Load15Current | DU3 load 15 current | 配电单元3负载15电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load15 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.214 | hwdcpdcDu3Load16Current | DU3 load 16 current | 配电单元3负载16电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load16 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.215 | hwdcpdcDu3Load17Current | DU3 load 17 current | 配电单元3负载17电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load17 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.216 | hwdcpdcDu3Load18Current | DU3 load 18 current | 配电单元3负载18电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load18 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.217 | hwdcpdcDu3Load19Current | DU3 load 19 current | 配电单元3负载19电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load19 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.218 | hwdcpdcDu3Load20Current | DU3 load 20 current | 配电单元3负载20电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load20 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.219 | hwdcpdcDu3Load21Current | DU3 load 21 current | 配电单元3负载21电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load21 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.220 | hwdcpdcDu3Load22Current | DU3 load 22 current | 配电单元3负载22电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load22 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.221 | hwdcpdcDu3Load23Current | DU3 load 23 current | 配电单元3负载23电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load23 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.222 | hwdcpdcDu3Load24Current | DU3 load 24 current | 配电单元3负载24电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load24 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.223 | hwdcpdcDu3Load25Current | DU3 load 25 current | 配电单元3负载25电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load25 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.224 | hwdcpdcDu3Load26Current | DU3 load 26 current | 配电单元3负载26电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load26 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.225 | hwdcpdcDu3Load27Current | DU3 load 27 current | 配电单元3负载27电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load27 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.226 | hwdcpdcDu3Load28Current | DU3 load 28 current | 配电单元3负载28电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load28 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.227 | hwdcpdcDu3Load29Current | DU3 load 29 current | 配电单元3负载29电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load29 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.228 | hwdcpdcDu3Load30Current | DU3 load 30 current | 配电单元3负载30电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 load30 current of the device config table for the DC pdc.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.229 | hwdcpdcDu3DcLoad1Power | DU3 DC load 1 power | 配电单元3直流负载1功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load1 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.230 | hwdcpdcDu3DcLoad2Power | DU3 DC load 2 power | 配电单元3直流负载2功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load2 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.231 | hwdcpdcDu3DcLoad3Power | DU3 DC load 3 power | 配电单元3直流负载3功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load3 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.232 | hwdcpdcDu3DcLoad4Power | DU3 DC load 4 power | 配电单元3直流负载4功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load4 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.233 | hwdcpdcDu3DcLoad5Power | DU3 DC load 5 power | 配电单元3直流负载5功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load5 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.234 | hwdcpdcDu3DcLoad6Power | DU3 DC load 6 power | 配电单元3直流负载6功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load6 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.235 | hwdcpdcDu3DcLoad7Power | DU3 DC load 7 power | 配电单元3直流负载7功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load7 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.236 | hwdcpdcDu3DcLoad8Power | DU3 DC load 8 power | 配电单元3直流负载8功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load8 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.237 | hwdcpdcDu3DcLoad9Power | DU3 DC load 9 power | 配电单元3直流负载9功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load9 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.238 | hwdcpdcDu3DcLoad10Power | DU3 DC load 10 power | 配电单元3直流负载10功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load10 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.239 | hwdcpdcDu3DcLoad11Power | DU3 DC load 11 power | 配电单元3直流负载11功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load11 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.240 | hwdcpdcDu3DcLoad12Power | DU3 DC load 12 power | 配电单元3直流负载12功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load12 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.241 | hwdcpdcDu3DcLoad13Power | DU3 DC load 13 power | 配电单元3直流负载13功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load13 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.242 | hwdcpdcDu3DcLoad14Power | DU3 DC load 14 power | 配电单元3直流负载14功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load14 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.243 | hwdcpdcDu3DcLoad15Power | DU3 DC load 15 power | 配电单元3直流负载15功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load15 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.244 | hwdcpdcDu3DcLoad16Power | DU3 DC load 16 power | 配电单元3直流负载16功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load16 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.245 | hwdcpdcDu3DcLoad17Power | DU3 DC load 17 power | 配电单元3直流负载17功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load17 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.246 | hwdcpdcDu3DcLoad18Power | DU3 DC load 18 power | 配电单元3直流负载18功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load18 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.247 | hwdcpdcDu3DcLoad19Power | DU3 DC load 19 power | 配电单元3直流负载19功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load19 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.248 | hwdcpdcDu3DcLoad20Power | DU3 DC load 20 power | 配电单元3直流负载20功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load20 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.249 | hwdcpdcDu3DcLoad21Power | DU3 DC load 21 power | 配电单元3直流负载21功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load21 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.250 | hwdcpdcDu3DcLoad22Power | DU3 DC load 22 power | 配电单元3直流负载22功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load22 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.251 | hwdcpdcDu3DcLoad23Power | DU3 DC load 23 power | 配电单元3直流负载23功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load23 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.252 | hwdcpdcDu3DcLoad24Power | DU3 DC load 24 power | 配电单元3直流负载24功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load24 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.253 | hwdcpdcDu3DcLoad25Power | DU3 DC load 25 power | 配电单元3直流负载25功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load25 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.254 | hwdcpdcDu3DcLoad26Power | DU3 DC load 26 power | 配电单元3直流负载26功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load26 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.255 | hwdcpdcDu3DcLoad27Power | DU3 DC load 27 power | 配电单元3直流负载27功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load27 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.256 | hwdcpdcDu3DcLoad28Power | DU3 DC load 28 power | 配电单元3直流负载28功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load28 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.257 | hwdcpdcDu3DcLoad29Power | DU3 DC load 29 power | 配电单元3直流负载29功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load29 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.258 | hwdcpdcDu3DcLoad30Power | DU3 DC load 30 power | 配电单元3直流负载30功率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | DU3 DC load30 power of the device config table for the DC pdc.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.68.1.1.300 | hwdcpdcRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DC pdc.

## DDS3366D-W1
DDS3366D_W1
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.90 | DDS3366DW1 | DDS3366D_W1 | DDS3366D_W1 | / | / | / | / | DDS3366D_W1 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.90.1 | hwDDS3366DW1Running1Table | / | / |  |  | / | / | The running table of DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.1 | hwDDS3366DW1Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.2 | hwDDS3366DW1CombinedActiveEnergy | Combined active energy | 当前组合有功电能 | 0-Read_Only | 只读 | 0..99999999 | 0..99999999 | Combined active energy of the device config table for the DDS3366D_W1.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.3 | hwDDS3366DW1PositiveActiveEnergy | Positive active energy | 当前正向有功电能 | 0-Read_Only | 只读 | 0..99999999 | 0..99999999 | Positive active energy of the device config table for the DDS3366D_W1.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.4 | hwDDS3366DW1ReverseActiveEnergy | Reverse active energy | 当前反向有功电能 | 0-Read_Only | 只读 | 0..99999999 | 0..99999999 | Reverse active energy of the device config table for the DDS3366D_W1.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.5 | hwDDS3366DW1Voltage | Voltage | 电压 | 0-Read_Only | 只读 | 0..9999 | 0..9999 | Voltage of the device config table for the DDS3366D_W1.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.6 | hwDDS3366DW1Current | Current | 电流 | 0-Read_Only | 只读 | 0..999999 | 0..999999 | Current of the device config table for the DDS3366D_W1.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.7 | hwDDS3366DW1Power | Power | 功率 | 0-Read_Only | 只读 | -999999..999999 | -999999..999999 | Power of the device config table for the DDS3366D_W1.Multiple:10000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.8 | hwDDS3366DW1PowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Power factor of the device config table for the DDS3366D_W1.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.9 | hwDDS3366DW1Frequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..9999 | 0..9999 | Frequency of the device config table for the DDS3366D_W1.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.10 | hwDDS3366DW1CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the DDS3366D_W1. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.11 | hwDDS3366DW1PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.12 | hwDDS3366DW1ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..254 | 1..254 | Modbus address of the device config table for the DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.13 | hwDDS3366DW1SoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.1.1.101 | hwDDS3366DW1Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.2 | hwDDS3366DW1Config2Table | / | / |  |  | / | / | The config table of DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.2.1.1 | hwDDS3366DW1Config2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.2.1.2 | hwDDS3366DW1ZeroClearing | Zero clearing | 电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | Zero clearing of the device config table for the DDS3366D_W1. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.90.2.1.3 | hwDDS3366DW1Pt | PT | 电压互感器变比 | 1-Read_Write | 读写 | 1..9999 | 1..9999 | PT of the device config table for the DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.2.1.4 | hwDDS3366DW1Ct | CT | 电流互感器变比 | 1-Read_Write | 读写 | 1..9999 | 1..9999 | CT of the device config table for the DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.2.1.5 | hwDDS3366DW1DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the DDS3366D_W1.
1.3.6.1.4.1.2011.6.178.1.1.90.2.1.101 | hwDDS3366DW1Config2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DDS3366D_W1.

## DehumidifierHT-500
除湿机HT-500
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.80 | Dehumidifier | DehumidifierHT-500 | 除湿机HT-500 | / | / | / | / | Dehumidifier Equipment.
1.3.6.1.4.1.2011.6.178.1.1.80.1 | hwDehumidifierHT500Running1Table | / | / |  |  | / | / | The running table of DehumidifierHT-500.
1.3.6.1.4.1.2011.6.178.1.1.80.1.1.1 | hwDehumidifierHT500Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the DehumidifierHT-500.
1.3.6.1.4.1.2011.6.178.1.1.80.1.1.2 | hwDehumidifierHT500CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the DehumidifierHT-500. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.80.1.1.3 | hwDehumidifierHT500PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the DehumidifierHT-500.
1.3.6.1.4.1.2011.6.178.1.1.80.1.1.4 | hwDehumidifierHT500ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..50 | 1..50 | Modbus address of the device config table for the DehumidifierHT-500.
1.3.6.1.4.1.2011.6.178.1.1.80.1.1.5 | hwDehumidifierHT500Status | Status | 设备状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Status of the device config table for the DehumidifierHT-500. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.80.1.1.6 | hwDehumidifierHT500Humidity | Humidity | 湿度 | 0-Read_Only | 只读 | 200..990 | 200..990 | Humidity of the device config table for the DehumidifierHT-500.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.80.1.1.101 | hwDehumidifierHT500Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DehumidifierHT-500.
1.3.6.1.4.1.2011.6.178.1.1.80.2 | hwDehumidifierHT500Config2Table | / | / |  |  | / | / | The config table of DehumidifierHT-500.
1.3.6.1.4.1.2011.6.178.1.1.80.2.1.1 | hwDehumidifierHT500Config2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the DehumidifierHT-500.
1.3.6.1.4.1.2011.6.178.1.1.80.2.1.2 | hwDehumidifierHT500HumiditySetpoint | Humidity setpoint | 湿度设定点 | 1-Read_Write | 读写 | 300..900 | 300..900 | Humidity setpoint of the device config table for the DehumidifierHT-500.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.80.2.1.3 | hwDehumidifierHT500SwitchControl | / | / | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | / | Switch control of the device config table for the DehumidifierHT-500. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.80.2.1.4 | hwDehumidifierHT500DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the DehumidifierHT-500.
1.3.6.1.4.1.2011.6.178.1.1.80.2.1.101 | hwDehumidifierHT500Config2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of DehumidifierHT-500.

## eLight Actuator
eLight执行器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.52 | eLightActuator | eLight Actuator | eLight执行器 | / | / | / | / | eLightActuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.52.1 | hweLightActuatorRunningTable | / | / |  |  | / | / | The running table of eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.1.1.1 | hweLightActuatorRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.1.1.2 | hweLightActuatorCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the eLight Actuator. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.52.1.1.4 | hweLightActuatorPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.1.1.5 | hweLightActuatorModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.1.1.6 | hweLightActuatorSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Software version of the device config table for the eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.1.1.220 | hweLightActuatorRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.2 | hweLightActuatorConfigTable | / | / |  |  | / | / | The config table of eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.2.1.1 | hweLightActuatorConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.2.1.2 | hweLightActuatorDevicename | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device name for the eLight Actuator.
1.3.6.1.4.1.2011.6.178.1.1.52.2.1.4 | hweLightActuatorAssociatedAlarmSeverity | Associated alarm severity | 关联告警级别 | 1-Read_Write | 读写 | critical(1), criticalandMajor(2), criticalandMajorandMinor(3), criticalandMajorandMinorandWarning(4), none(5) | [紧急=1]/[紧急，重要=2]/[紧急，重要，次要=3]/[紧急，重要，次要，提示=4]/[无=5] | Associated alarm severity of the device config table for the eLight Actuator. Value 1 indicate critical Value 2 indicate critical,major Value 3 indicate critical,major,minor Value 4 indicate critical,major,minor,warning Value 5 indicate none
1.3.6.1.4.1.2011.6.178.1.1.52.2.1.5 | hweLightActuatorLogoLighting | Logo lighting | Logo灯开关 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [开灯=1]/[关灯=2] | Logo lighting of the device config table for the eLight Actuator. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.52.2.1.220 | hweLightActuatorConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of eLight Actuator.

## EnvicoolSC15
英维克SC15
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.82 | EnvicoolSC15 | EnvicoolSC15 | 英维克SC15 | / | / | / | / | EnvicoolSC15 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.82.1 | hwEnvicoolSC15Running1Table | / | / |  |  | / | / | The running table of EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.1 | hwEnvicoolSC15Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.2 | hwEnvicoolSC15CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the EnvicoolSC15. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.3 | hwEnvicoolSC15PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.4 | hwEnvicoolSC15ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.5 | hwEnvicoolSC15UnitRunningStatus | Unit running status | 设备工作状态 | 0-Read_Only | 只读 | standby(1), running(2), fault(3), unknown(255) | [待机=1]/[运行=2]/[故障=3] | Unit running status of the device config table for the EnvicoolSC15. Value 1 indicate standby Value 2 indicate running Value 3 indicate fault
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.6 | hwEnvicoolSC15InternalFanStatus | Internal fan status | 室内风机状态 | 0-Read_Only | 只读 | standby(1), running(2), fault(3), unknown(255) | [待机=1]/[运行=2]/[故障=3] | Internal fan status of the device config table for the EnvicoolSC15. Value 1 indicate standby Value 2 indicate running Value 3 indicate fault
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.7 | hwEnvicoolSC15ExternalFanStatus | External fan status | 室外风机状态 | 0-Read_Only | 只读 | standby(1), running(2), fault(3), unknown(255) | [待机=1]/[运行=2]/[故障=3] | External fan status of the device config table for the EnvicoolSC15. Value 1 indicate standby Value 2 indicate running Value 3 indicate fault
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.8 | hwEnvicoolSC15CompressorStatus | Compressor status | 压缩机状态 | 0-Read_Only | 只读 | standby(1), running(2), fault(3), unknown(255) | [待机=1]/[运行=2]/[故障=3] | Compressor status of the device config table for the EnvicoolSC15. Value 1 indicate standby Value 2 indicate running Value 3 indicate fault
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.9 | hwEnvicoolSC15InsideReturnTemperature | Inside return temperature | 柜内回风温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inside return temperature of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.10 | hwEnvicoolSC15OutsideTemperature | Outside temperature | 环境温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Outside temperature of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.11 | hwEnvicoolSC15InternalFanSpeed | Internal fan speed | 内风机转速 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Internal fan speed of the device config table for the EnvicoolSC15.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.12 | hwEnvicoolSC15ExternalFanSpeed | / | / | 0-Read_Only | 只读 | 0..65535 | / | External fan speed of the device config table for the EnvicoolSC15.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.13 | hwEnvicoolSC15AcInputVoltage | AC input voltage | 交流输入电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AC input voltage of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.14 | hwEnvicoolSC15DcInputVoltage | DC input voltage | 直流输入电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | DC input voltage of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.15 | hwEnvicoolSC15AcRunningCurrent | AC running current | 交流运行电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AC running current of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.16 | hwEnvicoolSC15UnitRunningTime | Unit running time | 设备运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Unit running time of the device config table for the EnvicoolSC15.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.17 | hwEnvicoolSC15CompressorRunningTime | Compressor running time | 压缩机运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor running time of the device config table for the EnvicoolSC15.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.18 | hwEnvicoolSC15InternalFanRunningTime | Internal fan running time | 内风机运行时间 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Internal fan running time of the device config table for the EnvicoolSC15.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.19 | hwEnvicoolSC15CompressorActionTimes | Compressor action times | 压缩机动作次数 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Compressor action times of the device config table for the EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.20 | hwEnvicoolSC15SupplyAirTemperature | Supply air temperature | 送风温度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Supply air temperature of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.21 | hwEnvicoolSC15InsideReturnHumidity | Inside return humidity | 柜内回风湿度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Inside return humidity of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.82.1.1.101 | hwEnvicoolSC15Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.2 | hwEnvicoolSC15Config2Table | / | / |  |  | / | / | The config table of EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.1 | hwEnvicoolSC15Config2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.2 | hwEnvicoolSC15CoolingSetPoint | Cooling set point | 制冷设定温度 | 1-Read_Write | 读写 | 70..500 | 70..500 | Cooling set point of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.3 | hwEnvicoolSC15CoolingSensitivitySetPoint | Cooling sensitivity set point | 制冷设定灵敏度 | 1-Read_Write | 读写 | 10..150 | 10..150 | Cooling sensitivity set point of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.4 | hwEnvicoolSC15HighTemperatureAlarmPoint | High temperature alarm point | 高温告警点 | 1-Read_Write | 读写 | 200..700 | 200..700 | High temperature alarm point of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.5 | hwEnvicoolSC15LowTemperatureAlarmPoint | Low temperature alarm point | 低温告警点 | 1-Read_Write | 读写 | -400..50 | -400..50 | Low temperature alarm point of the device config table for the EnvicoolSC15.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.6 | hwEnvicoolSC15ControlMode | Control mode | 温度控制模式 | 1-Read_Write | 读写 | returnavg(1), supplyavg(2), returnhot(3), supplyhot(4), monitor(5), unknown(255) | [回风平均=1]/[出风平均=2]/[回风热点=3]/[出风热点=4]/[监控温度=5] | Control mode of the device config table for the EnvicoolSC15. Value 1 indicate return avg Value 2 indicate supply avg Value 3 indicate return hot Value 4 indicate supply hot Value 5 indicate monitor
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.7 | hwEnvicoolSC15DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the EnvicoolSC15.
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.8 | hwEnvicoolSC15RemoteOnorOff | Remote ON/OFF | 远程开空调 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Remote ON/OFF of the device config table for the EnvicoolSC15. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.82.2.1.101 | hwEnvicoolSC15Config2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of EnvicoolSC15.

## FusionModule Actuator
智能微模块执行器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.116 | FusionModuleActuator | FusionModule Actuator | 智能微模块执行器 | / | / | / | / | FusionModule Actuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.116.1 | hwFusionModuleActuatorRunning1Table | / | / |  |  | / | / | The running table of FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.1 | hwFusionModuleActuatorRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.2 | hwFusionModuleActuatorLoadCurrent | Load current | 负载电流 | 0-Read_Only | 只读 | 0..200 | 0..200 | Load current of the device config table for the FusionModule Actuator.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.3 | hwFusionModuleActuatorCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the FusionModule Actuator. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.4 | hwFusionModuleActuatorELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.5 | hwFusionModuleActuatorEsn | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.6 | hwFusionModuleActuatorMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.7 | hwFusionModuleActuatorSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.8 | hwFusionModuleActuatorHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.9 | hwFusionModuleActuatorLoadVoltage | Load voltage | 负载电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Load voltage of the device config table for the FusionModule Actuator.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.10 | hwFusionModuleActuatorLoadPower | Load power | 负载功率 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Load power of the device config table for the FusionModule Actuator.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.11 | hwFusionModuleActuatorSwitch1Status | Switch 1 status | 第1路输出状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Switch 1 status of the device config table for the FusionModule Actuator. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.12 | hwFusionModuleActuatorSwitch2Status | Switch 2 status | 第2路输出状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Switch 2 status of the device config table for the FusionModule Actuator. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.13 | hwFusionModuleActuatorRelay1Life | Relay 1 life | 第1路开关继电器寿命 | 0-Read_Only | 只读 | 0..100 | 0..100 | Relay 1 life of the device config table for the FusionModule Actuator.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.14 | hwFusionModuleActuatorRelay2Life | Relay 2 life | 第2路开关继电器寿命 | 0-Read_Only | 只读 | 0..100 | 0..100 | Relay 2 life of the device config table for the FusionModule Actuator.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.15 | hwFusionModuleActuatorScuttleMagneticLockPowerState | Scuttle Magnetic lock power state | 天窗磁力锁供电状态 | 0-Read_Only | 只读 | poweredon(1), poweredoff(2), unknown(255) | [供电=1]/[断电=2] | Scuttle Magnetic lock power state of the device config table for the FusionModule Actuator. Value 1 indicate powered on Value 2 indicate powered off
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.16 | hwFusionModuleActuatorPowerSupplyStatusOfMagneticLock | Power supply status of magnetic lock | 门禁磁力锁供电状态 | 0-Read_Only | 只读 | poweredon(1), poweredoff(2), unknown(255) | [供电=1]/[断电=2] | Power supply status of magnetic lock of the device config table for the FusionModule Actuator. Value 1 indicate powered on Value 2 indicate powered off
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.17 | hwFusionModuleActuatorDoPowerState | DO power state | DO供电状态 | 0-Read_Only | 只读 | poweredon(1), poweredoff(2), unknown(255) | [供电=1]/[断电=2] | DO power state of the device config table for the FusionModule Actuator. Value 1 indicate powered on Value 2 indicate powered off
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.18 | hwFusionModuleActuatorDoorState | Door state | 门状态 | 0-Read_Only | 只读 | doorclose(1), dooropen(2), unknown(255) | [门关=1]/[门开=2] | Door state of the device config table for the FusionModule Actuator. Value 1 indicate door close Value 2 indicate door open
1.3.6.1.4.1.2011.6.178.1.1.116.1.1.101 | hwFusionModuleActuatorRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.2 | hwFusionModuleActuatorConfig2Table | / | / |  |  | / | / | The config table of FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.1 | hwFusionModuleActuatorConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.2 | hwFusionModuleActuatorDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.3 | hwFusionModuleActuatorOvercurrentAlarmThreshold | Overcurrent alarm threshold | 电流过流告警门限 | 1-Read_Write | 读写 | 0..100 | 0..100 | Overcurrent alarm threshold of the device config table for the FusionModule Actuator.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.4 | hwFusionModuleActuatorRelayLifeAlarmThreshold | Relay life alarm threshold | 继电器寿命告警门限 | 1-Read_Write | 读写 | 0..100 | 0..100 | Relay life alarm threshold of the device config table for the FusionModule Actuator.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.5 | hwFusionModuleActuatorDoorSensorAlarmLevel | Door sensor alarm level | 门磁告警电平 | 1-Read_Write | 读写 | lowlevelalarm(1), highlevelalarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | Door sensor alarm level of the device config table for the FusionModule Actuator. Value 1 indicate low level alarm Value 2 indicate high level alarm
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.6 | hwFusionModuleActuatorExitControlButtonLevel | Exit control button level | 出门控制按钮电平 | 1-Read_Write | 读写 | lowlevelalarm(1), highlevelalarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | Exit control button level of the device config table for the FusionModule Actuator. Value 1 indicate low level alarm Value 2 indicate high level alarm
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.7 | hwFusionModuleActuatorSkylightControlButtonLevel | Skylight control button level | 天窗控制按钮电平 | 1-Read_Write | 读写 | lowlevelalarm(1), highlevelalarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | Skylight control button level of the device config table for the FusionModule Actuator. Value 1 indicate low level alarm Value 2 indicate high level alarm
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.8 | hwFusionModuleActuatorSmokeSensorAlarmLevel | Smoke sensor alarm level | 烟感告警电平 | 1-Read_Write | 读写 | lowlevelalarm(1), highlevelalarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | Smoke sensor alarm level of the device config table for the FusionModule Actuator. Value 1 indicate low level alarm Value 2 indicate high level alarm
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.9 | hwFusionModuleActuatorDiStatusAlarmLevel | DI status alarm level | DI状态告警电平 | 1-Read_Write | 读写 | lowlevelalarm(1), highlevelalarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | DI status alarm level of the device config table for the FusionModule Actuator. Value 1 indicate low level alarm Value 2 indicate high level alarm
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.10 | hwFusionModuleActuatorRemoteDoorOpening | Remote door opening | 远程开门 | 1-Read_Write | 读写 | opendoor(1) | [开门=1] | Remote door opening of the device config table for the FusionModule Actuator. Value 1 indicate open door
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.11 | hwFusionModuleActuatorRemoteOpenScuttle | Remote open scuttle | 远程开窗 | 1-Read_Write | 读写 | openscuttle(1) | [开窗=1] | Remote open scuttle of the device config table for the FusionModule Actuator. Value 1 indicate open scuttle
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.12 | hwFusionModuleActuatorRfZEnable | RF_Z enable | RF_Z使能 | 1-Read_Write | 读写 | disabled(1), enabled(2), unknown(255) | [禁止=1]/[使能=2] | RF_Z enable of the device config table for the FusionModule Actuator. Value 1 indicate disabled Value 2 indicate enabled
| hwFusionModuleActuatorLogicalLevelConfigurationForReader1Removed | Logical level configuration for reader 1 removed | 读卡器1被拆告警逻辑电平配置 | 1-Read_Write | 读写 | lowlevelalarm(1), highlevelalarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | Logical level configuration for reader 1 removed of the device config table for the FusionModule Actuator. Value 1 indicate low level alarm Value 2 indicate high level alarm
| hwFusionModuleActuatorLogicalLevelConfigurationForReader2Removed | Logical level configuration for reader 2 removed | 读卡器2被拆告警逻辑电平配置 | 1-Read_Write | 读写 | lowlevelalarm(1), highlevelalarm(2), unknown(255) | [低电平告警=1]/[高电平告警=2] | Logical level configuration for reader2 removed of the device config table for the FusionModule Actuator. Value 1 indicate low level alarm Value 2 indicate high level alarm
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.15 | hwFusionModuleActuatorCom1BaudRate | COM1 baud rate | COM1的波特率 | 1-Read_Write | 读写 | baud2400(1), baud4800(2), baud9600(3), baud19200(4), baud38400(5), baud115200(6), unknown(255) | [2400=1]/[4800=2]/[9600=3]/[19200=4]/[38400=5]/[115200=6] | COM1 baud rate of the device config table for the FusionModule Actuator. Value 1 indicate 2400 Value 2 indicate 4800 Value 3 indicate 9600 Value 4 indicate 19200 Value 6 indicate 38400 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.16 | hwFusionModuleActuatorCom1CheckBit | COM1 check bit | COM1的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无校验=1]/[奇校验=2]/[偶校验=3] | COM1 check bit of the device config table for the FusionModule Actuator. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.17 | hwFusionModuleActuatorCom1DataBit | COM1 data bit | COM1的数据位 | 1-Read_Write | 读写 | eightbit(1) | [8位=1] | COM1 data bit of the device config table for the FusionModule Actuator. Value 1 indicate eight bit
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.18 | hwFusionModuleActuatorCom1StopBit | COM1 stop bit | COM1的停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM1 stop bit of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.19 | hwFusionModuleActuatorCom1SplitFrameTime | COM1 split frame time | COM1口断帧时间 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | COM1 split frame time of the device config table for the FusionModule Actuator.SigUnitInfo:ms.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.20 | hwFusionModuleActuatorCom2BaudRate | COM2 baud rate | COM2的波特率 | 1-Read_Write | 读写 | baud2400(1), baud4800(2), baud9600(3), baud19200(4), baud38400(5), baud115200(6), unknown(255) | [2400=1]/[4800=2]/[9600=3]/[19200=4]/[38400=5]/[115200=6] | COM2 baud rate of the device config table for the FusionModule Actuator. Value 1 indicate 2400 Value 2 indicate 4800 Value 3 indicate 9600 Value 4 indicate 19200 Value 6 indicate 38400 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.21 | hwFusionModuleActuatorCom2CheckBit | COM2 check bit | COM2的校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无校验=1]/[奇校验=2]/[偶校验=3] | COM2 check bit of the device config table for the FusionModule Actuator. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.22 | hwFusionModuleActuatorCom2DataBit | COM2 data bit | COM2的数据位 | 1-Read_Write | 读写 | eightbit(1) | [8位=1] | COM2 data bit of the device config table for the FusionModule Actuator. Value 1 indicate eight bit
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.23 | hwFusionModuleActuatorCom2StopBit | COM2 stop bit | COM2的停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM2 stop bit of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.24 | hwFusionModuleActuatorCom2SplitFrameTime | COM2 split frame time | COM2口断帧时间 | 1-Read_Write | 读写 | 1..1000 | 1..1000 | COM2 split frame time of the device config table for the FusionModule Actuator.SigUnitInfo:ms.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.25 | hwFusionModuleActuatorRoute1ControlMode | Route 1 control mode | 第1路控制模式 | 1-Read_Write | 读写 | none(1), light(2), unknown(255) | [无=1]/[照明=2] | Route 1 control mode of the device config table for the FusionModule Actuator. Value 1 indicate none Value 2 indicate light
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.26 | hwFusionModuleActuatorRoute2ControlMode | Route 2 control mode | 第2路控制模式 | 1-Read_Write | 读写 | none(1), padCharging(2), unknown(255) | [无=1]/[PAD充电=2] | Route 2 control mode of the device config table for the FusionModule Actuator. Value 1 indicate none Value 2 indicate pad charging
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.27 | hwFusionModuleActuatorSetLightMode | Set light mode | 照明控制模式 | 1-Read_Write | 读写 | automatic(1), manual(2), unknown(255) | [自动=1]/[手动=2] | Set light mode of the device config table for the FusionModule Actuator. Value 1 indicate automatic Value 2 indicate manual
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.28 | hwFusionModuleActuatorLightcontrol | Light control | 开关灯控制 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关=1]/[开=2] | Light control of the device config table for the FusionModule Actuator. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.29 | hwFusionModuleActuatorPadBatteryLevelThresholdToStartCharging | PAD battery level threshold to start charging | PAD低电量充电阈值 | 1-Read_Write | 读写 | 30..50 | 30..50 | PAD battery level threshold to start charging of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.30 | hwFusionModuleActuatorPadBatteryLevelThresholdToStopCharging | PAD battery level threshold to stop charging | PAD高电量停止充电阈值 | 1-Read_Write | 读写 | 60..75 | 60..75 | PAD battery level threshold to stop charging of the device config table for the FusionModule Actuator.
1.3.6.1.4.1.2011.6.178.1.1.116.2.1.101 | hwFusionModuleActuatorConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of FusionModule Actuator.

## STM32HeadCabinet
STM32高压直流列头柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.94 | STM32HeadCabinet | STM32HeadCabinet | STM32高压直流列头柜 | / | / | / | / | STM32HeadCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.94.1 | hwSTM32HeadCabinetRunning1Table | / | / |  |  | / | / | The running table of STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.1 | hwSTM32HeadCabinetRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.2 | hwSTM32HeadCabinetFirstDcInput1 | First DC input1 | Ⅰ直流主路总开关1 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC input1 of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.3 | hwSTM32HeadCabinetFirstDcSpd | First DC SPD | Ⅰ直流主路防雷 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC SPD of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.4 | hwSTM32HeadCabinetSecondDcInput1 | Second DC input1 | Ⅱ直流主路总开关1 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC input1 of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.5 | hwSTM32HeadCabinetSecondDcSpd | Second DC SPD | Ⅱ直流主路防雷 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC SPD of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.6 | hwSTM32HeadCabinetFirstDcBranch01Switch | First DC branch01 switch | Ⅰ直流支路01 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch01 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.7 | hwSTM32HeadCabinetFirstDcBranch02Switch | First DC branch02 switch | Ⅰ直流支路02 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch02 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.8 | hwSTM32HeadCabinetFirstDcBranch03Switch | First DC branch03 switch | Ⅰ直流支路03 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch03 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.9 | hwSTM32HeadCabinetFirstDcBranch04Switch | First DC branch04 switch | Ⅰ直流支路04 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch04 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.10 | hwSTM32HeadCabinetFirstDcBranch05Switch | First DC branch05 switch | Ⅰ直流支路05 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch05 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.11 | hwSTM32HeadCabinetFirstDcBranch06Switch | First DC branch06 switch | Ⅰ直流支路06 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch06 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.12 | hwSTM32HeadCabinetFirstDcBranch07Switch | First DC branch07 switch | Ⅰ直流支路07 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch07 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.13 | hwSTM32HeadCabinetFirstDcBranch08Switch | First DC branch08 switch | Ⅰ直流支路08 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch08 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.14 | hwSTM32HeadCabinetFirstDcBranch09Switch | First DC branch09 switch | Ⅰ直流支路09 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch09 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.15 | hwSTM32HeadCabinetFirstDcBranch10Switch | First DC branch10 switch | Ⅰ直流支路10 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch10 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.16 | hwSTM32HeadCabinetFirstDcBranch11Switch | First DC branch11 switch | Ⅰ直流支路11 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch11 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.17 | hwSTM32HeadCabinetFirstDcBranch12Switch | First DC branch12 switch | Ⅰ直流支路12 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch12 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.18 | hwSTM32HeadCabinetFirstDcBranch13Switch | First DC branch13 switch | Ⅰ直流支路13 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch13 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.19 | hwSTM32HeadCabinetFirstDcBranch14Switch | First DC branch14 switch | Ⅰ直流支路14 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch14 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.20 | hwSTM32HeadCabinetFirstDcBranch15Switch | First DC branch15 switch | Ⅰ直流支路15 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch15 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.21 | hwSTM32HeadCabinetFirstDcBranch16Switch | First DC branch16 switch | Ⅰ直流支路16 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | First DC branch16 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.22 | hwSTM32HeadCabinetSecondDcBranch01Switch | Second DC branch01 switch | Ⅱ直流支路01 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch01 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.23 | hwSTM32HeadCabinetSecondDcBranch02Switch | Second DC branch02 switch | Ⅱ直流支路02 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch02 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.24 | hwSTM32HeadCabinetSecondDcBranch03Switch | Second DC branch03 switch | Ⅱ直流支路03 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch03 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.25 | hwSTM32HeadCabinetSecondDcBranch04Switch | Second DC branch04 switch | Ⅱ直流支路04 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch04 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.26 | hwSTM32HeadCabinetSecondDcBranch05Switch | Second DC branch05 switch | Ⅱ直流支路05 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch05 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.27 | hwSTM32HeadCabinetSecondDcBranch06Switch | Second DC branch06 switch | Ⅱ直流支路06 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch06 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.28 | hwSTM32HeadCabinetSecondDcBranch07Switch | Second DC branch07 switch | Ⅱ直流支路07 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch07 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.29 | hwSTM32HeadCabinetSecondDcBranch08Switch | Second DC branch08 switch | Ⅱ直流支路08 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch08 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.30 | hwSTM32HeadCabinetSecondDcBranch09Switch | Second DC branch09 switch | Ⅱ直流支路09 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch09 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.31 | hwSTM32HeadCabinetSecondDcBranch10Switch | Second DC branch10 switch | Ⅱ直流支路10 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch10 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.32 | hwSTM32HeadCabinetSecondDcBranch11Switch | Second DC branch11 switch | Ⅱ直流支路11 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch11 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.33 | hwSTM32HeadCabinetSecondDcBranch12Switch | Second DC branch12 switch | Ⅱ直流支路12 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch12 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.34 | hwSTM32HeadCabinetSecondDcBranch13Switch | Second DC branch13 switch | Ⅱ直流支路13 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch13 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.35 | hwSTM32HeadCabinetSecondDcBranch14Switch | Second DC branch14 switch | Ⅱ直流支路14 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch14 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.36 | hwSTM32HeadCabinetSecondDcBranch15Switch | Second DC branch15 switch | Ⅱ直流支路15 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch15 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.37 | hwSTM32HeadCabinetSecondDcBranch16Switch | Second DC branch16 switch | Ⅱ直流支路16 开关 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Second DC branch16 switch of the device config table for the STM32HeadCabinet. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.38 | hwSTM32HeadCabinetFirstDcVoltage | First DC voltage | Ⅰ直流电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.39 | hwSTM32HeadCabinetFirstDcCurrent | First DC current | Ⅰ直流电流 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.40 | hwSTM32HeadCabinetFirstDcPower | First DC power | Ⅰ直流功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.41 | hwSTM32HeadCabinetFirstDcEnergy | First DC energy | Ⅰ直流电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.42 | hwSTM32HeadCabinetFirstInsulationPositiveBusVoltage | First insulation positive bus voltage | Ⅰ绝缘母线正电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First insulation positive bus voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.43 | hwSTM32HeadCabinetFirstInsulationNegativeBusVoltage | First insulation negative bus voltage | Ⅰ绝缘母线负电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First insulation negative bus voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.44 | hwSTM32HeadCabinetFirstInsulationPositiveBusResistance | First insulation positive bus resistance | Ⅰ绝缘母线正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First insulation positive bus resistance of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.45 | hwSTM32HeadCabinetFirstInsulationNegativeBusResistance | First insulation negative bus resistance | Ⅰ绝缘母线负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First insulation negative bus resistance of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.46 | hwSTM32HeadCabinetSecondDcVoltage | Second DC voltage | Ⅱ直流电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.47 | hwSTM32HeadCabinetSecondDcCurrent | Second DC current | Ⅱ直流电流 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.48 | hwSTM32HeadCabinetSecondDcPower | Second DC power | Ⅱ直流功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.49 | hwSTM32HeadCabinetSecondDcEnergy | Second DC energy | Ⅱ直流电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.50 | hwSTM32HeadCabinetSecondInsulationPositiveBusVoltage | Second insulation positive bus voltage | Ⅱ绝缘母线正电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second insulation positive bus voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.51 | hwSTM32HeadCabinetSecondInsulationNegativeBusVoltage | Second insulation negative bus voltage | Ⅱ绝缘母线负电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second insulation negative bus voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.52 | hwSTM32HeadCabinetSecondInsulationPositiveBusResistance | Second insulation positive bus resistance | Ⅱ绝缘母线正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second insulation positive bus resistance of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.53 | hwSTM32HeadCabinetSecondInsulationNegativeBusResistance | Second insulation negative bus resistance | Ⅱ绝缘母线负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second insulation negative bus resistance of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.54 | hwSTM32HeadCabinetFirstDcBranch01Voltage | First DC branch01 voltage | Ⅰ直流支路01 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch01 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.55 | hwSTM32HeadCabinetFirstDcBranch02Voltage | First DC branch02 voltage | Ⅰ直流支路02 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch02 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.56 | hwSTM32HeadCabinetFirstDcBranch03Voltage | First DC branch03 voltage | Ⅰ直流支路03 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch03 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.57 | hwSTM32HeadCabinetFirstDcBranch04Voltage | First DC branch04 voltage | Ⅰ直流支路04 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch04 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.58 | hwSTM32HeadCabinetFirstDcBranch05Voltage | First DC branch05 voltage | Ⅰ直流支路05 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch05 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.59 | hwSTM32HeadCabinetFirstDcBranch06Voltage | First DC branch06 voltage | Ⅰ直流支路06 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch06 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.60 | hwSTM32HeadCabinetFirstDcBranch07Voltage | First DC branch07 voltage | Ⅰ直流支路07 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch07 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.61 | hwSTM32HeadCabinetFirstDcBranch08Voltage | First DC branch08 voltage | Ⅰ直流支路08 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch08 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.62 | hwSTM32HeadCabinetFirstDcBranch09Voltage | First DC branch09 voltage | Ⅰ直流支路09 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch09 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.63 | hwSTM32HeadCabinetFirstDcBranch10Voltage | First DC branch10 voltage | Ⅰ直流支路10 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch10 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.64 | hwSTM32HeadCabinetFirstDcBranch11Voltage | First DC branch11 voltage | Ⅰ直流支路11 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch11 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.65 | hwSTM32HeadCabinetFirstDcBranch12Voltage | First DC branch12 voltage | Ⅰ直流支路12 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch12 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.66 | hwSTM32HeadCabinetFirstDcBranch13Voltage | First DC branch13 voltage | Ⅰ直流支路13 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch13 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.67 | hwSTM32HeadCabinetFirstDcBranch14Voltage | First DC branch14 voltage | Ⅰ直流支路14 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch14 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.68 | hwSTM32HeadCabinetFirstDcBranch15Voltage | First DC branch15 voltage | Ⅰ直流支路15 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch15 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.69 | hwSTM32HeadCabinetFirstDcBranch16Voltage | First DC branch16 voltage | Ⅰ直流支路16 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch16 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.70 | hwSTM32HeadCabinetFirstDcBranch01Current | First DC branch01 current | Ⅰ直流支路01 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch01 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.71 | hwSTM32HeadCabinetFirstDcBranch02Current | First DC branch02 current | Ⅰ直流支路02 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch02 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.72 | hwSTM32HeadCabinetFirstDcBranch03Current | First DC branch03 current | Ⅰ直流支路03 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch03 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.73 | hwSTM32HeadCabinetFirstDcBranch04Current | First DC branch04 current | Ⅰ直流支路04 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch04 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.74 | hwSTM32HeadCabinetFirstDcBranch05Current | First DC branch05 current | Ⅰ直流支路05 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch05 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.75 | hwSTM32HeadCabinetFirstDcBranch06Current | First DC branch06 current | Ⅰ直流支路06 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch06 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.76 | hwSTM32HeadCabinetFirstDcBranch07Current | First DC branch07 current | Ⅰ直流支路07 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch07 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.77 | hwSTM32HeadCabinetFirstDcBranch08Current | First DC branch08 current | Ⅰ直流支路08 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch08 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.78 | hwSTM32HeadCabinetFirstDcBranch09Current | First DC branch09 current | Ⅰ直流支路09 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch09 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.79 | hwSTM32HeadCabinetFirstDcBranch10Current | First DC branch10 current | Ⅰ直流支路10 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch10 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.80 | hwSTM32HeadCabinetFirstDcBranch11Current | First DC branch11 current | Ⅰ直流支路11 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch11 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.81 | hwSTM32HeadCabinetFirstDcBranch12Current | First DC branch12 current | Ⅰ直流支路12 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch12 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.82 | hwSTM32HeadCabinetFirstDcBranch13Current | First DC branch13 current | Ⅰ直流支路13 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch13 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.83 | hwSTM32HeadCabinetFirstDcBranch14Current | First DC branch14 current | Ⅰ直流支路14 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch14 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.84 | hwSTM32HeadCabinetFirstDcBranch15Current | First DC branch15 current | Ⅰ直流支路15 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch15 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.85 | hwSTM32HeadCabinetFirstDcBranch16Current | First DC branch16 current | Ⅰ直流支路16 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | First DC branch16 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.86 | hwSTM32HeadCabinetFirstDcBranch01ActivePower | First DC branch01 active power | Ⅰ直流支路01 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch01 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.87 | hwSTM32HeadCabinetFirstDcBranch02ActivePower | First DC branch02 active power | Ⅰ直流支路02 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch02 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.88 | hwSTM32HeadCabinetFirstDcBranch03ActivePower | First DC branch03 active power | Ⅰ直流支路03 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch03 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.89 | hwSTM32HeadCabinetFirstDcBranch04ActivePower | First DC branch04 active power | Ⅰ直流支路04 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch04 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.90 | hwSTM32HeadCabinetFirstDcBranch05ActivePower | First DC branch05 active power | Ⅰ直流支路05 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch05 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.91 | hwSTM32HeadCabinetFirstDcBranch06ActivePower | First DC branch06 active power | Ⅰ直流支路06 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch06 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.92 | hwSTM32HeadCabinetFirstDcBranch07ActivePower | First DC branch07 active power | Ⅰ直流支路07 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch07 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.93 | hwSTM32HeadCabinetFirstDcBranch08ActivePower | First DC branch08 active power | Ⅰ直流支路08 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch08 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.94 | hwSTM32HeadCabinetFirstDcBranch09ActivePower | First DC branch09 active power | Ⅰ直流支路09 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch09 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.95 | hwSTM32HeadCabinetFirstDcBranch10ActivePower | First DC branch10 active power | Ⅰ直流支路10 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch10 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.96 | hwSTM32HeadCabinetFirstDcBranch11ActivePower | First DC branch11 active power | Ⅰ直流支路11 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch11 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.97 | hwSTM32HeadCabinetFirstDcBranch12ActivePower | First DC branch12 active power | Ⅰ直流支路12 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch12 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.98 | hwSTM32HeadCabinetFirstDcBranch13ActivePower | First DC branch13 active power | Ⅰ直流支路13 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch13 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.99 | hwSTM32HeadCabinetFirstDcBranch14ActivePower | First DC branch14 active power | Ⅰ直流支路14 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch14 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.100 | hwSTM32HeadCabinetFirstDcBranch15ActivePower | First DC branch15 active power | Ⅰ直流支路15 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch15 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.101 | hwSTM32HeadCabinetFirstDcBranch16ActivePower | First DC branch16 active power | Ⅰ直流支路16 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | First DC branch16 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.102 | hwSTM32HeadCabinetFirstDcBranch01Energy | First DC branch01 energy | Ⅰ直流支路01 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch01 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.103 | hwSTM32HeadCabinetFirstDcBranch02Energy | First DC branch02 energy | Ⅰ直流支路02 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch02 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.104 | hwSTM32HeadCabinetFirstDcBranch03Energy | First DC branch03 energy | Ⅰ直流支路03 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch03 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.105 | hwSTM32HeadCabinetFirstDcBranch04Energy | First DC branch04 energy | Ⅰ直流支路04 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch04 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.106 | hwSTM32HeadCabinetFirstDcBranch05Energy | First DC branch05 energy | Ⅰ直流支路05 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch05 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.107 | hwSTM32HeadCabinetFirstDcBranch06Energy | First DC branch06 energy | Ⅰ直流支路06 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch06 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.108 | hwSTM32HeadCabinetFirstDcBranch07Energy | First DC branch07 energy | Ⅰ直流支路07 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch07 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.109 | hwSTM32HeadCabinetFirstDcBranch08Energy | First DC branch08 energy | Ⅰ直流支路08 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch08 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.110 | hwSTM32HeadCabinetFirstDcBranch09Energy | First DC branch09 energy | Ⅰ直流支路09 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch09 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.111 | hwSTM32HeadCabinetFirstDcBranch10Energy | First DC branch10 energy | Ⅰ直流支路10 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch10 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.112 | hwSTM32HeadCabinetFirstDcBranch11Energy | First DC branch11 energy | Ⅰ直流支路11 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch11 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.113 | hwSTM32HeadCabinetFirstDcBranch12Energy | First DC branch12 energy | Ⅰ直流支路12 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch12 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.114 | hwSTM32HeadCabinetFirstDcBranch13Energy | First DC branch13 energy | Ⅰ直流支路13 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch13 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.115 | hwSTM32HeadCabinetFirstDcBranch14Energy | First DC branch14 energy | Ⅰ直流支路14 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch14 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.116 | hwSTM32HeadCabinetFirstDcBranch15Energy | First DC branch15 energy | Ⅰ直流支路15 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch15 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.117 | hwSTM32HeadCabinetFirstDcBranch16Energy | First DC branch16 energy | Ⅰ直流支路16 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | First DC branch16 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.118 | hwSTM32HeadCabinetSecondDcBranch01Voltage | Second DC branch01 voltage | Ⅱ直流支路01 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch01 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.119 | hwSTM32HeadCabinetSecondDcBranch02Voltage | Second DC branch02 voltage | Ⅱ直流支路02 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch02 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.120 | hwSTM32HeadCabinetSecondDcBranch03Voltage | Second DC branch03 voltage | Ⅱ直流支路03 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch03 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.121 | hwSTM32HeadCabinetSecondDcBranch04Voltage | Second DC branch04 voltage | Ⅱ直流支路04 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch04 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.122 | hwSTM32HeadCabinetSecondDcBranch05Voltage | Second DC branch05 voltage | Ⅱ直流支路05 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch05 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.123 | hwSTM32HeadCabinetSecondDcBranch06Voltage | Second DC branch06 voltage | Ⅱ直流支路06 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch06 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.124 | hwSTM32HeadCabinetSecondDcBranch07Voltage | Second DC branch07 voltage | Ⅱ直流支路07 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch07 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.125 | hwSTM32HeadCabinetSecondDcBranch08Voltage | Second DC branch08 voltage | Ⅱ直流支路08 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch08 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.126 | hwSTM32HeadCabinetSecondDcBranch09Voltage | Second DC branch09 voltage | Ⅱ直流支路09 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch09 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.127 | hwSTM32HeadCabinetSecondDcBranch10Voltage | Second DC branch10 voltage | Ⅱ直流支路10 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch10 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.128 | hwSTM32HeadCabinetSecondDcBranch11Voltage | Second DC branch11 voltage | Ⅱ直流支路11 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch11 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.129 | hwSTM32HeadCabinetSecondDcBranch12Voltage | Second DC branch12 voltage | Ⅱ直流支路12 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch12 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.130 | hwSTM32HeadCabinetSecondDcBranch13Voltage | Second DC branch13 voltage | Ⅱ直流支路13 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch13 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.131 | hwSTM32HeadCabinetSecondDcBranch14Voltage | Second DC branch14 voltage | Ⅱ直流支路14 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch14 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.132 | hwSTM32HeadCabinetSecondDcBranch15Voltage | Second DC branch15 voltage | Ⅱ直流支路15 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch15 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.133 | hwSTM32HeadCabinetSecondDcBranch16Voltage | Second DC branch16 voltage | Ⅱ直流支路16 电压 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch16 voltage of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.134 | hwSTM32HeadCabinetSecondDcBranch01Current | Second DC branch01 current | Ⅱ直流支路01 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch01 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.135 | hwSTM32HeadCabinetSecondDcBranch02Current | Second DC branch02 current | Ⅱ直流支路02 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch02 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.136 | hwSTM32HeadCabinetSecondDcBranch03Current | Second DC branch03 current | Ⅱ直流支路03 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch03 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.137 | hwSTM32HeadCabinetSecondDcBranch04Current | Second DC branch04 current | Ⅱ直流支路04 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch04 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.138 | hwSTM32HeadCabinetSecondDcBranch05Current | Second DC branch05 current | Ⅱ直流支路05 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch05 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.139 | hwSTM32HeadCabinetSecondDcBranch06Current | Second DC branch06 current | Ⅱ直流支路06 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch06 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.140 | hwSTM32HeadCabinetSecondDcBranch07Current | Second DC branch07 current | Ⅱ直流支路07 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch07 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.141 | hwSTM32HeadCabinetSecondDcBranch08Current | Second DC branch08 current | Ⅱ直流支路08 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch08 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.142 | hwSTM32HeadCabinetSecondDcBranch09Current | Second DC branch09 current | Ⅱ直流支路09 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch09 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.143 | hwSTM32HeadCabinetSecondDcBranch10Current | Second DC branch10 current | Ⅱ直流支路10 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch10 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.144 | hwSTM32HeadCabinetSecondDcBranch11Current | Second DC branch11 current | Ⅱ直流支路11 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch11 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.145 | hwSTM32HeadCabinetSecondDcBranch12Current | Second DC branch12 current | Ⅱ直流支路12 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch12 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.146 | hwSTM32HeadCabinetSecondDcBranch13Current | Second DC branch13 current | Ⅱ直流支路13 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch13 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.147 | hwSTM32HeadCabinetSecondDcBranch14Current | Second DC branch14 current | Ⅱ直流支路14 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch14 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.148 | hwSTM32HeadCabinetSecondDcBranch15Current | Second DC branch15 current | Ⅱ直流支路15 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch15 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.149 | hwSTM32HeadCabinetSecondDcBranch16Current | Second DC branch16 current | Ⅱ直流支路16 电流 | 0-Read_Only | 只读 | 0..320 | 0..320 | Second DC branch16 current of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.150 | hwSTM32HeadCabinetSecondDcBranch01ActivePower | Second DC branch01 active power | Ⅱ直流支路01 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch01 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.151 | hwSTM32HeadCabinetSecondDcBranch02ActivePower | Second DC branch02 active power | Ⅱ直流支路02 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch02 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.152 | hwSTM32HeadCabinetSecondDcBranch03ActivePower | Second DC branch03 active power | Ⅱ直流支路03 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch03 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.153 | hwSTM32HeadCabinetSecondDcBranch04ActivePower | Second DC branch04 active power | Ⅱ直流支路04 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch04 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.154 | hwSTM32HeadCabinetSecondDcBranch05ActivePower | Second DC branch05 active power | Ⅱ直流支路05 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch05 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.155 | hwSTM32HeadCabinetSecondDcBranch06ActivePower | Second DC branch06 active power | Ⅱ直流支路06 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch06 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.156 | hwSTM32HeadCabinetSecondDcBranch07ActivePower | Second DC branch07 active power | Ⅱ直流支路07 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch07 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.157 | hwSTM32HeadCabinetSecondDcBranch08ActivePower | Second DC branch08 active power | Ⅱ直流支路08 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch08 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.158 | hwSTM32HeadCabinetSecondDcBranch09ActivePower | Second DC branch09 active power | Ⅱ直流支路09 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch09 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.159 | hwSTM32HeadCabinetSecondDcBranch10ActivePower | Second DC branch10 active power | Ⅱ直流支路10 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch10 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.160 | hwSTM32HeadCabinetSecondDcBranch11ActivePower | Second DC branch11 active power | Ⅱ直流支路11 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch11 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.161 | hwSTM32HeadCabinetSecondDcBranch12ActivePower | Second DC branch12 active power | Ⅱ直流支路12 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch12 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.162 | hwSTM32HeadCabinetSecondDcBranch13ActivePower | Second DC branch13 active power | Ⅱ直流支路13 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch13 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.163 | hwSTM32HeadCabinetSecondDcBranch14ActivePower | Second DC branch14 active power | Ⅱ直流支路14 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch14 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.164 | hwSTM32HeadCabinetSecondDcBranch15ActivePower | Second DC branch15 active power | Ⅱ直流支路15 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch15 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.165 | hwSTM32HeadCabinetSecondDcBranch16ActivePower | Second DC branch16 active power | Ⅱ直流支路16 有功功率 | 0-Read_Only | 只读 | 0..65500 | 0..65500 | Second DC branch16 active power of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.166 | hwSTM32HeadCabinetSecondDcBranch01Energy | Second DC branch01 energy | Ⅱ直流支路01 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch01 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.167 | hwSTM32HeadCabinetSecondDcBranch02Energy | Second DC branch02 energy | Ⅱ直流支路02 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch02 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.168 | hwSTM32HeadCabinetSecondDcBranch03Energy | Second DC branch03 energy | Ⅱ直流支路03 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch03 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.169 | hwSTM32HeadCabinetSecondDcBranch04Energy | Second DC branch04 energy | Ⅱ直流支路04 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch04 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.170 | hwSTM32HeadCabinetSecondDcBranch05Energy | Second DC branch05 energy | Ⅱ直流支路05 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch05 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.171 | hwSTM32HeadCabinetSecondDcBranch06Energy | Second DC branch06 energy | Ⅱ直流支路06 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch06 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.172 | hwSTM32HeadCabinetSecondDcBranch07Energy | Second DC branch07 energy | Ⅱ直流支路07 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch07 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.173 | hwSTM32HeadCabinetSecondDcBranch08Energy | Second DC branch08 energy | Ⅱ直流支路08 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch08 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.174 | hwSTM32HeadCabinetSecondDcBranch09Energy | Second DC branch09 energy | Ⅱ直流支路09 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch09 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.175 | hwSTM32HeadCabinetSecondDcBranch10Energy | Second DC branch10 energy | Ⅱ直流支路10 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch10 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.176 | hwSTM32HeadCabinetSecondDcBranch11Energy | Second DC branch11 energy | Ⅱ直流支路11 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch11 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.177 | hwSTM32HeadCabinetSecondDcBranch12Energy | Second DC branch12 energy | Ⅱ直流支路12 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch12 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.178 | hwSTM32HeadCabinetSecondDcBranch13Energy | Second DC branch13 energy | Ⅱ直流支路13 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch13 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.179 | hwSTM32HeadCabinetSecondDcBranch14Energy | Second DC branch14 energy | Ⅱ直流支路14 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch14 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.180 | hwSTM32HeadCabinetSecondDcBranch15Energy | Second DC branch15 energy | Ⅱ直流支路15 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch15 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.181 | hwSTM32HeadCabinetSecondDcBranch16Energy | Second DC branch16 energy | Ⅱ直流支路16 电能 | 0-Read_Only | 只读 | 0..42949672 | 0..42949672 | Second DC branch16 energy of the device config table for the STM32HeadCabinet.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.182 | hwSTM32HeadCabinetFirstDcBranch01PositiveInsulationValue | First DC branch01 positive insulation value | Ⅰ直流支路01 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch01 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.183 | hwSTM32HeadCabinetFirstDcBranch01NegativeInsulationValue | First DC branch01 negative insulation value | Ⅰ直流支路01 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch01 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.184 | hwSTM32HeadCabinetFirstDcBranch02PositiveInsulationValue | First DC branch02 positive insulation value | Ⅰ直流支路02 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch02 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.185 | hwSTM32HeadCabinetFirstDcBranch02NegativeInsulationValue | First DC branch02 negative insulation value | Ⅰ直流支路02 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch02 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.186 | hwSTM32HeadCabinetFirstDcBranch03PositiveInsulationValue | First DC branch03 positive insulation value | Ⅰ直流支路03 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch03 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.187 | hwSTM32HeadCabinetFirstDcBranch03NegativeInsulationValue | First DC branch03 negative insulation value | Ⅰ直流支路03 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch03 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.188 | hwSTM32HeadCabinetFirstDcBranch04PositiveInsulationValue | First DC branch04 positive insulation value | Ⅰ直流支路04 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch04 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.189 | hwSTM32HeadCabinetFirstDcBranch04NegativeInsulationValue | First DC branch04 negative insulation value | Ⅰ直流支路04 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch04 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.190 | hwSTM32HeadCabinetFirstDcBranch05PositiveInsulationValue | First DC branch05 positive insulation value | Ⅰ直流支路05 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch05 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.191 | hwSTM32HeadCabinetFirstDcBranch05NegativeInsulationValue | First DC branch05 negative insulation value | Ⅰ直流支路05 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch05 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.192 | hwSTM32HeadCabinetFirstDcBranch06PositiveInsulationValue | First DC branch06 positive insulation value | Ⅰ直流支路06 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch06 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.193 | hwSTM32HeadCabinetFirstDcBranch06NegativeInsulationValue | First DC branch06 negative insulation value | Ⅰ直流支路06 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch06 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.194 | hwSTM32HeadCabinetFirstDcBranch07PositiveInsulationValue | First DC branch07 positive insulation value | Ⅰ直流支路07 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch07 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.195 | hwSTM32HeadCabinetFirstDcBranch07NegativeInsulationValue | First DC branch07 negative insulation value | Ⅰ直流支路07 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch07 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.196 | hwSTM32HeadCabinetFirstDcBranch08PositiveInsulationValue | First DC branch08 positive insulation value | Ⅰ直流支路08 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch08 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.197 | hwSTM32HeadCabinetFirstDcBranch08NegativeInsulationValue | First DC branch08 negative insulation value | Ⅰ直流支路08 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch08 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.198 | hwSTM32HeadCabinetFirstDcBranch09PositiveInsulationValue | First DC branch09 positive insulation value | Ⅰ直流支路09 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch09 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.199 | hwSTM32HeadCabinetFirstDcBranch09NegativeInsulationValue | First DC branch09 negative insulation value | Ⅰ直流支路09 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch09 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.200 | hwSTM32HeadCabinetFirstDcBranch10PositiveInsulationValue | First DC branch10 positive insulation value | Ⅰ直流支路10 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch10 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.1.1.201 | hwSTM32HeadCabinetRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.2 | hwSTM32HeadCabinetRunning2Table | / | / |  |  | / | / | The running table of STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.1 | hwSTM32HeadCabinetRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.2 | hwSTM32HeadCabinetFirstDcBranch10NegativeInsulationValue | First DC branch10 negative insulation value | Ⅰ直流支路10 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch10 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.3 | hwSTM32HeadCabinetFirstDcBranch11PositiveInsulationValue | First DC branch11 positive insulation value | Ⅰ直流支路11 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch11 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.4 | hwSTM32HeadCabinetFirstDcBranch11NegativeInsulationValue | First DC branch11 negative insulation value | Ⅰ直流支路11 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch11 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.5 | hwSTM32HeadCabinetFirstDcBranch12PositiveInsulationValue | First DC branch12 positive insulation value | Ⅰ直流支路12 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch12 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.6 | hwSTM32HeadCabinetFirstDcBranch12NegativeInsulationValue | First DC branch12 negative insulation value | Ⅰ直流支路12 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch12 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.7 | hwSTM32HeadCabinetFirstDcBranch13PositiveInsulationValue | First DC branch13 positive insulation value | Ⅰ直流支路13 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch13 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.8 | hwSTM32HeadCabinetFirstDcBranch13NegativeInsulationValue | First DC branch13 negative insulation value | Ⅰ直流支路13 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch13 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.9 | hwSTM32HeadCabinetFirstDcBranch14PositiveInsulationValue | First DC branch14 positive insulation value | Ⅰ直流支路14 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch14 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.10 | hwSTM32HeadCabinetFirstDcBranch14NegativeInsulationValue | First DC branch14 negative insulation value | Ⅰ直流支路14 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch14 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.11 | hwSTM32HeadCabinetFirstDcBranch15PositiveInsulationValue | First DC branch15 positive insulation value | Ⅰ直流支路15 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch15 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.12 | hwSTM32HeadCabinetFirstDcBranch15NegativeInsulationValue | First DC branch15 negative insulation value | Ⅰ直流支路15 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch15 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.13 | hwSTM32HeadCabinetFirstDcBranch16PositiveInsulationValue | First DC branch16 positive insulation value | Ⅰ直流支路16 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch16 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.14 | hwSTM32HeadCabinetFirstDcBranch16NegativeInsulationValue | First DC branch16 negative insulation value | Ⅰ直流支路16 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | First DC branch16 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.15 | hwSTM32HeadCabinetSecondDcBranch01PositiveInsulationValue | Second DC branch01 positive insulation value | Ⅱ直流支路01 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch01 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.16 | hwSTM32HeadCabinetSecondDcBranch01NegativeInsulationValue | Second DC branch01 negative insulation value | Ⅱ直流支路01 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch01 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.17 | hwSTM32HeadCabinetSecondDcBranch02PositiveInsulationValue | Second DC branch02 positive insulation value | Ⅱ直流支路02 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch02 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.18 | hwSTM32HeadCabinetSecondDcBranch02NegativeInsulationValue | Second DC branch02 negative insulation value | Ⅱ直流支路02 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch02 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.19 | hwSTM32HeadCabinetSecondDcBranch03PositiveInsulationValue | Second DC branch03 positive insulation value | Ⅱ直流支路03 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch03 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.20 | hwSTM32HeadCabinetSecondDcBranch03NegativeInsulationValue | Second DC branch03 negative insulation value | Ⅱ直流支路03 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch03 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.21 | hwSTM32HeadCabinetSecondDcBranch04PositiveInsulationValue | Second DC branch04 positive insulation value | Ⅱ直流支路04 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch04 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.22 | hwSTM32HeadCabinetSecondDcBranch04NegativeInsulationValue | Second DC branch04 negative insulation value | Ⅱ直流支路04 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch04 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.23 | hwSTM32HeadCabinetSecondDcBranch05PositiveInsulationValue | Second DC branch05 positive insulation value | Ⅱ直流支路05 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch05 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.24 | hwSTM32HeadCabinetSecondDcBranch05NegativeInsulationValue | Second DC branch05 negative insulation value | Ⅱ直流支路05 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch05 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.25 | hwSTM32HeadCabinetSecondDcBranch06PositiveInsulationValue | Second DC branch06 positive insulation value | Ⅱ直流支路06 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch06 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.26 | hwSTM32HeadCabinetSecondDcBranch06NegativeInsulationValue | Second DC branch06 negative insulation value | Ⅱ直流支路06 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch06 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.27 | hwSTM32HeadCabinetSecondDcBranch07PositiveInsulationValue | Second DC branch07 positive insulation value | Ⅱ直流支路07 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch07 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.28 | hwSTM32HeadCabinetSecondDcBranch07NegativeInsulationValue | Second DC branch07 negative insulation value | Ⅱ直流支路07 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch07 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.29 | hwSTM32HeadCabinetSecondDcBranch08PositiveInsulationValue | Second DC branch08 positive insulation value | Ⅱ直流支路08 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch08 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.30 | hwSTM32HeadCabinetSecondDcBranch08NegativeInsulationValue | Second DC branch08 negative insulation value | Ⅱ直流支路08 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch08 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.31 | hwSTM32HeadCabinetSecondDcBranch09PositiveInsulationValue | Second DC branch09 positive insulation value | Ⅱ直流支路09 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch09 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.32 | hwSTM32HeadCabinetSecondDcBranch09NegativeInsulationValue | Second DC branch09 negative insulation value | Ⅱ直流支路09 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch09 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.33 | hwSTM32HeadCabinetSecondDcBranch10PositiveInsulationValue | Second DC branch10 positive insulation value | Ⅱ直流支路10 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch10 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.34 | hwSTM32HeadCabinetSecondDcBranch10NegativeInsulationValue | Second DC branch10 negative insulation value | Ⅱ直流支路10 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch10 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.35 | hwSTM32HeadCabinetSecondDcBranch11PositiveInsulationValue | Second DC branch11 positive insulation value | Ⅱ直流支路11 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch11 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.36 | hwSTM32HeadCabinetSecondDcBranch11NegativeInsulationValue | Second DC branch11 negative insulation value | Ⅱ直流支路11 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch11 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.37 | hwSTM32HeadCabinetSecondDcBranch12PositiveInsulationValue | Second DC branch12 positive insulation value | Ⅱ直流支路12 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch12 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.38 | hwSTM32HeadCabinetSecondDcBranch12NegativeInsulationValue | Second DC branch12 negative insulation value | Ⅱ直流支路12 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch12 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.39 | hwSTM32HeadCabinetSecondDcBranch13PositiveInsulationValue | Second DC branch13 positive insulation value | Ⅱ直流支路13 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch13 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.40 | hwSTM32HeadCabinetSecondDcBranch13NegativeInsulationValue | Second DC branch13 negative insulation value | Ⅱ直流支路13 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch13 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.41 | hwSTM32HeadCabinetSecondDcBranch14PositiveInsulationValue | Second DC branch14 positive insulation value | Ⅱ直流支路14 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch14 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.42 | hwSTM32HeadCabinetSecondDcBranch14NegativeInsulationValue | Second DC branch14 negative insulation value | Ⅱ直流支路14 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch14 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.43 | hwSTM32HeadCabinetSecondDcBranch15PositiveInsulationValue | Second DC branch15 positive insulation value | Ⅱ直流支路15 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch15 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.44 | hwSTM32HeadCabinetSecondDcBranch15NegativeInsulationValue | Second DC branch15 negative insulation value | Ⅱ直流支路15 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch15 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.45 | hwSTM32HeadCabinetSecondDcBranch16PositiveInsulationValue | Second DC branch16 positive insulation value | Ⅱ直流支路16 正绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch16 positive insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.46 | hwSTM32HeadCabinetSecondDcBranch16NegativeInsulationValue | Second DC branch16 negative insulation value | Ⅱ直流支路16 负绝缘电阻 | 0-Read_Only | 只读 | 0..65530 | 0..65530 | Second DC branch16 negative insulation value of the device config table for the STM32HeadCabinet.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.47 | hwSTM32HeadCabinetCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the STM32HeadCabinet. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.48 | hwSTM32HeadCabinetPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.49 | hwSTM32HeadCabinetModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.50 | hwSTM32HeadCabinetELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E label of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.2.1.101 | hwSTM32HeadCabinetRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.3 | hwSTM32HeadCabinetConfig3Table | / | / |  |  | / | / | The config table of STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.1 | hwSTM32HeadCabinetConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.2 | hwSTM32HeadCabinetDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.3 | hwSTM32HeadCabinetFirstDcMainCircuitRatedCurrent | First DC main circuit rated current | Ⅰ直流主路额定电流 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | First DC main circuit rated current of the device config table for the STM32HeadCabinet.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.4 | hwSTM32HeadCabinetFirstDcCurrentRatio | First DC current ratio | Ⅰ直流主路电流变比（CT） | 1-Read_Write | 读写 | 0..1 | 0..1 | First DC current ratio of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.5 | hwSTM32HeadCabinetFirstBusPositiveInsulationAlarmValue | First bus positive insulation alarm value | Ⅰ母线正绝缘电阻告警值 | 1-Read_Write | 读写 | 0..999 | 0..999 | First bus positive insulation alarm value of the device config table for the STM32HeadCabinet.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.6 | hwSTM32HeadCabinetFirstBusNegativeInsulationAlarmValue | First bus negative insulation alarm value | Ⅰ母线负绝缘电阻告警值 | 1-Read_Write | 读写 | 0..999 | 0..999 | First bus negative insulation alarm value of the device config table for the STM32HeadCabinet.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.7 | hwSTM32HeadCabinetFirstBusBranchPositiveInsulationAlarmValue | First bus branch positive insulation alarm value | Ⅰ支路正绝缘电阻告警值 | 1-Read_Write | 读写 | 0..999 | 0..999 | First bus branch positive insulation alarm value of the device config table for the STM32HeadCabinet.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.8 | hwSTM32HeadCabinetFirstBusBranchNegativeInsulationAlarmValue | First bus branch negative insulation alarm value | Ⅰ支路负绝缘电阻告警值 | 1-Read_Write | 读写 | 0..999 | 0..999 | First bus branch negative insulation alarm value of the device config table for the STM32HeadCabinet.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.9 | hwSTM32HeadCabinetFirstBusBranchSet | First bus branch set | Ⅰ母线支路设置 | 1-Read_Write | 读写 | 0..16 | 0..16 | First bus branch set of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.10 | hwSTM32HeadCabinetSecondDcMainCircuitRatedCurrent | Second DC main circuit rated current | Ⅱ直流主路额定电流 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | Second DC main circuit rated current of the device config table for the STM32HeadCabinet.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.11 | hwSTM32HeadCabinetSecondDcCurrentRatio | Second DC current ratio | Ⅱ直流主路电流变比（CT） | 1-Read_Write | 读写 | 0..1 | 0..1 | Second DC current ratio of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.12 | hwSTM32HeadCabinetSecondBusPositiveInsulationAlarmValue | Second bus positive insulation alarm value | Ⅱ母线正绝缘电阻告警值 | 1-Read_Write | 读写 | 0..999 | 0..999 | Second bus positive insulation alarm value of the device config table for the STM32HeadCabinet.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.13 | hwSTM32HeadCabinetSecondBusNegativeInsulationAlarmValue | Second bus negative insulation alarm value | Ⅱ母线负绝缘电阻告警值 | 1-Read_Write | 读写 | 0..999 | 0..999 | Second bus negative insulation alarm value of the device config table for the STM32HeadCabinet.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.14 | hwSTM32HeadCabinetSecondBusBranchPositiveInsulationAlarmValue | Second bus branch positive insulation alarm value | Ⅱ支路正绝缘电阻告警值 | 1-Read_Write | 读写 | 0..999 | 0..999 | Second bus branch positive insulation alarm value of the device config table for the STM32HeadCabinet.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.15 | hwSTM32HeadCabinetSecondBusBranchNegativeInsulationAlarmValue | Second bus branch negative insulation alarm value | Ⅱ支路负绝缘电阻告警值 | 1-Read_Write | 读写 | 0..999 | 0..999 | Second bus branch negative insulation alarm value of the device config table for the STM32HeadCabinet.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.16 | hwSTM32HeadCabinetSecondBusBranchSet | Second bus branch set | Ⅱ母线支路设置 | 1-Read_Write | 读写 | 0..16 | 0..16 | Second bus branch set of the device config table for the STM32HeadCabinet.
1.3.6.1.4.1.2011.6.178.1.1.94.3.1.101 | hwSTM32HeadCabinetConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of STM32HeadCabinet.

## iACMETER
iACMETER
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.131.6 | iACMETER | iACMETER | iACMETER | / | / | / | / | iACMETER Equipment.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1 | hwiACMETERRunningAndConfig1Table | / | / |  |  | / | / | The running table of iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.1 | hwiACMETERRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iACMETER.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.2 | hwiACMETERVoltageChannel1AcFrequencyPhaseL1 | Voltage channel 1 ac frequency (phase L1) | 电压通道1交流频率(L1相) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage channel 1 ac frequency (phase L1) of the device config table for the iACMETER.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.3 | hwiACMETERVoltageChannel1ThreePhaseAverageLineVoltage | Voltage channel 1 three-phase average line voltage | 电压通道1三相平均线电压 | 0-Read_Only | 只读 | -20000..20000 | -20000..20000 | Voltage channel 1 three-phase average line voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.4 | hwiACMETERVoltageChannel1L1L2LineVoltage | Voltage channel 1 L1-L2 line voltage | 电压通道1L1-L2线电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 1 L1-L2 line voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.5 | hwiACMETERVoltageChannel1L2L3LineVoltage | Voltage channel 1 L2-L3 line voltage | 电压通道1L2-L3线电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 1 L2-L3 line voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.6 | hwiACMETERVoltageChannel1L3L1LineVoltage | Voltage channel 1 L3-L1 line voltage | 电压通道1L3-L1线电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 1 L3-L1 line voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.7 | hwiACMETERVoltageChannel1ThreePhaseAveragePhaseVoltage | Voltage channel 1 three-phase average phase voltage | 电压通道1三相平均相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Voltage channel 1 three-phase average phase voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.8 | hwiACMETERVoltageChannel1L1NPhaseVoltage | Voltage channel 1 L1-N phase voltage | 电压通道1L1-N相电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 1 L1-N phase voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.9 | hwiACMETERVoltageChannel1L2NPhaseVoltage | Voltage channel 1 L2-N phase voltage | 电压通道1L2-N相电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 1 L2-N phase voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.10 | hwiACMETERVoltageChannel1L3NPhaseVoltage | Voltage channel 1 L3-N phase voltage | 电压通道1L3-N相电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 1 L3-N phase voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.11 | hwiACMETERVoltageChannel1PhaseAngleOfTheL1PhaseVoltage | Voltage channel 1 phase angle of the L1 phase voltage | 电压通道1L1相电压相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Voltage channel 1 phase angle of the L1 phase voltage of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.12 | hwiACMETERVoltageChannel1PhaseAngleOfTheL2PhaseVoltage | Voltage channel 1 phase angle of the L2 phase voltage | 电压通道1L2相电压相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Voltage channel 1 phase angle of the L2 phase voltage of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.13 | hwiACMETERVoltageChannel1PhaseAngleOfTheL3PhaseVoltage | Voltage channel 1 phase angle of the L3 phase voltage | 电压通道1L3相电压相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Voltage channel 1 phase angle of the L3 phase voltage of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.14 | hwiACMETERVoltageChannel1L1PhaseVoltageThd | Voltage channel 1 L1 phase voltage THD | 电压通道1L1相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage channel 1 L1 phase voltage THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.15 | hwiACMETERVoltageChannel1L2PhaseVoltageThd | Voltage channel 1 L2 phase voltage THD | 电压通道1L2相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage channel 1 L2 phase voltage THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.16 | hwiACMETERVoltageChannel1L3PhaseVoltageThd | Voltage channel 1 L3 phase voltage THD | 电压通道1L3相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage channel 1 L3 phase voltage THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.17 | hwiACMETERVoltageChannel2AcFrequencyPhaseL1 | Voltage channel 2 ac frequency (phase L1) | 电压通道2交流频率(L1相) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Voltage channel 2 ac frequency (phase L1) of the device config table for the iACMETER.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.18 | hwiACMETERVoltageChannel2ThreePhaseAverageLineVoltage | Voltage channel 2 three-phase average line voltage | 电压通道2三相平均线电压 | 0-Read_Only | 只读 | -20000..20000 | -20000..20000 | Voltage channel 2 three-phase average line voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.19 | hwiACMETERVoltageChannel2L1L2LineVoltage | Voltage channel 2 L1-L2 line voltage | 电压通道2L1-L2线电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 2 L1-L2 line voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.20 | hwiACMETERVoltageChannel2L2L3LineVoltage | Voltage channel 2 L2-L3 line voltage | 电压通道2L2-L3线电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 2 L2-L3 line voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.21 | hwiACMETERVoltageChannel2L3L1LineVoltage | Voltage channel 2 L3-L1 line voltage | 电压通道2L3-L1线电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 2 L3-L1 line voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.22 | hwiACMETERVoltageChannel2ThreePhaseAveragePhaseVoltage | Voltage channel 2 three-phase average phase voltage | 电压通道2三相平均相电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Voltage channel 2 three-phase average phase voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.23 | hwiACMETERVoltageChannel2L1NPhaseVoltage | Voltage channel 2 L1-N phase voltage | 电压通道2L1-N相电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 2 L1-N phase voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.24 | hwiACMETERVoltageChannel2L2NPhaseVoltage | Voltage channel 2 L2-N phase voltage | 电压通道2L2-N相电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 2 L2-N phase voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.25 | hwiACMETERVoltageChannel2L3NPhaseVoltage | Voltage channel 2 L3-N phase voltage | 电压通道2L3-N相电压 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Voltage channel 2 L3-N phase voltage of the device config table for the iACMETER.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.26 | hwiACMETERVoltageChannel2PhaseAngleOfTheL1PhaseVoltage | Voltage channel 2 phase angle of the L1 phase voltage | 电压通道2L1相电压相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Voltage channel 2 phase angle of the L1 phase voltage of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.27 | hwiACMETERVoltageChannel2PhaseAngleOfTheL2PhaseVoltage | Voltage channel 2 phase angle of the L2 phase voltage | 电压通道2L2相电压相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Voltage channel 2 phase angle of the L2 phase voltage of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.28 | hwiACMETERVoltageChannel2PhaseAngleOfTheL3PhaseVoltage | Voltage channel 2 phase angle of the L3 phase voltage | 电压通道2L3相电压相位角 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Voltage channel 2 phase angle of the L3 phase voltage of the device config table for the iACMETER.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.29 | hwiACMETERVoltageChannel2L1PhaseVoltageThd | Voltage channel 2 L1 phase voltage THD | 电压通道2L1相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage channel 2 L1 phase voltage THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.30 | hwiACMETERVoltageChannel2L2PhaseVoltageThd | Voltage channel 2 L2 phase voltage THD | 电压通道2L2相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage channel 2 L2 phase voltage THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.31 | hwiACMETERVoltageChannel2L3PhaseVoltageThd | Voltage channel 2 L3 phase voltage THD | 电压通道2L3相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage channel 2 L3 phase voltage THD of the device config table for the iACMETER.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.32 | hwiACMETERChannel1L1PhaseCurrent | Channel 1 L1 phase current | 通道1L1相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 1 L1 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.33 | hwiACMETERChannel1L2PhaseCurrent | Channel 1 L2 phase current | 通道1L2相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 1 L2 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.34 | hwiACMETERChannel1L3PhaseCurrent | Channel 1 L3 phase current | 通道1L3相电流 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | Channel 1 L3 phase current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.35 | hwiACMETERChannel1ThreePhaseAverageCurrent | Channel 1 three-phase average current | 通道1三相平均电流 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Channel 1 three-phase average current of the device config table for the iACMETER.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.36 | hwiACMETERChannel1TotalActivePower | Channel 1 total active power | 通道1总有功功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 1 total active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.37 | hwiACMETERChannel1TotalReactivePower | Channel 1 total reactive power | 通道1总无功功率 | 0-Read_Only | 只读 | -480000..480000 | -480000..480000 | Channel 1 total reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.38 | hwiACMETERChannel1TotalApparentPower | Channel 1 total apparent power | 通道1总视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 1 total apparent power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.39 | hwiACMETERChannel1L1PhaseActivePower | Channel 1 L1 phase active power | 通道1L1相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 1 L1 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.40 | hwiACMETERChannel1L2PhaseActivePower | Channel 1 L2 phase active power | 通道1L2相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 1 L2 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.41 | hwiACMETERChannel1L3PhaseActivePower | Channel 1 L3 phase active power | 通道1L3相有功功率 | 0-Read_Only | 只读 | -1000000000..1000000000 | -1000000000..1000000000 | Channel 1 L3 phase active power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.42 | hwiACMETERChannel1L1PhaseReactivePower | Channel 1 L1 phase reactive power | 通道1L1相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 1 L1 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.43 | hwiACMETERChannel1L2PhaseReactivePower | Channel 1 L2 phase reactive power | 通道1L2相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 1 L2 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.44 | hwiACMETERChannel1L3PhaseReactivePower | Channel 1 L3 phase reactive power | 通道1L3相无功功率 | 0-Read_Only | 只读 | -160000..160000 | -160000..160000 | Channel 1 L3 phase reactive power of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.45 | hwiACMETERChannel1ApparentPowerOfL1Phase | Channel 1 apparent power of L1 phase | 通道1L1相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 1 apparent power of L1 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.46 | hwiACMETERChannel1ApparentPowerOfL2Phase | Channel 1 apparent power of L2 phase | 通道1L2相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 1 apparent power of L2 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.47 | hwiACMETERChannel1ApparentPowerOfL3Phase | Channel 1 apparent power of L3 phase | 通道1L3相视在功率 | 0-Read_Only | 只读 | 0..480000 | 0..480000 | Channel 1 apparent power of L3 phase of the device config table for the iACMETER.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.48 | hwiACMETERChannel1TotalPowerFactor | Channel 1 total power factor | 通道1总功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 1 total power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.49 | hwiACMETERChannel1L1PhasePowerFactor | Channel 1 L1 phase power factor | 通道1L1相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 1 L1 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.50 | hwiACMETERChannel1L2PhasePowerFactor | Channel 1 L2 phase power factor | 通道1L2相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 1 L2 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.51 | hwiACMETERChannel1L3PhasePowerFactor | Channel 1 L3 phase power factor | 通道1L3相功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Channel 1 L3 phase power factor of the device config table for the iACMETER.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.52 | hwiACMETERChannel1TotalPositiveActiveEnergy | Channel 1 total positive active energy | 通道1总正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 1 total positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.53 | hwiACMETERChannel1L1PhasePositiveActiveEnergy | Channel 1 L1 phase positive active energy | 通道1L1相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 1 L1 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.54 | hwiACMETERChannel1L2PhasePositiveActiveEnergy | Channel 1 L2 phase positive active energy | 通道1L2相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 1 L2 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.55 | hwiACMETERChannel1L3PhasePositiveActiveEnergy | Channel 1 L3 phase positive active energy | 通道1L3相正向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 1 L3 phase positive active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.56 | hwiACMETERChannel1TotalNegativeActiveEnergy | Channel 1 total negative active energy | 通道1总负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 1 total negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.57 | hwiACMETERChannel1L1PhaseNegativeActiveEnergy | Channel 1 L1 phase negative active energy | 通道1L1相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 1 L1 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.58 | hwiACMETERChannel1L2PhaseNegativeActiveEnergy | Channel 1 L2 phase negative active energy | 通道1L2相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 1 L2 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.59 | hwiACMETERChannel1L3PhaseNegativeActiveEnergy | Channel 1 L3 phase negative active energy | 通道1L3相负向有功电能 | 0-Read_Only | 只读 | 0..99999900 | 0..99999900 | Channel 1 L3 phase negative active energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.60 | hwiACMETERChannel1TotalPositiveReactiveEnergy | Channel 1 total positive reactive energy | 通道1总正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 total positive reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.61 | hwiACMETERChannel1L1PhaseForwardReactiveEnergy | Channel 1 L1 phase forward reactive energy | 通道1L1相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 L1 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.62 | hwiACMETERChannel1L2PhaseForwardReactiveEnergy | Channel 1 L2 phase forward reactive energy | 通道1L2相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 L2 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.63 | hwiACMETERChannel1L3PhaseForwardReactiveEnergy | Channel 1 L3 phase forward reactive energy | 通道1L3相正向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 L3 phase forward reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.64 | hwiACMETERChannel1TotalNegativeReactiveEnergy | Channel 1 total negative reactive energy | 通道1总负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 total negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.
1.3.6.1.4.1.2011.6.178.1.1.131.6.1.1.65 | hwiACMETERChannel1L1PhaseNegativeReactiveEnergy | Channel 1 L1 phase negative reactive energy | 通道1L1相负向无功电能 | 0-Read_Only | 只读 | 0..1000000000 | 0..1000000000 | Channel 1 L1 phase negative reactive energy of the device config table for the iACMETER.Multiple:100.SigUnitInfo:kVarh.